## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-09-08 | Sunday
|  | Date (day): | 2024-09-08 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14349.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15540 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-09-07 | 2024-09-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 394 | 402 | 400 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 45 | 55 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 | 75 |  | Fuel shortage
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 316 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 8 | 8 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 96 | 143 | 48 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 35 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 39 | 39 | 39 |  | 41 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 33 | 33 | 33
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 12 | 12 | 12 |  | 21 | Engine problem
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 17 | 16 | 8 | 16 | 36 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 65 | 277 | 200 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 96 | 112 | 70 | 112 |  | 37 | Engine problem
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 17 | 52 | 53 |  | Fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 51 | 60 | 53 | 60 | 44 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 72 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 21 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem.
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1842 | 2316 | 1957 | 2342 | 2597 | 919
35 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
36 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 8 | 25
37 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
38 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
39 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 211 | 212 | 210 | 212
40 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 211 | 205 | 210
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
42 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105
43 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 65 | 80 | 18 |  | Fuel shortage
44 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 83 |  | 19 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0
45 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 25 | 25 | 25 | 75 |  | Fuel shortage
46 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 22 | 10 | 20
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 15 | 15 | 15 | 285 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 17 | 51 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 24 | 24 | 25 | 75 |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 108 | 108 |  | 8 | Engine problem
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 145 | 35 | 163
55 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 530 | 610 | 612 | 612 |  | 612 | Unit-2 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 10 | 42 | 60 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 705 | 645 | 600 | 650 |  |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1857 | 2087 | 2295 | 2607 | 741 | 969
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 172 | 202 | 200 | 210 |  | 11
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 300 | 290 | 300 | 60 |  | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 240 | 240 | 120 |  | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 250 | 230 | 230 | 230 | 170 |  | Gas shortage
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 10 | 35 | 35 | 10 |  | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 46 | 10 | 0 | 0 | 55 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 87 | 100 | 120 |  | 30 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 34 | 34 | 34 |  | 18 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 70 | 70 | 70 | 93 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 200 | 100 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 60 | 74 | 90 | 90
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 |  | 44 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 106 | 52 | 106 |  | 8 | Engine problem
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 9 | 9 | 9 | 104 |  | Fuel shortage
76 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 49 | 87 | 65 | 90 |  | 25 | Engine problem
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 74 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1559 | 1728 | 1654 | 1803 | 807 | 151
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 9 | 13 | 12 | 15 | 187 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 96 | 121 | 98 | 125 | 75 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 77 | 58 | 77 | 38 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 42 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 18 | 12 | 18 |  | 4 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 0 | 17 | 17 |  | 37 | Engine prblem
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 220 | 229 | 248.6 | 252 | 187 | 41
84 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 39 | 39 | 39 | 39 |  | 31 | Machine problem.
85 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Machine problem
86 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
87 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
88 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 49 | 0 | 30 | 30 | 21 |  | Gas shortage
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 11 | 0 | 36 | 36 | 14 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 30 | 30 | 36 |  | Gas shortage
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 16 | 40 | 40 | 46 |  | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 203 | 205 | 205 | 205 |  | 26 | ST under maint
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 300 | 300 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 268 | 80 | 350 |  |  | FGMO
99 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 345 | 365 | 350 | 365 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1240 | 1388 | 1287 | 1572 | 117 | 499
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 877 | 874 | 880 | 880
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 33 | 41 |  | 13 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 55 | 0 | 55 |  | 54 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 343 | 320 | 300 | 320 | 90 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 70 | 70 | 70 | 35 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 96 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 575 | 1128 | 1100 | 1200
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1908 | 2488 | 2483 | 2566 | 812 | 67
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 16 | 110 | 110
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 8 | 10 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 130 | 130 | 130 |  | 64 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1160 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 54 | 96 |  | Fuel shortage
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 200 | 270 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1591 | 1823 | 2038 | 2075 | 96 | 64
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 28 | 29 | 30 | 30 |  | 22 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 0 | 20 |  | 51 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 21 | 35 | 28 | 35
122 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 25 | 46
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 414 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 5 | 8 |  | 3 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 55 | 113 | 113 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 113 | 113 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1014 | 1011 | 1000 | 1000
135 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 61 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1653 | 1891 | 1829 | 1899 | 873 | 110
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 210 | 200 | 210 |  | 64 | Under maint.
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 22 | 98 | 35 | 99 |  | 14 | Engine problem
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 115 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 207 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 581 | 423 | 558 | 424 | 40 | 188
| Total |  |  |  |  | 27791 | 27086 | 12451 | 14373 | 14349.6 | 15540 | 6270 | 3008
A. |  | 2024-09-07 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 14373 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 11542 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15500 | MW
3 | Day peak Generation : |  |  | 12451 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14932.82 | MW
4 | Evening peak Generation : |  |  | 14373 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1076 | MW
5 | Total Energy Generation : |  | 314.1191 | MKWHr | By Solar | 3.8116 | MKWHr
| By Gas : | 120.909 | MKWHr |  | By Oil: | 49.0019 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 87.4518 | MKWHr |  | By Hydro: | 4.893 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 24.3873 | MKWHr |  | By Wind: | 0.16704 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6270 | MW | Dhaka | 5409.12 | 5184.12 |  | 225 |  | 18:00 |  | 1003.705
|  |  | For Plants S/D or M/C prob = |  |  | 3008 | MW | Chittagong | 1242 | 1242 |  | 0 |  | 19:00 |  | 1359.92
|  |  | Total = |  |  | 9278 | MW | Khulna | 1829 | 1829 |  | 0 |  | 19:30 |  | 1115.44
7 | Total Gas Supplied : |  | 877.36 | MMCFD | **Import Adani: | Taka | 161199874.53 | Rajshahi | 1519.4 | 1372.4 |  | 147 |  | 20:00 |  | 1076.285
8 | Fuel Cost : | i) Gas : | Taka | 359664089.414 | ii) Oil : | Taka | 895334734.21 | Comilla | 1464 | 1247 |  | 217 |  | 21:00 |  | 1305
|  | iii) Coal : | Taka | 593676895.42 | Total | Taka | 2009875593.574 | Mymensingh | 1282 | 1025 |  | 257 |  | 22:00 |  | 1358.01
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7943.1 | MKWHr. | Sylhet | 669 | 564 |  | 105 |  | 23:00 |  | 1351.325
| ii) During Peak Demand : |  |  | 750 | MW (W to E) at | 20:00 | hrs | Barisal | 479.3 | 479.3 |  | 0 |  | 24:00 |  | 1366.605
| iii) Maximum : |  |  | 504 | MW at | 5:00 | hrs | Rangpur | 1039 | 914 |  | 125
10 | Maximum Temperature in Dhaka was |  |  |  | 34.3°C |  |  | Total | 14932.82 | 13856.82 |  | 1076
B. |  | 2024-09-08 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 34.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 340 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15540 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13850 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 347.4914 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12595 | MW at | 6:00 | 0 | 0 | 0 | 90 | 80 | 80 | 40 | 0 | 50
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.9615 | MKWHr. | ii) HVDC Flow at Peak Time |  | 874 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.536 | MKWHr. | iii) Maximum HVDC Flow : |  | 880 | MW at | 15:00 | hrs.
* Import Through Adani : |  |  |  |  | i) Energy | 24.3873 | MKWHr.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 108.31 |  | (b) Today: | 108.26 |  | (c) Rule Curve: |  | 100.61

## YesterdayGen
2024-09-07 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 327 | 0 | 0 | 0 | 33 | 64 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 20 | 23 | 30 | 20 | 0 | 0 | 131 | 80 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 6 | 71 | 68 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 290 | 240 | 140 | 0 | 85 | 33 | 5 | 0 | 51 | 0 | 42 | 8 | 0 | 0 | 0 | 18 | 64 | 23 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 30 | 16 | 0 | 204 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 296 | 0 | 0 | 87 | 0 | 68 | 0 | 25 | 106 | 5 | 225 | 49 | 17 | 85 | 0 | 50 | 52 | 110 | 52 | 28 | 24 | 341 | 40 | 0 | 108 | 50 | 0 | 0 | 0 | 72 | 35 | 230 | 17 | 0 | 612 | 1 | 702 | 0 | 0 | 0 | 0 |  | 878 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 27 | 38 | 0 | 134 | 10 | 64 | 0 | 0 | 0 | 30 | 16 | 0 | 35 | 0 | 28 | 0 | 22 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 89 | 0 | 95 | 0 | 77 | 0 | 0 | 95 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 618 | 0 | 307 | 1022 | 0 | 0 | 0 | 0 |  | 7397 | 6109 | 13506 | 3414 | 878 | 1627 | 0 | 2183 | 3683 | 211 | 0 | 423 | 64 | 1022 | 0 | 1 | 901.52 | 108.32
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 329 | 0 | 0 | 0 | 33 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 20 | 23 | 30 | 21 | 0 | 0 | 131 | 80 | 0 | 0 | 0 | 198 | 0 | 0 | 0 |  | 6 | 0 | 34 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 290 | 240 | 140 | 0 | 70 | 33 | 5 | 0 | 51 | 0 | 42 | 8 | 0 | 0 | 0 | 18 | 62 | 23 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 30 | 16 | 0 | 205 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 143 | 0 | 0 | 87 | 0 | 55 | 0 | 25 | 104 | 7 | 280 | 48 | 17 | 85 | 0 | 50 | 54 | 110 | 52 | 28 | 24 | 341 | 52 | 0 | 108 | 57 | 0 | 0 | 0 | 59 | 35 | 230 | 17 | 0 | 612 | 3 | 702 | 0 | 0 | 0 | 0 |  | 878 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 27 | 38 | 0 | 134 | 7 | 48 | 0 | 0 | 0 | 30 | 0 | 0 | 35 | 0 | 28 | 0 | 22 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 89 | 0 | 50 | 0 | 70 | 0 | 0 | 95 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 619 | 0 | 307 | 1022 | 0 | 0 | 0 | 0 |  | 7115 | 6048 | 13163 | 3453 | 878 | 1652 | 0 | 1928 | 3684 | 211 | 0 | 270 | 62 | 1022 | 0 | 3 | 894.835 | 108.32
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 328 | 0 | 0 | 0 | 33 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 20 | 23 | 30 | 21 | 0 | 0 | 129 | 80 | 0 | 0 | 0 | 182 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 240 | 140 | 0 | 70 | 33 | 5 | 0 | 51 | 0 | 42 | 8 | 0 | 0 | 0 | 18 | 62 | 23 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 30 | 16 | 0 | 206 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 97 | 0 | 0 | 87 | 0 | 52 | 0 | 25 | 102 | 7 | 279 | 49 | 17 | 85 | 0 | 50 | 54 | 110 | 52 | 28 | 24 | 341 | 52 | 0 | 108 | 72 | 0 | 0 | 0 | 56 | 35 | 230 | 17 | 0 | 612 | 0 | 701 | 0 | 0 | 0 | 0 |  | 877 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 9 | 16 | 0 | 0 | 0 | 30 | 0 | 0 | 35 | 0 | 28 | 0 | 22 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 89 | 0 | 50 | 0 | 70 | 0 | 0 | 70 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 615 | 0 | 307 | 1015 | 0 | 0 | 0 | 0 |  | 7026 | 5898 | 12924 | 3437 | 877 | 1641 | 0 | 1833 | 3679 | 209 | 0 | 171 | 62 | 1015 | 0 | 0 | 884.33 | 108.32
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 321 | 0 | 0 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 20 | 23 | 30 | 21 | 0 | 0 | 129 | 80 | 0 | 0 | 0 | 182 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 240 | 31 | 0 | 70 | 33 | 22 | 0 | 51 | 0 | 42 | 8 | 0 | 0 | 0 | 18 | 60 | 23 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 30 | 16 | 0 | 208 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 97 | 0 | 0 | 87 | 0 | 52 | 0 | 25 | 102 | 7 | 279 | 49 | 17 | 83 | 0 | 52 | 54 | 110 | 52 | 28 | 24 | 341 | 52 | 0 | 108 | 72 | 0 | 0 | 0 | 55 | 35 | 230 | 17 | 0 | 614 | 0 | 700 | 0 | 0 | 0 | 0 |  | 878 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 8 | 16 | 0 | 0 | 0 | 30 | 0 | 0 | 28 | 0 | 28 | 0 | 22 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 89 | 0 | 50 | 0 | 49 | 0 | 0 | 70 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 616 | 0 | 307 | 1024 | 0 | 0 | 0 | 0 |  | 6914 | 5892 | 12806 | 3324 | 878 | 1664 | 0 | 1795 | 3681 | 209 | 0 | 171 | 60 | 1024 | 0 | 0 | 662.77 | 108.31
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 24 | 31 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 20 | 23 | 30 | 21 | 0 | 0 | 129 | 80 | 0 | 0 | 0 | 168 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 240 | 37 | 8 | 70 | 33 | 41 | 0 | 51 | 0 | 42 | 8 | 0 | 0 | 0 | 18 | 54 | 23 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 30 | 16 | 0 | 208 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 95 | 0 | 0 | 87 | 0 | 52 | 0 | 25 | 104 | 5 | 279 | 49 | 17 | 68 | 0 | 52 | 54 | 110 | 52 | 28 | 24 | 345 | 52 | 0 | 72 | 35 | 0 | 0 | 0 | 54 | 35 | 250 | 17 | 0 | 521 | 0 | 702 | 0 | 0 | 0 | 0 |  | 878 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 16 | 0 | 0 | 0 | 30 | 0 | 0 | 28 | 0 | 0 | 0 | 22 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 89 | 0 | 35 | 0 | 49 | 0 | 0 | 70 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 614 | 0 | 307 | 1021 | 0 | 0 | 0 | 0 |  | 6728 | 5784 | 12512 | 3300 | 878 | 1631 | 0 | 1689 | 3588 | 209 | 0 | 142 | 54 | 1021 | 0 | 0 | 657.04 | 108.31
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 20 | 23 | 30 | 21 | 0 | 0 | 129 | 80 | 0 | 0 | 0 | 167 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 240 | 38 | 8 | 70 | 33 | 51 | 0 | 51 | 0 | 42 | 8 | 0 | 0 | 0 | 18 | 56 | 23 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 30 | 16 | 0 | 208 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 82 | 0 | 0 | 87 | 0 | 52 | 0 | 25 | 100 | 7 | 268 | 49 | 17 | 68 | 0 | 52 | 54 | 98 | 52 | 28 | 25 | 345 | 52 | 0 | 54 | 35 | 0 | 0 | 0 | 49 | 35 | 250 | 17 | 0 | 545 | 0 | 701 | 0 | 0 | 2 | 0 |  | 878 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 16 | 0 | 0 | 0 | 29 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 89 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1120 | 220 | 0 | 17 | 0 | 1 | 115 | 0 | 0 | 556 | 0 | 307 | 1018 | 2 | 0 | 0 | 0 |  | 6643 | 5430 | 12073 | 3286 | 878 | 1537 | 0 | 1535 | 3429 | 209 | 0 | 120 | 56 | 1018 | 5 | 0 | 598.785 | 108.31
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 23 | 30 | 19 | 8 | 0 | 129 | 80 | 0 | 0 | 0 | 167 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 240 | 63 | 8 | 70 | 33 | 51 | 0 | 43 | 0 | 36 | 8 | 0 | 0 | 0 | 18 | 50 | 23 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 130 | 0 | 30 | 16 | 0 | 207 | 0 | 0 | 0 | 260 | 12 | 2 | 0 | 62 | 0 | 0 | 87 | 0 | 52 | 2 | 25 | 100 | 7 | 268 | 49 | 17 | 68 | 1 | 52 | 54 | 110 | 52 | 28 | 25 | 330 | 52 | 6 | 54 | 35 | 0 | 0 | 2 | 48 | 35 | 250 | 17 | 0 | 570 | 0 | 700 | 0 | 0 | 5 | 0 |  | 878 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 89 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 1040 | 220 | 0 | 17 | 0 | 8 | 115 | 0 | 0 | 546 | 0 | 236 | 1011 | 0 | 0 | 0 | 2 |  | 6557 | 5230 | 11787 | 3269 | 878 | 1475 | 0 | 1464 | 3292 | 209 | 0 | 113 | 50 | 1011 | 26 | 0 | 298.915 | 108.3
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 350 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 23 | 30 | 18 | 8 | 0 | 130 | 80 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 290 | 240 | 113 | 8 | 70 | 32 | 51 | 0 | 43 | 0 | 36 | 8 | 0 | 0 | 0 | 18 | 48 | 21 | 0 | 0 | 1 | 39 | 0 | 0 | 0 | 130 | 0 | 30 | 16 | 0 | 208 | 0 | 0 | 0 | 260 | 12 | 2 | 0 | 62 | 0 | 0 | 87 | 0 | 53 | 12 | 25 | 100 | 6 | 268 | 48 | 17 | 68 | 2 | 52 | 17 | 110 | 52 | 28 | 25 | 340 | 52 | 10 | 54 | 17 | 0 | 0 | 12 | 49 | 35 | 250 | 17 | 0 | 530 | 0 | 705 | 0 | 0 | 28 | 0 |  | 877 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 89 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 960 | 220 | 0 | 17 | 0 | 21 | 73 | 0 | 0 | 517 | 15 | 200 | 1015 | 52 | 0 | 0 | 8 |  | 6446 | 5096 | 11542 | 3353 | 877 | 1314 | 0 | 1339 | 3112 | 210 | 0 | 113 | 48 | 1015 | 161 | 0 | 313.24 | 108.3
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 420 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 23 | 30 | 18 | 17 | 0 | 130 | 80 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 285 | 240 | 136 | 8 | 50 | 28 | 49 | 0 | 43 | 0 | 39 | 8 | 0 | 0 | 0 | 18 | 48 | 19 | 0 | 0 | 1 | 39 | 0 | 0 | 0 | 130 | 0 | 30 | 16 | 0 | 209 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 65 | 0 | 0 | 87 | 0 | 59 | 15 | 25 | 100 | 5 | 268 | 49 | 17 | 34 | 3 | 52 | 17 | 51 | 52 | 29 | 24 | 340 | 52 | 32 | 54 | 17 | 0 | 0 | 22 | 48 | 35 | 250 | 17 | 0 | 530 | 0 | 702 | 0 | 0 | 44 | 0 |  | 877 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 35 | 0 | 54 | 0 | 0 | 0 | 0 | 35 | 960 | 220 | 0 | 17 | 1 | 66 | 80 | 0 | 0 | 506 | 26 | 200 | 1014 | 155 | 0 | 0 | 17 |  | 6528 | 5348 | 11876 | 3352 | 877 | 1527 | 0 | 1236 | 3098 | 210 | 0 | 132 | 48 | 1014 | 382 | 0 | 338.07 | 108.29
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 |  | 0 | 420 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 24 | 82 | 0 | 0 | 0 | 0 | 17 | 3 | 0 | 0 | 17 | 16 | 30 | 18 | 17 | 0 | 131 | 80 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 300 | 240 | 212 | 8 | 50 | 30 | 11 | 0 | 43 | 0 | 42 | 8 | 0 | 0 | 0 | 18 | 52 | 16 | 0 | 0 | 2 | 39 | 0 | 0 | 0 | 130 | 0 | 28 | 16 | 0 | 208 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 65 | 0 | 0 | 87 | 0 | 95 | 0 | 12 | 100 | 6 | 279 | 49 | 52 | 17 | 2 | 30 | 17 | 34 | 52 | 28 | 12 | 340 | 52 | 45 | 54 | 17 | 0 | 8 | 32 | 48 | 35 | 250 | 36 | 0 | 530 | 1 | 701 | 0 | 0 | 58 | 0 |  | 878 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 8 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 16 | 0 | 55 | 0 | 0 | 0 | 0 | 35 | 950 | 220 | 0 | 17 | 2 | 86 | 115 | 0 | 0 | 516 | 31 | 200 | 1017 | 182 | 0 | 0 | 28 |  | 6641 | 5416 | 12057 | 3433 | 878 | 1503 | 0 | 1229 | 3077 | 211 | 0 | 188 | 52 | 1017 | 468 | 1 | 328 | 108.29
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 324 | 0 | 0 | 0 | 24 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 17 | 16 | 30 | 12 | 17 | 0 | 131 | 80 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 240 | 211 | 8 | 50 | 29 | 32 | 0 | 43 | 0 | 42 | 8 | 0 | 0 | 0 | 18 | 56 | 11 | 0 | 0 | 2 | 39 | 0 | 0 | 0 | 163 | 0 | 28 | 16 | 0 | 208 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 65 | 0 | 0 | 96 | 0 | 96 | 10 | 12 | 100 | 6 | 265 | 48 | 52 | 17 | 5 | 30 | 17 | 34 | 52 | 28 | 12 | 345 | 51 | 43 | 54 | 17 | 0 | 17 | 19 | 49 | 35 | 270 | 36 | 0 | 530 | 0 | 704 | 0 | 0 | 57 | 0 |  | 877 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 6 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 55 | 970 | 220 | 0 | 17 | 5 | 95 | 115 | 0 | 0 | 510 | 35 | 200 | 1016 | 191 | 0 | 0 | 58 |  | 6847 | 5470 | 12317 | 3491 | 877 | 1585 | 0 | 1273 | 3084 | 211 | 0 | 204 | 56 | 1016 | 520 | 0 | 318 | 108.28
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 |  | 0 | 450 | 0 | 0 | 0 | 45 | 315 | 0 | 0 | 0 | 24 | 96 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 17 | 16 | 30 | 12 | 17 | 0 | 131 | 80 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 172 | 0 | 70 | 29 | 46 | 0 | 43 | 0 | 35 | 8 | 0 | 0 | 0 | 18 | 60 | 9 | 0 | 0 | 2 | 39 | 0 | 49 | 11 | 163 | 0 | 30 | 76 | 0 | 203 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 65 | 0 | 0 | 96 | 0 | 96 | 19 | 12 | 100 | 5 | 0 | 48 | 52 | 17 | 4 | 30 | 17 | 34 | 52 | 28 | 12 | 345 | 51 | 42 | 54 | 17 | 0 | 17 | 21 | 49 | 35 | 250 | 36 | 0 | 530 | 0 | 705 | 0 | 0 | 74 | 0 |  | 877 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 55 | 0 | 22 | 0 | 0 | 55 | 1000 | 220 | 0 | 17 | 5 | 96 | 115 | 0 | 0 | 575 | 37 | 200 | 1014 | 207 | 0 | 0 | 61 |  | 6718 | 5733 | 12451 | 3169 | 877 | 1790 | 0 | 1357 | 3210 | 211 | 0 | 195 | 60 | 1014 | 568 | 0 | 763.045 | 108.28
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 319 | 0 | 0 | 0 | 24 | 96 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 17 | 16 | 25 | 12 | 17 | 0 | 132 | 80 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 194 | 0 | 50 | 29 | 21 | 0 | 43 | 0 | 35 | 7 | 0 | 0 | 0 | 18 | 66 | 9 | 0 | 0 | 2 | 39 | 0 | 52 | 27 | 163 | 0 | 59 | 86 | 0 | 202 | 0 | 0 | 0 | 310 | 11 | 2 | 0 | 65 | 0 | 0 | 96 | 0 | 96 | 19 | 12 | 100 | 6 | 0 | 47 | 52 | 17 | 5 | 30 | 17 | 34 | 52 | 28 | 23 | 345 | 53 | 48 | 54 | 17 | 0 | 17 | 28 | 49 | 35 | 230 | 36 | 0 | 530 | 9 | 703 | 0 | 0 | 72 | 0 |  | 879 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 16 | 0 | 0 | 0 | 29 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 17 | 0 | 55 | 0 | 33 | 0 | 0 | 55 | 1000 | 220 | 0 | 17 | 5 | 95 | 115 | 0 | 0 | 725 | 34 | 150 | 1015 | 185 | 0 | 0 | 59 |  | 6779 | 5774 | 12553 | 3175 | 879 | 1772 | 0 | 1397 | 3280 | 212 | 0 | 196 | 66 | 1015 | 552 | 9 | 1000 | 108.27
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 319 | 0 | 0 | 0 | 24 | 80 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 17 | 16 | 25 | 12 | 17 | 0 | 132 | 80 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 280 | 240 | 209 | 0 | 50 | 10 | 10 | 0 | 43 | 0 | 35 | 7 | 0 | 0 | 0 | 18 | 72 | 9 | 0 | 0 | 2 | 39 | 0 | 52 | 27 | 120 | 0 | 59 | 84 | 0 | 202 | 0 | 0 | 0 | 305 | 11 | 2 | 0 | 65 | 0 | 0 | 95 | 0 | 96 | 15 | 25 | 110 | 6 | 71 | 57 | 52 | 17 | 4 | 30 | 17 | 34 | 52 | 27 | 24 | 345 | 50 | 32 | 54 | 17 | 0 | 17 | 28 | 49 | 35 | 230 | 36 | 0 | 580 | 25 | 700 | 0 | 0 | 62 | 0 |  | 879 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 8 | 16 | 0 | 0 | 0 | 29 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 17 | 0 | 55 | 0 | 33 | 0 | 7 | 55 | 990 | 220 | 0 | 17 | 4 | 93 | 115 | 0 | 0 | 765 | 17 | 150 | 1019 | 171 | 0 | 0 | 57 |  | 6871 | 5816 | 12687 | 3245 | 879 | 1708 | 0 | 1462 | 3393 | 212 | 0 | 180 | 72 | 1019 | 492 | 25 | 1062.915 | 108.28
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 318 | 0 | 0 | 0 | 24 | 80 | 0 | 0 | 0 | 0 | 35 | 35 | 30 | 0 | 17 | 16 | 33 | 12 | 17 | 0 | 132 | 80 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 210 | 0 | 50 | 10 | 10 | 0 | 43 | 0 | 34 | 7 | 0 | 0 | 0 | 18 | 74 | 10 | 0 | 0 | 2 | 39 | 0 | 52 | 28 | 163 | 0 | 56 | 22 | 0 | 202 | 0 | 0 | 0 | 300 | 11 | 2 | 0 | 65 | 0 | 0 | 96 | 0 | 96 | 12 | 25 | 103 | 23 | 71 | 57 | 52 | 17 | 3 | 15 | 17 | 17 | 52 | 28 | 24 | 345 | 53 | 36 | 54 | 17 | 0 | 17 | 25 | 42 | 23 | 230 | 36 | 0 | 612 | 17 | 706 | 0 | 0 | 48 | 0 |  | 880 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 9 | 16 | 0 | 0 | 0 | 29 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 55 | 0 | 33 | 0 | 5 | 55 | 990 | 220 | 0 | 17 | 3 | 8 | 115 | 0 | 0 | 762 | 27 | 150 | 1014 | 144 | 0 | 0 | 39 |  | 6848 | 5701 | 12549 | 3244 | 880 | 1713 | 0 | 1444 | 3420 | 212 | 0 | 179 | 74 | 1014 | 352 | 17 | 1242.455 | 108.25
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 320 | 0 | 0 | 0 | 24 | 80 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 17 | 16 | 33 | 12 | 17 | 0 | 131 | 80 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 280 | 240 | 208 | 0 | 70 | 10 | 10 | 0 | 43 | 0 | 34 | 7 | 0 | 0 | 0 | 18 | 70 | 10 | 0 | 0 | 1 | 39 | 0 | 52 | 34 | 163 | 0 | 59 | 22 | 0 | 202 | 0 | 0 | 0 | 285 | 11 | 2 | 0 | 62 | 0 | 0 | 96 | 0 | 95 | 8 | 25 | 100 | 62 | 71 | 57 | 52 | 17 | 2 | 15 | 17 | 17 | 52 | 15 | 24 | 370 | 48 | 16 | 54 | 17 | 0 | 17 | 14 | 47 | 35 | 230 | 17 | 0 | 612 | 32 | 705 | 0 | 0 | 34 | 0 |  | 880 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 9 | 16 | 0 | 0 | 0 | 29 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 17 | 0 | 70 | 0 | 33 | 0 | 3 | 55 | 990 | 220 | 0 | 17 | 1 | 12 | 115 | 0 | 0 | 762 | 17 | 150 | 1008 | 108 | 0 | 0 | 30 |  | 6870 | 5572 | 12442 | 3295 | 880 | 1619 | 0 | 1502 | 3419 | 211 | 0 | 160 | 70 | 1008 | 246 | 32 | 1325.54 | 108.24
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 316 | 0 | 0 | 0 | 24 | 78 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 16 | 16 | 33 | 12 | 8 | 0 | 130 | 80 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 280 | 240 | 211 | 0 | 50 | 10 | 10 | 0 | 43 | 0 | 34 | 7 | 0 | 0 | 0 | 18 | 66 | 11 | 0 | 0 | 1 | 39 | 0 | 52 | 34 | 163 | 0 | 60 | 22 | 0 | 200 | 0 | 0 | 0 | 305 | 11 | 2 | 0 | 65 | 0 | 0 | 96 | 0 | 95 | 3 | 25 | 118 | 78 | 80 | 57 | 34 | 17 | 0 | 15 | 17 | 17 | 52 | 9 | 24 | 370 | 41 | 6 | 72 | 17 | 0 | 17 | 5 | 56 | 35 | 230 | 17 | 0 | 612 | 16 | 700 | 0 | 0 | 13 | 0 |  | 880 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 16 | 0 | 0 | 0 | 29 | 0 | 0 | 35 | 0 | 0 | 0 | 26 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 17 | 0 | 110 | 0 | 40 | 0 | 0 | 55 | 1000 | 220 | 0 | 17 | 1 | 8 | 115 | 0 | 0 | 762 | 8 | 150 | 1009 | 20 | 0 | 0 | 8 |  | 6833 | 5578 | 12411 | 3277 | 880 | 1697 | 0 | 1575 | 3424 | 210 | 0 | 184 | 66 | 1009 | 73 | 16 | 1278.745 | 108.23
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 320 | 0 | 0 | 0 | 24 | 88 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 16 | 23 | 33 | 12 | 8 | 0 | 130 | 80 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 290 | 240 | 211 | 0 | 50 | 10 | 10 | 0 | 43 | 0 | 34 | 8 | 0 | 0 | 0 | 18 | 66 | 11 | 0 | 0 | 0 | 39 | 0 | 30 | 34 | 120 | 0 | 60 | 11 | 0 | 202 | 0 | 0 | 0 | 290 | 11 | 2 | 0 | 62 | 0 | 0 | 94 | 0 | 109 | 0 | 25 | 192 | 75 | 71 | 57 | 34 | 17 | 0 | 15 | 17 | 17 | 102 | 9 | 24 | 370 | 41 | 0 | 162 | 17 | 0 | 0 | 0 | 70 | 35 | 230 | 17 | 0 | 612 | 7 | 655 | 0 | 0 | 0 | 0 |  | 879 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 80 | 8 | 32 | 0 | 0 | 0 | 29 | 0 | 40 | 35 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 83 | 0 | 0 | 113 | 980 | 220 | 0 | 17 | 0 | 1 | 115 | 0 | 0 | 762 | 1 | 156 | 1013 | 3 | 0 | 0 | 0 |  | 6940 | 5709 | 12649 | 3244 | 879 | 1648 | 0 | 1936 | 3373 | 210 | 0 | 268 | 66 | 1013 | 5 | 7 | 1003.705 | 108.22
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 320 | 0 | 0 | 0 | 24 | 143 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 17 | 22 | 33 | 12 | 16 | 0 | 131 | 80 | 0 | 0 | 1 | 211 | 0 | 0 | 0 |  | 18 | 23 | 51 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 300 | 240 | 212 | 0 | 70 | 10 | 10 | 0 | 43 | 0 | 34 | 8 | 0 | 0 | 0 | 18 | 76 | 11 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 60 | 16 | 0 | 204 | 0 | 0 | 0 | 300 | 11 | 2 | 0 | 232 | 0 | 0 | 122 | 0 | 112 | 0 | 25 | 200 | 88 | 120 | 76 | 52 | 17 | 0 | 15 | 17 | 17 | 106 | 9 | 24 | 375 | 53 | 0 | 162 | 17 | 0 | 0 | 0 | 72 | 20 | 230 | 145 | 0 | 612 | 0 | 645 | 0 | 0 | 0 | 0 |  | 875 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 40 | 37 | 0 | 130 | 10 | 32 | 0 | 0 | 0 | 29 | 0 | 88 | 35 | 0 | 9 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 35 | 0 | 113 | 0 | 98 | 0 | 0 | 113 | 1090 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 1020 | 0 | 270 | 1006 | 0 | 0 | 0 | 0 |  | 7544 | 6332 | 13876 | 3375 | 875 | 1617 | 0 | 2240 | 3847 | 211 | 0 | 629 | 76 | 1006 | 0 | 0 | 1359.92 | 108.23
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 322 | 0 | 0 | 0 | 8 | 143 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 17 | 21 | 33 | 12 | 16 | 0 | 132 | 80 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 18 | 24 | 51 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 300 | 240 | 212 | 0 | 70 | 10 | 10 | 0 | 43 | 0 | 34 | 8 | 0 | 0 | 0 | 18 | 76 | 13 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 31 | 16 | 0 | 202 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 275 | 0 | 0 | 122 | 0 | 112 | 0 | 25 | 200 | 88 | 279 | 76 | 52 | 17 | 0 | 15 | 17 | 17 | 106 | 9 | 24 | 375 | 60 | 0 | 162 | 17 | 0 | 0 | 0 | 88 | 35 | 230 | 145 | 0 | 612 | 0 | 645 | 0 | 0 | 0 | 0 |  | 875 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 46 | 40 | 0 | 130 | 10 | 64 | 0 | 0 | 0 | 29 | 4 | 88 | 35 | 0 | 26 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 60 | 0 | 113 | 0 | 98 | 0 | 0 | 113 | 1160 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 1114 | 0 | 270 | 1011 | 0 | 0 | 0 | 0 |  | 7743 | 6589 | 14332 | 3514 | 875 | 1595 | 0 | 2378 | 4011 | 212 | 0 | 660 | 76 | 1011 | 0 | 0 | 1115.44 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 316 | 0 | 0 | 0 | 8 | 143 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 17 | 22 | 33 | 12 | 16 | 0 | 132 | 80 | 0 | 0 | 25 | 211 | 0 | 0 | 0 |  | 18 | 24 | 51 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 300 | 240 | 202 | 0 | 70 | 10 | 10 | 0 | 43 | 0 | 34 | 8 | 0 | 0 | 0 | 18 | 74 | 13 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 28 | 16 | 0 | 205 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 277 | 0 | 0 | 121 | 0 | 112 | 0 | 25 | 200 | 87 | 268 | 77 | 52 | 17 | 0 | 15 | 17 | 17 | 106 | 9 | 24 | 365 | 60 | 0 | 162 | 17 | 0 | 0 | 0 | 87 | 35 | 230 | 145 | 0 | 610 | 10 | 645 | 0 | 0 | 0 | 0 |  | 874 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 41 | 55 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 29 | 5 | 88 | 35 | 0 | 45 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 70 | 0 | 113 | 0 | 98 | 0 | 0 | 113 | 1160 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 1128 | 0 | 270 | 1011 | 0 | 0 | 0 | 0 |  | 7748 | 6625 | 14373 | 3473 | 874 | 1638 | 0 | 2368 | 4023 | 212 | 0 | 690 | 74 | 1011 | 0 | 10 | 1076.285 | 108.22
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 322 | 0 | 0 | 0 | 8 | 143 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 17 | 22 | 33 | 11 | 16 | 0 | 132 | 80 | 0 | 0 | 25 | 211 | 0 | 0 | 0 |  | 18 | 24 | 51 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 300 | 240 | 212 | 0 | 50 | 0 | 9 | 0 | 43 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 74 | 16 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 30 | 16 | 0 | 204 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 277 | 0 | 0 | 122 | 0 | 113 | 0 | 25 | 180 | 103 | 268 | 77 | 52 | 17 | 0 | 15 | 17 | 17 | 106 | 9 | 24 | 375 | 65 | 0 | 108 | 17 | 0 | 0 | 0 | 88 | 35 | 230 | 145 | 0 | 610 | 18 | 645 | 0 | 0 | 0 | 0 |  | 875 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 41 | 41 | 0 | 81 | 10 | 16 | 0 | 0 | 0 | 29 | 13 | 88 | 35 | 0 | 45 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 71 | 0 | 113 | 0 | 98 | 0 | 0 | 113 | 1160 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 1118 | 0 | 270 | 1010 | 0 | 0 | 0 | 0 |  | 7689 | 6544 | 14233 | 3386 | 875 | 1661 | 0 | 2300 | 4013 | 212 | 0 | 684 | 74 | 1010 | 0 | 18 | 1305 | 108.23
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 324 | 0 | 0 | 0 | 8 | 142 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 17 | 22 | 33 | 11 | 16 | 0 | 132 | 80 | 0 | 0 | 25 | 209 | 0 | 0 | 0 |  | 18 | 24 | 51 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 300 | 240 | 200 | 0 | 50 | 10 | 10 | 0 | 43 | 0 | 34 | 8 | 0 | 0 | 0 | 18 | 78 | 16 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 30 | 16 | 0 | 204 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 250 | 0 | 0 | 122 | 0 | 112 | 0 | 25 | 192 | 103 | 268 | 77 | 52 | 17 | 0 | 15 | 17 | 17 | 106 | 9 | 24 | 375 | 49 | 0 | 90 | 17 | 0 | 12 | 0 | 74 | 35 | 230 | 17 | 0 | 608 | 4 | 645 | 0 | 0 | 0 | 0 |  | 875 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 35 | 40 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 30 | 17 | 88 | 35 | 0 | 42 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 17 | 0 | 113 | 0 | 98 | 0 | 0 | 113 | 1210 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 1127 | 0 | 307 | 1012 | 0 | 0 | 0 | 0 |  | 7502 | 6626 | 14128 | 3451 | 875 | 1665 | 0 | 2174 | 4107 | 212 | 0 | 550 | 78 | 1012 | 0 | 4 | 1358.01 | 108.33
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 316 | 0 | 0 | 0 | 8 | 143 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 17 | 0 | 33 | 11 | 8 | 0 | 132 | 80 | 0 | 0 | 25 | 201 | 0 | 0 | 0 |  | 18 | 24 | 51 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 300 | 240 | 201 | 0 | 70 | 10 | 10 | 0 | 43 | 0 | 34 | 8 | 0 | 0 | 0 | 18 | 76 | 17 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 30 | 16 | 0 | 204 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 220 | 0 | 0 | 123 | 0 | 113 | 0 | 25 | 200 | 102 | 268 | 77 | 35 | 17 | 0 | 15 | 17 | 24 | 106 | 9 | 24 | 375 | 49 | 0 | 54 | 17 | 0 | 17 | 0 | 58 | 35 | 230 | 17 | 0 | 612 | 0 | 645 | 0 | 0 | 0 | 0 |  | 874 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 32 | 36 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 30 | 20 | 88 | 35 | 0 | 42 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 98 | 0 | 0 | 113 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 1164 | 0 | 307 | 1006 | 0 | 0 | 0 | 0 |  | 7392 | 6693 | 14085 | 3438 | 874 | 1662 | 0 | 2088 | 4182 | 212 | 0 | 547 | 76 | 1006 | 0 | 0 | 1351.325 | 108.33
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 316 | 0 | 0 | 0 | 8 | 143 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 17 | 15 | 33 | 11 | 8 | 0 | 132 | 80 | 0 | 0 | 25 | 198 | 0 | 0 | 0 |  | 18 | 24 | 51 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 300 | 240 | 201 | 0 | 50 | 10 | 10 | 0 | 43 | 0 | 34 | 8 | 0 | 0 | 0 | 18 | 74 | 17 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 31 | 16 | 0 | 204 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 195 | 0 | 0 | 123 | 0 | 114 | 0 | 25 | 152 | 102 | 270 | 77 | 35 | 20 | 0 | 30 | 17 | 51 | 106 | 9 | 24 | 383 | 50 | 0 | 54 | 17 | 0 | 17 | 0 | 55 | 35 | 230 | 17 | 0 | 612 | 4 | 645 | 0 | 0 | 0 | 0 |  | 874 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 22 | 36 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 30 | 14 | 55 | 35 | 0 | 35 | 0 | 22 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 95 | 0 | 98 | 0 | 0 | 113 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 1166 | 0 | 307 | 1006 | 0 | 0 | 0 | 0 |  | 7361 | 6608 | 13969 | 3434 | 874 | 1675 | 0 | 2023 | 4184 | 212 | 0 | 483 | 74 | 1006 | 0 | 4 | 1366.605 | 108.33
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9579600 | 0 |  | 0 | 10212500 | 0 | 0 | 0 | 1291832 | 7513476 | 0 | 0 | 0 | 540288 | 1929600 | 0 | 0 | 0 | 0 | 638280 | 684472 | 670293 | 0 | 438600 | 457200 | 756360 | 339700 | 240000 | 0 | 2969018 | 1924000 | 0 | 0 | 140317 | 4737386 | 0 | 0 | 0 |  | 240240 | 242064 | 425703 | 0 | 0 | 0 | 0 | 545760 | 0 | 0 | 0 | 7479400 | 6066000 | 3944000 | 66909 | 1472570 | 540288 | 504000 | 0 | 994640 | 0 | 861676 | 189211 | 0 | 0 | 0 | 399250 | 1536000 | 380160 | 0 | 0 | 14800 | 925000 | 0 | 324600 | 205776 | 3626264 | 0 | 901920 | 600960 | 0 | 5127380 | 0 | 0 | 0 | 7212500 | 263040 | 60384 | 0 | 3048545 | 0 | 0 | 2352000 | 0 | 2065392 | 111780 | 551040 | 3104640 | 913309 | 5045000 | 1365600 | 841920 | 963491 | 31281 | 825491 | 743804 | 1492909 | 1625640 | 513240 | 550080 | 8573200 | 1227840 | 338130 | 1964160 | 677455 | 0 | 241560 | 198077 | 1392960 | 837000 | 5866300 | 879854 | 0 | 14012726 | 167040 | 16610909 | 0 | 0 | 461882 | 0 |  | 21961454 | 0 | 8039808 | 0 | 0 | 0 | 0 | 0 | 272640 | 307072 | 0 | 3038000 | 199930 | 537984 | 0 | 0 | 0 | 703785 | 79220 | 502256 | 659290 | 0 | 264485 | 0 | 315148 | 0 | 0 | 138852 | 0 | 0 | 4808000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8957454 | 1144800 | 0 | 1790784 | 0 | 1193078 | 0 | 17491 | 1790592 | 28288700 | 5374860 | 0 | 448800 | 33120 | 591120 | 2720064 | 0 | 0 | 17905457 | 250102 | 5826000 | 24387273 | 1362960 | 0 | 4125 | 396750 |  | 169807672 | 144311454 | 314119126 | 82082874 | 21961454 | 38826153 | 0 | 42218401 | 87451792 | 4893018 | 0 | 6783503 | 1536000 | 24387273 | 3811618 | 167040 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27589248 | 0 |  | 0 | 32475750 | 0 | 0 | 0 | 22762079.84 | 22916101.8 | 0 | 0 | 0 | 9698169.6 | 37472832 | 0 | 0 | 0 | 0 | 11654992.8 | 10787278.72 | 12259658.97 | 0 | 328950 | 0 | 0 | 0 | 4298400 | 0 | 0 | 0 | 0 | 0 | 2657603.98 | 15112261.34 | 0 | 0 | 0 |  | 4225821.6 | 4262747.04 | 7624340.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20867526 | 18561960 | 13094080 | 224145.15 | 4756401.1 | 1820770.56 | 2207520 | 0 | 3988506.4 | 0 | 15432617.16 | 3417150.66 | 0 | 0 | 0 | 299437.5 | 10076160 | 1182297.6 | 0 | 0 | 0 | 3607500 | 0 | 1476930 | 936280.8 | 12401822.88 | 0 | 5005656 | 3137011.2 | 0 | 14305390.2 | 0 | 0 | 0 | 22286625 | 197280 | 45891.84 | 0 | 62190318 | 0 | 0 | 45181920 | 0 | 36371553.12 | 0 | 9814022.4 | 53865504 | 15142663.22 | 13369250 | 26028336 | 15794419.2 | 17285028.54 | 0 | 13496777.85 | 14459549.76 | 26782787.46 | 31065980.4 | 9961988.4 | 9796924.8 | 22804712 | 20959228.8 | 0 | 35924486.4 | 11367694.9 | 0 | 4316677.2 | 0 | 25101139.2 | 14178780 | 17422911 | 12388344.32 | 0 | 97668700.22 | 0 | 98004363.1 | 0 | 0 | 0 | 0 |  | 61711685.74 | 0 | 23717433.6 | 0 | 0 | 0 | 0 | 0 | 5128358.4 | 5776024.32 | 0 | 9600080 | 947668.2 | 9274844.16 | 0 | 0 | 0 | 12604789.35 | 1453687 | 8442923.36 | 14029691.2 | 0 | 4736926.35 | 0 | 5644300.68 | 0 | 0 | 105110.964 | 0 | 0 | 40579520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26155765.68 | 19553184 | 0 | 35493338.88 | 0 | 23766113.76 | 0 | 0 | 35525345.28 | 183310776 | 16715814.6 | 0 | 8684280 | 0 | 0 | 47193110.4 | 0 | 0 | 130709836.1 | 0 | 43403700 | 161199874.53 | 0 | 0 | 0 | 0 |  | 1146199256.76 | 935464182.554 | 2081663439.314 | 236710249.504 | 61711685.74 | 122953839.91 | 0 | 774366843.5 | 593676895.42 | 0 | 0 | 120967890.71 | 10076160 | 161199874.53 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 |  | 0 | 450 | 0 | 0 | 0 | 45 | 315 | 0 | 0 | 0 | 24 | 96 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 17 | 16 | 30 | 12 | 17 | 0 | 131 | 80 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 172 | 0 | 70 | 29 | 46 | 0 | 43 | 0 | 35 | 8 | 0 | 0 | 0 | 18 | 60 | 9 | 0 | 0 | 2 | 39 | 0 | 49 | 11 | 163 | 0 | 30 | 76 | 0 | 203 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 65 | 0 | 0 | 96 | 0 | 96 | 19 | 12 | 100 | 5 | 0 | 48 | 52 | 17 | 4 | 30 | 17 | 34 | 52 | 28 | 12 | 345 | 51 | 42 | 54 | 17 | 0 | 17 | 21 | 49 | 35 | 250 | 36 | 0 | 530 | 0 | 705 | 0 | 0 | 74 | 0 |  | 877 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 55 | 0 | 22 | 0 | 0 | 55 | 1000 | 220 | 0 | 17 | 5 | 96 | 115 | 0 | 0 | 575 | 37 | 200 | 1014 | 207 | 0 | 0 | 61 |  | 12451 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 316 | 0 | 0 | 0 | 8 | 143 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 17 | 22 | 33 | 12 | 16 | 0 | 132 | 80 | 0 | 0 | 25 | 211 | 0 | 0 | 0 | 0 | 18 | 24 | 51 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 300 | 240 | 202 | 0 | 70 | 10 | 10 | 0 | 43 | 0 | 34 | 8 | 0 | 0 | 0 | 18 | 74 | 13 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 28 | 16 | 0 | 205 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 277 | 0 | 0 | 121 | 0 | 112 | 0 | 25 | 200 | 87 | 268 | 77 | 52 | 17 | 0 | 15 | 17 | 17 | 106 | 9 | 24 | 365 | 60 | 0 | 162 | 17 | 0 | 0 | 0 | 87 | 35 | 230 | 145 | 0 | 610 | 10 | 645 | 0 | 0 | 0 | 0 |  | 874 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 41 | 55 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 29 | 5 | 88 | 35 | 0 | 45 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 70 | 0 | 113 | 0 | 98 | 0 | 0 | 113 | 1160 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 1128 | 0 | 270 | 1011 | 0 | 0 | 0 | 0 |  | 14373 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 17 | 22 | 33 | 12 | 16 | 0 | 132 | 80 | 0 | 0 | 25 | 210 | 0 | 0 | 0 |  | 18 | 80 | 83 | 0 | 0 | 50 | 0 | 20 | 0 | 0 | 0 | 300 | 240 | 210 | 0 | 70 | 35 | 0 | 0 | 43 | 0 | 34 | 8 | 0 | 0 |  | 18 | 90 | 15 | 0 | 0 | 0 | 39 | 0 | 30 | 36 | 163 | 0 | 30 | 40 | 0 | 205 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 280 | 0 | 0 | 125 | 0 | 112 | 0 | 25 | 200 | 120 | 350 | 77 | 52 | 105 | 0 | 15 | 54 | 110 | 106 | 9 | 25 | 365 | 60 | 0 | 162 | 108 | 0 | 17 | 0 | 90 | 35 | 230 | 163 | 0 | 612 | 60 | 650 | 0 | 0 |  |  |  | 880 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 41 | 55 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 30 | 20 | 90 | 35 | 0 | 46 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 70 | 0 | 113 | 0 | 99 | 0 | 0 | 113 | 1244 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 1200 | 0 | 307 | 1000 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 17 | 22 | 33 | 12 | 8 | 0 | 130 | 80 | 0 | 0 | 8 | 205 |  | 0 | 0 | 0 | 12 | 65 | 51 | 0 | 0 | 50 | 0 | 10 | 0 | 0 | 0 | 290 | 240 | 200 | 0 | 70 | 35 | 0 | 0 | 43 | 0 | 34 | 8 | 0 | 0 |  | 18 | 90 | 12 | 0 | 0 | 1.6 | 39 | 0 | 30 | 36 | 163 | 0 | 30 | 40 | 0 | 205 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 200 | 0 | 0 | 98 | 0 | 70 | 20 | 25 | 100 | 100 | 80 | 58 | 17 | 105 | 5 | 15 | 54 | 51 | 52 | 9 | 24 | 350 | 53 | 50 | 72 | 108 | 0 | 17 | 35 | 65 | 35 | 230 | 35 | 0 | 612 | 42 | 600 | 0 | 0 | 70 |  |  | 880 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 30 | 0 | 50 | 28 | 0 | 25 | 0 | 25 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 70 | 0 | 113 | 0 | 35 | 0 | 8 | 113 | 1244 | 220 |  | 17 | 6 | 100 | 115 | 0 | 0 | 1100 | 30 | 307 | 1000 | 170 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 303 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 23 | 33 | 12 | 8 | 0 | 132 | 40 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 300 | 240 | 195 | 0 | 50 | 33 | 0 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 58 | 12 | 0 | 0 | 1 | 39 | 0 | 31 | 36 | 163 | 0 | 30 | 76 | 0 | 207 | 0 | 0 | 0 | 310 | 12 | 5 | 0 | 97 | 0 | 0 | 95 | 0 | 52 | 0 | 25 | 103 | 90 | 80 | 49 | 17 | 17 | 3 | 15 | 17 | 17 | 52 | 9 | 24 | 377 | 52 | 34 | 54 | 17 | 0 | 17 | 19 | 49 | 35 | 230 | 17 | 0 | 612 | 12 | 565 | 0 | 0 | 37 | 0 | 0 | 879 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 16 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 33 | 0 | 3 | 35 | 1200 | 220 | 0 | 17 | 0 | 32 | 115 | 0 | 0 | 1063 | 15 | 250 | 1009 | 70 | 0 | 0 | 8 | 0 |  |  |  | 120909027 | 21961454 | 0 | 87451792 | 49001904 | 1536000 | 3811618 | 167040 | 4893018 |  |  |  | 289731853
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [6 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 120.909 | 21.9615 | 0 | 87.4518 | 49.0019 | 1.536 | 3.8116 | 0.16704 | 4.893
| Minimum Generation |  | 11542 | 8:00
| Highest Generation |  | 14373 | 20:00 | [129 empty] | 0 | [74 empty] | 289.7319
| Day Peak Generation |  | 12451 | 12:00
| Evening Peak Generation |  | 14373 | 20:00 | [204 empty] | 202699852
| HVDC Max Flow |  | 880 | 15:00 | [204 empty] | 202.6999
| HVDC EvPeak Flow |  | 874 | 20:00
| Load factor L.F |  | 91.06% | [168 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-09-08
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-09-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12451 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 12595
Evening Peak Generation : |  |  | 14373 | MW Hour : | 20:00 | Available Max Generation : |  | 15540
E.P. Demand (at gen end) : |  |  | 15500 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 15900
Maximum Generation : |  |  | 14373 | MW Hour : | 20:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 314.1191 | System Load Factor : | 91.06% | Load Shed : |  | 340
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 504 | MW at | 5:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-09-08
Actual : |  | 108.26 | Ft.(MSL) , | Rule curve : | 100.61 | Ft.( MSL )
Gas Consumed : |  | Total = | 877.36 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 359664089.414 | Adani: | 161199874.53
: |  |  | Coal : | 593676895.42 | Oil : | 895334734.21 | Total : | 2009875593.574
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 225 | 5400:00 | 4695.4665 |  |  | 0 | -11.34%
Chittagong Area |  | 0 | 0:00 | 1291.088 |  |  | 0 | -9.43%
Khulna Area |  | 0 | 0:00 | 1808.7915 |  |  | 0 | -9.022%
Rajshahi Area |  | 147 | 3528:00 | 1572.379 |  |  | 90 | -8.59%
Cumilla Area |  | 217 | 5208:00 | 1293.6804 |  |  | 80 | -8.858%
Mymensingh Area |  | 257 | 6168:00 | 962.2882 |  |  | 80 | -8.483%
Sylhet Area |  | 105 | 2520:00 | 539.2681 |  |  | 40 | -9.199%
Barisal Area |  | 0 | 0:00 | 449.5289 |  |  | 0 | -8.414%
Rangpur Area |  | 125 | 3000:00 | 879.1971 |  |  | 50 | -8.423%
Total |  | 1076 |  | 13491.6877 |  |  | 340
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1, 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:00 | 12:16 | Palashbari 132/33kV S/S TR2-404T HT Scheduled S/D Due to T2 33kv Bus Red Hot Maintenance |  |  |  |  | 45.0MW load interruption.
| 08:08 | Barapukuria-Rangpur 132 kV Ckt-1 is restored.
| 08:11 | Barapukuria-Rangpur 132 kV Ckt-2 is restored.
08:13 | 10:20 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Red-hot Maintenance
08:15 | 10:19 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Red-hot Maintenance
| 08:20 | Kushtia 132/33kV S/S T2 HT is restored.
| 08:21 | Kushtia 132/33kV S/S T2 LT is restored.
08:25 | 14:18 | Kushtia 132/33kV S/S T-3 LT Project Work S/D Due to 33 kV T-3 bus extension, bus PT, and isolator |  |  |  |  | 25.0MW load interruption.
installation work.
08:26 | 14:17 | Kushtia 132/33kV S/S T-3 HT Project Work S/D Due to 33 kV T-3 bus extension, bus PT, and
isolator installation work.
| 08:29 | Noapara 132/33kV S/S T-1 HT is restored.
| 08:29 | Noapara 132/33kV S/S T-1 LT is restored.
08:57 | 11:49 | Amnura 132/33kV S/S Bus-33KV Scheduled S/D Due to 33KV Bus Section -4 Shutdown.
08:57 | 11:49 | Amnura 132/33kV S/S T-3 (426T) LT Scheduled S/D Due to 33KV Section -4 Shutdown.
08:57 | 11:48 | Amnura 132/33kV S/S T-3 (426T) HT Scheduled S/D Due to 33KV Section -4 Shutdown.
09:06 | 11:06 | Ramganj 132/33kV S/S Ramgonj- Desh Energy Ckt-01 Scheduled S/D Due to temperature raising |  |  |  |  | 25.0MW load interruption.
point maintenance
09:06 | 12:56 | Shariatpur 132/33kV S/S T2-416T LT Scheduled S/D Due to Oil Leakage Maintenance.
09:07 | 12:55 | Shariatpur 132/33kV S/S T2-416T HT Scheduled S/D Due to Oil Leakage Maintenance.
09:22 |  | Rangpur 132/33kV S/S Rangpur-GTPS Forced S/D Due to 132kv Line Fault
09:45 | 18:48 | Ghatail 132/33kV S/S Bus-2 Scheduled S/D Due to 33kv feeder source and Load side Clamp and Lugs change by pbs. |  |  |  |  | 25.0MW load interruption.
10:22 | 14:47 | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Payra 400/132/33kV end Due to Red hot maintenance
11:24 | 16:22 | Chandpur 132/33kV S/S 422T HT Scheduled S/D
11:24 | 16:24 | Chandpur 132/33kV S/S 422T LT Scheduled S/D
11:31 |  | Bibiyana-III 400 MW CCPP Tripped with remarks:- GT
12:00 |  | Day Peak Generation: 12451 MW.
| 12:16 | Palashbari 132/33kV S/S TR2-404T LT is restored.
13:32 | 14:04 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Scheduled S/D Due to Red hot maintenance
13:33 | 14:04 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT Forced S/D Due to Red hot maintenance
13:40 |  | Bibiyana-III 400 MW CCPP Synchronized with remarks:- GT
13:40 | 13:54 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Tripped from Sirajganj 132/33kV end showing Distance Relay (21) relays.
| 14:08 | Khulna (C) S/S TR-1 425T HT is restored.
| 14:09 | Khulna (C) S/S TR-1 425T LT is restored.
15:23 | 17:10 | Patuakhali-Payra 132kV Ckt-2 Forced S/D from Payra 400/132/33kV end Due to Red hot maintenance and from
Patuakhali 132/33kV end Due to Aldc
15:23 | 17:10 | Patuakhali-Payra 132kV Ckt-2 Forced S/D from Payra 400/132/33kV end Due to Red hot maintenance and from
Patuakhali 132/33kV end Due to Aldc
| 15:50 | Madanganj 132/33kV S/S Madanganj -Summit 102 MW 132 kv Ckt is restored.
20:00 |  | Evening Peak Gen. 14374 MW
20:21 | 20:48 | Ashuganj-Ghorasal 132kV Ckt-2 Tripped from Ashuganj 230/132/33kV end showing Distance A relays Due to Trip
23:15 | 00:15 | Chowmuhani 132/33kV S/S TR2-425T LT Forced S/D Due to 132/33 KV Tr-02 shutdown for 33 kv Bus Isulator |  |  |  |  | 36.0MW load interruption.
maintenance. Load shed will occur 36.0MW. Informed to all utilities and XEN sir, GMD, PGCB, Cumilla.
Work will be done by BPDB, Noakhali
02:49 | 02:51 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing O/C, E/F ABC ints. relays Due to Bad weather
02:54 | 03:04 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT Tripped showing F51 relays Due to Over Current
| 03:04 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT is restored.
07:00 |  | Minimum Generation = 12,609MW
07:25 |  | Maniknagar 132/33kV S/S Mero Rail - 2 Scheduled S/D Due to পদ্মা সেতু রেল সংযোগ প্রকল্পের কাজের
নিরাপত্তার স্বার্থে। শাট ডাউন নেন জনাব আলী মোহাম্মদ সালেহ, সহকারী ব্যবস্থাপক, মেট্রোরেল।
07:54 |  | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Coxsbazar 132/33kV end Due to Shutdown has been
taken at Matarbari side. and from Dohazari 132/33kV end Due to Due to Matarbari Grid

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-09-07
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 402 | 9579600
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10212500
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1291832
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve NENP
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
| Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 316 | 7513476
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 540288 | Engine problem
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 638280
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 143 | 1929600
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 684472 | Fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 670293
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 39 | 895800 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 756360
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 12 | 339700 | Engine problem
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 240000 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 277 | 3048545 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 112 | 2065392 | Engine problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 841920 | Fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 60 | 1227840 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1964160
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 198077
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 837000 | Fuel shortage
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5915 | 2316 | 45475135
35 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 140317
37 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 111780
38 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Meghnaghat Bus section limitation
39 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 212 | 4893018
40 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 211 | 4737386
41 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
42 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 963491 | Meghnaghat Bus section limitation
43 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 242064 | Meghnaghat Bus section limitation
44 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 425703 | Meghnaghat Bus section limitation
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0
45 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 551040 | Fuel shortage
46 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 545760
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31281
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 825491 | Fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 743804 | Meghnaghat Bus section limitation
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 1492909 | Meghnaghat Bus section limitation
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 550080 | Fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 677455 | Meghnaghat Bus section limitation
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 145 | 879854 | Engine problem
55 | SS Power I |  | SS Power | 2*612 | 1224 | 610 | 14012726 | Unit-1 under maint
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 10 | 167040
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 645 | 16610909 | coal shortage.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 2087 | 48602108
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 202 | 3944000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7479400 | Gas shortage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6066000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5866300 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 540288 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 10 | 504000 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 66909 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 994640 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 87 | 913309 | Fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 34 | 861676 | Engine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1472570 | Machine problem.
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3104640
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
71 | Impoprt (Tripura) |  | Imported power | 0 | 160 | 74 | 1536000
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 189211 | Fuel shortage
73 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 399250 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
74 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1625640 | Engine problem
75 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 513240 | Fuel shortage
76 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 87 | 1392960 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 461882
| Cumilla Area Total |  |  |  | 2917 | 1728 | 37931915
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 13 | 380160 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14800
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 121 | 2352000 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1365600 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 338130
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 240240 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 241560 | Bad Weather
| Mymensingh Area Total |  |  |  | 646 | 229 | 4932490
84 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 39 | 925000 | Machine problem.
85 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
86 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3626264
87 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
88 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 324600 | Gas shortage
89 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 205776 | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 60384 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 901920 | Gas shortage Unit-8 under S/D
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 16 | 600960 | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 205 | 5127380
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
96 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 263040 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7212500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 268 | 5045000 | ST under maint
99 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 365 | 8573200 | Machine problem.
| Sylhet Area Total |  |  |  | 2417 | 1388 | 32866024
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 874 | 21961454
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 272640 | Engine problem
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 55 | 307072 | Fuel shortage
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 8039808 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 1144800 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 591120
109 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 1128 | 17905457 | Aminbazar Transformer limitation
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 2488 | 50222351
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 537984 | Aminbazar Transformer limitation
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 199930
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 3038000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1160 | 28288700 | Aminbazar Transformer limitation
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5374860
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 448800 | Fuel shortage
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 270 | 5826000 | Aminbazar Transformer limitation
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 4125
| Barisal Area Total |  |  |  | 2236 | 1823 | 43718399
118 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 29 | 703785 | Engine problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 79220 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 35 | 659290
122 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 264485 | Engine problem
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8957454 | FGMO
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 315148 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 138852 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 502256 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1790784
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1790592
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33120
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1011 | 24387273 | coal shortage.
135 | Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 396750
| Rajshahi Area Total |  |  |  | 3449 | 1891 | 40019009
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4808000 | coal shortage.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1193078 | Engine problem
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 17491
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2720064
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 250102
144 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1362960
| Rangpur Area Total |  |  |  | 950 | 423 | 10351695
| Total |  |  |  | 27086 | 14373 | 314119126
| Eastern Grid Total |  |  |  | 16752 | 7748 | 169807672
| Western Grid Total |  |  |  | 10334 | 6625 | 144311454
| National Grid Total |  |  |  | 27086 | 14373 | 314119126
*Data collected from respective power station over telephone.
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-09-07
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8866.64 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4767.8 | MW
i) Dhaka area |  |  | 4566.64 |  | MW | i) Khulna area |  |  |  | 1791.8 | MW
ii) Chattogram area |  |  | 1288 |  | MW | ii) Barishal area |  |  |  | 490 | MW
iii) Cumilla area |  |  | 1287 |  | MW | iii) Rajshahi area |  |  |  | 1523 | MW
iv) Mymensingh area |  |  | 1084 |  | MW | iv) Rangpur area |  |  |  | 963 | MW
v) Sylhet area |  |  | 641 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13634.44 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 05:00 | 67 | Jamalpur | 103 | 20:00 | 133 | Rahim | 53 | 17:00
2 | AKSML | 107 | 11:00 | 68 | Jashore | 144 | 19:00 | 134 | Rajbari | 88 | 19:00
3 | Aftabnagar | 38 | 18:30 | 69 | Jhenaidah | 135 | 19:00 | 135 | Rajendrapur | 106 | 21:00
4 | Agargaon | 114 | 13:00 | 70 | Joydebpur | 193 | 19:30 | 136 | Rajshahi | 139 | 00:00
5 | Agrabad | 92 | 16:00 | 71 | Joypurhat | 67 | 00:00 | 137 | Rajshahi-230 | 73 | 00:00
6 | Amnura | 73 | 00:00 | 72 | Juldah | 19 | 09:00 | 138 | Ramganj | 106 | 07:00
7 | Ashuganj | 100 | 20:00 | 73 | KSRM | 29 | 09:00 | 139 | Rampur | 42 | 18:30
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 273 | 20:00 | 140 | Rangamati | 17 | 22:00
9 | BSRM | 84 | 00:00 | 75 | Kachua | 80 | 20:00 | 141 | Rangpur | 157 | 09:00
10 | Bagerhat | 100 | 01:00 | 76 | Kallyanpur | 123 | 00:00 | 142 | Ruppur | 6 | 10:00
11 | Bakulia | 112 | 11:00 | 77 | Kalurghat | 36 | 16:00 | 143 | SSM | 14 | 23:00
12 | Banani | 55.6 | 13:00 | 78 | Kamrangirchar | 55 | 13:00 | 144 | Saidpur | 110 | 09:00
13 | Bangabhaban | 10 | 11:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 135 | 22:00
14 | Barapukuria | 68 | 20:00 | 80 | Kazla | 120 | 13:00 | 146 | Satmasjid | 110 | 19:00
15 | Barguna | 23 | 00:00 | 81 | Keranigonj | 72 | 19:00 | 147 | Savar | 208 | 10:00
16 | Barishal | 112 | 19:30 | 82 | Khagrachori | 32 | 00:00 | 148 | SevenRings | 16.59 | 12:00
17 | Barishal-230 | 104 | 22:00 | 83 | Khulna | 85 | 18:30 | 149 | ShahCement | 25 | 00:00
18 | Baroaulia | 60 | 11:00 | 84 | Khulshi | 173 | 15:00 | 150 | Shahjadpur | 74 | 21:00
19 | Baroirhat | 64 | 22:00 | 85 | Kishoreganj | 134 | 00:00 | 151 | Shahjibazar | 120 | 19:30
20 | Bashundhara | 183 | 13:00 | 86 | Kodda | 279 | 21:00 | 152 | Shahmirpur | 57 | 00:00
21 | BashundharaCement | 1 | 07:00 | 87 | Kulaura | 48 | 04:00 | 153 | Shariatpur | 94 | 22:00
22 | Beanibazar | 74 | 05:00 | 88 | Kurigram | 72 | 09:00 | 154 | Sherpur | 128 | 00:00
23 | Benapole | 66 | 14:00 | 89 | Kushtia | 153 | 19:00 | 155 | Shikalbaha | 24 | 23:00
24 | Bhaluka | 120 | 08:00 | 90 | Lalbag | 85 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 55 | 02:00 | 91 | Lalmonirhat | 56 | 00:00 | 157 | Shitalakhya | 85.8 | 15:00
26 | Bhangura | 45 | 00:00 | 92 | MI_Cement | 15.2 | 13:00 | 158 | Sholosohor | 49 | 15:00
27 | Bheramara(GK) | 71 | 21:00 | 93 | Madanganj | 34 | 18:30 | 159 | Shyampur | 160 | 12:00
28 | Bhulta | 255 | 04:00 | 94 | Madaripur | 122 | 22:00 | 160 | Siddhirganj | 131 | 12:00
29 | Bog-Sherpur | 68 | 00:00 | 95 | Madartek | 92.09 | 23:00 | 161 | Sirajganj | 112 | 22:00
30 | Bogura | 165 | 00:00 | 96 | Madunaghat | 61 | 19:00 | 162 | Sonargaon | 86 | 18:30
31 | Borhanuddin | 88 | 00:00 | 97 | Magura | 69 | 19:00 | 163 | Sreemongol | 74 | 20:00
32 | Brahmanbaria | 171 | 03:00 | 98 | Mahasthangarh | 82 | 00:00 | 164 | Sreepur | 106 | 20:00
33 | Cantonment | 118 | 13:00 | 99 | Manikganj | 112 | 10:00 | 165 | Srinagar | 46.4 | 18:30
34 | Chandpur | 59 | 20:00 | 100 | Maniknagar | 65 | 13:00 | 166 | Sunamganj | 56 | 05:00
35 | Chandraghona | 34 | 00:00 | 101 | Matarbari | 47 | 01:00 | 167 | Sylhet | 42 | 05:00
36 | Chapai | 73 | 00:00 | 102 | Matuail | 61 | 12:00 | 168 | Sylhet-132 | 139 | 22:00
37 | Charsaidpur | 39 | 11:00 | 103 | Millgate | 128 | 16:00 | 169 | TK | 34 | 02:00
38 | Chauddagram | 58 | 02:00 | 104 | Mirpur | 150 | 19:00 | 170 | Tangail | 182 | 21:00
39 | Chhatak | 33 | 05:00 | 105 | Mirsorai | 4 | 12:00 | 171 | Thakurgaon | 112 | 19:00
40 | Chowmuhani | 180 | 07:00 | 106 | Mirzapur | 38 | 15:00 | 172 | Tongi | 125 | 14:00
41 | Chuadanga | 119 | 19:30 | 107 | Mithapukur | 68 | 20:00 | 173 | Ullahpara | 28 | 21:00
42 | Coxsbazar | 109 | 00:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 64 | 23:00
43 | Cumilla(N) | 154 | 20:00 | 109 | Mogbazar | 106.3 | 13:00 | 175 | Uttara | 87 | 18:30
44 | Cumilla(S) | 165 | 18:30 | 110 | Mongla | 28 | 00:00 | 176 | UttaraNew | 64 | 23:00
45 | Daudkandi | 130 | 07:00 | 111 | Motijheel | 41 | 13:00 | 177 | Zigatola | 103 | 18:30
46 | Dhaka | 42 | 12:00 | 112 | Munshiganj | 108 | 18:30
47 | Dhamrai | 136 | 18:30 | 113 | Mymensingh | 240 | 19:30
48 | Dhanmondi | 134 | 13:00 | 114 | Naogaon | 143 | 00:00
49 | Dohazari | 100 | 00:00 | 115 | Narail | 62 | 22:00
50 | Faridpur | 179 | 22:00 | 116 | Narinda | 76.5 | 13:00
51 | Fatullah | 94 | 12:00 | 117 | Narshingdi | 156 | 19:00
52 | Fenchuganj | 40 | 03:00 | 118 | Natore | 149 | 00:00
53 | Feni | 99 | 21:00 | 119 | Nawabganj | 50.6 | 18:30
54 | GPH | 93 | 12:00 | 120 | Netrakona | 102 | 20:00
55 | Ghatail | 48 | 20:00 | 121 | New | 57.5 | 10:00
56 | Ghorashal | 58 | 20:00 | 122 | Niamatpur | 79 | 00:00
57 | Goalpara | 40 | 23:00 | 123 | Noapara | 53 | 15:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-09-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 388 | 07:00 | 372 | 23:00 | Kaliakoir | 372 | 06:00 | 358 | 11:00
| Ashuganj | 406 | 7:00 | 389 | 11:00 | Madunaghat | 403 | 01:00 | 394 | 14:00
| Bhulta | 394 | 06:00 | 377 | 12:00 | Meghnaghat | 381 | 08:00 | 370 | 11:00
| Bibiana | 395 | 18:30 | 386 | 11:00 | Payra | 409 | 07:00 | 401 | 23:00
| BIPTC | 401 | 06:00 | 389 | 00:00 | Rahanpur | 401 | 12:00 | 391 | 00:00
| Bogura | 390 | 16:00 | 378 | 00:00 | Rampal | 401 | 07:00 | 390 | 02:00
| Gopalganj | 398 | 07:00 | 382 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 230 | 06:00 | 219 | 11:00 | Haripur | 231 | 06:00 | 221 | 12:00
| AKSML | 238 | 13:00 | 227 | 01:00 | Hasnabad | 230 | 06:00 | 219 | 11:00
| Aminbazar | 230 | 04:00 | 220 | 10:00 | Hathazari | 239 | 05:00 | 231 | 22:00
| Ashuganj | 235 | 07:00 | 224 | 13:00 | Ishurdi | 235 | 07:00 | 225 | 20:00
| Ashuganj-400 | 235 | 7:00 | 224 | 13:00 | Jhenaidah | 229 | 08:00 | 213 | 23:00
| Baghabari | 230 | 05:00 | 224 | 19:30 | Kaliakoir | 231 | 06:00 | 222 | 11:00
| Barapukuria | 222 | 07:00 | 211 | 00:00 | Keranigonj | 229 | 06:00 | 219 | 11:00
| Barapukuria-230 | 222 | 7:00 | 211 | 0:00 | Khulna(S) | 230 | 08:00 | 216 | 23:00
| Barishal | 236 | 07:00 | 227 | 23:00 | Madunaghat | 238 | 01:00 | 231 | 13:00
| Bheramara | 233 | 07:00 | 222 | 20:00 | Maniknagar | 231 | 06:00 | 220 | 12:00
| Bhulta | 236 | 18:30 | 221 | 12:00 | Meghnaghat | 236 | 00:00 | 230 | 11:00
| Bibiana | 227 | 17:00 | 220 | 11:00 | Meghnaghat-400 | 234 | 06:00 | 224 | 11:00
| BIPTC | 235 | 07:00 | 223 | 20:00 | Mirsorai | 236 | 19:00 | 228 | 02:00
| Bogura | 228 | 17:00 | 222 | 00:00 | Rajshahi | 233 | 16:00 | 223 | 20:00
| Bogura-400 | 230 | 13:00 | 222 | 00:00 | Rampal | 229 | 07:00 | 218 | 23:00
| Borhanuddin | 241 | 07:00 | 234 | 19:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 236 | 19:00 | 229 | 16:00 | Rampura | 231 | 04:00 | 219 | 12:00
| Cumilla(N) | 228 | 06:00 | 222 | 11:00 | Shikalbaha | 238 | 06:00 | 229 | 12:00
| Faridpur | 236 | 07:00 | 225 | 23:00 | Shyampur | 230 | 06:00 | 220 | 11:00
| Fenchuganj | 228 | 18:30 | 222 | 03:00 | Siddhirganj | 231 | 00:00 | 223 | 12:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 235 | 07:00 | 230 | 00:00
| Ghorashal-230 | 231 | 06:00 | 220 | 12:00 | Sreepur | 228 | 06:00 | 220 | 20:00
| Gopalganj | 235 | 07:00 | 226 | 23:00 | Tongi | 233 | 04:00 | 220 | 11:00
| GPH | 235 | 06:00 | 229 | 14:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 136 | 07:00 | 125 | 12:00 | Kushtia | 136 | 07:00 | 128 | 00:00
| Agargaon | 134 | 06:00 | 126 | 11:00 | Lalbag | 134 | 06:00 | 125 | 12:00
| Agrabad | 135 | 07:00 | 128 | 15:00 | Lalmonirhat | 131 | 03:00 | 121 | 00:00
| AKS | 133 | 01:00 | 127 | 15:00 | Madanganj | 132 | 06:00 | 125 | 10:00
| Aminbazar | 138 | 02:00 | 126 | 11:00 | Madaripur | 132 | 07:00 | 126 | 21:00
| Amnura | 139 | 07:00 | 124 | 00:00 | Madartek | 135 | 06:00 | 124 | 12:00
| Ashuganj | 137 | 04:00 | 134 | 11:00 | Madunaghat | 135 | 02:00 | 130 | 14:00
| Bagerhat | 135 | 08:00 | 119 | 23:00 | Magura | 136 | 07:00 | 125 | 23:00
| Bakulia | 135 | 00:00 | 130 | 11:00 | Mahasthangarh | 135 | 12:00 | 127 | 00:00
| Banani | 134 | 06:00 | 124 | 13:00 | Manikganj | 130 | 19:00 | 121 | 03:00
| Bangabhaban | 131 | 05:00 | 121 | 13:00 | Maniknagar | 131 | 06:00 | 123 | 11:00
| Barapukuria | 139 | 12:00 | 129 | 00:00 | Matarbari | 122 | 10:00 | 116 | 02:00
| Barguna | 135 | 07:00 | 129 | 23:00 | Matuail | 131 | 05:00 | 125.7 | 12:00
| Barishal | 133 | 07:00 | 127 | 20:00 | Millgate | 135 | 07:00 | 124 | 12:00
| Barishal-230 | 134 | 07:00 | 126 | 23:00 | Mirpur | 138 | 06:00 | 129 | 11:00
| Baroaulia | 135 | 07:00 | 131 | 17:00 | Mirzapur | 129 | 18:30 | 120 | 19:30
| Baroirhat | 132 | 08:00 | 122 | 14:00 | Mithapukur | 134 | 15:00 | 124 | 04:00
| Bashundhara | 136 | 07:00 | 124 | 12:00 | MI_Cement | 133 | 00:00 | 126.5 | 11:00
| BashundharaCement | 132 | 06:00 | 125 | 11:00 | Modern | 135 | 00:00 | 129 | 14:00
| Beanibazar | 128 | 23:00 | 122 | 01:00 | Mogbazar | 136 | 06:00 | 126 | 12:00
| Benapole | 133 | 07:00 | 121 | 22:00 | Mongla | 135 | 08:00 | 118 | 23:00
| Bhaluka | 126 | 06:00 | 119 | 11:00 | Motijheel | 131 | 05:00 | 122 | 12:00
| Bhandaria | 130 | 06:00 | 117 | 23:00 | Munshiganj | 131 | 06:00 | 126 | 11:00
| Bhangura | 135 | 06:00 | 130 | 20:00 | Mymensingh | 132 | 22:00 | 114 | 20:00
| Bheramara | 136 | 07:00 | 131 | 20:00 | Naogaon | 132 | 13:00 | 124 | 00:00
| Bheramara(GK) | 136 | 07:00 | 131 | 20:00 | Narail | 137 | 08:00 | 125 | 22:00
| Bhulta | 122 | 02:00 | 117 | 11:00 | Narinda | 131 | 8:00 | 122 | 13:00
| Bog-Sherpur | 135 | 16:00 | 130 | 00:00 | Narshingdi | 124 | 01:00 | 117 | 11:00
| Bogura | 137 | 13:00 | 131 | 00:00 | Natore | 138 | 23:00 | 128 | 20:00
| Bogura-230 | 138 | 18:30 | 132 | 00:00 | Nawabganj | 134 | 07:00 | 126 | 11:00
| Brahmanbaria | 130 | 13:00 | 122 | 20:00 | Netrakona | 133 | 23:00 | 118 | 13:00
| Cantonment | 134 | 06:00 | 125 | 12:00 | New | 134 | 03:00 | 125 | 11:00
| Chandpur | 135 | 22:00 | 126 | 03:00 | Niamatpur | 134 | 07:00 | 129 | 00:00
| Chandraghona | 137 | 07:00 | 133 | 11:00 | Noapara | 136 | 07:00 | 124 | 23:00
| Chapai | 131 | 15:00 | 125 | 00:00 | Pabna | 135 | 09:00 | 128 | 20:00
| Charsaidpur | 133 | 06:00 | 126 | 11:00 | Palashbari | 132 | 12:00 | 121 | 00:00
| Chauddagram | 131 | 18:30 | 123 | 02:00 | Panchagarh | 140 | 17:00 | 123 | 18:30
| Chhatak | 127 | 12:00 | 121 | 20:00 | Patuakhali | 136 | 06:00 | 131 | 19:30
| Chowmuhani | 127 | 17:00 | 120 | 04:00 | Payra | 137 | 08:00 | 133 | 20:00
| Chuadanga | 133 | 07:00 | 117 | 00:00 | PHP | 131 | 08:00 | 121 | 15:00
| Coxsbazar | 122 | 08:00 | 117 | 10:00 | Postogola | 134 | 04:00 | 128 | 11:00
| Cumilla(N) | 132 | 17:00 | 128 | 02:00 | Purbachal | 137 | 06:00 | 124 | 12:00
| Cumilla(S) | 132 | 02:00 | 126 | 15:00 | Purbasadipur | 136 | 17:00 | 120 | 00:00
| Daudkandi | 129 | 06:00 | 125 | 10:00 | Rahanpur | 136 | 12:00 | 131 | 00:00
| Dhaka | 135 | 06:00 | 125 | 13:00 | Rahim | 131 | 06:00 | 126 | 12:00
| Dhamrai | 132 | 00:00 | 125 | 20:00 | Rajbari | 132 | 07:00 | 125 | 23:00
| Dhanmondi | 136 | 06:00 | 125 | 12:00 | Rajendrapur | 133 | 19:00 | 122 | 03:00
| Dohazari | 131 | 07:00 | 124 | 13:00 | Rajshahi | 134 | 07:00 | 129 | 20:00
| Faridpur | 132 | 07:00 | 126 | 23:00 | Rajshahi-230 | 135 | 16:00 | 120 | 00:00
| Fatullah | 133 | 06:00 | 127 | 11:00 | Ramganj | 130 | 17:00 | 119 | 05:00
| Fenchuganj | 136 | 15:00 | 129 | 02:00 | Rampur | 135 | 08:00 | 129 | 15:00
| Feni | 129 | 18:00 | 124 | 05:00 | Rampura | 135 | 04:00 | 125 | 12:00
| Ghatail | 128 | 18:30 | 120 | 13:00 | Rangamati | 136 | 08:00 | 131 | 18:30
| Ghorashal | 139 | 05:00 | 131 | 13:00 | Rangpur | 133 | 13:00 | 122 | 00:00
| Goalpara | 138 | 07:00 | 125 | 23:00 | Ruppur | 137 | 17:00 | 131 | 20:00
| Gollamari | 136 | 07:00 | 126 | 23:00 | Saidpur | 136 | 17:00 | 121 | 00:00
| Gopalganj | 132 | 06:00 | 125 | 22:00 | Satkhira | 132 | 08:00 | 118 | 23:00
| Gopalganj-400 | 133 | 07:00 | 126 | 23:00 | Satmasjid | 134 | 06:00 | 125 | 12:00
| Gulshan | 135 | 07:00 | 125 | 12:00 | Savar | 137 | 01:00 | 127 | 11:00
| Halishahar | 136 | 07:00 | 129 | 11:00 | SevenRings | 139 | 06:00 | 131 | 13:00
| Haripur | 131 | 06:00 | 126 | 12:00 | ShahCement | 133 | 06:00 | 126 | 11:00
| HaripurSBU | 131 | 06:00 | 126 | 12:00 | Shahjadpur | 140 | 04:00 | 134 | 19:30
| Hasnabad | 135 | 05:00 | 128 | 11:00 | Shahjibazar | 131 | 13:00 | 121 | 20:00
| Hathazari | 139 | 05:00 | 133 | 14:00 | Shahmirpur | 135 | 07:00 | 130 | 14:00
| Ishurdi | 137 | 07:00 | 132 | 20:00 | Shariatpur | 131 | 08:00 | 123 | 23:00
| Jaldhaka | 134 | 17:00 | 117 | 03:00 | Sherpur | 133 | 21:00 | 120 | 13:00
| Jamalpur | 135 | 23:00 | 122 | 13:00 | Shikalbaha | 125 | 07:00 | 119 | 11:00
| Jashore | 135 | 07:00 | 122 | 23:00 | Shikalbaha-230 | 138 | 01:00 | 130 | 12:00
| Jhenaidah | 138 | 07:00 | 127 | 23:00 | Shitalakhya | 133 | 00:00 | 126.5 | 11:00
| Jhenaidah-230 | 138 | 08:00 | 128 | 23:00 | Sholosohor | 135 | 00:00 | 130 | 14:00
| Joydebpur | 140 | 05:00 | 126 | 15:00 | Shyampur | 134 | 19:00 | 128 | 00:00
| Joypurhat | 130 | 13:00 | 121 | 00:00 | Shyampur-230 | 133 | 06:00 | 126 | 11:00
| Juldah | 136 | 06:00 | 129 | 14:00 | Siddhirganj | 132 | 06:00 | 126 | 11:00
| Kabirpur | 133 | 18:30 | 123 | 11:00 | Sirajganj | 134 | 17:00 | 127 | 20:00
| Kachua | 132 | 18:30 | 126 | 02:00 | Sonargaon | 130 | 00:00 | 125 | 11:00
| Kaliakoir | 133 | 06:00 | 125 | 11:00 | Sreemongol | 131 | 14:00 | 124 | 02:00
| Kallyanpur | 132 | 06:00 | 125 | 11:00 | Sreepur | 129 | 04:00 | 123 | 20:00
| Kalurghat | 137 | 07:00 | 131 | 11:00 | Srinagar | 134 | 05:00 | 126 | 12:00
| Kamrangirchar | 134 | 05:00 | 124 | 11:00 | SSM | 140 | 00:00 | 136 | 16:00
| Kaptai | 138 | 8:00 | 134 | 15:00 | Sunamganj | 125 | 16:00 | 119 | 05:00
| Kazla | 131 | 07:00 | 121 | 13:00 | Sylhet | 129 | 23:00 | 124 | 03:00
| Keranigonj | 134 | 06:00 | 127 | 11:00 | Sylhet-132 | 129 | 17:00 | 125 | 11:00
| Khagrachori | 136 | 08:00 | 130 | 22:00 | Tangail | 128 | 22:00 | 119 | 14:00
| Khulna | 136 | 07:00 | 124 | 23:00 | Thakurgaon | 140 | 17:00 | 123 | 00:00
| Khulna(S) | 137 | 08:00 | 126 | 22:00 | TK | 136 | 08:00 | 130 | 13:00
| Khulshi | 134 | 06:00 | 128 | 14:00 | Tongi | 135 | 04:00 | 127 | 11:00
| Kishoreganj | 127 | 04:00 | 123 | 08:00 | Ullahpara | 135 | 16:00 | 130 | 20:00
| Kodda | 135 | 05:00 | 122 | 03:00 | Ullon | 135 | 05:00 | 124 | 12:00
| KSRM | 137 | 07:00 | 131 | 11:00 | Uttara | 138 | 07:00 | 129 | 11:00
| Kulaura | 132 | 13:00 | 128 | 20:00 | UttaraNew | 137 | 06:00 | 128 | 11:00
| Kurigram | 133 | 15:00 | 120 | 09:00 | Zigatola | 134 | 07:00 | 126 | 13:00

## L-Curve
Date | 2024-09-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 710 | 7361 | 6608 | 13969 |  |  |  | QF-LDC-11
0:30 | 636 | 7379 | 6358.5 | 13737.5 | Date: | 2024-09-07
1:00 | 562 | 7397 | 6109 | 13506
1:30 | 588 | 7256 | 6078.5 | 13334.5
2:00 | 614 | 7115 | 6048 | 13163
2:30 | 587 | 7070.5 | 5973 | 13043.5 | [5 empty] | Gen. at Eve. Peak | 14373 | 14373 MW (20:00 )
3:00 | 560 | 7026 | 5898 | 12924 | [6 empty] | 20:00
3:30 | 579 | 6970 | 5895 | 12865 | [5 empty] | Gen. at Day Peak | 12451 | 12451 MW (12:00 )
4:00 | 598 | 6914 | 5892 | 12806 | [6 empty] | 12:00
4:30 | 551 | 6821 | 5838 | 12659 | [5 empty] | Highest Generation | 14373
5:00 | 504 | 6728 | 5784 | 12512 | [6 empty] | 20:00
5:30 | 508 | 6685.5 | 5607 | 12292.5
6:00 | 512 | 6643 | 5430 | 12073
6:30 | 608 | 6600 | 5330 | 11930
7:00 | 704 | 6557 | 5230 | 11787
7:30 | 758 | 6501.5 | 5163 | 11664.5
8:00 | 812 | 6446 | 5096 | 11542
8:30 | 877 | 6487 | 5222 | 11709
9:00 | 942 | 6528 | 5348 | 11876
9:30 | 1001 | 6584.5 | 5382 | 11966.5
10:00 | 1060 | 6641 | 5416 | 12057
10:30 | 1135 | 6744 | 5443 | 12187
11:00 | 1210 | 6847 | 5470 | 12317
11:30 | 1286 | 6782.5 | 5601.5 | 12384
12:00 | 1362 | 6718 | 5733 | 12451
12:30 | 1370 | 6748.5 | 5753.5 | 12502
13:00 | 1378 | 6779 | 5774 | 12553
13:30 | 1353 | 6825 | 5795 | 12620
14:00 | 1328 | 6871 | 5816 | 12687
14:30 | 1321 | 6859.5 | 5758.5 | 12618
15:00 | 1314 | 6848 | 5701 | 12549
15:30 | 1251 | 6859 | 5636.5 | 12495.5
16:00 | 1188 | 6870 | 5572 | 12442
16:30 | 1171 | 6851.5 | 5575 | 12426.5
17:00 | 1154 | 6833 | 5578 | 12411
17:30 | 1089 | 6886.5 | 5643.5 | 12530
18:00 | 1024 | 6940 | 5709 | 12649
18:30 | 894 | 7242 | 6020.5 | 13262.5
19:00 | 764 | 7544 | 6332 | 13876
19:30 | 758 | 7743 | 6589 | 14332
20:00 | 750 | 7748 | 6625 | 14373 |  |  |  | Executive Engineer
20:30 | 730 | 7718.5 | 6584.5 | 14303 |  |  |  | Network Operation Division
21:00 | 710 | 7689 | 6544 | 14233
21:30 | 719 | 7595.5 | 6585 | 14180.5
22:00 | 728 | 7502 | 6626 | 14128 |  |  |  |  | Page 6 of 7
22:30 | 746 | 7447 | 6659.5 | 14106.5
23:00 | 764 | 7392 | 6693 | 14085
23:30 | 737 | 7376.5 | 6650.5 | 14027
24:00 | 710 | 7361 | 6608 | 13969
14373 MW (20:00 )
12451 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-09-07 |  | Energy |  | 314119126
[16 empty] | 2024-09-07 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3434 | 874 | 1675 | 0 | 2023 | 4184 | 212 | 0 | 483 | 74 | 1006 | 0 | 4 | 1366.605
0:30 | 3424 | 876 | 1651 | 0 | 2103 | 3933.5 | 211.5 | 0 | 453 | 69 | 1014 | 0 | 2.5 | 1134.0625 |  |  | Date: | 44080
1:00 | 3414 | 878 | 1627 | 0 | 2183 | 3683 | 211 | 0 | 423 | 64 | 1022 | 0 | 1 | 901.52
1:30 | 3433.5 | 878 | 1639.5 | 0 | 2055.5 | 3683.5 | 211 | 0 | 346.5 | 63 | 1022 | 0 | 2 | 898.1775 | [8 empty] | Total Energy | 314.1191 | 314.1191 | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 3453 | 878 | 1652 | 0 | 1928 | 3684 | 211 | 0 | 270 | 62 | 1022 | 0 | 3 | 894.835 | [8 empty] | Energy not Served | 21.5379 | 21.5379
2:30 | 3445 | 877.5 | 1646.5 | 0 | 1880.5 | 3681.5 | 210 | 0 | 220.5 | 62 | 1018.5 | 0 | 1.5 | 889.5825 | [8 empty] | Energy Requirement | 335.657 | 335.657
3:00 | 3437 | 877 | 1641 | 0 | 1833 | 3679 | 209 | 0 | 171 | 62 | 1015 | 0 | 0 | 884.33
3:30 | 3380.5 | 877.5 | 1652.5 | 0 | 1814 | 3680 | 209 | 0 | 171 | 61 | 1019.5 | 0 | 0 | 773.55 | [7 empty] | Shortage
4:00 | 3324 | 878 | 1664 | 0 | 1795 | 3681 | 209 | 0 | 171 | 60 | 1024 | 0 | 0 | 662.77
4:30 | 3312 | 878 | 1647.5 | 0 | 1742 | 3634.5 | 209 | 0 | 156.5 | 57 | 1022.5 | 0 | 0 | 659.905
5:00 | 3300 | 878 | 1631 | 0 | 1689 | 3588 | 209 | 0 | 142 | 54 | 1021 | 0 | 0 | 657.04
5:30 | 3293 | 878 | 1584 | 0 | 1612 | 3508.5 | 209 | 0 | 131 | 55 | 1019.5 | 2.5 | 0 | 627.9125
6:00 | 3286 | 878 | 1537 | 0 | 1535 | 3429 | 209 | 0 | 120 | 56 | 1018 | 5 | 0 | 598.785
6:30 | 3277.5 | 878 | 1506 | 0 | 1499.5 | 3360.5 | 209 | 0 | 116.5 | 53 | 1014.5 | 15.5 | 0 | 448.85 | [6 empty] | Coal
7:00 | 3269 | 878 | 1475 | 0 | 1464 | 3292 | 209 | 0 | 113 | 50 | 1011 | 26 | 0 | 298.915
7:30 | 3311 | 877.5 | 1394.5 | 0 | 1401.5 | 3202 | 209.5 | 0 | 113 | 49 | 1013 | 93.5 | 0 | 306.0775 | [5 empty] | Oil
8:00 | 3353 | 877 | 1314 | 0 | 1339 | 3112 | 210 | 0 | 113 | 48 | 1015 | 161 | 0 | 313.24
8:30 | 3352.5 | 877 | 1420.5 | 0 | 1287.5 | 3105 | 210 | 0 | 122.5 | 48 | 1014.5 | 271.5 | 0 | 325.655
9:00 | 3352 | 877 | 1527 | 0 | 1236 | 3098 | 210 | 0 | 132 | 48 | 1014 | 382 | 0 | 338.07
9:30 | 3392.5 | 877.5 | 1515 | 0 | 1232.5 | 3087.5 | 210.5 | 0 | 160 | 50 | 1015.5 | 425 | 0.5 | 333.035
10:00 | 3433 | 878 | 1503 | 0 | 1229 | 3077 | 211 | 0 | 188 | 52 | 1017 | 468 | 1 | 328
10:30 | 3462 | 877.5 | 1544 | 0 | 1251 | 3080.5 | 211 | 0 | 196 | 54 | 1016.5 | 494 | 0.5 | 323
11:00 | 3491 | 877 | 1585 | 0 | 1273 | 3084 | 211 | 0 | 204 | 56 | 1016 | 520 | 0 | 318
11:30 | 3330 | 877 | 1687.5 | 0 | 1315 | 3147 | 211 | 0 | 199.5 | 58 | 1015 | 544 | 0 | 540.5225
12:00 | 3169 | 877 | 1790 | 0 | 1357 | 3210 | 211 | 0 | 195 | 60 | 1014 | 568 | 0 | 763.045
12:30 | 3172 | 878 | 1781 | 0 | 1377 | 3245 | 211.5 | 0 | 195.5 | 63 | 1014.5 | 560 | 4.5 | 912.98
13:00 | 3175 | 879 | 1772 | 0 | 1397 | 3280 | 212 | 0 | 196 | 66 | 1015 | 552 | 9 | 1062.915
13:30 | 3175 | 879 | 1772 | 0 | 1397 | 3280 | 212 | 0 | 196 | 66 | 1015 | 552 | 9 | 1062.915
14:00 | 3175 | 879 | 1772 | 0 | 1397 | 3280 | 212 | 0 | 196 | 66 | 1015 | 552 | 9 | 1062.915
14:30 | 3209.5 | 879.5 | 1742.5 | 0 | 1420.5 | 3350 | 212 | 0 | 187.5 | 70 | 1014.5 | 452 | 13 | 1152.685
15:00 | 3244 | 880 | 1713 | 0 | 1444 | 3420 | 212 | 0 | 179 | 74 | 1014 | 352 | 17 | 1242.455
15:30 | 3269.5 | 880 | 1666 | 0 | 1473 | 3419.5 | 211.5 | 0 | 169.5 | 72 | 1011 | 299 | 24.5 | 1283.9975
16:00 | 3295 | 880 | 1619 | 0 | 1502 | 3419 | 211 | 0 | 160 | 70 | 1008 | 246 | 32 | 1325.54
16:30 | 3286 | 880 | 1658 | 0 | 1538.5 | 3421.5 | 210.5 | 0 | 172 | 68 | 1008.5 | 159.5 | 24 | 1302.1425
17:00 | 3277 | 880 | 1697 | 0 | 1575 | 3424 | 210 | 0 | 184 | 66 | 1009 | 73 | 16 | 1278.745
17:30 | 3260.5 | 879.5 | 1672.5 | 0 | 1755.5 | 3398.5 | 210 | 0 | 226 | 66 | 1011 | 39 | 11.5 | 1141.225
18:00 | 3244 | 879 | 1648 | 0 | 1936 | 3373 | 210 | 0 | 268 | 66 | 1013 | 5 | 7 | 1003.705
18:30 | 3309.5 | 877 | 1632.5 | 0 | 2088 | 3610 | 210.5 | 0 | 448.5 | 71 | 1009.5 | 2.5 | 3.5 | 1181.8125
19:00 | 3375 | 875 | 1617 | 0 | 2240 | 3847 | 211 | 0 | 629 | 76 | 1006 | 0 | 0 | 1359.92
19:30 | 3514 | 875 | 1595 | 0 | 2378 | 4011 | 212 | 0 | 660 | 76 | 1011 | 0 | 0 | 1218.1025
20:00 | 3473 | 874 | 1638 | 0 | 2368 | 4023 | 212 | 0 | 690 | 74 | 1011 | 0 | 10 | 1076.285
20:30 | 3429.5 | 874.5 | 1649.5 | 0 | 2334 | 4018 | 212 | 0 | 687 | 74 | 1010.5 | 0 | 14 | 1190.6425
21:00 | 3386 | 875 | 1661 | 0 | 2300 | 4013 | 212 | 0 | 684 | 74 | 1010 | 0 | 18 | 1305 |  |  | Max Temp. in Dhaka |  | 34.3°C
21:30 | 3418.5 | 875 | 1663 | 0 | 2237 | 4060 | 212 | 0 | 617 | 76 | 1011 | 0 | 11 | 1331.505
22:00 | 3451 | 875 | 1665 | 0 | 2174 | 4107 | 212 | 0 | 550 | 78 | 1012 | 0 | 4 | 1358.01
22:30 | 3444.5 | 874.5 | 1663.5 | 0 | 2131 | 4144.5 | 212 | 0 | 548.5 | 77 | 1009 | 0 | 2 | 1354.6675
23:00 | 3438 | 874 | 1662 | 0 | 2088 | 4182 | 212 | 0 | 547 | 76 | 1006 | 0 | 0 | 1351.325 | [5 empty] | Page 5 of 7
23:30 | 3436 | 874 | 1668.5 | 0 | 2055.5 | 4183 | 212 | 0 | 515 | 75 | 1006 | 0 | 2 | 1358.965
24:00 | 3434 | 874 | 1675 | 0 | 2023 | 4184 | 212 | 0 | 483 | 74 | 1006 | 0 | 4 | 1366.605
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on X13: Author:

## Generation
2024-09-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 131 | 131 | 129 | 129 | 129 | 129 | 129 | 130 | 130 | 131 | 131 | 131 | 132 | 132 | 132 | 131 | 130 | 130 |  | 131 | 132 | 132 | 132 | 132 | 132 | 132 | 2969018
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1924000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 0 | [17 empty] | 1 | 17 | 25 | 25 | 25 | 25 | 25 | 140317
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 12 | 15 |  | 10 | 19 | 19 | 15 | 12 | 8 | 3 | 0 | [8 empty] | 111780
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 198 | 182 | 182 | 168 | 167 | 167 | 205 | 213 | 212 | 212 | 213 | 212 | 212 | 212 | 212 | 211 | 211 |  | 211 | 211 | 211 | 211 | 209 | 201 | 198 | 4737386
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 34 | 0 | [16 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 425703
12 | Hathazari 100 MW peaking PP | 71 | 0 | [17 empty] | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 242064
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 85 | 85 | 85 | 83 | 68 | 68 | 68 | 68 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 963491
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 42 | 42 | 42 | 42 | 42 | 42 | 36 | 36 | 39 | 42 | 42 | 35 | 35 | 35 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 861676
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 327 | 329 | 328 | 321 | 280 | 280 | 280 | 280 | 280 | 280 | 324 | 315 | 319 | 319 | 318 | 320 | 316 | 320 |  | 320 | 322 | 316 | 322 | 324 | 316 | 316 | 7513476
18 | Kodda 300 MW PP Unit-2 (Summit) | 296 | 143 | 97 | 97 | 95 | 82 | 62 | 62 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 62 | 65 | 62 |  | 232 | 275 | 277 | 277 | 250 | 220 | 195 | 3048545
19 | Ashuganj 195 MW PP (APSCL-United) |  |  |  | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [15 empty] | 66909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 612 | 612 | 614 | 521 | 545 | 570 | 530 | 530 | 530 | 530 | 530 | 530 | 580 | 612 | 612 | 612 | 612 |  | 612 | 612 | 610 | 610 | 608 | 612 | 612 | 14012726
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 28 | 30 | 29 | 29 | 29 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 |  | 10 | 10 | 10 | 540288
33 | Ashuganj 225 MW CCPP | 140 | 140 | 140 | 31 | 37 | 38 | 63 | 113 | 136 | 212 | 211 | 172 | 194 | 209 | 210 | 208 | 211 | 211 |  | 212 | 212 | 202 | 212 | 200 | 201 | 201 | 3944000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6066000
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 285 | 300 | 290 | 280 | 280 | 280 | 280 | 280 | 280 | 290 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7479400
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 250 | 250 | 250 | 250 | 250 | 250 | 270 | 250 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5866300
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 22 | 41 | 51 | 51 | 51 | 49 | 11 | 32 | 46 | 21 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 504000
36 | Chandpur 150 MW CCPP | 85 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 70 | 50 | 50 | 50 | 70 | 50 | 50 |  | 70 | 70 | 70 | 50 | 50 | 70 | 50 | 1472570
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 406 | 406 | 406 | 407 | 408 | 405 | 388 | 352 | 350 | 349 | 386 | 394 | 394 | 398 | 398 | 397 | 397 | 404 |  | 403 | 407 | 402 | 400 | 400 | 402 | 400 | 9579600
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 350 | 420 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10212500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 21 | 19 | 16 | 11 | 9 | 9 | 9 | 10 | 10 | 11 | 11 |  | 11 | 13 | 13 | 16 | 16 | 17 | 17 | 380160
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 10 | 32 | 45 | 43 | 42 | 48 | 32 | 36 | 16 | 6 | 0 | [8 empty] | 338130
44 | Fenchugonj CCPP Phase-1 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 925000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 30 | 59 | 59 | 56 | 59 | 60 | 60 |  | 60 | 31 | 28 | 30 | 30 | 30 | 31 | 901920
48 | Shahjibazar 86 MW PP (Shahjibazar) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 76 | 86 | 84 | 22 | 22 | 22 | 11 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 600960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 204 | 205 | 206 | 208 | 208 | 208 | 207 | 208 | 209 | 208 | 208 | 203 | 202 | 202 | 202 | 202 | 200 | 202 |  | 204 | 202 | 205 | 204 | 204 | 204 | 204 | 5127380
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 60384
55 | Fenchugonj 51 MW PP (Barakatullah) | [11 empty] | 49 | 52 | 52 | 52 | 52 | 52 | 30 | [8 empty] | 324600
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 263040
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 285 | 290 | 285 | 285 | 280 | 260 | 260 | 290 | 295 | 300 | 310 | 310 | 305 | 300 | 285 | 305 | 290 |  | 300 | 280 | 290 | 305 | 310 | 300 | 310 | 7212500
| Bibiyana South 400 MW | 341 | 341 | 341 | 341 | 345 | 345 | 330 | 340 | 340 | 340 | 345 | 345 | 345 | 345 | 345 | 370 | 370 | 370 |  | 375 | 375 | 365 | 375 | 375 | 375 | 383 | 8573200
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 35 | [7 empty] | 17 | 30 | 35 | 35 | 35 |  | 35 | 35 | 55 | 55 | 35 | 35 | 35 | 670293
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 0 | 5 | 12 | 14 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 240240
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 64 | 62 | 62 | 60 | 54 | 56 | 50 | 48 | 48 | 52 | 56 | 60 | 66 | 72 | 74 | 70 | 66 | 66 |  | 76 | 76 | 74 | 74 | 78 | 76 | 74 | 1536000
64 | Malancha, Ctg. EPZ (United) | 37 | 41 | 42 | 42 | 42 | 42 | 42 | 10 | 4 | 3 | 0 | 0 | 2 | 4 | 2 | 4 | 10 | 18 |  | 20 | 20 | 22 | 31 | 35 | 36 | 39 | 545760
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 0 | 18 | 18 | 18 | 399250
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 20 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 438600
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 23 |  | 22 | 21 | 22 | 22 | 22 |  | 15 | 457200
71 | Maona 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 756360
72 | Rupganj 33 MW PP(Summit) | 20 | 21 | 21 | 21 | 21 | 21 | 19 | 18 | 18 | 18 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 339700
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 102 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 1625640
| Chowmuhani 113 MW | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 28 | 28 | 28 | 28 | 27 | 28 | 15 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 513240
| Manikgonj 162MW PP(MPGL) | 108 | 108 | 108 | 108 | 72 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 72 | 162 |  | 162 | 162 | 162 | 108 | 90 | 54 | 54 | 1964160
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 240000
79 | Kodda 150 MW PP | 64 | 32 | 32 | 32 | 31 | 32 | 32 | 32 | 48 | 82 | 98 | 96 | 96 | 80 | 80 | 80 | 78 | 88 |  | 143 | 143 | 143 | 143 | 142 | 143 | 143 | 1929600
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 189211
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 34 | 34 |  | 52 | 52 | 52 | 52 | 52 | 35 | 35 | 841920
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 2 | 5 | 4 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 31281
| Jodiac Power | 52 | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 743804
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 98 | 110 | 110 | 51 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 24 | 51 | 1492909
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 40 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 53 | 50 | 53 | 48 | 41 | 41 |  | 53 | 60 | 60 | 65 | 49 | 49 | 50 | 1227840
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | [11 empty] | 11 | 27 | 27 | 28 | 34 | 34 | 34 | [8 empty] | 205776
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 994640
94 | Gagnagar 102 MW PP (Digital Power) | 33 | 33 | 33 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 540288
95 | Patenga 50MW PP (Baraka) | [26 empty] | 0
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 45 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1291832
100 | Manikganj 55 MW PP (Northern) | 55 | 35 | 35 | 35 | 35 | 0 |  |  |  | 3 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 684472
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 120 | 163 | 163 | 163 | 120 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3626264
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | [9 empty] | 14800
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 35 | 35 | 35 | 17 | 638280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 96 | 96 | 96 | 95 | 96 | 96 | 96 | 94 |  | 122 | 122 | 121 | 122 | 122 | 123 | 123 | 2352000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 68 | 55 | 52 | 52 | 52 | 52 | 52 | 53 | 59 | 95 | 96 | 96 | 96 | 96 | 96 | 95 | 95 | 109 |  | 112 | 112 | 112 | 113 | 112 | 113 | 114 | 2065392
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 551040
116 | Chandpur 200 MW (Desh energy) | 106 | 104 | 102 | 102 | 104 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 110 | 103 | 100 | 118 | 192 |  | 200 | 200 | 200 | 180 | 192 | 200 | 152 | 3104640
117 | Ashuganj 150 MW PP (Midland) | 5 | 7 | 7 | 7 | 5 | 7 | 7 | 6 | 5 | 6 | 6 | 5 | 6 | 6 | 23 | 62 | 78 | 75 |  | 88 | 88 | 87 | 103 | 103 | 102 | 102 | 913309
118 | Bibiyana-III 400 MW CCPP | 225 | 280 | 279 | 279 | 279 | 268 | 268 | 268 | 268 | 279 | 265 |  |  | 71 | 71 | 71 | 80 | 71 |  | 120 | 279 | 268 | 268 | 268 | 268 | 270 | 5045000
| Jamalpur 115 MW PP (United) | 49 | 48 | 49 | 49 | 49 | 49 | 49 | 48 | 49 | 49 | 48 | 48 | 47 | 57 | 57 | 57 | 57 | 57 |  | 76 | 76 | 77 | 77 | 77 | 77 | 77 | 1365600
| Anwara 300 MW PP (United) | 50 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 30 | 30 | 30 | 30 | 30 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 825491
| Juldah unit-2 (Acorn) | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 24 | 12 | 12 | 12 | 23 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 550080
| Anlima Energy Ltd. | 50 | 57 | 72 | 72 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 677455
| Bhairob 54.5 MW | [9 empty] | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 0 |  | 12 | 17 | 17 | 241560
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 12 | 22 | 32 | 19 | 21 | 28 | 28 | 25 | 14 | 5 | 0 | [8 empty] | 198077
| Chandpur 115(Doreen) | 72 | 59 | 56 | 55 | 54 | 49 | 48 | 49 | 48 | 48 | 49 | 49 | 49 | 49 | 42 | 47 | 56 | 70 |  | 72 | 88 | 87 | 88 | 74 | 58 | 55 | 1392960
| Kanchan Purbachal Power Generation Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 23 | 35 | 35 | 35 |  | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 837000
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 |  | 145 | 145 | 145 | 145 | 17 | 17 | 17 | 879854
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 9 | 25 | 17 | 32 | 16 | 7 |  | 0 | 0 | 10 | 18 | 4 | 0 | 4 | 167040
| Sonagazi 75 MW Solar Plant |  |  |  |  | 0 | 2 | 5 | 28 | 44 | 58 | 57 | 74 | 72 | 62 | 48 | 34 | 13 | 0 | [8 empty] | 461882
| Matarbari 2*600 MW (CPGCL) | 702 | 702 | 701 | 700 | 702 | 701 | 700 | 705 | 702 | 701 | 704 | 705 | 703 | 700 | 706 | 705 | 700 | 655 |  | 645 | 645 | 645 | 645 | 645 | 645 | 645 | 16610909
Meghnaghat (Reliance) 718MW CCPP
120 | Eastern Zone Total | 7397 | 7115 | 7026 | 6914 | 6728 | 6643 | 6557 | 6446 | 6528 | 6641 | 6847 | 6718 | 6779 | 6871 | 6848 | 6870 | 6833 | 6940 |  | 7544 | 7743 | 7748 | 7689 | 7502 | 7392 | 7361 | 169807672
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [26 empty] | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 27 | 27 | 0 | [14 empty] | 20 |  | 40 | 46 | 41 | 41 | 35 | 32 | 22 | 272640
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 35 | 16 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 60 | 70 | 71 | 17 | 17 | 17 | 1144800
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 8 | 21 | 66 | 86 | 95 | 96 | 95 | 93 | 8 | 12 | 8 | 1 | [8 empty] | 591120
131 | Rampal 1320 MW (BIFPCL) | 618 | 619 | 615 | 616 | 614 | 556 | 546 | 517 | 506 | 516 | 510 | 575 | 725 | 765 | 762 | 762 | 762 | 762 |  | 1020 | 1114 | 1128 | 1118 | 1127 | 1164 | 1166 | 17905457
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 448800
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5374860
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 |  | 32 | 64 | 16 | 16 | 16 | 16 | 16 | 537984
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 307 | 307 | 307 | 307 | 307 | 307 | 236 | 200 | 200 | 200 | 200 | 200 | 150 | 150 | 150 | 150 | 150 | 156 |  | 270 | 270 | 270 | 270 | 307 | 307 | 307 | 5826000
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 4125
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 132 | 132 | 130 | 130 | 134 | 134 | 134 | 134 | 80 |  | 130 | 130 | 130 | 81 | 130 | 130 | 130 | 3038000
140 | Bhola 33 MW PP (Venture) | 10 | 7 | 9 | 8 | 7 | 6 | 5 | 6 | 6 | 8 | 6 | 8 | 8 | 8 | 9 | 9 | 7 | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 199930
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 38 | 38 | 0 | [14 empty] | 10 |  | 37 | 40 | 55 | 41 | 40 | 36 | 36 | 307072
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 878 | 878 | 877 | 878 | 878 | 878 | 878 | 877 | 877 | 878 | 877 | 877 | 879 | 879 | 880 | 880 | 880 | 879 |  | 875 | 875 | 874 | 875 | 875 | 874 | 874 | 21961454
147 | Bheramara 410 MW CCPP | 330 | 331 | 335 | 335 | 335 | 335 | 332 | 353 | 355 | 350 | 344 | 343 | 337 | 332 | 325 | 329 | 325 | 325 |  | 320 | 320 | 320 | 303 | 303 | 304 | 299 | 8039808
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1120 | 1040 | 960 | 960 | 950 | 970 | 1000 | 1000 | 990 | 990 | 990 | 1000 | 980 |  | 1090 | 1160 | 1160 | 1160 | 1210 | 1244 | 1244 | 28288700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 180 | 170 | 200 | 172 | 208 | 200 | 200 | 200 | 208 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 4808000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 30 | 30 | 30 | 703785
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 2 | 5 | 5 | 5 | 4 | 3 | 1 | 1 | 0 | [8 empty] | 33120
| Sirajganj 68 MW Solar Park | [6 empty] | 2 | 8 | 17 | 28 | 58 | 61 | 59 | 57 | 39 | 30 | 8 | 0 | [8 empty] | 396750
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 390 | 414 | 395 | 407 | 348 | 250 | 250 | 220 | 341 | 349 | 347 | 414 | 390 | 385 | 414 | 327 | 381 | 414 |  | 385 | 383 | 414 | 414 | 408 | 414 | 414 | 8957454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 16 | 0 | [18 empty] | 4 | 5 | 13 | 17 | 20 | 14 | 79220
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 138852
165 | Amnura 50 MW PP(Sinha) | 35 | 35 | 35 | 28 | 28 | 28 | 28 |  |  |  | 8 | 21 | 28 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 659290
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 28 | 28 | 28 | 28 | 0 | [14 empty] | 9 | 26 | 45 | 45 | 42 | 42 | 35 | 264485
168 | Santahar 50 MW Peaking PP | 22 | 22 | 22 | 22 | 22 | 0 | [10 empty] | 26 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 22 | 315148
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 40 |  | 88 | 88 | 88 | 88 | 88 | 88 | 55 | 502256
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 95 | 50 | 50 | 50 | 35 | 35 | 35 | 35 | 54 | 55 | 55 | 55 | 55 | 55 | 55 | 70 | 110 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 95 | 1790784
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1790592
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 77 | 70 | 70 | 49 | 49 | 34 | [5 empty] | 22 | 33 | 33 | 33 | 33 | 40 | 83 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 1193078
177 | Sympa Solar Power 8MW | [13 empty] | 7 | 5 | 3 | 0 | 0 | [8 empty] | 17491
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 73 | 80 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2720064
| Intraco Solar 30 MW | [5 empty] | 0 |  | 15 | 26 | 31 | 35 | 37 | 34 | 17 | 27 | 17 | 8 | 1 | [8 empty] | 250102
| Adani Power Jharkhanda Ltd | 1022 | 1022 | 1015 | 1024 | 1021 | 1018 | 1011 | 1015 | 1014 | 1017 | 1016 | 1014 | 1015 | 1019 | 1014 | 1008 | 1009 | 1013 |  | 1006 | 1011 | 1011 | 1010 | 1012 | 1006 | 1006 | 24387273
178 | Teesta Solar Limited |  |  |  |  | 0 | 2 | 0 | 52 | 155 | 182 | 191 | 207 | 185 | 171 | 144 | 108 | 20 | 3 | [8 empty] | 1362960