## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-09-18 | Wednesday
|  | Date (day): | 2024-09-18 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15201.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16131 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-09-18 | 2024-09-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 404 | 410 | 400 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 |  | 225 | GT-1 Under maint.
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 13 | 13 | 62 |  | Fuel shortage
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 328 | 325 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 97 | 90 | 100
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 78 | 130 | 48 | 130 |  | 19 | Engine problem
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 36 | 36 | 36 |  | 44 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 30 | 30 | 30
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 11 | 10 | 12 | 12 |  | 21 | Engine problem
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 16 | 25 | 16 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 145 | 260 | 270 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 95 | 132 | 130 | 132 |  | 17 | Engine problem
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 50 | 50 | 50 | 60 | 44 |  | Lub Oil problem
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 |  | 38 | Engine problem.
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1722 | 2233 | 2061 | 2281 | 2428 | 1144
35 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 80 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
36 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
37 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
38 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
39 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 216 | 214 | 212 | 214
40 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
42 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 47 | 51 | 105 | 105
43 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 71 | 65 | 75 | 23 |  | Fuel shortage
44 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 84 | 51 | 84 |  | 18 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
45 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 38 | 38 | 38
46 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 20 | 10 | 20
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 35 | 44 | 0 | 40 | 68 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 135 | 40 | 50 | 50 | 250 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 97 | 51 | 92 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 36 | 36 | 90 | 100
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 105 | 108
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 145 | 35 | 163
55 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 590 | 612 | 612 | 612 |  | 612 | Unit-1 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 0 | 42 | 60 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 751 | 753 | 750 | 750
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 2042 | 2210 | 2474 | 2750 | 429 | 1185
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 190 | 187 | 210 | 210
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 285 | 340 | 350
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 315 | 285 | 300 | 300 | 100 |  | Gas shortage
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 36 | 36 | 36 | 9 |  | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 47 | 52 | 52 | 52
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 178 | 128 | 108 | 128 | 67 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 81 | 97 | 50 | 120 |  | 30 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 34 | 35 | 35 | 35 |  | 17 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 42 | 70 | 80 | 83 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 188 | 180 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 58 | 78 | 90 | 90
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 43 | 16 | 43 |  | 9 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 10 | 10 | 10 |  | 15 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 106 | 74 | 106 | 106
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 99 | 95 | 70 | 95 |  | 18 | Engine problem
76 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 48 | 90 | 65 | 90 |  | 25 | Engine problem
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 75 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1745 | 1776 | 1859 | 1996 | 259 | 474
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 3 | 11 | 10 | 15 | 187 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 133 | 151 | 125 | 160 | 40 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 63 | 90 | 58 | 90 | 25 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 38 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 6 | 6 |  | 16 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 54 | 17 | 54
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 245 | 306 | 267.6 | 325 | 187 | 16
84 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 40 | 38 | 40 |  | 30 | Machine problem.
85 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 0 | 0 | 0 |  | 90 | Machine problem
86 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
87 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
88 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 30 | 30 | 30 | 36 |  | Gas shortage
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 71 | 64 | 71 | 15 |  | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 206 | 205 | 210 | 210 |  | 21 | Machine problem
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 11 | 12 | 12 | 12 |  | 13 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 260 | 300 | 300 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 197 | 335 | 350 | 350 |  |  | FGMO
99 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 380 | 346 | 350 | 360 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1469 | 1467 | 1522 | 1541 | 172 | 490
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 884 | 885 | 894 | 900
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Engine problem
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 30 | 35 |  | 19 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 55 |  | 54 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 259 | 233 | 230 | 230 | 180 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 70 | 72 | 33 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 0 | 0 | 105 |  | Fuel shortage
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 100 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 860 | 1230 | 1200 | 1230
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 2103 | 2433 | 2524 | 2522 | 900 | 73
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 64 | 110
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 8 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 134 | 135 | 135 |  | 59 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 990 | 1130 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 54 | 96 |  | Fuel shortage
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 200 | 307 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1546 | 1799 | 1997 | 2080 | 96 | 59
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 17 | 30 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 6 | 0 | 20 |  | 51 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 28
122 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 25 | 46
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 165 | 160 | 160 | 160 | 50 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 331 | 414 | 350 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 8 | 5 | 8 |  | 3 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 86 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 25 | 113 | 113 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 95 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1020 | 1119 | 1000 | 1100
135 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 52 | 0 | 20 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 3 | 0 | 0 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1638 | 2090 | 1879 | 2162 | 713 | 100
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 62 | 60 | 60 | 60 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 210 | 200 | 200 | 200 |  | 74 | Under maint.
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 40 | 82 | 35 | 99 |  | 14 | Engine problem
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 25 | 96 | 115 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 204 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 581 | 438 | 618 | 474 | 40 | 198
| Total |  |  |  |  | 27791 | 27086 | 13091 | 14752 | 15201.6 | 16131 | 5224 | 3739
A. |  | 2024-09-18 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 14752 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 10778 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15150 | MW
3 | Day peak Generation : |  |  | 13091 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14574.31 | MW
4 | Evening peak Generation : |  |  | 14752 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 380 | MW
5 | Total Energy Generation : |  | 312.5628 | MKWHr | By Solar | 4.1098 | MKWHr
| By Gas : | 113.7342 | MKWHr |  | By Oil: | 46.1866 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 95.3694 | MKWHr |  | By Hydro: | 5.1615 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 25.0636 | MKWHr |  | By Wind: | 0.07728 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5224 | MW | Dhaka | 5337.31 | 5222.31 |  | 115 |  | 18:00 |  | 354.305
|  |  | For Plants S/D or M/C prob = |  |  | 3739 | MW | Chittagong | 1407.8 | 1407.8 |  | 0 |  | 19:00 |  | 427
|  |  | Total = |  |  | 8963 | MW | Khulna | 1646 | 1646 |  | 0 |  | 19:30 |  | 380
7 | Total Gas Supplied : |  | 811.04 | MMCFD | **Import Adani: | Taka | 165670640.57 | Rajshahi | 1440.8 | 1440.8 |  | 0 |  | 20:00 |  | 350
8 | Fuel Cost : | i) Gas : | Taka | 342850054.98 | ii) Oil : | Taka | 848764799.35 | Comilla | 1325.5 | 1265.5 |  | 60 |  | 21:00 |  | 352
|  | iii) Coal : | Taka | 655046566.09 | Total | Taka | 2012332060.99 | Mymensingh | 1247 | 1087 |  | 160 |  | 22:00 |  | 362
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 10756.35 | MKWHr. | Sylhet | 682 | 682 |  | 0 |  | 23:00 |  | 381
| ii) During Peak Demand : |  |  | 830 | MW (W to E) at | 19:30 | hrs | Barisal | 455.9 | 455.9 |  | 0 |  | 24:00 |  | 396
| iii) Maximum : |  |  | 498 | MW at | 22:00 | hrs | Rangpur | 1032 | 987 |  | 45
10 | Maximum Temperature in Dhaka was |  |  |  | 34.8°C |  |  | Total | 14574.31 | 14194.31 |  | 380
B. |  | 2024-09-18 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 34.8°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16131 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13500 | MW
4 | Reserve(Generation end) |  |  |  | 731 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 326.2926 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12280 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.3207 | MKWHr. | ii) HVDC Flow at Peak Time |  | 885 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.5398 | MKWHr. | iii) Maximum HVDC Flow : |  | 887 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 108.3 |  | (b) Today: | 108.17 |  | (c) Rule Curve: |  | 102.91

## YesterdayGen
2024-09-18 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 187 | 0 | 0 | 0 | 49 | 113 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 17 | 21 | 33 | 10 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 40 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 192 | 177 | 50 | 36 | 52 | 0 | 51 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 66 | 16 | 0 | 0 | 0 | 40 | 20 | 0 | 0 | 163 | 0 | 64 | 86 | 0 | 207 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 278 | 0 | 0 | 97 | 0 | 81 | 0 | 25 | 103 | 0 | 195 | 58 | 50 | 17 | 0 | 15 | 0 | 17 | 70 | 94 | 12 | 346 | 50 | 0 | 54 | 0 | 0 | 17 | 0 | 48 | 17 | 320 | 17 | 0 | 550 | 7 | 752 | 0 | 0 | 0 | 0 |  | 886 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 61 | 0 | 210 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 15 | 92 | 0 | 0 | 113 | 1100 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 1006 | 0 | 275 | 1017 | 0 | 0 | 0 | 0 | 0 |  | 6302 | 6092 | 12394 | 2922 | 886 | 1480 | 0 | 1678 | 3954 | 214 | 0 | 170 | 66 | 1017 | 0 | 7 | 293.185 | 108.31
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 49 | 113 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 17 | 21 | 33 | 10 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 24 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 192 | 177 | 0 | 36 | 53 | 0 | 51 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 64 | 16 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 163 | 0 | 63 | 86 | 0 | 208 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 195 | 0 | 0 | 97 | 0 | 37 | 0 | 12 | 103 | 0 | 198 | 58 | 17 | 17 | 0 | 15 | 0 | 17 | 70 | 94 | 12 | 346 | 40 | 0 | 54 | 0 | 0 | 17 | 0 | 55 | 17 | 325 | 0 | 0 | 550 | 4 | 754 | 0 | 0 | 0 | 0 |  | 887 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 61 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 50 | 0 | 52 | 0 | 0 | 35 | 1100 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 1010 | 0 | 275 | 1006 | 0 | 0 | 0 | 0 | 0 |  | 6045 | 5849 | 11894 | 2916 | 887 | 1459 | 0 | 1249 | 3960 | 212 | 0 | 137 | 64 | 1006 | 0 | 4 | 388.685 | 108.31
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 0 | 49 | 112 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 19 | 21 | 33 | 10 | 0 | 0 | 133 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 192 | 178 | 0 | 36 | 53 | 0 | 51 | 0 | 0 | 20 | 0 | 0 | 0 | 18 | 62 | 16 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 163 | 0 | 63 | 86 | 0 | 208 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 145 | 0 | 0 | 97 | 0 | 34 | 0 | 0 | 103 | 0 | 195 | 58 | 17 | 17 | 0 | 15 | 0 | 17 | 70 | 94 | 0 | 346 | 17 | 0 | 54 | 0 | 0 | 17 | 0 | 56 | 17 | 320 | 0 | 0 | 550 | 3 | 754 | 0 | 0 | 0 | 0 |  | 886 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 61 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1100 | 180 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 906 | 0 | 275 | 1020 | 0 | 0 | 0 | 0 | 0 |  | 5987 | 5656 | 11643 | 3001 | 886 | 1472 | 0 | 1018 | 3856 | 213 | 0 | 112 | 62 | 1020 | 0 | 3 | 275.04 | 108.31
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 19 | 21 | 33 | 11 | 0 | 0 | 133 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 192 | 178 | 0 | 30 | 53 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 60 | 16 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 163 | 0 | 63 | 86 | 0 | 208 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 45 | 0 | 0 | 97 | 0 | 34 | 0 | 0 | 103 | 0 | 199 | 59 | 17 | 0 | 0 | 0 | 0 | 17 | 34 | 94 | 0 | 346 | 0 | 0 | 54 | 0 | 0 | 17 | 0 | 56 | 17 | 320 | 0 | 0 | 550 | 14 | 756 | 0 | 0 | 0 | 0 |  | 886 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 60 | 0 | 210 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 275 | 1020 | 0 | 0 | 0 | 0 | 0 |  | 5746 | 5584 | 11330 | 3026 | 886 | 1455 | 0 | 683 | 3861 | 213 | 0 | 112 | 60 | 1020 | 0 | 14 | 247.345 | 108.31
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 19 | 21 | 33 | 11 | 0 | 0 | 133 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 192 | 178 | 0 | 30 | 53 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 58 | 18 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 163 | 0 | 63 | 86 | 0 | 208 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 34 | 0 | 0 | 85 | 0 | 196 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 73 | 0 | 346 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 52 | 17 | 325 | 0 | 0 | 480 | 8 | 752 | 0 | 0 | 0 | 0 |  | 885 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 61 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 275 | 1019 | 0 | 0 | 0 | 0 | 0 |  | 5554 | 5595 | 11149 | 3075 | 885 | 1467 | 0 | 524 | 3788 | 213 | 0 | 112 | 58 | 1019 | 0 | 8 | 221.56 | 108.3
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 33 | 11 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 320 | 0 | 213 | 150 | 0 | 30 | 53 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 56 | 18 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 120 | 0 | 63 | 86 | 0 | 210 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 34 | 0 | 0 | 68 | 0 | 196 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 376 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 49 | 17 | 325 | 0 | 0 | 480 | 2 | 757 | 0 | 0 | 1 | 0 |  | 885 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 61 | 0 | 210 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 180 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 907 | 0 | 200 | 1024 | 4 | 0 | 0 | 1 | 0 |  | 5479 | 5299 | 10778 | 3149 | 885 | 1333 | 0 | 449 | 3575 | 214 | 0 | 82 | 56 | 1024 | 9 | 2 | 215.83 | 108.3
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 11 | 8 | 0 | 135 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 310 | 0 | 210 | 108 | 0 | 30 | 53 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 54 | 16 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 163 | 0 | 62 | 86 | 0 | 209 | 0 | 0 | 0 | 315 | 12 | 2 | 0 | 0 | 0 | 0 | 126 | 0 | 36 | 2 | 0 | 68 | 0 | 196 | 74 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 73 | 0 | 376 | 0 | 10 | 0 | 0 | 0 | 17 | 4 | 49 | 17 | 300 | 0 | 0 | 528 | 7 | 756 | 0 | 0 | 8 | 0 |  | 885 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 61 | 0 | 210 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 960 | 220 | 0 | 0 | 1 | 16 | 0 | 0 | 0 | 960 | 6 | 200 | 1024 | 38 | 0 | 1 | 11 | 0 |  | 5584 | 5540 | 11124 | 3151 | 885 | 1424 | 0 | 507 | 3675 | 215 | 0 | 82 | 54 | 1024 | 100 | 7 | 135.61 | 108.3
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 5 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 21 | 33 | 11 | 8 | 0 | 135 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 360 | 0 | 192 | 72 | 0 | 33 | 54 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 52 | 5 | 0 | 0 | 1 | 40 | 30 | 0 | 0 | 163 | 0 | 62 | 86 | 0 | 207 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 15 | 0 | 0 | 126 | 0 | 34 | 11 | 0 | 68 | 0 | 196 | 74 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 73 | 0 | 346 | 2 | 25 | 54 | 0 | 0 | 17 | 18 | 49 | 17 | 300 | 0 | 0 | 530 | 2 | 754 | 0 | 0 | 36 | 0 |  | 884 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 62 | 0 | 210 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2 | 0 | 17 | 0 | 3 | 0 | 980 | 180 | 0 | 0 | 3 | 53 | 0 | 0 | 0 | 966 | 11 | 200 | 1022 | 95 | 0 | 1 | 29 | 0 |  | 5688 | 5683 | 11371 | 3174 | 884 | 1333 | 0 | 617 | 3702 | 215 | 0 | 82 | 52 | 1022 | 288 | 2 | 128.925 | 108.3
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 16 | 82 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 15 | 21 | 33 | 11 | 8 | 0 | 136 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 345 | 0 | 212 | 110 | 0 | 32 | 52 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 54 | 5 | 0 | 0 | 2 | 40 | 30 | 0 | 0 | 163 | 0 | 60 | 86 | 0 | 208 | 0 | 0 | 0 | 310 | 12 | 5 | 0 | 55 | 0 | 0 | 124 | 0 | 36 | 15 | 0 | 70 | 0 | 196 | 74 | 35 | 0 | 4 | 0 | 0 | 0 | 0 | 78 | 0 | 373 | 17 | 38 | 54 | 0 | 0 | 17 | 17 | 49 | 17 | 360 | 17 | 0 | 567 | 0 | 757 | 0 | 0 | 55 | 0 |  | 884 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 62 | 0 | 210 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 28 | 0 | 33 | 0 | 3 | 0 | 1000 | 180 | 0 | 0 | 3 | 72 | 0 | 0 | 0 | 952 | 23 | 200 | 1020 | 146 | 0 | 1 | 33 | 0 |  | 6008 | 5725 | 11733 | 3218 | 884 | 1315 | 0 | 767 | 3748 | 216 | 0 | 99 | 54 | 1020 | 412 | 0 | 146.115 | 108.29
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 50 | 0 | 0 | 0 | 30 | 330 | 0 | 0 | 0 | 16 | 80 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 21 | 33 | 11 | 16 | 0 | 136 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 330 | 0 | 206 | 160 | 0 | 32 | 49 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 56 | 5 | 0 | 0 | 1 | 41 | 30 | 0 | 0 | 163 | 0 | 61 | 86 | 0 | 208 | 0 | 0 | 0 | 315 | 12 | 5 | 0 | 140 | 0 | 0 | 124 | 0 | 90 | 19 | 12 | 100 | 20 | 196 | 74 | 35 | 9 | 4 | 15 | 0 | 9 | 70 | 92 | 22 | 366 | 41 | 45 | 54 | 0 | 0 | 17 | 22 | 49 | 17 | 330 | 35 | 0 | 585 | 0 | 757 | 0 | 0 | 68 | 0 |  | 884 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 62 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 1000 | 180 | 0 | 0 | 5 | 99 | 0 | 0 | 0 | 900 | 26 | 200 | 1022 | 176 | 0 | 1 | 45 | 0 |  | 6571 | 5686 | 12257 | 3136 | 884 | 1403 | 0 | 1195 | 3714 | 216 | 0 | 115 | 56 | 1022 | 516 | 0 | 143 | 108.29
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 60 | 0 | 0 | 0 | 55 | 328 | 0 | 0 | 0 | 16 | 80 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 21 | 33 | 11 | 16 | 0 | 136 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 2 | 0 | 0 | 0 | 305 | 0 | 203 | 175 | 0 | 35 | 48 | 0 | 43 | 0 | 26 | 16 | 0 | 0 | 0 | 18 | 60 | 3 | 0 | 0 | 2 | 41 | 30 | 0 | 0 | 163 | 0 | 60 | 86 | 0 | 206 | 0 | 0 | 0 | 315 | 11 | 5 | 0 | 152 | 0 | 0 | 133 | 0 | 95 | 19 | 28 | 100 | 55 | 197 | 63 | 35 | 27 | 5 | 100 | 5 | 26 | 106 | 92 | 34 | 366 | 51 | 52 | 54 | 1 | 0 | 0 | 31 | 49 | 17 | 315 | 36 | 0 | 610 | 0 | 753 | 0 | 0 | 74 | 0 |  | 885 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 62 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 1000 | 220 | 0 | 0 | 6 | 98 | 0 | 0 | 0 | 865 | 27 | 200 | 1029 | 195 | 0 | 1 | 51 | 3 |  | 6886 | 5777 | 12663 | 3138 | 885 | 1465 | 0 | 1459 | 3700 | 216 | 0 | 142 | 60 | 1029 | 569 | 0 | 255 | 108.29
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 328 | 0 | 0 | 0 | 16 | 78 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 21 | 25 | 11 | 16 | 0 | 136 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 35 | 0 | 0 | 2 | 0 | 0 | 0 | 305 | 0 | 190 | 178 | 0 | 32 | 47 | 0 | 43 | 0 | 34 | 16 | 0 | 0 | 0 | 18 | 58 | 3 | 0 | 0 | 2 | 40 | 30 | 0 | 0 | 163 | 0 | 61 | 86 | 0 | 206 | 0 | 0 | 0 | 290 | 11 | 5 | 0 | 145 | 0 | 0 | 133 | 0 | 95 | 20 | 38 | 100 | 81 | 197 | 63 | 35 | 47 | 5 | 135 | 17 | 97 | 106 | 99 | 36 | 380 | 50 | 38 | 72 | 17 | 0 | 0 | 27 | 48 | 17 | 315 | 36 | 0 | 590 | 0 | 751 | 0 | 0 | 75 | 0 |  | 884 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 210 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 25 | 0 | 40 | 0 | 4 | 35 | 990 | 220 | 0 | 0 | 5 | 100 | 25 | 0 | 0 | 860 | 36 | 200 | 1020 | 204 | 0 | 0 | 52 | 3 |  | 7223 | 5868 | 13091 | 3153 | 884 | 1591 | 0 | 1787 | 3663 | 216 | 0 | 148 | 58 | 1020 | 571 | 0 | 266 | 108.28
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 322 | 0 | 0 | 0 | 17 | 78 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 21 | 25 | 11 | 16 | 0 | 133 | 80 | 0 | 0 | 5 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 37 | 0 | 0 | 8 | 0 | 0 | 0 | 310 | 0 | 190 | 182 | 50 | 34 | 47 | 0 | 43 | 0 | 34 | 16 | 0 | 0 | 0 | 18 | 68 | 3 | 0 | 0 | 2 | 40 | 30 | 0 | 0 | 163 | 0 | 61 | 86 | 0 | 206 | 0 | 0 | 0 | 280 | 11 | 5 | 0 | 143 | 0 | 0 | 142 | 0 | 99 | 19 | 38 | 100 | 92 | 197 | 63 | 35 | 51 | 3 | 170 | 17 | 107 | 106 | 101 | 36 | 345 | 50 | 37 | 72 | 17 | 0 | 0 | 34 | 48 | 17 | 315 | 36 | 0 | 612 | 2 | 752 | 0 | 0 | 72 | 0 |  | 886 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 210 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 70 | 0 | 61 | 0 | 4 | 50 | 990 | 220 | 0 | 0 | 5 | 43 | 35 | 0 | 0 | 814 | 35 | 200 | 1017 | 196 | 0 | 0 | 50 | 0 |  | 7351 | 5929 | 13280 | 3173 | 886 | 1623 | 0 | 1959 | 3641 | 213 | 0 | 198 | 68 | 1017 | 500 | 2 | 239 | 108.28
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 322 | 0 | 0 | 0 | 17 | 78 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 21 | 25 | 10 | 16 | 0 | 133 | 80 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 37 | 0 | 0 | 2 | 0 | 0 | 0 | 300 | 0 | 201 | 187 | 40 | 33 | 46 | 0 | 43 | 0 | 34 | 16 | 0 | 0 | 0 | 18 | 70 | 4 | 0 | 0 | 2 | 40 | 30 | 0 | 0 | 163 | 0 | 61 | 86 | 0 | 206 | 0 | 0 | 0 | 310 | 11 | 5 | 0 | 145 | 0 | 0 | 133 | 0 | 108 | 17 | 38 | 103 | 92 | 197 | 62 | 35 | 59 | 4 | 175 | 19 | 110 | 106 | 98 | 36 | 350 | 50 | 45 | 72 | 17 | 0 | 0 | 29 | 48 | 17 | 300 | 36 | 0 | 612 | 8 | 751 | 0 | 0 | 64 | 0 |  | 884 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 210 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 105 | 0 | 61 | 0 | 6 | 90 | 1030 | 180 | 0 | 0 | 4 | 58 | 38 | 0 | 0 | 816 | 33 | 220 | 1019 | 178 | 0 | 0 | 43 | 0 |  | 7364 | 6005 | 13369 | 3073 | 884 | 1663 | 0 | 2059 | 3699 | 213 | 0 | 198 | 70 | 1019 | 483 | 8 | 249.255 | 108.29
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 318 | 0 | 0 | 0 | 24 | 78 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 21 | 25 | 10 | 8 | 0 | 134 | 80 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 38 | 0 | 0 | 2 | 0 | 0 | 0 | 340 | 0 | 208 | 158 | 36 | 33 | 48 | 0 | 43 | 0 | 34 | 24 | 0 | 0 | 0 | 18 | 74 | 5 | 0 | 0 | 1 | 39 | 30 | 0 | 0 | 163 | 0 | 57 | 86 | 0 | 202 | 0 | 0 | 0 | 315 | 11 | 5 | 0 | 145 | 0 | 0 | 133 | 0 | 104 | 13 | 38 | 103 | 78 | 194 | 62 | 35 | 51 | 3 | 200 | 53 | 110 | 106 | 92 | 36 | 360 | 50 | 35 | 72 | 17 | 0 | 0 | 23 | 50 | 17 | 335 | 36 | 0 | 612 | 8 | 755 | 0 | 0 | 50 | 0 |  | 885 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 210 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 61 | 0 | 5 | 95 | 1100 | 220 | 0 | 0 | 2 | 66 | 72 | 0 | 0 | 767 | 22 | 220 | 1020 | 143 | 0 | 0 | 24 | 0 |  | 7440 | 6094 | 13534 | 3197 | 885 | 1683 | 0 | 2143 | 3725 | 214 | 0 | 198 | 74 | 1020 | 387 | 8 | 254.03 | 108.27
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 318 | 0 | 0 | 0 | 24 | 78 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 14 | 21 | 30 | 10 | 8 | 0 | 132 | 80 | 0 | 0 | 8 | 0 | 0 | 0 | 0 |  | 6 | 25 | 0 | 0 | 38 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 192 | 128 | 36 | 33 | 45 | 0 | 43 | 0 | 34 | 24 | 0 | 0 | 0 | 18 | 72 | 5 | 0 | 0 | 1 | 39 | 30 | 0 | 0 | 163 | 0 | 60 | 83 | 0 | 201 | 0 | 0 | 0 | 315 | 11 | 2 | 0 | 145 | 0 | 0 | 132 | 0 | 96 | 8 | 38 | 103 | 80 | 189 | 62 | 17 | 57 | 2 | 52 | 54 | 96 | 106 | 95 | 36 | 345 | 50 | 22 | 72 | 38 | 0 | 0 | 15 | 83 | 17 | 285 | 36 | 0 | 612 | 13 | 755 | 0 | 0 | 31 | 0 |  | 884 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 180 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 113 | 0 | 60 | 0 | 4 | 113 | 1120 | 220 | 0 | 0 | 2 | 41 | 90 | 0 | 0 | 768 | 10 | 220 | 1015 | 83 | 0 | 0 | 12 | 0 |  | 7180 | 5959 | 13139 | 3060 | 884 | 1602 | 0 | 2112 | 3715 | 212 | 0 | 223 | 72 | 1015 | 231 | 13 | 440 | 108.27
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 305 | 0 | 0 | 0 | 24 | 78 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 14 | 21 | 30 | 10 | 8 | 0 | 133 | 80 | 0 | 0 | 9 | 0 | 0 | 0 | 0 |  | 6 | 72 | 55 | 0 | 39 | 8 | 0 | 5 | 0 | 0 | 0 | 285 | 0 | 190 | 128 | 34 | 33 | 47 | 0 | 43 | 0 | 35 | 33 | 0 | 0 | 0 | 18 | 69 | 6 | 0 | 0 | 1 | 39 | 30 | 0 | 0 | 130 | 0 | 63 | 86 | 0 | 202 | 0 | 0 | 0 | 280 | 11 | 2 | 0 | 145 | 0 | 0 | 133 | 0 | 110 | 2 | 38 | 133 | 83 | 203 | 62 | 35 | 61 | 0 | 52 | 54 | 103 | 106 | 96 | 36 | 330 | 50 | 5 | 90 | 95 | 0 | 17 | 5 | 88 | 17 | 295 | 17 | 0 | 600 | 1 | 743 | 0 | 0 | 10 | 0 |  | 885 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 210 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 113 | 0 | 70 | 0 | 1 | 113 | 960 | 220 | 0 | 0 | 0 | 14 | 90 | 0 | 0 | 758 | 4 | 180 | 1021 | 16 | 0 | 0 | 6 | 0 |  | 7302 | 5633 | 12935 | 3057 | 885 | 1490 | 0 | 2316 | 3512 | 213 | 0 | 307 | 69 | 1021 | 64 | 1 | 348.575 | 108.26
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 33 | 83 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 15 | 21 | 30 | 10 | 12 | 0 | 134 | 80 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 7 | 71 | 84 | 0 | 44 | 17 | 0 | 5 | 0 | 0 | 0 | 285 | 0 | 189 | 128 | 36 | 35 | 48 | 0 | 43 | 0 | 35 | 43 | 0 | 0 | 0 | 18 | 62 | 7 | 0 | 0 | 0 | 39 | 10 | 0 | 0 | 130 | 0 | 62 | 86 | 0 | 205 | 0 | 0 | 0 | 290 | 11 | 5 | 0 | 150 | 0 | 0 | 134 | 0 | 122 | 0 | 38 | 180 | 94 | 281 | 62 | 35 | 34 | 0 | 52 | 35 | 51 | 106 | 94 | 36 | 360 | 50 | 0 | 162 | 108 | 0 | 17 | 0 | 89 | 17 | 290 | 17 | 0 | 575 | 0 | 752 | 0 | 0 | 0 | 0 |  | 884 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 0 | 3 | 0 | 6 | 0 | 0 | 2 | 60 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 70 | 0 | 81 | 0 | 0 | 70 | 920 | 180 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 749 | 0 | 205 | 1018 | 0 | 0 | 0 | 0 | 0 |  | 7448 | 5381 | 12829 | 3009 | 884 | 1463 | 0 | 2354 | 3461 | 214 | 0 | 364 | 62 | 1018 | 0 | 0 | 354.305 | 108.26
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 97 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 21 | 30 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 18 | 71 | 84 | 0 | 42 | 0 | 0 | 20 | 0 | 0 | 0 | 285 | 0 | 192 | 130 | 42 | 32 | 49 | 0 | 51 | 0 | 35 | 43 | 0 | 0 | 0 | 18 | 86 | 10 | 0 | 0 | 0 | 39 | 10 | 0 | 0 | 163 | 0 | 63 | 86 | 0 | 204 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 265 | 0 | 0 | 151 | 0 | 132 | 0 | 38 | 188 | 99 | 320 | 91 | 105 | 51 | 0 | 52 | 17 | 51 | 106 | 94 | 36 | 346 | 50 | 0 | 162 | 107 | 0 | 21 | 0 | 89 | 17 | 285 | 145 | 0 | 612 | 0 | 753 | 0 | 0 | 0 | 0 |  | 885 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 134 | 9 | 0 | 0 | 0 | 0 | 17 | 6 | 86 | 0 | 0 | 15 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 105 | 15 | 82 | 0 | 0 | 100 | 1120 | 220 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 1110 | 0 | 307 | 1102 | 0 | 0 | 0 | 0 | 0 |  | 8131 | 6472 | 14603 | 3124 | 885 | 1563 | 0 | 2806 | 4162 | 214 | 0 | 661 | 86 | 1102 | 0 | 0 | 427 | 108.25
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 325 | 0 | 0 | 0 | 97 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 21 | 30 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 0 | 71 | 84 | 0 | 44 | 0 | 0 | 20 | 0 | 0 | 0 | 285 | 0 | 187 | 128 | 42 | 36 | 52 | 0 | 51 | 0 | 35 | 43 | 0 | 0 | 0 | 10 | 78 | 11 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 30 | 71 | 0 | 205 | 0 | 0 | 0 | 260 | 12 | 5 | 0 | 260 | 0 | 0 | 151 | 0 | 132 | 0 | 38 | 188 | 97 | 335 | 90 | 105 | 51 | 0 | 40 | 17 | 51 | 74 | 95 | 36 | 346 | 50 | 0 | 162 | 17 | 0 | 54 | 0 | 90 | 17 | 285 | 145 | 0 | 612 | 0 | 753 | 0 | 0 | 0 | 0 |  | 885 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 134 | 8 | 0 | 0 | 0 | 0 | 17 | 6 | 86 | 0 | 0 | 24 | 0 | 30 | 0 | 0 | 8 | 60 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 113 | 15 | 82 | 0 | 0 | 113 | 1130 | 220 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 1230 | 0 | 307 | 1119 | 0 | 0 | 0 | 0 | 0 |  | 7992 | 6760 | 14752 | 3175 | 885 | 1612 | 0 | 2714 | 4292 | 214 | 0 | 663 | 78 | 1119 | 0 | 0 | 380 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 325 | 0 | 0 | 0 | 97 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 15 | 21 | 17 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 0 | 71 | 84 | 0 | 32 | 0 | 0 | 28 | 0 | 0 | 0 | 310 | 0 | 212 | 130 | 51 | 36 | 52 | 0 | 51 | 0 | 35 | 43 | 0 | 0 | 0 | 18 | 80 | 13 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 30 | 60 | 0 | 205 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 195 | 0 | 0 | 152 | 0 | 132 | 0 | 12 | 185 | 97 | 336 | 90 | 105 | 17 | 0 | 30 | 17 | 17 | 70 | 94 | 12 | 346 | 16 | 0 | 162 | 17 | 0 | 54 | 0 | 89 | 17 | 320 | 54 | 0 | 612 | 0 | 753 | 0 | 0 | 0 | 0 |  | 886 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 26 | 10 | 86 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 8 | 60 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 113 | 15 | 91 | 0 | 0 | 113 | 1170 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 1242 | 0 | 307 | 1110 | 0 | 0 | 0 | 0 | 0 |  | 7705 | 6828 | 14533 | 3257 | 886 | 1638 | 0 | 2438 | 4344 | 214 | 0 | 566 | 80 | 1110 | 0 | 0 | 350 | 108.25
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 49 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 15 | 21 | 30 | 11 | 25 | 0 | 134 | 80 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 0 | 71 | 84 | 0 | 11 | 0 | 0 | 31 | 0 | 0 | 0 | 310 | 0 | 216 | 128 | 51 | 36 | 52 | 0 | 51 | 0 | 35 | 41 | 0 | 0 | 0 | 18 | 80 | 13 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 31 | 60 | 0 | 206 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 145 | 0 | 0 | 152 | 0 | 132 | 0 | 12 | 192 | 105 | 375 | 90 | 105 | 17 | 0 | 30 | 17 | 17 | 70 | 94 | 12 | 346 | 16 | 0 | 162 | 17 | 0 | 35 | 0 | 89 | 17 | 320 | 17 | 0 | 612 | 0 | 753 | 0 | 0 | 0 | 0 |  | 887 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 26 | 25 | 86 | 0 | 0 | 46 | 0 | 30 | 0 | 0 | 8 | 60 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 15 | 91 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 1247 | 0 | 307 | 1115 | 0 | 0 | 0 | 0 | 0 |  | 7618 | 6913 | 14531 | 3318 | 887 | 1649 | 0 | 2295 | 4423 | 214 | 0 | 550 | 80 | 1115 | 0 | 0 | 352 | 108.25
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 326 | 0 | 0 | 0 | 49 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 134 | 80 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 0 | 64 | 84 | 0 | 12 | 0 | 0 | 34 | 0 | 0 | 0 | 353 | 0 | 215 | 185 | 70 | 36 | 50 | 0 | 51 | 0 | 35 | 41 | 0 | 0 | 0 | 18 | 66 | 14 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 130 | 0 | 30 | 60 | 0 | 204 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 145 | 0 | 0 | 152 | 0 | 131 | 0 | 25 | 154 | 107 | 377 | 90 | 70 | 20 | 0 | 97 | 24 | 20 | 70 | 95 | 36 | 350 | 16 | 0 | 162 | 22 | 0 | 17 | 0 | 89 | 17 | 330 | 17 | 0 | 612 | 0 | 753 | 0 | 0 | 0 | 0 |  | 887 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 8 | 60 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 113 | 15 | 94 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 1241 | 0 | 307 | 1113 | 0 | 0 | 0 | 0 | 0 |  | 7727 | 6744 | 14471 | 3391 | 887 | 1605 | 0 | 2332 | 4417 | 214 | 0 | 446 | 66 | 1113 | 0 | 0 | 362 | 108.24
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 318 | 0 | 0 | 0 | 49 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 16 | 21 | 30 | 11 | 17 | 0 | 134 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 64 | 84 | 0 | 12 | 0 | 0 | 36 | 0 | 0 | 0 | 345 | 0 | 214 | 185 | 50 | 36 | 49 | 0 | 51 | 0 | 35 | 41 | 0 | 0 | 0 | 18 | 72 | 14 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 30 | 60 | 0 | 205 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 145 | 0 | 0 | 152 | 0 | 100 | 0 | 25 | 147 | 115 | 379 | 90 | 70 | 34 | 0 | 99 | 35 | 34 | 90 | 94 | 24 | 364 | 16 | 0 | 126 | 35 | 0 | 17 | 0 | 89 | 17 | 380 | 17 | 0 | 612 | 0 | 753 | 0 | 0 | 0 | 0 |  | 886 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 8 | 61 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 15 | 99 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 1224 | 0 | 307 | 1101 | 0 | 0 | 0 | 0 | 0 |  | 7787 | 6784 | 14571 | 3431 | 886 | 1713 | 0 | 2307 | 4401 | 214 | 0 | 446 | 72 | 1101 | 0 | 0 | 381 | 108.24
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 327 | 0 | 0 | 0 | 49 | 130 | 0 | 0 | 0 | 0 | 42 | 35 | 35 | 0 | 16 | 21 | 30 | 11 | 8 | 0 | 133 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 64 | 84 | 0 | 12 | 0 | 0 | 38 | 0 | 0 | 0 | 350 | 0 | 212 | 147 | 70 | 36 | 51 | 0 | 51 | 0 | 36 | 41 | 0 | 0 | 0 | 18 | 62 | 12 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 30 | 61 | 0 | 205 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 143 | 0 | 0 | 152 | 0 | 74 | 0 | 25 | 185 | 114 | 355 | 91 | 34 | 55 | 0 | 106 | 35 | 61 | 106 | 94 | 24 | 364 | 35 | 0 | 108 | 35 | 0 | 17 | 0 | 51 | 17 | 320 | 53 | 0 | 612 | 0 | 758 | 0 | 0 | 0 | 0 |  | 887 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 8 | 61 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 15 | 99 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 1241 | 0 | 307 | 1065 | 0 | 0 | 0 | 0 | 0 |  | 7720 | 6765 | 14485 | 3366 | 887 | 1675 | 0 | 2311 | 4423 | 213 | 0 | 483 | 62 | 1065 | 0 | 0 | 396 | 108.23
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9514800 | 0 |  | 0 | 2740000 | 0 | 0 | 0 | 836589 | 7112439 | 0 | 0 | 0 | 717984 | 2364000 | 0 | 0 | 0 | 0 | 572760 | 670061 | 686170 | 0 | 404400 | 499680 | 727400 | 252600 | 276480 | 0 | 3217462 | 1944000 | 50000 | 0 | 132906 | 0 | 0 | 0 | 0 |  | 123600 | 585744 | 586186 | 0 | 420480 | 35520 | 0 | 525600 | 0 | 0 | 0 | 8017200 | 0 | 4934000 | 3696727 | 510850 | 796608 | 1205280 | 0 | 1013204 | 0 | 454752 | 640181 | 0 | 0 | 0 | 396480 | 1539840 | 225600 | 0 | 0 | 13400 | 945000 | 550200 | 0 | 0 | 3646964 | 0 | 1326240 | 1953600 | 0 | 5140310 | 0 | 0 | 0 | 7321000 | 267216 | 93744 | 0 | 3369709 | 0 | 0 | 3036000 | 0 | 1994544 | 142695 | 502080 | 2896800 | 1313090 | 5931000 | 1660800 | 1003200 | 762764 | 27719 | 1339855 | 452055 | 1088104 | 1657560 | 2219280 | 472320 | 8526300 | 763200 | 360090 | 1961280 | 582109 | 0 | 383400 | 232091 | 1525440 | 432360 | 7813000 | 618909 | 0 | 13821817 | 77280 | 18218181 | 0 | 0 | 550536 | 0 |  | 21320727 | 0 | 6223392 | 0 | 0 | 0 | 0 | 0 | 52320 | 0 | 0 | 2591000 | 200742 | 19104 | 0 | 0 | 0 | 33199 | 38847 | 807904 | 0 | 0 | 71476 | 0 | 156438 | 0 | 0 | 98820 | 1405090 | 0 | 5033000 | 0 | 0 | 4031273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9312072 | 228000 | 0 | 1627584 | 107712 | 1291785 | 0 | 38512 | 1410528 | 27990000 | 5139410 | 0 | 0 | 33960 | 655200 | 1203456 | 0 | 0 | 22967270 | 237216 | 5934000 | 25063637 | 1452000 | 0 | 4273 | 352500 | 9570 |  | 165420825 | 147142017 | 312562842 | 76979552 | 21320727 | 36754599 | 0 | 40416850 | 95369358 | 5161462 | 0 | 5769775 | 1539840 | 25063637 | 4109762 | 77280 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27402624 | 0 |  | 0 | 8713200 | 0 | 0 | 0 | 14740698.18 | 21692938.95 | 0 | 0 | 0 | 12887812.8 | 45908880 | 0 | 0 | 0 | 0 | 10458597.6 | 10560161.36 | 12550049.3 | 0 | 303300 | 0 | 0 | 0 | 4951756.8 | 0 | 0 | 0 | 273000 | 0 | 2517239.64 | 0 | 0 | 0 | 0 |  | 2174124 | 10314951.84 | 10498591.26 | 0 | 8228793.6 | 584659.2 | 0 | 0 | 0 | 0 | 0 | 22367988 | 0 | 16380880 | 12384035.45 | 1650045.5 | 2684568.96 | 5279126.4 | 0 | 4062948.04 | 0 | 8144608.32 | 11561668.86 | 0 | 0 | 0 | 297360 | 10101350.4 | 701616 | 0 | 0 | 0 | 3685500 | 2052246 | 0 | 0 | 12472616.88 | 0 | 7360632 | 10197792 | 0 | 14341464.9 | 0 | 0 | 0 | 22621890 | 200412 | 71245.44 | 0 | 68742063.6 | 0 | 0 | 58321560 | 0 | 35123919.84 | 0 | 8942044.8 | 50259480 | 21771032.2 | 15717150 | 31654848 | 18820032 | 13683986.16 | 0 | 21906629.25 | 8787949.2 | 19520585.76 | 31675971.6 | 43076224.8 | 8412019.2 | 22679958 | 13027824 | 0 | 35871811.2 | 9767789.02 | 0 | 6851358 | 0 | 27488428.8 | 7324178.4 | 23204610 | 8714238.72 | 0 | 96338064.49 | 0 | 107487267.9 | 0 | 0 | 0 | 0 |  | 59911242.87 | 0 | 18359006.4 | 0 | 0 | 0 | 0 | 0 | 984139.2 | 0 | 0 | 8187560 | 951517.08 | 329352.96 | 0 | 0 | 0 | 594594.09 | 712842.45 | 13580866.24 | 0 | 0 | 1280135.16 | 0 | 2801804.58 | 0 | 0 | 74806.74 | 15498142.7 | 0 | 42478520 | 0 | 0 | 13303200.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27191250.24 | 3894240 | 0 | 32258714.88 | 1904348.16 | 25732357.2 | 0 | 0 | 27984875.52 | 181375200 | 15983565.1 | 0 | 0 | 0 | 0 | 20879961.6 | 0 | 0 | 167661071 | 0 | 44208300 | 165670640.57 | 0 | 0 | 0 | 0 | 0 |  | 1188552398.62 | 893792255.64 | 2082344654.26 | 222992113.79 | 59911242.87 | 119857941.19 | 0 | 745229147.49 | 655046566.09 | 0 | 0 | 103535651.86 | 10101350.4 | 165670640.57 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 328 | 0 | 0 | 0 | 16 | 78 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 21 | 25 | 11 | 16 | 0 | 136 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 35 | 0 | 0 | 2 | 0 | 0 | 0 | 305 | 0 | 190 | 178 | 0 | 32 | 47 | 0 | 43 | 0 | 34 | 16 | 0 | 0 | 0 | 18 | 58 | 3 | 0 | 0 | 2 | 40 | 30 | 0 | 0 | 163 | 0 | 61 | 86 | 0 | 206 | 0 | 0 | 0 | 290 | 11 | 5 | 0 | 145 | 0 | 0 | 133 | 0 | 95 | 20 | 38 | 100 | 81 | 197 | 63 | 35 | 47 | 5 | 135 | 17 | 97 | 106 | 99 | 36 | 380 | 50 | 38 | 72 | 17 | 0 | 0 | 27 | 48 | 17 | 315 | 36 | 0 | 590 | 0 | 751 | 0 | 0 | 75 | 0 |  | 884 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 210 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 25 | 0 | 40 | 0 | 4 | 35 | 990 | 220 | 0 | 0 | 5 | 100 | 25 | 0 | 0 | 860 | 36 | 200 | 1020 | 204 | 0 | 0 | 52 | 3 |  | 13091 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 325 | 0 | 0 | 0 | 97 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 21 | 30 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 84 | 0 | 44 | 0 | 0 | 20 | 0 | 0 | 0 | 285 | 0 | 187 | 128 | 42 | 36 | 52 | 0 | 51 | 0 | 35 | 43 | 0 | 0 | 0 | 10 | 78 | 11 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 30 | 71 | 0 | 205 | 0 | 0 | 0 | 260 | 12 | 5 | 0 | 260 | 0 | 0 | 151 | 0 | 132 | 0 | 38 | 188 | 97 | 335 | 90 | 105 | 51 | 0 | 40 | 17 | 51 | 74 | 95 | 36 | 346 | 50 | 0 | 162 | 17 | 0 | 54 | 0 | 90 | 17 | 285 | 145 | 0 | 612 | 0 | 753 | 0 | 0 | 0 | 0 |  | 885 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 134 | 8 | 0 | 0 | 0 | 0 | 17 | 6 | 86 | 0 | 0 | 24 | 0 | 30 | 0 | 0 | 8 | 60 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 113 | 15 | 82 | 0 | 0 | 113 | 1130 | 220 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 1230 | 0 | 307 | 1119 | 0 | 0 | 0 | 0 | 0 |  | 14752 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 225 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 100 | 130 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 21 | 30 | 12 | 25 | 0 | 134 | 80 | 100 | 0 | 17 | 0 | 0 | 0 | 0 |  | 6 | 75 | 84 | 0 | 40 | 50 | 0 | 20 | 0 | 0 |  | 350 | 0 | 210 | 128 | 80 | 36 | 52 | 0 | 51 | 0 | 35 | 43 | 0 | 0 |  | 10 | 90 | 15 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 30 | 71 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 280 | 0 | 0 | 160 | 0 | 132 | 0 | 38 | 200 | 120 | 350 | 90 | 105 | 105 | 0 | 50 | 54 | 110 | 106 | 95 | 100 | 360 | 60 | 0 | 162 | 108 | 0 | 54 | 0 | 90 | 17 | 300 | 163 | 0 | 612 | 60 | 750 | 0 | 0 |  |  |  | 900 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 135 | 10 | 110 | 0 | 0 | 0 | 40 | 20 | 90 | 28 | 0 | 46 | 0 | 30 | 0 | 0 | 8 | 60 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 72 | 0 | 113 | 0 | 99 | 0 | 0 | 113 | 1244 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 1230 | 0 | 307 | 1100 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 48 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 21 | 30 | 12 | 16 | 0 | 132 | 80 | 80 | 0 | 8 | 0 |  | 0 | 0 | 0 | 6 | 65 | 51 | 0 | 0 | 50 | 0 | 10 | 0 | 0 | 0 | 340 | 0 | 210 | 108 | 70 | 36 | 52 | 0 | 51 | 0 | 35 | 16 | 0 | 0 |  | 10 | 90 | 10 | 0 | 0 | 1.6 | 38 | 0 | 0 | 0 | 163 | 0 | 30 | 64 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 270 | 0 | 0 | 125 | 0 | 130 | 20 | 38 | 180 | 50 | 350 | 58 | 50 | 105 | 5 | 50 | 54 | 92 | 106 | 70 | 90 | 350 | 50 | 50 | 162 | 105 | 0 | 17 | 35 | 65 | 17 | 300 | 35 | 0 | 612 | 42 | 750 | 0 | 0 | 70 |  |  | 894 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 135 | 10 | 64 | 0 | 0 | 0 | 30 | 0 | 50 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 70 | 0 | 113 | 0 | 35 | 0 | 8 | 95 | 1244 | 220 |  | 17 | 6 | 100 | 115 | 0 | 0 | 1200 | 30 | 307 | 1000 | 170 | 0 |  | 20 | [5 empty] | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 21 | 30 | 13 | 8 | 0 | 132 | 80 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 357 | 0 | 191 | 108 | 80 | 36 | 52 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 5 | 62 | 4 | 0 | 0 | 1 | 40 | 0 | 0 | 0 | 120 | 0 | 31 | 61 | 0 | 211 | 0 | 0 | 0 | 275 | 12 | 5 | 0 | 90 | 0 | 0 | 125 | 0 | 35 | 10 | 0 | 103 | 0 | 347 | 73 | 17 | 34 | 2 | 52 | 17 | 68 | 106 | 94 | 0 | 346 | 0 | 24 | 54 | 0 | 0 | 0 | 13 | 50 | 17 | 320 | 0 | 0 | 572 | 0 | 750 | 0 | 0 | 31 | 0 | 0 | 885 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59 | 0 | 200 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 70 | 0 | 84 | 0 | 3 | 35 | 1000 | 180 | 0 | 0 | 2 | 46 | 35 | 0 | 0 | 1114 | 16 | 250 | 1013 | 93 | 0 | 0 | 27 | 1 | 0 |  |  |  | 113734151 | 21320727 | 0 | 95369358 | 46186625 | 1539840 | 4109762 | 77280 | 5161462 |  |  |  | 287499205
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [6 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 113.7342 | 21.3207 | 0 | 95.3694 | 46.1866 | 1.5398 | 4.1098 | 0.07728 | 5.1615
| Minimum Generation |  | 10778 | 6:00
| Highest Generation |  | 14752 | 19:30 | [129 empty] | 0 | [75 empty] | 287.4992
| Day Peak Generation |  | 13091 | 12:00
| Evening Peak Generation |  | 14752 | 19:30 | [205 empty] | 202699852
| HVDC Max Flow |  | 887 | 2:00 | [205 empty] | 202.6999
| HVDC EvPeak Flow |  | 885 | 19:30
| Load factor L.F |  | 88.28% | [168 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-09-18
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-09-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13091 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 12280
Evening Peak Generation : |  |  | 14752 | MW Hour : | 19:30 | Available Max Generation : |  | 16131
E.P. Demand (at gen end) : |  |  | 15150 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 15400
Maximum Generation : |  |  | 14752 | MW Hour : | 19:30 | Reserve(Generation end) |  | 731
Total Gen. (MKWH) : |  |  | 312.5628 | System Load Factor : | 88.28% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 498 | MW at | 22:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-09-18
Actual : |  | 108.17 | Ft.(MSL) , | Rule curve : | 102.91 | Ft.( MSL )
Gas Consumed : |  | Total = | 811.04 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 342850054.98 | Adani : | 165670640.57
: |  |  | Coal : | 655046566.09 | Oil : | 848764799.35 | Total : | 2012332060.99
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 115 | 2760:00 | 5018.7141 |  |  | 0 | -12.35%
Chittagong Area |  | 0 | 0:00 | 1381.88 |  |  | 0 | -10.59%
Khulna Area |  | 0 | 0:00 | 1936.5624 |  |  | 0 | -10.21%
Rajshahi Area |  | 0 | 0:00 | 1683.9775 |  |  | 0 | -9.816%
Cumilla Area |  | 60 | 1440:00 | 1385.229 |  |  | 0 | -10.06%
Mymensingh Area |  | 160 | 3840:00 | 1030.6659 |  |  | 0 | -9.718%
Sylhet Area |  | 0 | 0:00 | 577.2872 |  |  | 0 | -10.38%
Barisal Area |  | 0 | 0:00 | 481.4952 |  |  | 0 | -9.655%
Rangpur Area |  | 45 | 1080:00 | 941.7111 |  |  | 0 | -9.663%
Total |  | 380 |  | 14437.5225 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Ashuganj south
8) Megnaghat(MPL) GT-1
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:00 | 11:58 | Patuakhali-Payra 132kV Ckt-1 Project Work S/D from Payra 400/132/33kV end Due to Line maintenance by BCPCL
08:00 | 11:58 | Patuakhali-Payra 132kV Ckt-1 Project Work S/D from Payra 400/132/33kV end Due to Line maintenance
09:22 | 17:12 | Gopalganj 400/132kV S/S 230kV Barisal CKT-01 Project Work S/D
09:23 | 17:12 | Barishal 230/132kV S/S Gopalgonj CKT-1 Scheduled S/D
09:30 | 14:26 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to Red hot maintenance works.
09:30 | 14:26 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to Red hot maintenance works.
09:38 | 15:53 | Gopalganj-Madhumati 132kV Ckt-1 Scheduled S/D from Gopalganj 132/33kV end Due to Energy meter change.
09:45 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT2
10:20 | 14:46 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to UF Relay test by SPMD.
10:20 | 14:46 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to UF Relay test by SPMD.
11:11 |  | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- ST
11:25 | 13:07 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to 33 kv bus s/d required due to 33 kv langalband feeder | [5 empty] | 40 MW load interruption.
DS redhot maintenance
11:26 | 13:05 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to 33 kv bus s/d required due to 33 kv langalband feeder
DS redhot maintenance
11:35 |  | Barishal 132/33kV S/S Bus B Scheduled S/D Due to Loop conductor change.
11:37 |  | Barishal 132/33kV S/S 132 kV Capacitor Bank Tripped showing Under voltage, switching synchroning. relays Due to N/A
| 11:58 | Patuakhali-Payra 132kV Ckt-1 is restored.
12:00 |  | Day Peak Generation: 13091 MW.
12:10 | 13:07 | Goalpara 132/33kV S/S T-6 LT Forced S/D Due to Maintenence works.
12:12 | 13:05 | Goalpara 132/33kV S/S T-6 HT Forced S/D Due to Works of maintenence.
14:44 | 17:17 | Magura-Narail 132kV Ckt-1 Forced S/D from Narail 132/33kV end Due to R phase LA of Narail grid bay-01
change due to created bad noise. and from Magura 132/33kV end Due to Maintenance work at Narail substation
15:58 | 17:42 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT Scheduled S/D Due to Auction listed spare 33 kv PT remove from bay.
15:58 | 17:42 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Scheduled S/D Due to Auction listed Spare PT remove from bay.
16:02 | 16:58 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Scheduled S/D from Gopalganj 132/33kV end Due to Meter change by meter Division dhaka
16:50 | 17:58 | Madunaghat 132/33kV S/S TR-2(517T) LT Scheduled S/D Due to Red hot maintenance work by BPDB for Old
WASA 33kv Feeder at different point.
16:51 | 17:57 | Madunaghat 132/33kV S/S TR-2(517T) HT Scheduled S/D
19:30 |  | Evening Peak Gen.14753 MW
23:15 | 23:33 | Hathazari 230/132/33kV S/S T-01 LT Tripped showing MCGGT-1 Sec trip C ph, E/F inst relays Due to New charia | [5 empty] | 35 MW load interruption.
-02 33kV fault E/F& O/C inst with T-1 Sec trip C ph, E/F
06:20 | 06:26 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Deff. O/c, time delay o/c relays Due to Pbs Nalchity 33kv feeder fault | [5 empty] | 60 MW load interruption.
06:23 |  | Bhandaria 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Khatalia pbs work | [5 empty] | 15 MW load interruption.
06:24 |  | Bhandaria 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Kathalia pbs maintenance work
07:00 |  | Minimum Generation = 12,284MW
07:09 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to 33 kV source ds repair of Nabogram Feeder by Jhalokathi PBS | [5 empty] | 25 MW load interruption.
07:10 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to 33 kV source ds repair of Nabogram Feeder by Jhalokathi PBS
07:13 |  | Madaripur 132/33kV S/S T1-405T HT Scheduled S/D Due to High temperature maintenance | [5 empty] | 10 MW load interruption.
07:13 |  | Madaripur 132/33kV S/S T1-405T LT Scheduled S/D Due to High temperature maintenance

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-09-18
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 410 | 9514800
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 2740000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Reserve NENP
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Reserve NENP
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 836589
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve NENP
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0 | Reserve NENP
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 325 | 7112439
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 97 | 717984
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 572760
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 130 | 2364000 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 670061
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 686170 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 36 | 904080 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 727400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 10 | 252600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 276480 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 3369709 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1994544 | Engine problem
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1003200 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 50 | 763200 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1961280
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 232091
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432360 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5915 | 2233 | 37131747
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 50000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 132906 | Meghnaghat Bus section O/L
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 142695
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 35520 | Meghnaghat Bus section O/L
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 214 | 5161462
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 0 | 0
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 51 | 762764 | Meghnaghat Bus section O/L
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 71 | 585744
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 586186 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 38 | 502080 | Meghnaghat Bus section O/L
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 525600
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 44 | 420480 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27719
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 40 | 1339855 | Meghnaghat Bus section O/L
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 452055
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 1088104 | Meghnaghat Bus section O/L
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 472320 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 582109 | Meghnaghat Bus section O/L
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 145 | 618909 | Fuel shortage
60 | SS Power I |  | SS Power | 2*612 | 1224 | 612 | 13821817
| Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 77280
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 753 | 18218181
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 2210 | 45603786
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 187 | 4934000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 8017200 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 285 | 7813000 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 796608
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 52 | 1205280 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 128 | 3696727 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1013204
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 97 | 1313090 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 454752 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 42 | 510850 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 188 | 2896800 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 78 | 1539840
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 640181 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 10 | 396480 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 74 | 1657560 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 2219280 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1525440 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 550536
| Cumilla Area Total |  |  |  | 2917 | 1776 | 41180828
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 11 | 225600 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13400
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 151 | 3036000 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 90 | 1660800 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 360090
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 123600 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 54 | 383400 | Fuel shortage
| Mymensingh Area Total |  |  |  | 646 | 306 | 5802890
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 945000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 550200 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3646964
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 93744 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 1326240
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 71 | 1953600 | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 205 | 5140310 | Under maint.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 267216 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 7321000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 335 | 5931000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 346 | 8526300 | FGMO
| Sylhet Area Total |  |  |  | 2417 | 1467 | 35701574
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 885 | 21320727
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Reserve NENP
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 52320 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 233 | 6223392 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 228000 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 107712 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 655200
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 1230 | 22967270 | Unit-1 under maint
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 2433 | 51554621
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 19104 | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 8 | 200742
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 134 | 2591000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1130 | 27990000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5139410
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 5934000
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 4273
| Barisal Area Total |  |  |  | 2236 | 1799 | 41878529
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 17 | 33199 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 6 | 38847 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 71476 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 160 | 4031273
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9312072 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 156438 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 98820 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 807904 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1627584
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1410528 | Fuel shortage
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33960
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1119 | 25063637
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 352500
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 9570
| Rajshahi Area Total |  |  |  | 3449 | 2090 | 43047808
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 60 | 1405090
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 5033000 | Under maint.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 82 | 1291785 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38512
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 96 | 1203456
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 237216
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1452000
| Rangpur Area Total |  |  |  | 950 | 438 | 10661059
| Total |  |  |  | 27086 | 14752 | 312562842
| Eastern Grid Total |  |  |  | 16752 | 7992 | 165420825
| Western Grid Total |  |  |  | 10334 | 6760 | 147142017
| National Grid Total |  |  |  | 27086 | 14752 | 312562842
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-09-2024
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9664.61 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4529.7 | MW
i) Dhaka area |  |  | 5222.31 |  | MW | i) Khulna area |  |  |  | 1646 | MW
ii) Chattogram area |  |  | 1407.8 |  | MW | ii) Barishal area |  |  |  | 455.9 | MW
iii) Cumilla area |  |  | 1265.5 |  | MW | iii) Rajshahi area |  |  |  | 1440.8 | MW
iv) Mymensingh area |  |  | 1087 |  | MW | iv) Rangpur area |  |  |  | 987 | MW
v) Sylhet area |  |  | 682 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14194.31 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 19 | 17:00 | 67 | Jamalpur | 108 | 00:00 | 133 | Rahim | 53 | 08:00
2 | AKSML | 94 | 16:00 | 68 | Jashore | 119 | 18:30 | 134 | Rajbari | 84 | 18:30
3 | Aftabnagar | 36 | 13:00 | 69 | Jhenaidah | 124 | 19:00 | 135 | Rajendrapur | 102 | 20:00
4 | Agargaon | 118 | 14:00 | 70 | Joydebpur | 218 | 18:30 | 136 | Rajshahi | 111 | 22:00
5 | Agrabad | 98 | 16:00 | 71 | Joypurhat | 65 | 19:30 | 137 | Rajshahi-230 | 73 | 20:00
6 | Amnura | 63 | 21:00 | 72 | Juldah | 19 | 07:00 | 138 | Ramganj | 120 | 22:00
7 | Ashuganj | 87.5 | 20:00 | 73 | KSRM | 35 | 14:00 | 139 | Rampur | 42 | 23:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 272 | 19:00 | 140 | Rangamati | 19 | 19:30
9 | BSRM | 138 | 15:00 | 75 | Kachua | 84 | 22:00 | 141 | Rangpur | 159 | 18:30
10 | Bagerhat | 60 | 18:30 | 76 | Kallyanpur | 117 | 18:30 | 142 | Ruppur | 7.2 | 16:00
11 | Bakulia | 103 | 18:30 | 77 | Kalurghat | 38 | 17:00 | 143 | SSM | 0 | 00:00
12 | Banani | 67.6 | 13:00 | 78 | Kamrangirchar | 56 | 13:00 | 144 | Saidpur | 115 | 20:00
13 | Bangabhaban | 26 | 11:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 124 | 22:00
14 | Barapukuria | 64 | 19:00 | 80 | Kazla | 114 | 12:00 | 146 | Satmasjid | 102 | 18:30
15 | Barguna | 22 | 22:00 | 81 | Keranigonj | 74 | 00:00 | 147 | Savar | 203 | 18:00
16 | Barishal | 112 | 20:00 | 82 | Khagrachori | 32 | 19:00 | 148 | SevenRings | 3.72 | 16:00
17 | Barishal-230 | 94 | 19:30 | 83 | Khulna | 92 | 19:00 | 149 | ShahCement | 21 | 23:00
18 | Baroaulia | 56 | 21:00 | 84 | Khulshi | 189 | 12:00 | 150 | Shahjadpur | 84 | 19:00
19 | Baroirhat | 72 | 18:30 | 85 | Kishoreganj | 152 | 00:00 | 151 | Shahjibazar | 142 | 19:00
20 | Bashundhara | 177 | 13:00 | 86 | Kodda | 279 | 23:00 | 152 | Shahmirpur | 50 | 01:00
21 | BashundharaCement | 6 | 01:00 | 87 | Kulaura | 54 | 22:00 | 153 | Shariatpur | 92 | 22:00
22 | Beanibazar | 84 | 20:00 | 88 | Kurigram | 70 | 18:00 | 154 | Sherpur | 134 | 18:00
23 | Benapole | 66 | 18:30 | 89 | Kushtia | 134 | 19:00 | 155 | Shikalbaha | 30 | 18:30
24 | Bhaluka | 120 | 11:00 | 90 | Lalbag | 84 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 51.5 | 22:00 | 91 | Lalmonirhat | 65 | 18:30 | 157 | Shitalakhya | 83.8 | 16:00
26 | Bhangura | 48 | 21:00 | 92 | MI_Cement | 4.3 | 17:00 | 158 | Sholosohor | 47 | 16:00
27 | Bheramara(GK) | 63 | 22:00 | 93 | Madanganj | 32 | 19:30 | 159 | Shyampur | 156 | 11:00
28 | Bhulta | 223 | 06:00 | 94 | Madaripur | 113 | 23:00 | 160 | Siddhirganj | 124 | 18:30
29 | Bog-Sherpur | 64 | 19:00 | 95 | Madartek | 82.02 | 23:00 | 161 | Sirajganj | 120 | 19:30
30 | Bogura | 171 | 22:00 | 96 | Madunaghat | 53 | 18:00 | 162 | Sonargaon | 90 | 15:00
31 | Borhanuddin | 85 | 22:00 | 97 | Magura | 63 | 18:30 | 163 | Sreemongol | 82 | 23:00
32 | Brahmanbaria | 134 | 11:00 | 98 | Mahasthangarh | 83 | 23:00 | 164 | Sreepur | 108 | 18:30
33 | Cantonment | 110 | 13:00 | 99 | Manikganj | 130 | 19:00 | 165 | Srinagar | 46.2 | 20:00
34 | Chandpur | 76 | 15:00 | 100 | Maniknagar | 69 | 13:00 | 166 | Sunamganj | 64 | 18:30
35 | Chandraghona | 37 | 19:00 | 101 | Matarbari | 47 | 22:00 | 167 | Sylhet | 52 | 19:00
36 | Chapai | 61 | 21:00 | 102 | Matuail | 56 | 15:00 | 168 | Sylhet-132 | 138 | 18:00
37 | Charsaidpur | 25 | 00:00 | 103 | Millgate | 125 | 12:00 | 169 | TK | 33.4 | 22:00
38 | Chauddagram | 71 | 22:00 | 104 | Mirpur | 143 | 19:00 | 170 | Tangail | 189 | 21:00
39 | Chhatak | 41 | 19:30 | 105 | Mirsorai | 4 | 00:00 | 171 | Thakurgaon | 109 | 19:00
40 | Chowmuhani | 222 | 21:00 | 106 | Mirzapur | 42 | 21:00 | 172 | Tongi | 134 | 15:00
41 | Chuadanga | 110 | 18:30 | 107 | Mithapukur | 62 | 18:30 | 173 | Ullahpara | 28 | 19:00
42 | Coxsbazar | 114 | 14:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 59 | 18:30
43 | Cumilla(N) | 169 | 22:00 | 109 | Mogbazar | 113.2 | 16:00 | 175 | Uttara | 70 | 15:00
44 | Cumilla(S) | 178 | 19:00 | 110 | Mongla | 38 | 14:00 | 176 | UttaraNew | 62 | 14:00
45 | Daudkandi | 167 | 19:30 | 111 | Motijheel | 41 | 13:00 | 177 | Zigatola | 99 | 18:30
46 | Dhaka | 46 | 15:00 | 112 | Munshiganj | 105 | 22:00
47 | Dhamrai | 132 | 18:30 | 113 | Mymensingh | 255 | 20:00
48 | Dhanmondi | 131 | 13:00 | 114 | Naogaon | 132 | 23:00
49 | Dohazari | 96 | 22:00 | 115 | Narail | 60 | 19:00
50 | Faridpur | 166 | 20:00 | 116 | Narinda | 73.5 | 13:00
51 | Fatullah | 110 | 17:00 | 117 | Narshingdi | 156 | 18:00
52 | Fenchuganj | 47 | 23:00 | 118 | Natore | 149 | 22:00
53 | Feni | 107 | 23:00 | 119 | Nawabganj | 49.2 | 22:00
54 | GPH | 95 | 16:00 | 120 | Netrakona | 119 | 00:00
55 | Ghatail | 46 | 18:30 | 121 | New | 52 | 12:00
56 | Ghorashal | 62 | 23:00 | 122 | Niamatpur | 68 | 21:00
57 | Goalpara | 36 | 19:30 | 123 | Noapara | 43 | 19:30

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-09-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 381 | 03:00 | 368 | 15:00 | Kaliakoir | 372 | 00:00 | 358 | 14:00
| Ashuganj | N/A | N/A | N/A | N/A | Madunaghat | 403 | 17:00 | 388 | 09:00
| Bhulta | 396 | 03:00 | 38 | 23:00 | Meghnaghat | 376 | 02:00 | 365 | 10:00
| Bibiana | 393 | 03:00 | 385 | 12:00 | Payra | 409 | 18:00 | 401 | 19:30
| BIPTC | 404 | 06:00 | 395 | 22:00 | Rahanpur | 402 | 17:00 | 390 | 20:00
| Bogura | 390 | 17:00 | 376 | 21:00 | Rampal | 400 | 06:00 | 389 | 23:00
| Gopalganj | 394 | 18:00 | 382 | 21:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 02:00 | 210 | 14:00 | Haripur | 228 | 01:00 | 219 | 09:00
| AKSML | 242 | 17:00 | 227 | 09:00 | Hasnabad | 227 | 00:00 | 216 | 15:00
| Aminbazar | 228 | 03:00 | 217 | 10:00 | Hathazari | 243 | 18:30 | 232 | 09:00
| Ashuganj | 233 | 18:00 | 225 | 09:00 | Ishurdi | 231 | 17:00 | 224 | 21:00
| Ashuganj-400 | 233 | 18:00 | 225 | 09:00 | Jhenaidah | 226 | 06:00 | 216 | 21:00
| Baghabari | 230 | 01:00 | 224 | 20:00 | Kaliakoir | 231 | 00:00 | 221 | 09:00
| Barapukuria | 221 | 17:00 | 212 | 18:30 | Keranigonj | 227 | 02:00 | 215 | 15:00
| Barapukuria-230 | 221 | 17:00 | 212 | 18:30 | Khulna(S) | 228 | 06:00 | 219 | 18:30
| Barishal | 235 | 17:00 | 225 | 21:00 | Madunaghat | 244 | 17:00 | 232 | 09:00
| Bheramara | 233 | 11:00 | 221 | 21:00 | Maniknagar | 229 | 03:00 | 218 | 15:00
| Bhulta | 230 | 01:00 | 220 | 14:00 | Meghnaghat | 238 | 00:00 | 225 | 13:00
| Bibiana | 225 | 03:00 | 219 | 15:00 | Meghnaghat-400 | 231 | 02:00 | 222 | 09:00
| BIPTC | 231 | 06:00 | 222 | 12:00 | Mirsorai | 239 | 19:00 | 224 | 09:00
| Bogura | 229 | 17:00 | 219 | 22:00 | Rajshahi | 231 | 17:00 | 221 | 12:00
| Bogura-400 | 230 | 17:00 | 221 | 21:00 | Rampal | 229 | 18:00 | 219 | 22:00
| Borhanuddin | 239 | 08:00 | 233 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 239 | 19:00 | 224 | 09:00 | Rampura | 229 | 04:00 | 216 | 15:00
| Cumilla(N) | 228 | 17:00 | 218 | 09:00 | Shikalbaha | 244 | 17:00 | 228 | 09:00
| Faridpur | 231 | 17:00 | 222 | 21:00 | Shyampur | 229 | 02:00 | 217 | 15:00
| Fenchuganj | 227 | 13:00 | 222 | 23:00 | Siddhirganj | 231 | 03:00 | 220 | 15:00
| Ghorashal | 234 | 00:00 | 225 | 15:00 | Sirajgonj | 236 | 05:00 | 231 | 09:00
| Ghorashal-230 | 229 | 02:00 | 218 | 09:00 | Sreepur | 227 | 00:00 | 221 | 09:00
| Gopalganj | 232 | 06:00 | 224 | 21:00 | Tongi | 232 | 04:00 | 218 | 09:00
| GPH | 241 | 18:30 | 226 | 09:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 135 | 03:00 | 124 | 12:00 | Kushtia | 134 | 05:00 | 127 | 21:00
| Agargaon | 133 | 02:00 | 124 | 15:00 | Lalbag | 132 | 02:00 | 123 | 15:00
| Agrabad | 137 | 17:00 | 128 | 08:00 | Lalmonirhat | 130 | 17:00 | 115 | 18:30
| AKS | 136 | 18:00 | 128 | 08:00 | Madanganj | 127 | 01:00 | 122 | 15:00
| Aminbazar | 137 | 00:00 | 125 | 15:00 | Madaripur | 129 | 05:00 | 125 | 14:00
| Amnura | 136 | 17:00 | 123 | 21:00 | Madartek | 134 | 02:00 | 124 | 14:00
| Ashuganj | 138 | 06:00 | 135 | 08:00 | Madunaghat | 138 | 17:00 | 130 | 09:00
| Bagerhat | 129 | 18:00 | 120 | 14:00 | Magura | 132 | 05:00 | 123 | 18:30
| Bakulia | 139 | 18:30 | 129 | 09:00 | Mahasthangarh | 135 | 17:00 | 126 | 18:30
| Banani | 134 | 02:00 | 122 | 15:00 | Manikganj | 125 | 00:00 | 118 | 08:00
| Bangabhaban | 129 | 01:00 | 120 | 15:00 | Maniknagar | 130 | 02:00 | 120 | 15:00
| Barapukuria | 137 | 17:00 | 128 | 18:30 | Matarbari | 130 | 18:30 | 116 | 00:00
| Barguna | 134 | 07:00 | 128 | 23:00 | Matuail | 129 | 01:00 | 123 | 09:00
| Barishal | 133 | 05:00 | 120 | 21:00 | Millgate | 133 | 01:00 | 122 | 15:00
| Barishal-230 | 131 | 08:00 | 123 | 23:00 | Mirpur | 136 | 02:00 | 128 | 09:00
| Baroaulia | 138 | 18:00 | 129 | 08:00 | Mirzapur | 127 | 19:00 | 119 | 08:00
| Baroirhat | 133 | 18:00 | 119 | 05:00 | Mithapukur | 132 | 16:00 | 122 | 18:30
| Bashundhara | 134 | 01:00 | 122 | 15:00 | MI_Cement | 135 | 01:00 | 125 | 15:00
| BashundharaCement | 127 | 01:00 | 122 | 15:00 | Modern | 138 | 18:30 | 129 | 09:00
| Beanibazar | 123 | 06:00 | 118 | 20:00 | Mogbazar | 135 | 00:00 | 124 | 15:00
| Benapole | 129 | 04:00 | 118 | 18:30 | Mongla | 128 | 05:00 | 120 | 21:00
| Bhaluka | 126 | 05:00 | 119 | 09:00 | Motijheel | 129 | 01:00 | 120 | 15:00
| Bhandaria | 125 | 03:00 | 115 | 22:00 | Munshiganj | 128 | 17:00 | 122 | 09:00
| Bhangura | 136 | 01:00 | 131 | 21:00 | Mymensingh | 133 | 00:00 | 115 | 14:00
| Bheramara | 134 | 01:00 | 130 | 20:00 | Naogaon | 132 | 17:00 | 123 | 23:00
| Bheramara(GK) | 135 | 04:00 | 130 | 20:00 | Narail | 132 | 06:00 | 121 | 18:30
| Bhulta | 119 | 18:00 | 114 | 09:00 | Narinda | 130 | 02:00 | 120 | 15:00
| Bog-Sherpur | 134 | 14:00 | 125 | 22:00 | Narshingdi | 119 | 02:00 | 113 | 15:00
| Bogura | 138 | 17:00 | 130 | 22:00 | Natore | 134 | 17:00 | 128 | 18:30
| Bogura-230 | 138 | 17:00 | 130 | 22:00 | Nawabganj | 132 | 03:00 | 124 | 15:00
| Brahmanbaria | 130 | 00:00 | 125 | 10:00 | Netrakona | 132 | 19:30 | 120 | 23:00
| Cantonment | 133 | 02:00 | 123 | 15:00 | New | 133 | 00:00 | 124 | 10:00
| Chandpur | 137 | 17:00 | 121 | 00:00 | Niamatpur | 134 | 17:00 | 129 | 20:00
| Chandraghona | 139 | 17:00 | 132 | 09:00 | Noapara | 130 | 06:00 | 122 | 18:30
| Chapai | 131 | 01:00 | 125 | 21:00 | Pabna | 133 | 01:00 | 127 | 18:30
| Charsaidpur | 128 | 00:00 | 123 | 09:00 | Palashbari | 130 | 16:00 | 119 | 18:30
| Chauddagram | 133 | 17:00 | 120 | 09:00 | Panchagarh | 138 | 17:00 | 119 | 18:30
| Chhatak | 125 | 06:00 | 120 | 19:30 | Patuakhali | 133 | 02:00 | 130 | 18:30
| Chowmuhani | 132 | 16:00 | 117 | 00:00 | Payra | 135 | 03:00 | 132 | 11:00
| Chuadanga | 129 | 05:00 | 116 | 18:30 | PHP | 131 | 16:00 | 120 | 04:00
| Coxsbazar | 129 | 17:00 | 117 | 00:00 | Postogola | 134 | 00:00 | 127 | 15:00
| Cumilla(N) | 133 | 18:00 | 126 | 09:00 | Purbachal | 135 | 03:00 | 122 | 09:00
| Cumilla(S) | 133 | 18:00 | 124 | 09:00 | Purbasadipur | 133 | 17:00 | 117 | 18:30
| Daudkandi | 127 | 18:00 | 118 | 09:00 | Rahanpur | 136 | 17:00 | 131 | 20:00
| Dhaka | 136 | 00:00 | 124 | 15:00 | Rahim | 128 | 18:30 | 123 | 09:00
| Dhamrai | 132 | 02:00 | 122 | 15:00 | Rajbari | 128 | 08:00 | 121 | 21:00
| Dhanmondi | 134 | 02:00 | 124 | 15:00 | Rajendrapur | 127 | 19:00 | 118 | 09:00
| Dohazari | 136 | 17:00 | 125 | 10:00 | Rajshahi | 133 | 02:00 | 128 | 18:30
| Faridpur | 130 | 08:00 | 124 | 22:00 | Rajshahi-230 | 134 | 17:00 | 119 | 21:00
| Fatullah | 134 | 04:00 | 125 | 15:00 | Ramganj | 133 | 16:00 | 117 | 00:00
| Fenchuganj | 134 | 17:00 | 129 | 22:00 | Rampur | 137 | 16:00 | 129 | 09:00
| Feni | 132 | 17:00 | 121 | 07:00 | Rampura | 134 | 03:00 | 123 | 15:00
| Ghatail | 128 | 19:00 | 118 | 20:00 | Rangamati | 137 | 18:00 | 4 | 04:00
| Ghorashal | 138 | 00:00 | 130 | 15:00 | Rangpur | 131 | 16:00 | 117 | 18:30
| Goalpara | 132 | 17:00 | 125 | 18:30 | Ruppur | 136 | 17:00 | 131 | 20:00
| Gollamari | 132 | 18:00 | 125 | 21:00 | Saidpur | 134 | 17:00 | 120 | 18:30
| Gopalganj | 130 | 17:00 | 123 | 23:00 | Satkhira | 128 | 04:00 | 119 | 22:00
| Gopalganj-400 | 130 | 06:00 | 126 | 14:00 | Satmasjid | 133 | 02:00 | 123 | 15:00
| Gulshan | 133 | 00:00 | 123 | 15:00 | Savar | 135 | 00:00 | 126 | 09:00
| Halishahar | 139 | 18:30 | 129 | 09:00 | SevenRings | 136 | 01:00 | 130 | 09:00
| Haripur | 128 | 18:30 | 123 | 09:00 | ShahCement | 128 | 00:00 | 123 | 09:00
| HaripurSBU | 128 | 00:00 | 123 | 09:00 | Shahjadpur | 140 | 00:00 | 130 | 21:00
| Hasnabad | 134 | 00:00 | 127 | 14:00 | Shahjibazar | 130 | 00:00 | 126 | 21:00
| Hathazari | 140 | 16:00 | 134 | 09:00 | Shahmirpur | 139 | 16:00 | 129 | 08:00
| Ishurdi | 136 | 17:00 | 131 | 18:30 | Shariatpur | 129 | 17:00 | 121 | 22:00
| Jaldhaka | 131 | 17:00 | 117 | 18:30 | Sherpur | 137 | 19:00 | 122 | 03:00
| Jamalpur | 138 | 19:00 | 125 | 23:00 | Shikalbaha | 127 | 18:00 | 119 | 09:00
| Jashore | 129 | 01:00 | 122 | 15:00 | Shikalbaha-230 | 140 | 17:00 | 130 | 09:00
| Jhenaidah | 134 | 06:00 | 125 | 18:30 | Shitalakhya | 135 | 01:00 | 125 | 15:00
| Jhenaidah-230 | 134 | 06:00 | 125 | 18:30 | Sholosohor | 138 | 18:00 | 129 | 09:00
| Joydebpur | 132 | 18:30 | 124 | 09:00 | Shyampur | 133 | 00:00 | 125 | 09:00
| Joypurhat | 131 | 17:00 | 121 | 21:00 | Shyampur-230 | 133 | 02:00 | 125 | 15:00
| Juldah | 139 | 18:00 | 129 | 09:00 | Siddhirganj | 129 | 01:00 | 124 | 09:00
| Kabirpur | 131 | 01:00 | 120 | 08:00 | Sirajganj | 133 | 14:00 | 119 | 20:00
| Kachua | 135 | 18:00 | 122 | 00:00 | Sonargaon | 125 | 00:00 | 124 | 00:00
| Kaliakoir | 133 | 00:00 | 124 | 12:00 | Sreemongol | 129 | 00:00 | 126 | 03:00
| Kallyanpur | 129 | 01:00 | 123 | 15:00 | Sreepur | 128 | 03:00 | 124 | 09:00
| Kalurghat | 138 | 17:00 | 13 | 03:00 | Srinagar | 133 | 05:00 | 125 | 14:00
| Kamrangirchar | 131 | 00:00 | 121 | 15:00 | SSM | 140 | 18:00 | 136 | 01:00
| Kaptai | 140 | 18:00 | 134 | 9:00 | Sunamganj | 122 | 06:00 | 117 | 21:00
| Kazla | 129 | 00:00 | 120 | 13:00 | Sylhet | 127 | 07:00 | 123 | 23:00
| Keranigonj | 133 | 02:00 | 125 | 15:00 | Sylhet-132 | 126 | 00:00 | 125 | 19:30
| Khagrachori | 137 | 18:00 | 130 | 09:00 | Tangail | 126 | 19:00 | 115 | 23:00
| Khulna | 131 | 04:00 | 124 | 21:00 | Thakurgaon | 137 | 17:00 | 119 | 18:30
| Khulna(S) | 132 | 17:00 | 125 | 18:30 | TK | 139 | 17:00 | 130 | 08:00
| Khulshi | 137 | 18:30 | 127 | 09:00 | Tongi | 136 | 04:00 | 126 | 09:00
| Kishoreganj | 128 | 06:00 | 124 | 09:00 | Ullahpara | 138 | 02:00 | 133 | 15:00
| Kodda | 131 | 19:00 | 119 | 08:00 | Ullon | 135 | 07:00 | 123 | 15:00
| KSRM | 139 | 17:00 | 130 | 09:00 | Uttara | 136 | 02:00 | 128 | 09:00
| Kulaura | 130 | 02:00 | 127 | 22:00 | UttaraNew | 136 | 01:00 | 128 | 09:00
| Kurigram | 130 | 18:00 | 114 | 18:30 | Zigatola | 132 | 03:00 | 124 | 15:00

## L-Curve
Date | 2024-09-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 548 | 7720 | 6765 | 14485 |  |  |  | QF-LDC-11
0:30 | 997 | 7011 | 6428.5 | 13439.5 | Date: | 2024-09-18
1:00 | 1446 | 6302 | 6092 | 12394
1:30 | 1401 | 6173.5 | 5970.5 | 12144
2:00 | 1356 | 6045 | 5849 | 11894
2:30 | 1344 | 6016 | 5752.5 | 11768.5 | [5 empty] | Gen. at Eve. Peak | 14752 | 14752 MW (19:30 )
3:00 | 1332 | 5987 | 5656 | 11643 | [6 empty] | 19:30
3:30 | 1343 | 5866.5 | 5620 | 11486.5 | [5 empty] | Gen. at Day Peak | 13091 | 13091 MW (12:00 )
4:00 | 1354 | 5746 | 5584 | 11330 | [6 empty] | 12:00
4:30 | 1383 | 5650 | 5589.5 | 11239.5 | [5 empty] | Highest Generation | 14752
5:00 | 1412 | 5554 | 5595 | 11149 | [6 empty] | 19:30
5:30 | 1399 | 5516.5 | 5447 | 10963.5
6:00 | 1386 | 5479 | 5299 | 10778
6:30 | 1463 | 5531.5 | 5419.5 | 10951
7:00 | 1540 | 5584 | 5540 | 11124
7:30 | 1538 | 5636 | 5611.5 | 11247.5
8:00 | 1536 | 5688 | 5683 | 11371
8:30 | 1586 | 5848 | 5704 | 11552
9:00 | 1636 | 6008 | 5725 | 11733
9:30 | 1602 | 6289.5 | 5705.5 | 11995
10:00 | 1568 | 6571 | 5686 | 12257
10:30 | 1462 | 6728.5 | 5731.5 | 12460
11:00 | 1356 | 6886 | 5777 | 12663
11:30 | 1414 | 7054.5 | 5822.5 | 12877
12:00 | 1472 | 7223 | 5868 | 13091
12:30 | 1428 | 7287 | 5898.5 | 13185.5
13:00 | 1384 | 7351 | 5929 | 13280
13:30 | 1424 | 7357.5 | 5967 | 13324.5
14:00 | 1464 | 7364 | 6005 | 13369
14:30 | 1464 | 7402 | 6049.5 | 13451.5
15:00 | 1464 | 7440 | 6094 | 13534
15:30 | 1430 | 7310 | 6026.5 | 13336.5
16:00 | 1396 | 7180 | 5959 | 13139
16:30 | 1416 | 7241 | 5796 | 13037
17:00 | 1436 | 7302 | 5633 | 12935
17:30 | 1281 | 7375 | 5507 | 12882
18:00 | 1126 | 7448 | 5381 | 12829
18:30 | 875 | 7789.5 | 5926.5 | 13716
19:00 | 624 | 8131 | 6472 | 14603
19:30 | 830 | 7992 | 6760 | 14752
20:00 | 874 | 7705 | 6828 | 14533 |  |  |  | Executive Engineer
20:30 | 840 | 7661.5 | 6870.5 | 14532 |  |  |  | Network Operation Division
21:00 | 806 | 7618 | 6913 | 14531
21:30 | 652 | 7672.5 | 6828.5 | 14501
22:00 | 498 | 7727 | 6744 | 14471 |  |  |  |  | Page 6 of 7
22:30 | 548 | 7757 | 6764 | 14521
23:00 | 598 | 7787 | 6784 | 14571
23:30 | 573 | 7753.5 | 6774.5 | 14528
24:00 | 548 | 7720 | 6765 | 14485
14752 MW (19:30 )
13091 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-09-18 |  | Energy |  | 312562842
[16 empty] | 2024-09-18 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3366 | 887 | 1675 | 0 | 2311 | 4423 | 213 | 0 | 483 | 62 | 1065 | 0 | 0 | 396
0:30 | 3144 | 886.5 | 1577.5 | 0 | 1994.5 | 4188.5 | 213.5 | 0 | 326.5 | 64 | 1041 | 0 | 3.5 | 344.5925 |  |  | Date: | 44091
1:00 | 2922 | 886 | 1480 | 0 | 1678 | 3954 | 214 | 0 | 170 | 66 | 1017 | 0 | 7 | 293.185
1:30 | 2919 | 886.5 | 1469.5 | 0 | 1463.5 | 3957 | 213 | 0 | 153.5 | 65 | 1011.5 | 0 | 5.5 | 340.935 | [8 empty] | Total Energy | 312.5628 | 312.5628 | Total Energy Gen 312.563 MKWHr Energy Not Served 6.795 MKWHr Energy Requirement 319.357 MKWHr
2:00 | 2916 | 887 | 1459 | 0 | 1249 | 3960 | 212 | 0 | 137 | 64 | 1006 | 0 | 4 | 388.685 | [8 empty] | Energy not Served | 6.7946 | 6.7946
2:30 | 2958.5 | 886.5 | 1465.5 | 0 | 1133.5 | 3908 | 212.5 | 0 | 124.5 | 63 | 1013 | 0 | 3.5 | 331.8625 | [8 empty] | Energy Requirement | 319.3574 | 319.3574
3:00 | 3001 | 886 | 1472 | 0 | 1018 | 3856 | 213 | 0 | 112 | 62 | 1020 | 0 | 3 | 275.04
3:30 | 3013.5 | 886 | 1463.5 | 0 | 850.5 | 3858.5 | 213 | 0 | 112 | 61 | 1020 | 0 | 8.5 | 261.1925 | [7 empty] | Shortage
4:00 | 3026 | 886 | 1455 | 0 | 683 | 3861 | 213 | 0 | 112 | 60 | 1020 | 0 | 14 | 247.345
4:30 | 3050.5 | 885.5 | 1461 | 0 | 603.5 | 3824.5 | 213 | 0 | 112 | 59 | 1019.5 | 0 | 11 | 234.4525
5:00 | 3075 | 885 | 1467 | 0 | 524 | 3788 | 213 | 0 | 112 | 58 | 1019 | 0 | 8 | 221.56
5:30 | 3112 | 885 | 1400 | 0 | 486.5 | 3681.5 | 213.5 | 0 | 97 | 57 | 1021.5 | 4.5 | 5 | 218.695
6:00 | 3149 | 885 | 1333 | 0 | 449 | 3575 | 214 | 0 | 82 | 56 | 1024 | 9 | 2 | 215.83
6:30 | 3150 | 885 | 1378.5 | 0 | 478 | 3625 | 214.5 | 0 | 82 | 55 | 1024 | 54.5 | 4.5 | 175.72 | [6 empty] | Coal
7:00 | 3151 | 885 | 1424 | 0 | 507 | 3675 | 215 | 0 | 82 | 54 | 1024 | 100 | 7 | 135.61
7:30 | 3162.5 | 884.5 | 1378.5 | 0 | 562 | 3688.5 | 215 | 0 | 82 | 53 | 1023 | 194 | 4.5 | 132.2675 | [5 empty] | Oil
8:00 | 3174 | 884 | 1333 | 0 | 617 | 3702 | 215 | 0 | 82 | 52 | 1022 | 288 | 2 | 128.925
8:30 | 3196 | 884 | 1324 | 0 | 692 | 3725 | 215.5 | 0 | 90.5 | 53 | 1021 | 350 | 1 | 137.52
9:00 | 3218 | 884 | 1315 | 0 | 767 | 3748 | 216 | 0 | 99 | 54 | 1020 | 412 | 0 | 146.115
9:30 | 3177 | 884 | 1359 | 0 | 981 | 3731 | 216 | 0 | 107 | 55 | 1021 | 464 | 0 | 144.5575
10:00 | 3136 | 884 | 1403 | 0 | 1195 | 3714 | 216 | 0 | 115 | 56 | 1022 | 516 | 0 | 143
10:30 | 3137 | 884.5 | 1434 | 0 | 1327 | 3707 | 216 | 0 | 128.5 | 58 | 1025.5 | 542.5 | 0 | 199
11:00 | 3138 | 885 | 1465 | 0 | 1459 | 3700 | 216 | 0 | 142 | 60 | 1029 | 569 | 0 | 255
11:30 | 3145.5 | 884.5 | 1528 | 0 | 1623 | 3681.5 | 216 | 0 | 145 | 59 | 1024.5 | 570 | 0 | 260.5
12:00 | 3153 | 884 | 1591 | 0 | 1787 | 3663 | 216 | 0 | 148 | 58 | 1020 | 571 | 0 | 266
12:30 | 3163 | 885 | 1607 | 0 | 1873 | 3652 | 214.5 | 0 | 173 | 63 | 1018.5 | 535.5 | 1 | 257.6275
13:00 | 3173 | 886 | 1623 | 0 | 1959 | 3641 | 213 | 0 | 198 | 68 | 1017 | 500 | 2 | 249.255
13:30 | 3173 | 886 | 1623 | 0 | 1959 | 3641 | 213 | 0 | 198 | 68 | 1017 | 500 | 2 | 249.255
14:00 | 3173 | 886 | 1623 | 0 | 1959 | 3641 | 213 | 0 | 198 | 68 | 1017 | 500 | 2 | 249.255
14:30 | 3185 | 885.5 | 1653 | 0 | 2051 | 3683 | 213.5 | 0 | 198 | 71 | 1018.5 | 443.5 | 5 | 251.6425
15:00 | 3197 | 885 | 1683 | 0 | 2143 | 3725 | 214 | 0 | 198 | 74 | 1020 | 387 | 8 | 254.03
15:30 | 3128.5 | 884.5 | 1642.5 | 0 | 2127.5 | 3720 | 213 | 0 | 210.5 | 73 | 1017.5 | 309 | 10.5 | 347.015
16:00 | 3060 | 884 | 1602 | 0 | 2112 | 3715 | 212 | 0 | 223 | 72 | 1015 | 231 | 13 | 440
16:30 | 3058.5 | 884.5 | 1546 | 0 | 2214 | 3613.5 | 212.5 | 0 | 265 | 70.5 | 1018 | 147.5 | 7 | 394.2875
17:00 | 3057 | 885 | 1490 | 0 | 2316 | 3512 | 213 | 0 | 307 | 69 | 1021 | 64 | 1 | 348.575
17:30 | 3033 | 884.5 | 1476.5 | 0 | 2335 | 3486.5 | 213.5 | 0 | 335.5 | 65.5 | 1019.5 | 32 | 0.5 | 351.44
18:00 | 3009 | 884 | 1463 | 0 | 2354 | 3461 | 214 | 0 | 364 | 62 | 1018 | 0 | 0 | 354.305
18:30 | 3066.5 | 884.5 | 1513 | 0 | 2580 | 3811.5 | 214 | 0 | 512.5 | 74 | 1060 | 0 | 0 | 390.6525
19:00 | 3124 | 885 | 1563 | 0 | 2806 | 4162 | 214 | 0 | 661 | 86 | 1102 | 0 | 0 | 427
19:30 | 3175 | 885 | 1612 | 0 | 2714 | 4292 | 214 | 0 | 663 | 78 | 1119 | 0 | 0 | 388.5
20:00 | 3257 | 886 | 1638 | 0 | 2438 | 4344 | 214 | 0 | 566 | 80 | 1110 | 0 | 0 | 350
20:30 | 3287.5 | 886.5 | 1643.5 | 0 | 2366.5 | 4383.5 | 214 | 0 | 558 | 80 | 1112.5 | 0 | 0 | 351
21:00 | 3318 | 887 | 1649 | 0 | 2295 | 4423 | 214 | 0 | 550 | 80 | 1115 | 0 | 0 | 352
21:30 | 3354.5 | 887 | 1627 | 0 | 2313.5 | 4420 | 214 | 0 | 498 | 73 | 1114 | 0 | 0 | 357
22:00 | 3391 | 887 | 1605 | 0 | 2332 | 4417 | 214 | 0 | 446 | 66 | 1113 | 0 | 0 | 362
22:30 | 3411 | 886.5 | 1659 | 0 | 2319.5 | 4409 | 214 | 0 | 446 | 69 | 1107 | 0 | 0 | 371.5
23:00 | 3431 | 886 | 1713 | 0 | 2307 | 4401 | 214 | 0 | 446 | 72 | 1101 | 0 | 0 | 381
23:30 | 3398.5 | 886.5 | 1694 | 0 | 2309 | 4412 | 213.5 | 0 | 464.5 | 67 | 1083 | 0 | 0 | 388.5 |  |  | Max Temp. in Dhaka |  | 34.8°C
24:00 | 3366 | 887 | 1675 | 0 | 2311 | 4423 | 213 | 0 | 483 | 62 | 1065 | 0 | 0 | 396
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 312.563 MKWHr Energy Not Served 6.795 MKWHr Energy Requirement 319.357 MKWHr
Note on X13: Author:

## Generation
2024-09-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 134 | 132 | 133 | 133 | 133 | 134 | 135 | 135 | 136 | 136 | 136 | 136 | 133 | 133 | 134 | 132 | 133 | 134 |  | 134 | 134 | 134 | 134 | 134 | 134 | 133 | 3217462
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1944000
3 | Chattogram TPP-1 | [24 empty] | 10 | 0 | 50000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [12 empty] | 5 | 8 | 8 | 8 | 9 | 17 |  | 25 | 17 | 17 | 17 | 17 |  |  | 132906
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 11 | 15 | 19 | 19 | 20 | 19 | 17 | 13 | 8 | 2 | 0 | [8 empty] | 142695
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 55 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 586186
12 | Hathazari 100 MW peaking PP | 40 | 24 | [13 empty] | 25 | 72 | 71 |  | 71 | 71 | 71 | 71 | 64 | 64 | 64 | 585744
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | [6 empty] | 9 | 27 | 47 | 51 | 59 | 51 | 57 | 61 | 34 |  | 51 | 51 | 17 | 17 | 20 | 34 | 55 | 762764
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [10 empty] | 26 | 34 | 34 | 34 | 34 | 34 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 454752
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 187 | 187 | 238 | 242 | 263 | 293 | 327 | 331 | 330 | 330 | 328 | 328 | 322 | 322 | 318 | 318 | 305 | 280 |  | 280 | 325 | 325 | 330 | 326 | 318 | 327 | 7112439
18 | Kodda 300 MW PP Unit-2 (Summit) | 278 | 195 | 145 | 45 |  |  |  | 15 | 55 | 140 | 152 | 145 | 143 | 145 | 145 | 145 | 145 | 150 |  | 265 | 260 | 195 | 145 | 145 | 145 | 143 | 3369709
19 | Ashuganj 195 MW PP (APSCL-United) | 177 | 177 | 178 | 178 | 178 | 150 | 108 | 72 | 110 | 160 | 175 | 178 | 182 | 187 | 158 | 128 | 128 | 128 |  | 130 | 128 | 130 | 128 | 185 | 185 | 147 | 3696727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 550 | 550 | 550 | 550 | 480 | 480 | 528 | 530 | 567 | 585 | 610 | 590 | 612 | 612 | 612 | 612 | 600 | 575 |  | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 13821817
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 36 | 36 | 36 | 30 | 30 | 30 | 30 | 33 | 32 | 32 | 35 | 32 | 34 | 33 | 33 | 33 | 33 | 35 |  | 32 | 36 | 36 | 36 | 36 | 36 | 36 | 796608
33 | Ashuganj 225 MW CCPP | 192 | 192 | 192 | 192 | 192 | 213 | 210 | 192 | 212 | 206 | 203 | 190 | 190 | 201 | 208 | 192 | 190 | 189 |  | 192 | 187 | 212 | 216 | 215 | 214 | 212 | 4934000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 320 | 310 | 360 | 345 | 330 | 305 | 305 | 310 | 300 | 340 | 285 | 285 | 285 |  | 285 | 285 | 310 | 310 | 353 | 345 | 350 | 8017200
| Ashuganj 420 MW CCPP(East) | 320 | 325 | 320 | 320 | 325 | 325 | 300 | 300 | 360 | 330 | 315 | 315 | 315 | 300 | 335 | 285 | 295 | 290 |  | 285 | 285 | 320 | 320 | 330 | 380 | 320 | 7813000
35 | Ashuganj 55 MW PP (Precision) | 52 | 53 | 53 | 53 | 53 | 53 | 53 | 54 | 52 | 49 | 48 | 47 | 47 | 46 | 48 | 45 | 47 | 48 |  | 49 | 52 | 52 | 52 | 50 | 49 | 51 | 1205280
36 | Chandpur 150 MW CCPP | 50 | [10 empty] | 0 | 50 | 40 | 36 | 36 | 34 | 36 |  | 42 | 42 | 51 | 51 | 70 | 50 | 70 | 510850
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 294 | 321 | 361 | 383 | 407 | 410 | 407 | 410 | 406 | 404 | 402 | 404 | 403 | 385 | 400 | 400 | 401 | 373 |  | 377 | 410 | 400 | 400 | 403 | 404 | 404 | 9514800
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | [9 empty] | 50 | 60 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 2740000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 16 | 16 | 16 | 16 | 18 | 18 | 16 | 5 | 5 | 5 | 3 | 3 | 3 | 4 | 5 | 5 | 6 | 7 |  | 10 | 11 | 13 | 13 | 14 | 14 | 12 | 225600
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 10 | 25 | 38 | 45 | 52 | 38 | 37 | 45 | 35 | 22 | 5 | 0 | [8 empty] | 360090
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 40 | 40 | 40 | 39 | 39 | 39 | 39 |  | 39 | 40 | 40 | 40 | 41 | 40 | 40 | 945000
45 | Fenchugonj CCPP Phase-2 | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 |  | 10 | [6 empty] | 550200
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 64 | 63 | 63 | 63 | 63 | 63 | 62 | 62 | 60 | 61 | 60 | 61 | 61 | 61 | 57 | 60 | 63 | 62 |  | 63 | 30 | 30 | 31 | 30 | 30 | 30 | 1326240
48 | Shahjibazar 86 MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 83 | 86 | 86 |  | 86 | 71 | 60 | 60 | 60 | 60 | 61 | 1953600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 207 | 208 | 208 | 208 | 208 | 210 | 209 | 207 | 208 | 208 | 206 | 206 | 206 | 206 | 202 | 201 | 202 | 205 |  | 204 | 205 | 205 | 206 | 204 | 205 | 205 | 5140310
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 93744
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 267216
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 290 | 295 | 290 | 290 | 295 | 315 | 300 | 310 | 315 | 315 | 290 | 280 | 310 | 315 | 315 | 280 | 290 |  | 290 | 260 | 285 | 295 | 290 | 300 | 295 | 7321000
| Bibiyana South 400 MW | 346 | 346 | 346 | 346 | 346 | 376 | 376 | 346 | 373 | 366 | 366 | 380 | 345 | 350 | 360 | 345 | 330 | 360 |  | 346 | 346 | 346 | 346 | 350 | 364 | 364 | 8526300
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | [5 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 686170
59 | Tangail Palli Power Gen 22 MW | 3 | 6 | 6 | 6 | 6 | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 |  | 18 | [6 empty] | 123600
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 66 | 64 | 62 | 60 | 58 | 56 | 54 | 52 | 54 | 56 | 60 | 58 | 68 | 70 | 74 | 72 | 69 | 62 |  | 86 | 78 | 80 | 80 | 66 | 72 | 62 | 1539840
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 7 | 7 | 2 | 2 | 2 | 2 | 8 | 2 | 2 | 2 | 5 | 5 |  | 20 | 20 | 28 | 31 | 34 | 36 | 38 | 525600
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 10 | 18 | 18 | 18 | 18 | 18 | 396480
69 | Summit Ashulia | 17 | 17 | 19 | 19 | 19 | 19 | 17 | 17 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 15 |  | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 404400
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 499680
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 30 | 30 | 30 |  | 30 | 30 | 17 | 30 | 30 | 30 | 30 | 727400
72 | Rupganj 33 MW PP(Summit) | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 252600
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 70 | 70 | 70 | 34 | 17 |  |  |  |  | 70 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 |  | 106 | 74 | 70 | 70 | 70 | 90 | 106 | 1657560
| Chowmuhani 113 MW | 94 | 94 | 94 | 94 | 73 | 73 | 73 | 73 | 78 | 92 | 92 | 99 | 101 | 98 | 92 | 95 | 96 | 94 |  | 94 | 95 | 94 | 94 | 95 | 94 | 94 | 2219280
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | 54 | 17 |  |  | 54 | 54 | 54 | 54 | 72 | 72 | 72 | 72 | 72 | 90 | 162 |  | 162 | 162 | 162 | 162 | 162 | 126 | 108 | 1961280
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 12 |  | 25 | 25 | 25 | 25 | 25 | 17 | 8 | 276480
79 | Kodda 150 MW PP | 113 | 113 | 112 | 112 | 112 | 82 | 82 | 82 | 82 | 80 | 80 | 78 | 78 | 78 | 78 | 78 | 78 | 83 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2364000
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 20 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 33 | 43 |  | 43 | 43 | 43 | 41 | 41 | 41 | 41 | 640181
| Gazipur 100 MW PP | 50 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 35 | 35 |  | 105 | 105 | 105 | 105 | 70 | 70 | 34 | 1003200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 5 | 3 | 4 | 3 | 2 | 0 | [9 empty] | 27719
| Jodiac Power | [10 empty] | 5 | 17 | 17 | 19 | 53 | 54 | 54 | 35 |  | 17 | 17 | 17 | 17 | 24 | 35 | 35 | 452055
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | [5 empty] | 9 | 26 | 97 | 107 | 110 | 110 | 96 | 103 | 51 |  | 51 | 51 | 17 | 17 | 20 | 34 | 61 | 1088104
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 50 | 40 | 17 |  |  |  |  | 2 | 17 | 41 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 16 | 16 | 16 | 16 | 35 | 763200
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1013204
94 | Gagnagar 102 MW PP (Digital Power) | 49 | 49 | 49 |  |  |  |  | 5 | 16 | 16 | 16 | 16 | 17 | 17 | 24 | 24 | 24 | 33 |  | 97 | 97 | 97 | 49 | 49 | 49 | 49 | 717984
95 | Patenga 50MW PP (Baraka) | [16 empty] | 8 | 17 |  | 0 | [6 empty] | 35520
96 | Chattogram 108 MW PP (ECPV) | 12 | [9 empty] | 6 | 35 | 37 | 37 | 38 | 38 | 39 | 44 |  | 42 | 44 | 32 | 11 | 12 | 12 | 12 | 420480
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | [8 empty] | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 836589
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 670061
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 130 |  | 163 | 163 | 163 | 163 | 130 | 163 | 163 | 3646964
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | [9 empty] | 13400
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 |  | 54 | 54 | 17 | 17 | 17 | 17 | 42 | 572760
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 97 | 97 | 97 | 97 | 97 | 126 | 126 | 124 | 124 | 133 | 133 | 142 | 133 | 133 | 132 | 133 | 134 |  | 151 | 151 | 152 | 152 | 152 | 152 | 152 | 3036000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 81 | 37 | 34 | 34 | 34 | 34 | 36 | 34 | 36 | 90 | 95 | 95 | 99 | 108 | 104 | 96 | 110 | 122 |  | 132 | 132 | 132 | 132 | 131 | 100 | 74 | 1994544
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 12 | [7 empty] | 12 | 28 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 12 | 12 | 25 | 25 | 25 | 502080
116 | Chandpur 200 MW (Desh energy) | 103 | 103 | 103 | 103 | 85 | 68 | 68 | 68 | 70 | 100 | 100 | 100 | 100 | 103 | 103 | 103 | 133 | 180 |  | 188 | 188 | 185 | 192 | 154 | 147 | 185 | 2896800
117 | Ashuganj 150 MW PP (Midland) | [9 empty] | 20 | 55 | 81 | 92 | 92 | 78 | 80 | 83 | 94 |  | 99 | 97 | 97 | 105 | 107 | 115 | 114 | 1313090
118 | Bibiyana-III 400 MW CCPP | 195 | 198 | 195 | 199 | 196 | 196 | 196 | 196 | 196 | 196 | 197 | 197 | 197 | 197 | 194 | 189 | 203 | 281 |  | 320 | 335 | 336 | 375 | 377 | 379 | 355 | 5931000
| Jamalpur 115 MW PP (United) | 58 | 58 | 58 | 59 | 59 | 59 | 74 | 74 | 74 | 74 | 63 | 63 | 63 | 62 | 62 | 62 | 62 | 62 |  | 91 | 90 | 90 | 90 | 90 | 90 | 91 | 1660800
| Anwara 300 MW PP (United) | 15 | 15 | 15 | [6 empty] | 15 | 100 | 135 | 170 | 175 | 200 | 52 | 52 | 52 |  | 52 | 40 | 30 | 30 | 97 | 99 | 106 | 1339855
| Juldah unit-2 (Acorn) | 12 | 12 | [7 empty] | 22 | 34 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 12 | 12 | 36 | 24 | 24 | 472320
| Anlima Energy Ltd. | [10 empty] | 1 | 17 | 17 | 17 | 17 | 38 | 95 | 108 |  | 107 | 17 | 17 | 17 | 22 | 35 | 35 | 582109
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 0 | 17 | 17 |  | 21 | 54 | 54 | 35 | 17 | 17 | 17 | 383400
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 18 | 17 | 22 | 31 | 27 | 34 | 29 | 23 | 15 | 5 | 0 | [8 empty] | 232091
| Chandpur 115(Doreen) | 48 | 55 | 56 | 56 | 52 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 50 | 83 | 88 | 89 |  | 89 | 90 | 89 | 89 | 89 | 89 | 51 | 1525440
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432360
| Mirsharai 150 MW (Oil) | 17 | [7 empty] | 17 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 |  | 145 | 145 | 54 | 17 | 17 | 17 | 53 | 618909
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 7 | 4 | 3 | 14 | 8 | 2 | 7 | 2 | 0 | 0 | 0 | 0 | 2 | 8 | 8 | 13 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77280
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 8 | 36 | 55 | 68 | 74 | 75 | 72 | 64 | 50 | 31 | 10 | 0 | [8 empty] | 550536
| Matarbari 2*600 MW (CPGCL) | 752 | 754 | 754 | 756 | 752 | 757 | 756 | 754 | 757 | 757 | 753 | 751 | 752 | 751 | 755 | 755 | 743 | 752 |  | 753 | 753 | 753 | 753 | 753 | 753 | 758 | 18218181
Meghnaghat (Reliance) 718MW CCPP
120
121 | Eastern Zone Total | 6302 | 6045 | 5987 | 5746 | 5554 | 5479 | 5584 | 5688 | 6008 | 6571 | 6886 | 7223 | 7351 | 7364 | 7440 | 7180 | 7302 | 7448 |  | 8131 | 7992 | 7705 | 7618 | 7727 | 7787 | 7720 | 165420825
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | [17 empty] | 10 |  | 42 | 35 | [5 empty] | 52320
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | 17 | [18 empty] | 17 | 35 | 35 | 17 | 17 | 17 | 17 | 228000
131 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 16 | 53 | 72 | 99 | 98 | 100 | 43 | 58 | 66 | 41 | 14 | 0 | [8 empty] | 655200
132 | Rampal 1320 MW (BIFPCL) | 1006 | 1010 | 906 | 910 | 910 | 907 | 960 | 966 | 952 | 900 | 865 | 860 | 814 | 816 | 767 | 768 | 758 | 749 |  | 1110 | 1230 | 1242 | 1247 | 1241 | 1224 | 1241 | 22967270
133 | United Payra Power Ltd. | [26 empty] | 0
| Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5139410
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | [25 empty] | 19104
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 275 | 275 | 275 | 275 | 275 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 220 | 220 | 220 | 180 | 205 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 5934000
137 | Barisal 1 MW Solar Plant | [6 empty] | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 4273
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 130 | 130 | 80 | 126 | 130 | 130 | 80 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 2591000
141 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 9 | 7 | 6 | 6 | 6 | 5 | 6 | 7 | 7 | 9 | 8 | 6 | 8 |  | 9 | 8 | 10 | 10 | 10 | 10 | 10 | 200742
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP | 15 | [18 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 107712
147 | Bheramara HVDC | 886 | 887 | 886 | 886 | 885 | 885 | 885 | 884 | 884 | 884 | 885 | 884 | 886 | 884 | 885 | 884 | 885 | 884 |  | 885 | 885 | 886 | 887 | 887 | 886 | 887 | 21320727
148 | Bheramara 410 MW CCPP | 267 | 267 | 267 | 266 | 267 | 276 | 276 | 276 | 268 | 259 | 260 | 259 | 254 | 247 | 239 | 238 | 238 | 235 |  | 233 | 233 | 233 | 230 | 227 | 227 | 226 | 6223392
149 | Payra 1320 MW | 1100 | 1100 | 1100 | 1100 | 1100 | 960 | 960 | 980 | 1000 | 1000 | 1000 | 990 | 990 | 1030 | 1100 | 1120 | 960 | 920 |  | 1120 | 1130 | 1170 | 1244 | 1244 | 1244 | 1244 | 27990000
150
151 | Barapukuria TPP Unit-1 | 61 | 61 | 61 | 60 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 62 | 63 | 60 | 61 | 60 | 61 | 60 |  | 60 | 60 | 60 | 60 | 60 | 61 | 61 | 1405090
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 180 | 210 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 5033000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 17 | 17 | 26 | 26 |  |  |  | 33199
| Sirajgonj 6.55 MW Solar | [5 empty] | 1 | 1 | 3 | 3 | 5 | 6 | 5 | 5 | 4 | 2 | 2 | 0 | 0 | [8 empty] | 33960
157 | Sirajganj 68 MW Solar Park | [5 empty] | 1 | 11 | 29 | 33 | 45 | 51 | 52 | 50 | 43 | 24 | 12 | 6 | 0 | [8 empty] | 352500
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 182 | 181 | 181 | 182 | 181 | 150 | 165 | 186 | 155 | 140 | 140 | 165 | 175 | 170 | 168 | 166 | 165 | 130 |  | 156 | 160 | 160 | 160 | 160 | 160 | 160 | 4031273
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 414 | 407 | 414 | 402 | 414 | 347 | 414 | 414 | 363 | 349 | 348 | 331 | 362 | 414 | 414 | 370 | 320 | 320 |  | 320 | 414 | 414 | 414 | 350 | 414 | 414 | 9312072
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 6 | 6 | 10 | 25 |  |  |  | 38847
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 98820
166 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | [17 empty] | 3 |  | 15 | 24 | 40 | 46 |  |  |  | 71476
169 | Santahar 50 MW Peaking PP | [17 empty] | 6 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 156438
170 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
171 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 50 | 50 | 50 | 50 | 50 | 50 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 807904
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | 113 | 50 | [5 empty] | 2 | 28 |  |  | 25 | 70 | 105 | 113 | 113 | 113 | 70 |  | 105 | 113 | 113 | 113 | 113 | 113 | 113 | 1627584
173 | Confidence Power Bogura Unit-1 113 MW | 113 | 35 | [9 empty] | 35 | 50 | 90 | 95 | 113 | 113 | 70 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1410528
175 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | Rangpur 113 MW PP (Confidence) | 92 | 52 | 34 |  |  |  |  | 17 | 33 | 34 | 34 | 40 | 61 | 61 | 61 | 60 | 70 | 81 |  | 82 | 82 | 91 | 91 | 94 | 99 | 99 | 1291785
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 2 | 3 | 3 | 5 | 5 | 4 | 4 | 6 | 5 | 4 | 1 | 0 | [8 empty] | 38512
| Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | 29 | [8 empty] | 25 | 35 | 38 | 72 | 90 | 90 | 95 |  | 96 | 96 | 115 | 115 | 115 | 115 | 115 | 1203456
| Intraco Solar 30 MW | [5 empty] | 0 | 6 | 11 | 23 | 26 | 27 | 36 | 35 | 33 | 22 | 10 | 4 | 0 | [8 empty] | 237216
178 | Adani Power Jharkhanda Ltd | 1017 | 1006 | 1020 | 1020 | 1019 | 1024 | 1024 | 1022 | 1020 | 1022 | 1029 | 1020 | 1017 | 1019 | 1020 | 1015 | 1021 | 1018 |  | 1102 | 1119 | 1110 | 1115 | 1113 | 1101 | 1065 | 25063637
| Teesta Solar Limited | [5 empty] | 4 | 38 | 95 | 146 | 176 | 195 | 204 | 196 | 178 | 143 | 83 | 16 | 0 | [8 empty] | 1452000