## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-09-22 | Sunday
|  | Date (day): | 2024-09-22 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14772.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15760 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-09-21 | 2024-09-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 400 | 411 | 400 | 410
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 |  | 0
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 13 | 62 |  | Fuel shortage
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 241 | 236 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 90 | 97
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 17 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 82 | 64 | 143 |  | 6 | Engine problem
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 17 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 35 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 37 | 37 | 40 |  | 40 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 30 | 33 | 33
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 11 | 18 | 18 |  | 15 | Engine problem
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 16 | 25 | 16 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 125 | 95 | 145 |  | 155 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 96 | 35 | 135 |  | 14 | Engine problem
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 70 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 16 | 52 | 68 | 36 |  | Lub Oil problem
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 90 | 162 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 12 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 17 | 17 |  | 38 | Engine problem.
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1493 | 1811 | 2031 | 2415 | 2420 | 1028
35 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 111 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
36 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25 | 0 |  | Fuel shortage
37 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
38 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
39 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 170 | 210 | 214 | 214
40 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 214 | 149 | 149 |  | 225 | Under maint
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
42 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17
43 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 65 | 75 | 23 |  | Fuel shortage
44 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 51 | 84 |  | 18 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
45 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 2 | 12 | 12 | 12 |  |  | fuel shortage.
46 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 24 | 35 | 35
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 38 | 50 | 58 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 20 | 15 | 50 | 50 | 250 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 100 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 90 | 100
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 105 | 108
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 5 | 0 | 35 | 163
55 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 545 | 540 | 612 | 612 |  | 612 | Unit-1 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 18 | 0 | 42 | 60 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 758 | 756 | 750 | 750
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1666 | 1891 | 2502 | 2718 | 511 | 1185
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 213 | 211 | 215 | 215
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 345 | 310 | 350 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 320 | 355 | 360 | 360 | 40 |  | FGMO
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 37 | 34 | 34 | 11 |  | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 47 | 52 | 51 | 51
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 185 | 142 | 185 | 185 | 10 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 50 | 120 |  | 30 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 35 | 35 |  | 17 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 50 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 1 | 120 | 100 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 60 | 62 | 60 | 70
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 42 | 24 | 41 |  | 11 | Engine problem
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 106 | 106 |  |  | Fuel shortag
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 3 | 96 | 84 | 96 |  | 17 | Fuel shortag
76 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 20 | 96 | 65 | 95 |  | 20 | Fuel shortag
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 15 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1327 | 1739 | 1868 | 2077 | 174 | 462
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 5 | 10 | 10 | 15 | 187 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 104 | 55 | 125 | 160 | 40 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 70 | 62 | 74 | 74 | 41 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 18 |  | 4 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 54
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 238 | 150 | 283.6 | 321 | 187 | 4
84 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 39 | 39 | 38 | 40 |  | 30 | Machine problem.
85 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | under maint
86 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | under maint
87 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
88 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 49 | 53 | 51 | 51
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 35 | 35 | 35 | 15 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 |  | 6 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 31 | 30 | 30 | 36 |  | Gas shortage
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 199 | 212 | 210 | 210 |  | 21
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 11 | 12 | 12 | 12 |  | 13 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 265 | 300 | 300 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 336 | 372 | 350 | 350 |  |  | FGMO
99 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 346 | 338 | 350 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1418 | 1445 | 1467 | 1469 | 71 | 490
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 876 | 756 | 450 | 450 |  |  | SEIL P2 CTU Unit # 1 tripped
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | Engine problem
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 35 |  | 19 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 55 |  | 54 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 212 | 210 | 204 | 204 | 206 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 70 | 72 | 33 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 0 | 0 | 105 |  | Fuel shortage
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 54 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 1010 | 1054 | 1200 | 1230
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 2152 | 2088 | 2054 | 2046 | 926 | 73
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 64 | 110
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 10 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 134 | 130 | 130 |  | 64 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 940 | 1060 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 54 | 96 |  | Fuel shortage
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 230 | 200 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1526 | 1640 | 1992 | 2075 | 96 | 64
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 30 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 24 |  | 47 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
122 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 46
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 164 | 181 | 180 | 180 | 30 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 380 | 414 | 350 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 0 | 5 | 8 |  | 3 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 75 | 0 | 113 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 0 | 95 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1016 | 1074 | 1000 | 1100
135 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 59 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 30 | 0 | 14 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1783 | 1669 | 1922 | 2158 | 693 | 96
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 60 | 63 | 60 | 60 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 210 | 200 | 200 | 200 |  | 74
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 70 | 70 | 106 |  | 7 | Engine problem
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 70 | 75 | 115 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 185 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 595 | 408 | 653 | 481 | 40 | 191
| Total |  |  |  |  | 27791 | 27086 | 12198 | 12841 | 14772.6 | 15760 | 5118 | 3593
A. |  | 2024-09-21 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 13417 | MW at | 24:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11396 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12880 | MW
3 | Day peak Generation : |  |  | 12198 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12546.21 | MW
4 | Evening peak Generation : |  |  | 12841 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 37 | MW
5 | Total Energy Generation : |  | 302.2717 | MKWHr | By Solar | 3.1858 | MKWHr
| By Gas : | 121.8908 | MKWHr |  | By Oil: | 34.3825 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 91.9044 | MKWHr |  | By Hydro: | 4.472 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 24.4637 | MKWHr |  | By Wind: | 0.1752 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5118 | MW | Dhaka | 4919.81 | 4882.81 |  | 37 |  | 18:00 |  | 37
|  |  | For Plants S/D or M/C prob = |  |  | 3593 | MW | Chittagong | 1223.9 | 1223.9 |  | 0 |  | 19:00 |  | 93
|  |  | Total = |  |  | 8711 | MW | Khulna | 1724.8 | 1724.8 |  | 0 |  | 19:30 |  | 91
7 | Total Gas Supplied : |  | 885.54 | MMCFD | **Import Adani: | Taka | 161705076.83 | Rajshahi | 790.2 | 790.2 |  | 0 |  | 20:00 |  | 69
8 | Fuel Cost : | i) Gas : | Taka | 372565655.306 | ii) Oil : | Taka | 630681857.85 | Comilla | 1237 | 1237 |  | 0 |  | 21:00 |  | 37
|  | iii) Coal : | Taka | 631138120.84 | Total | Taka | 1796090710.826 | Mymensingh | 836 | 836 |  | 0 |  | 22:00 |  | 42.02
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7205.55 | MKWHr. | Sylhet | 518 | 518 |  | 0 |  | 23:00 |  | 70.67
| ii) During Peak Demand : |  |  | 420 | MW (W to E) at | 21:00 | hrs | Barisal | 384.5 | 384.5 |  | 0 |  | 24:00 |  | 79.265
| iii) Maximum : |  |  | 420 | MW at | 21:00 | hrs | Rangpur | 912 | 912 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.8°C |  |  | Total | 12546.21 | 12509.21 |  | 37
B. |  | 2024-09-22 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.8°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 132 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15760 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13500 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 358.2112 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11543 | MW at | 7:00 | 30 | 19 | 19 | 15 | 15 | 15 | 5 | 0 | 14
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.3447 | MKWHr. | ii) HVDC Flow at Peak Time |  | 756 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.4525 | MKWHr. | iii) Maximum HVDC Flow : |  | 883 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 107.71 |  | (b) Today: | 107.61 |  | (c) Rule Curve: |  | 103.84
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-09-21 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 290 | 0 | 0 | 0 | 40 | 142 | 13 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 21 | 0 | 30 | 21 | 0 | 0 | 130 | 40 | 105 | 0 | 2 | 0 | 0 | 0 | 0 |  | 4 | 8 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 330 | 0 | 208 | 185 | 75 | 34 | 48 | 0 | 51 | 0 | 28 | 41 | 0 | 0 | 0 | 17 | 70 | 18 | 0 | 0 | 0 | 39 | 0 | 50 | 32 | 0 | 0 | 30 | 84 | 0 | 200 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 99 | 0 | 0 | 95 | 0 | 17 | 0 | 25 | 136 | 103 | 361 | 54 | 17 | 68 | 0 | 52 | 24 | 110 | 52 | 96 | 24 | 346 | 51 | 0 | 72 | 11 | 0 | 17 | 0 | 52 | 0 | 330 | 17 | 0 | 612 | 12 | 763 | 0 | 0 | 0 | 0 |  | 883 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 2 | 16 | 0 | 0 | 0 | 37 | 22 | 0 | 0 | 0 | 38 | 0 | 30 | 0 | 0 | 11 | 60 | 0 | 210 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 35 | 0 | 70 | 0 | 0 | 55 | 1100 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 1009 | 0 | 200 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 7294 | 5996 | 13290 | 3362 | 883 | 1828 | 0 | 1673 | 3954 | 170 | 0 | 322 | 70 | 1016 | 0 | 12 | 916.8 | 107.73
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 298 | 0 | 0 | 0 | 24 | 142 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 21 | 0 | 30 | 21 | 0 | 0 | 130 | 40 | 107 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 8 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 210 | 185 | 75 | 34 | 49 | 0 | 51 | 0 | 28 | 41 | 0 | 0 | 0 | 17 | 70 | 18 | 0 | 0 | 0 | 39 | 0 | 50 | 32 | 0 | 0 | 30 | 84 | 0 | 202 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 95 | 0 | 0 | 95 | 0 | 17 | 0 | 25 | 136 | 102 | 361 | 54 | 17 | 85 | 0 | 52 | 34 | 110 | 52 | 96 | 24 | 346 | 51 | 0 | 72 | 17 | 0 | 17 | 0 | 53 | 0 | 320 | 17 | 0 | 610 | 9 | 755 | 0 | 0 | 0 | 0 |  | 883 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 16 | 0 | 0 | 0 | 37 | 22 | 0 | 0 | 0 | 28 | 0 | 30 | 0 | 0 | 11 | 60 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 1100 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 1006 | 0 | 200 | 1019 | 0 | 0 | 0 | 0 | 0 |  | 7319 | 5966 | 13285 | 3341 | 883 | 1839 | 0 | 1701 | 3941 | 170 | 0 | 312 | 70 | 1019 | 0 | 9 | 749.675 | 107.73
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 294 | 0 | 0 | 0 | 8 | 98 | 13 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 21 | 21 | 30 | 21 | 0 | 0 | 128 | 40 | 105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 8 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 210 | 185 | 75 | 34 | 49 | 0 | 51 | 0 | 0 | 41 | 0 | 0 | 0 | 17 | 68 | 18 | 0 | 0 | 0 | 39 | 0 | 50 | 32 | 0 | 0 | 30 | 84 | 0 | 203 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 95 | 0 | 0 | 95 | 0 | 17 | 0 | 25 | 136 | 105 | 361 | 54 | 17 | 85 | 0 | 52 | 34 | 110 | 52 | 96 | 24 | 346 | 53 | 0 | 72 | 17 | 0 | 17 | 0 | 50 | 0 | 320 | 17 | 0 | 610 | 7 | 754 | 0 | 0 | 0 | 0 |  | 876 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 37 | 22 | 0 | 0 | 0 | 28 | 0 | 30 | 0 | 0 | 11 | 60 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 35 | 0 | 49 | 0 | 0 | 35 | 1080 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 1014 | 0 | 200 | 1020 | 0 | 0 | 0 | 0 | 0 |  | 7156 | 5928 | 13084 | 3358 | 876 | 1794 | 0 | 1625 | 3928 | 168 | 0 | 240 | 68 | 1020 | 0 | 7 | 683.78 | 107.72
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 290 | 0 | 0 | 0 | 8 | 64 | 13 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 21 | 21 | 30 | 23 | 0 | 0 | 127 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 8 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 211 | 185 | 75 | 34 | 50 | 0 | 51 | 0 | 0 | 42 | 0 | 0 | 0 | 17 | 66 | 18 | 0 | 0 | 0 | 39 | 0 | 50 | 32 | 0 | 0 | 30 | 85 | 0 | 203 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 95 | 0 | 0 | 96 | 0 | 17 | 0 | 25 | 136 | 105 | 368 | 54 | 17 | 85 | 0 | 49 | 34 | 110 | 52 | 96 | 24 | 346 | 52 | 0 | 72 | 17 | 0 | 17 | 0 | 51 | 0 | 320 | 17 | 0 | 612 | 2 | 759 | 0 | 0 | 0 | 0 |  | 877 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 16 | 0 | 0 | 0 | 37 | 22 | 0 | 0 | 0 | 28 | 0 | 30 | 0 | 0 | 8 | 60 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1080 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 1018 | 0 | 200 | 1021 | 0 | 0 | 0 | 0 | 0 |  | 7176 | 5908 | 13084 | 3367 | 877 | 1824 | 0 | 1615 | 3939 | 167 | 0 | 206 | 66 | 1021 | 0 | 2 | 540.53 | 107.72
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 272 | 0 | 0 | 0 | 8 | 64 | 13 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 21 | 21 | 30 | 23 | 0 | 0 | 126 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 210 | 185 | 80 | 34 | 51 | 0 | 51 | 0 | 0 | 24 | 0 | 0 | 0 | 17 | 54 | 18 | 0 | 0 | 0 | 39 | 0 | 50 | 32 | 0 | 0 | 30 | 85 | 0 | 206 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 95 | 0 | 0 | 96 | 0 | 17 | 0 | 12 | 100 | 107 | 354 | 55 | 17 | 34 | 0 | 49 | 34 | 51 | 17 | 96 | 24 | 356 | 52 | 0 | 72 | 17 | 0 | 17 | 0 | 50 | 0 | 320 | 17 | 0 | 608 | 0 | 760 | 0 | 0 | 0 | 0 |  | 876 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 15 | 0 | 30 | 0 | 0 | 8 | 60 | 0 | 210 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1060 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 1011 | 0 | 200 | 1020 | 0 | 0 | 0 | 0 | 0 |  | 6926 | 5834 | 12760 | 3358 | 876 | 1825 | 0 | 1389 | 3909 | 166 | 0 | 163 | 54 | 1020 | 0 | 0 | 448.85 | 107.71
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 264 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 21 | 21 | 30 | 23 | 0 | 0 | 126 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 350 | 0 | 212 | 185 | 90 | 35 | 51 | 0 | 51 | 0 | 0 | 24 | 0 | 0 | 0 | 17 | 62 | 18 | 0 | 0 | 0 | 39 | 0 | 50 | 32 | 0 | 0 | 31 | 85 | 0 | 206 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 45 | 0 | 0 | 96 | 0 | 17 | 0 | 12 | 17 | 50 | 353 | 55 | 17 | 17 | 0 | 15 | 17 | 34 | 17 | 44 | 12 | 346 | 52 | 0 | 35 | 17 | 0 | 17 | 0 | 52 | 0 | 320 | 17 | 0 | 590 | 7 | 755 | 0 | 0 | 0 | 0 |  | 877 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 0 | 210 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 980 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 959 | 0 | 200 | 1015 | 2 | 0 | 0 | 0 | 0 |  | 6535 | 5537 | 12072 | 3389 | 877 | 1786 | 0 | 933 | 3754 | 166 | 0 | 81 | 62 | 1015 | 2 | 7 | 389.64 | 107.71
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 380 | 0 | 0 | 0 | 15 | 270 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 19 | 18 | 30 | 20 | 8 | 0 | 127 | 40 | 108 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 12 | 0 | 0 | 36 | 0 | 0 | 0 | 305 | 0 | 212 | 185 | 80 | 35 | 49 | 0 | 51 | 0 | 0 | 24 | 0 | 0 | 0 | 17 | 58 | 18 | 0 | 0 | 0 | 39 | 0 | 50 | 32 | 0 | 0 | 31 | 85 | 0 | 206 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 45 | 0 | 0 | 123 | 0 | 17 | 1 | 12 | 17 | 10 | 347 | 73 | 17 | 17 | 0 | 15 | 17 | 34 | 17 | 44 | 12 | 316 | 52 | 10 | 35 | 17 | 0 | 17 | 4 | 51 | 0 | 295 | 17 | 0 | 555 | 18 | 756 | 0 | 0 | 1 | 0 |  | 877 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 61 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 940 | 220 | 0 | 0 | 1 | 1 | 14 | 0 | 0 | 890 | 6 | 200 | 1014 | 35 | 0 | 0 | 13 | 2 |  | 6298 | 5495 | 11793 | 3277 | 877 | 1748 | 0 | 867 | 3612 | 167 | 0 | 81 | 58 | 1014 | 74 | 18 | 312.285 | 107.7
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 340 | 0 | 0 | 0 | 15 | 277 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 21 | 30 | 18 | 8 | 0 | 129 | 40 | 106 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 295 | 0 | 210 | 137 | 75 | 35 | 49 | 0 | 51 | 0 | 0 | 24 | 0 | 0 | 0 | 17 | 56 | 11 | 0 | 0 | 1 | 39 | 0 | 11 | 32 | 0 | 0 | 29 | 85 | 0 | 207 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 15 | 0 | 0 | 123 | 0 | 17 | 0 | 12 | 17 | 10 | 350 | 73 | 17 | 17 | 1 | 15 | 17 | 34 | 17 | 26 | 12 | 316 | 52 | 23 | 17 | 17 | 0 | 17 | 8 | 51 | 0 | 290 | 17 | 0 | 500 | 23 | 758 | 0 | 0 | 6 | 0 |  | 878 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 860 | 220 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 870 | 14 | 200 | 1013 | 88 | 0 | 0 | 28 | 11 |  | 6049 | 5347 | 11396 | 3260 | 878 | 1543 | 0 | 770 | 3419 | 169 | 0 | 81 | 56 | 1013 | 184 | 23 | 319 | 107.7
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 420 | 0 | 0 | 0 | 15 | 278 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 17 | 21 | 30 | 16 | 16 | 0 | 129 | 40 | 105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 290 | 0 | 211 | 137 | 70 | 32 | 46 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 44 | 11 | 0 | 0 | 2 | 39 | 0 | 50 | 32 | 0 | 0 | 30 | 85 | 0 | 203 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 15 | 0 | 0 | 123 | 0 | 17 | 0 | 0 | 17 | 28 | 350 | 72 | 35 | 17 | 2 | 15 | 17 | 34 | 0 | 8 | 0 | 346 | 52 | 37 | 54 | 17 | 0 | 17 | 0 | 52 | 0 | 285 | 0 | 0 | 500 | 17 | 756 | 0 | 0 | 2 | 0 |  | 877 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 60 | 0 | 34 | 0 | 0 | 35 | 860 | 180 | 0 | 0 | 3 | 33 | 0 | 0 | 0 | 868 | 24 | 200 | 1016 | 136 | 0 | 0 | 43 | 13 |  | 6143 | 5463 | 11606 | 3258 | 877 | 1653 | 0 | 799 | 3414 | 169 | 0 | 64 | 44 | 1016 | 295 | 17 | 357 | 107.7
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 420 | 0 | 0 | 0 | 15 | 278 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 9 | 0 | 0 | 17 | 21 | 30 | 15 | 8 | 0 | 130 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 300 | 0 | 210 | 137 | 70 | 31 | 46 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 8 | 0 | 0 | 2 | 39 | 0 | 49 | 32 | 0 | 0 | 29 | 85 | 0 | 202 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 85 | 0 | 0 | 124 | 0 | 17 | 18 | 0 | 0 | 30 | 350 | 72 | 35 | 0 | 2 | 15 | 0 | 17 | 0 | 8 | 0 | 370 | 17 | 41 | 54 | 0 | 0 | 17 | 0 | 33 | 0 | 290 | 0 | 0 | 502 | 13 | 757 | 0 | 0 | 1 | 0 |  | 876 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 165 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 850 | 180 | 0 | 0 | 1 | 72 | 0 | 0 | 0 | 824 | 31 | 200 | 1017 | 176 | 0 | 0 | 48 | 24 |  | 6113 | 5410 | 11523 | 3286 | 876 | 1607 | 0 | 674 | 3358 | 170 | 0 | 64 | 42 | 1017 | 416 | 13 | 312.285 | 107.69
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 240 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 17 | 15 | 30 | 12 | 16 | 0 | 130 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 335 | 0 | 207 | 163 | 70 | 31 | 46 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44 | 6 | 0 | 0 | 2 | 39 | 0 | 49 | 10 | 0 | 0 | 20 | 51 | 0 | 201 | 0 | 0 | 0 | 285 | 11 | 2 | 0 | 15 | 0 | 0 | 113 | 0 | 17 | 0 | 0 | 0 | 0 | 337 | 72 | 35 | 0 | 1 | 15 | 0 | 17 | 0 | 0 | 0 | 356 | 0 | 40 | 72 | 0 | 0 | 0 | 0 | 17 | 0 | 290 | 0 | 0 | 490 | 13 | 758 | 0 | 0 | 6 | 0 |  | 876 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 165 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 920 | 180 | 0 | 0 | 4 | 64 | 0 | 0 | 0 | 858 | 34 | 200 | 1016 | 185 | 0 | 0 | 32 | 33 |  | 5872 | 5454 | 11326 | 3166 | 876 | 1586 | 0 | 539 | 3451 | 170 | 0 | 64 | 44 | 1016 | 401 | 13 | 262 | 107.69
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 241 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 16 | 20 | 30 | 12 | 16 | 0 | 130 | 40 | 111 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 305 | 0 | 213 | 185 | 70 | 33 | 47 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 5 | 0 | 0 | 2 | 39 | 0 | 49 | 30 | 0 | 0 | 30 | 86 | 0 | 199 | 0 | 0 | 0 | 290 | 11 | 2 | 0 | 15 | 0 | 0 | 104 | 0 | 17 | 0 | 2 | 1 | 0 | 336 | 70 | 35 | 0 | 3 | 20 | 0 | 17 | 0 | 3 | 12 | 346 | 0 | 51 | 72 | 0 | 0 | 0 | 12 | 20 | 0 | 320 | 5 | 0 | 545 | 18 | 758 | 0 | 0 | 15 | 0 |  | 876 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 210 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 75 | 0 | 34 | 0 | 0 | 50 | 940 | 220 | 0 | 0 | 4 | 54 | 70 | 0 | 0 | 1010 | 36 | 230 | 1016 | 185 | 0 | 0 | 59 | 30 |  | 6142 | 6056 | 12198 | 3262 | 876 | 1791 | 0 | 732 | 3753 | 170 | 0 | 69 | 60 | 1016 | 451 | 18 | 260 | 107.69
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 262 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 16 | 20 | 30 | 11 | 16 | 0 | 130 | 80 | 110 | 0 | 0 | 31 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 305 | 0 | 215 | 185 | 50 | 32 | 48 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 66 | 4 | 0 | 0 | 2 | 39 | 0 | 49 | 35 | 0 | 0 | 32 | 86 | 0 | 201 | 0 | 0 | 0 | 290 | 11 | 2 | 0 | 40 | 0 | 0 | 111 | 0 | 17 | 0 | 25 | 25 | 0 | 223 | 69 | 35 | 0 | 1 | 45 | 17 | 56 | 0 | 34 | 24 | 346 | 17 | 49 | 72 | 15 | 0 | 0 | 33 | 48 | 0 | 290 | 17 | 0 | 590 | 19 | 757 | 0 | 0 | 16 | 0 |  | 877 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 210 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 98 | 0 | 34 | 0 | 0 | 75 | 990 | 180 | 0 | 0 | 6 | 85 | 75 | 0 | 0 | 1016 | 34 | 230 | 1015 | 155 | 0 | 0 | 64 | 26 |  | 6465 | 6106 | 12571 | 3143 | 877 | 1754 | 0 | 1082 | 3853 | 210 | 0 | 81 | 66 | 1015 | 471 | 19 | 324 | 107.69
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 370 | 0 | 0 | 0 | 15 | 272 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 16 | 21 | 30 | 11 | 16 | 0 | 129 | 80 | 109 | 0 | 0 | 31 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 340 | 0 | 205 | 158 | 50 | 35 | 49 | 0 | 43 | 0 | 23 | 5 | 0 | 0 | 0 | 12 | 64 | 5 | 0 | 0 | 2 | 39 | 0 | 50 | 35 | 0 | 0 | 30 | 86 | 0 | 209 | 0 | 0 | 0 | 285 | 0 | 2 | 0 | 62 | 0 | 0 | 120 | 0 | 21 | 0 | 25 | 42 | 5 | 296 | 70 | 35 | 0 | 2 | 45 | 17 | 70 | 0 | 57 | 24 | 370 | 17 | 30 | 72 | 17 | 0 | 0 | 22 | 59 | 0 | 340 | 17 | 0 | 612 | 15 | 755 | 0 | 0 | 21 | 0 |  | 876 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59 | 0 | 165 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 113 | 0 | 34 | 0 | 6 | 95 | 940 | 220 | 0 | 0 | 1 | 59 | 75 | 0 | 0 | 980 | 19 | 197 | 1013 | 168 | 0 | 0 | 34 | 32 |  | 6639 | 5881 | 12520 | 3294 | 876 | 1627 | 0 | 1230 | 3708 | 209 | 0 | 88 | 64 | 1013 | 396 | 15 | 401 | 107.69
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 |  | 0 | 400 | 0 | 0 | 0 | 15 | 285 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 16 | 21 | 30 | 11 | 16 | 0 | 128 | 80 | 110 | 0 | 0 | 31 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 305 | 0 | 212 | 160 | 50 | 33 | 51 | 0 | 35 | 0 | 29 | 24 | 0 | 0 | 0 | 12 | 66 | 5 | 0 | 0 | 2 | 39 | 0 | 50 | 25 | 0 | 0 | 31 | 85 | 0 | 208 | 0 | 0 | 0 | 285 | 0 | 2 | 0 | 97 | 0 | 0 | 123 | 0 | 40 | 13 | 25 | 78 | 28 | 300 | 70 | 35 | 0 | 2 | 132 | 17 | 73 | 17 | 58 | 24 | 340 | 17 | 0 | 90 | 17 | 0 | 0 | 11 | 59 | 0 | 325 | 17 | 0 | 603 | 6 | 753 | 0 | 0 | 38 | 0 |  | 876 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 8 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 5 | 59 | 0 | 150 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 113 | 0 | 34 | 0 | 3 | 95 | 920 | 220 | 0 | 0 | 1 | 40 | 75 | 0 | 0 | 980 | 23 | 180 | 1020 | 134 | 0 | 0 | 9 | 19 |  | 6834 | 5809 | 12643 | 3225 | 876 | 1671 | 0 | 1491 | 3645 | 208 | 0 | 140 | 66 | 1020 | 295 | 6 | 341 | 107.69
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 |  | 0 | 350 | 0 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 8 | 69 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 0 | 21 | 0 | 11 | 8 | 0 | 128 | 80 | 110 | 0 | 0 | 32 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 217 | 160 | 50 | 35 | 51 | 0 | 43 | 0 | 29 | 42 | 0 | 0 | 0 | 12 | 60 | 5 | 0 | 0 | 0 | 38 | 0 | 51 | 35 | 0 | 0 | 32 | 85 | 0 | 210 | 0 | 0 | 0 | 270 | 0 | 2 | 0 | 45 | 0 | 0 | 9 | 0 | 61 | 8 | 25 | 111 | 30 | 337 | 8 | 17 | 11 | 1 | 50 | 17 | 73 | 17 | 57 | 24 | 316 | 16 | 0 | 54 | 17 | 0 | 0 | 2 | 59 | 0 | 305 | 17 | 0 | 512 | 0 | 750 | 0 | 0 | 19 | 0 |  | 873 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 16 | 0 | 0 | 0 | 28 | 0 | 32 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 5 | 59 | 0 | 180 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 50 | 0 | 32 | 0 | 2 | 35 | 860 | 180 | 0 | 0 | 0 | 25 | 74 | 0 | 0 | 906 | 13 | 180 | 1010 | 83 | 0 | 0 | 5 | 9 |  | 6225 | 5436 | 11661 | 3076 | 873 | 1532 | 0 | 1092 | 3447 | 208 | 0 | 196 | 60 | 1010 | 167 | 0 | 133 | 107.69
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 |  | 0 | 320 | 0 | 0 | 0 | 15 | 240 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 16 | 0 | 30 | 11 | 8 | 0 | 128 | 80 | 110 | 0 | 0 | 34 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 216 | 108 | 50 | 35 | 49 | 0 | 10 | 0 | 32 | 39 | 0 | 0 | 0 | 12 | 58 | 6 | 0 | 0 | 0 | 39 | 0 | 52 | 33 | 0 | 0 | 32 | 86 | 0 | 211 | 0 | 0 | 0 | 280 | 12 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 70 | 2 | 37 | 85 | 30 | 366 | 8 | 35 | 17 | 0 | 50 | 17 | 34 | 17 | 63 | 24 | 300 | 17 | 0 | 17 | 17 | 0 | 0 | 3 | 59 | 8 | 285 | 17 | 0 | 450 | 3 | 738 | 0 | 0 | 7 | 0 |  | 873 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 8 | 16 | 0 | 0 | 0 | 34 | 0 | 32 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 12 | 0 | 35 | 0 | 33 | 0 | 1 | 35 | 800 | 180 | 0 | 0 | 0 | 9 | 74 | 0 | 0 | 909 | 7 | 168 | 992 | 0 | 0 | 0 | 0 | 8 |  | 5924 | 5191 | 11115 | 3032 | 873 | 1386 | 0 | 1024 | 3304 | 208 | 0 | 198 | 58 | 992 | 37 | 3 | 110 | 107.69
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 |  | 0 | 300 | 0 | 0 | 0 | 15 | 240 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 129 | 80 | 75 | 0 | 1 | 56 | 0 | 0 | 0 |  | 6 | 16 | 27 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 335 | 0 | 209 | 45 | 50 | 35 | 22 | 0 | 10 | 0 | 34 | 35 | 0 | 0 | 0 | 12 | 62 | 5 | 0 | 0 | 0 | 39 | 0 | 22 | 10 | 0 | 0 | 30 | 41 | 0 | 212 | 0 | 0 | 0 | 270 | 12 | 2 | 0 | 48 | 0 | 0 | 14 | 0 | 78 | 0 | 37 | 85 | 37 | 372 | 32 | 35 | 17 | 0 | 50 | 17 | 34 | 17 | 66 | 37 | 340 | 17 | 0 | 17 | 17 | 0 | 7 | 0 | 67 | 17 | 315 | 17 | 0 | 438 | 5 | 756 | 0 | 0 | 0 | 0 |  | 873 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 17 | 0 | 0 | 15 | 75 | 0 | 0 | 0 | 750 | 180 | 0 | 0 | 0 | 1 | 35 | 0 | 0 | 863 | 0 | 164 | 905 | 0 | 0 | 0 | 0 | 0 |  | 6051 | 4885 | 10936 | 3148 | 873 | 1175 | 0 | 1120 | 3230 | 209 | 0 | 208 | 62 | 905 | 1 | 5 | 37 | 107.69
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431.66 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 420 | 0 | 0 | 0 | 15 | 265 | 0 | 0 | 0 | 8 | 98 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 130 | 80 | 0 | 0 | 0 | 72 | 0 | 0 | 0 |  | 0 | 40 | 34 | 0 | 6 | 0 | 0 | 11 | 0 | 0 | 0 | 320 | 0 | 212 | 100 | 50 | 35 | 41 | 0 | 36 | 0 | 38 | 42 | 0 | 0 | 0 | 17 | 60 | 5 | 0 | 0 | 0 | 39 | 0 | 53 | 35 | 0 | 0 | 31 | 86 | 0 | 212 | 0 | 0 | 0 | 275 | 12 | 2 | 0 | 102 | 0 | 0 | 32 | 0 | 95 | 0 | 12 | 102 | 53 | 371 | 52 | 105 | 17 | 0 | 50 | 17 | 34 | 34 | 80 | 12 | 320 | 16 | 0 | 90 | 17 | 0 | 17 | 0 | 95 | 17 | 290 | 17 | 0 | 500 | 0 | 757 | 0 | 0 | 0 | 0 |  | 731 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 30 | 0 | 0 | 32 | 49 | 0 | 0 | 0 | 920 | 220 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 990 | 0 | 200 | 859 | 0 | 0 | 0 | 0 | 0 |  | 6823 | 5130 | 11953 | 3205 | 731 | 1547 | 0 | 1453 | 3629 | 210 | 0 | 259 | 60 | 859 | 0 | 0 | 93 | 107.68
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 130 | 80 | 0 | 0 | 0 | 83 | 0 | 0 | 0 |  | 2 | 40 | 34 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 310 | 0 | 213 | 117 | 50 | 35 | 41 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 58 | 6 | 0 | 0 | 0 | 39 | 0 | 53 | 35 | 0 | 0 | 31 | 86 | 0 | 212 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 125 | 0 | 0 | 32 | 0 | 96 | 0 | 12 | 120 | 0 | 371 | 52 | 105 | 17 | 0 | 15 | 0 | 17 | 34 | 97 | 12 | 327 | 16 | 0 | 90 | 0 | 0 | 35 | 0 | 95 | 17 | 310 | 17 | 0 | 500 | 0 | 755 | 0 | 0 | 0 | 0 |  | 731 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 0 | 32 | 49 | 0 | 0 | 0 | 1020 | 220 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 982 | 0 | 200 | 906 | 0 | 0 | 0 | 0 | 0 |  | 6808 | 5442 | 12250 | 3252 | 731 | 1769 | 0 | 1395 | 3720 | 210 | 0 | 209 | 58 | 906 | 0 | 0 | 91 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 16 | 14 | 30 | 11 | 25 | 0 | 130 | 80 | 0 | 0 | 0 | 145 | 0 | 0 | 0 |  | 3 | 40 | 34 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 310 | 0 | 216 | 138 | 50 | 36 | 50 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 62 | 7 | 0 | 0 | 0 | 39 | 0 | 52 | 32 | 0 | 0 | 32 | 86 | 0 | 212 | 0 | 0 | 0 | 270 | 12 | 2 | 0 | 125 | 0 | 0 | 37 | 0 | 95 | 0 | 12 | 120 | 0 | 370 | 52 | 88 | 17 | 0 | 15 | 0 | 17 | 34 | 95 | 12 | 320 | 16 | 0 | 90 | 0 | 0 | 24 | 0 | 95 | 17 | 325 | 17 | 0 | 500 | 0 | 756 | 0 | 0 | 0 | 0 |  | 756 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 200 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 0 | 32 | 59 | 0 | 0 | 0 | 1030 | 220 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 1035 | 0 | 200 | 1007 | 0 | 0 | 0 | 0 | 0 |  | 6854 | 5669 | 12523 | 3314 | 756 | 1786 | 0 | 1395 | 3784 | 210 | 0 | 209 | 62 | 1007 | 0 | 0 | 69 | 107.68
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 130 | 80 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 6 | 40 | 34 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 345 | 0 | 211 | 142 | 50 | 37 | 52 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 62 | 10 | 0 | 0 | 0 | 39 | 0 | 53 | 35 | 0 | 0 | 31 | 86 | 0 | 212 | 0 | 0 | 0 | 265 | 12 | 2 | 0 | 125 | 0 | 0 | 55 | 0 | 96 | 0 | 12 | 120 | 0 | 372 | 62 | 70 | 17 | 0 | 15 | 0 | 17 | 34 | 96 | 12 | 338 | 16 | 0 | 90 | 0 | 0 | 17 | 0 | 96 | 17 | 355 | 0 | 0 | 540 | 0 | 756 | 0 | 0 | 0 | 0 |  | 756 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 0 | 15 | 70 | 0 | 0 | 0 | 1060 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 1054 | 0 | 200 | 1074 | 0 | 0 | 0 | 0 | 0 |  | 7036 | 5805 | 12841 | 3496 | 756 | 1794 | 0 | 1384 | 3873 | 210 | 0 | 192 | 62 | 1074 | 0 | 0 | 37 | 107.68
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 17 | 21 | 30 | 11 | 25 | 0 | 130 | 80 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 6 | 40 | 34 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 320 | 0 | 212 | 185 | 71 | 37 | 52 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 64 | 10 | 0 | 0 | 0 | 39 | 0 | 53 | 36 | 0 | 0 | 31 | 86 | 0 | 212 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 125 | 0 | 0 | 56 | 0 | 96 | 0 | 12 | 120 | 0 | 372 | 62 | 70 | 17 | 0 | 15 | 0 | 17 | 34 | 97 | 12 | 328 | 16 | 0 | 90 | 0 | 0 | 17 | 0 | 96 | 17 | 325 | 0 | 0 | 608 | 0 | 756 | 0 | 0 | 0 | 0 |  | 757 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 0 | 15 | 98 | 0 | 0 | 0 | 1140 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 1065 | 0 | 250 | 1105 | 0 | 0 | 0 | 0 | 0 |  | 7045 | 6051 | 13096 | 3412 | 757 | 1857 | 0 | 1416 | 4083 | 210 | 0 | 192 | 64 | 1105 | 0 | 0 | 42.02 | 107.68
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 17 | 21 | 30 | 11 | 16 | 0 | 130 | 80 | 0 | 0 | 0 | 147 | 0 | 0 | 0 |  | 6 | 40 | 34 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 350 | 0 | 210 | 189 | 70 | 37 | 52 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 64 | 11 | 0 | 0 | 0 | 39 | 0 | 53 | 36 | 0 | 0 | 31 | 86 | 0 | 210 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 125 | 0 | 0 | 80 | 0 | 82 | 0 | 12 | 120 | 0 | 379 | 82 | 70 | 17 | 0 | 15 | 0 | 17 | 34 | 97 | 12 | 378 | 0 | 0 | 90 | 0 | 0 | 17 | 0 | 67 | 17 | 365 | 0 | 0 | 612 | 0 | 758 | 0 | 0 | 0 | 0 |  | 756 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 200 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 0 | 15 | 106 | 0 | 0 | 0 | 1200 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 1115 | 0 | 250 | 1121 | 0 | 0 | 0 | 0 | 0 |  | 7126 | 6185 | 13311 | 3504 | 756 | 1865 | 0 | 1400 | 4199 | 210 | 0 | 192 | 64 | 1121 | 0 | 0 | 70.67 | 107.67
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 32 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 17 | 21 | 30 | 11 | 8 | 0 | 130 | 40 | 0 | 0 | 0 | 134 | 0 | 0 | 0 |  | 6 | 40 | 34 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 350 | 0 | 212 | 190 | 50 | 37 | 53 | 0 | 51 | 0 | 37 | 42 | 0 | 0 | 0 | 18 | 68 | 11 | 0 | 0 | 0 | 40 | 0 | 53 | 36 | 0 | 0 | 30 | 86 | 0 | 210 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 125 | 0 | 0 | 80 | 0 | 79 | 0 | 20 | 120 | 0 | 374 | 82 | 35 | 32 | 0 | 100 | 0 | 48 | 67 | 97 | 24 | 378 | 0 | 0 | 90 | 0 | 0 | 17 | 0 | 54 | 0 | 370 | 17 | 0 | 612 | 0 | 759 | 0 | 0 | 0 | 0 |  | 446 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 200 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 22 | 15 | 106 | 0 | 0 | 50 | 1230 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 1247 | 0 | 307 | 1099 | 0 | 0 | 0 | 0 | 0 |  | 7273 | 6144 | 13417 | 3505 | 446 | 1880 | 0 | 1604 | 4419 | 170 | 0 | 226 | 68 | 1099 | 0 | 0 | 79.265 | 107.67
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9489600 | 0 |  | 0 | 9966500 | 0 | 0 | 0 | 389215 | 6414703 | 0 | 0 | 0 | 254736 | 1863840 | 65000 | 0 | 0 | 0 | 701640 | 400531 | 669391 | 0 | 403200 | 385920 | 729900 | 368600 | 264000 | 0 | 3088015 | 1384000 | 1900000 | 0 | 12024 | 936182 | 0 | 0 | 0 |  | 128160 | 270976 | 203435 | 0 | 114240 | 0 | 0 | 470400 | 0 | 0 | 0 | 7926200 | 0 | 5138000 | 3830545 | 1552430 | 824832 | 1150560 | 0 | 975364 | 0 | 427152 | 666950 | 0 | 0 | 0 | 347430 | 1452480 | 238080 | 0 | 0 | 12900 | 920000 | 0 | 1135200 | 762048 | 0 | 0 | 732192 | 1966080 | 0 | 5179080 | 0 | 0 | 0 | 6931500 | 238512 | 46368 | 0 | 1952073 | 0 | 0 | 2109600 | 0 | 1046160 | 54000 | 423360 | 1950720 | 1005309 | 8755000 | 1437600 | 909120 | 645672 | 15719 | 935891 | 389268 | 1333158 | 579120 | 1606920 | 420480 | 8255800 | 674880 | 248160 | 1569600 | 278509 | 0 | 323640 | 97895 | 1416960 | 118800 | 7723000 | 327854 | 0 | 13325453 | 175200 | 18276363 | 0 | 0 | 131936 | 0 |  | 20344727 | 0 | 5120640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2580000 | 137741 | 218496 | 0 | 0 | 0 | 293723 | 92039 | 146064 | 0 | 0 | 175751 | 0 | 158833 | 0 | 0 | 111438 | 1405091 | 0 | 4719000 | 0 | 0 | 4194364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8984218 | 637440 | 0 | 1039200 | 144864 | 1220227 | 0 | 15693 | 820608 | 25800300 | 5069220 | 0 | 0 | 31380 | 475920 | 1549248 | 0 | 0 | 23338180 | 245796 | 5040000 | 24463703 | 1306080 | 0 | 2439 | 339000 | 208910 |  | 161841331 | 140430333 | 302271664 | 80511471 | 20344727 | 41379376 | 0 | 30422810 | 91904387 | 4472015 | 0 | 3959667 | 1452480 | 24463703 | 3185828 | 175200 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27330048 | 0 |  | 0 | 31693470 | 0 | 0 | 0 | 6857968.3 | 19564844.15 | 0 | 0 | 0 | 4572511.2 | 36195772.8 | 1212250 | 0 | 0 | 0 | 12811946.4 | 6312368.56 | 12243161.39 | 0 | 302400 | 0 | 0 | 0 | 4728240 | 0 | 0 | 0 | 10374000 | 0 | 227734.56 | 2986420.58 | 0 | 0 | 0 |  | 2254334.4 | 4771887.36 | 3643520.85 | 0 | 2235676.8 | 0 | 0 | 0 | 0 | 0 | 0 | 22114098 | 0 | 17058160 | 12832325.75 | 5014348.9 | 2779683.84 | 5039452.8 | 0 | 3911209.64 | 0 | 7650292.32 | 12045117 | 0 | 0 | 0 | 260572.5 | 9528268.8 | 740428.8 | 0 | 0 | 0 | 3588000 | 0 | 5165160 | 3467318.4 | 0 | 0 | 4063665.6 | 10262937.6 | 0 | 14449633.2 | 0 | 0 | 0 | 21418335 | 178884 | 35239.68 | 0 | 39822289.2 | 0 | 0 | 40525416 | 0 | 18422877.6 | 0 | 7540041.6 | 33844992 | 16668023.22 | 23200750 | 27400656 | 17055091.2 | 11583355.68 | 0 | 15301817.85 | 7567369.92 | 23916854.52 | 11066983.2 | 31190317.2 | 7488748.8 | 21960428 | 11520201.6 | 0 | 28707984 | 4673381.02 | 0 | 5783446.8 | 0 | 25533619.2 | 2012472 | 22937310 | 4616184.32 | 0 | 92878407.41 | 0 | 107830541.7 | 0 | 0 | 0 | 0 |  | 57168682.87 | 0 | 15105888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8152800 | 652892.34 | 3766871.04 | 0 | 0 | 0 | 5260578.93 | 1688915.65 | 2455335.84 | 0 | 0 | 3147700.41 | 0 | 2844699.03 | 0 | 0 | 84358.566 | 15498153.73 | 0 | 39828360 | 0 | 0 | 13841401.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26233916.56 | 10887475.2 | 0 | 20596944 | 2561195.52 | 24306921.84 | 0 | 0 | 16280862.72 | 167185944 | 15765274.2 | 0 | 0 | 0 | 0 | 26879452.8 | 0 | 0 | 170368714 | 0 | 37548000 | 161705076.83 | 0 | 0 | 0 | 0 | 0 |  | 1012971247.22 | 849816415.276 | 1862787662.496 | 236123363.016 | 57168682.87 | 136442292.29 | 0 | 558406970.34 | 631138120.84 | 0 | 0 | 72274887.51 | 9528268.8 | 161705076.83 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 241 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 16 | 20 | 30 | 12 | 16 | 0 | 130 | 40 | 111 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 305 | 0 | 213 | 185 | 70 | 33 | 47 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 5 | 0 | 0 | 2 | 39 | 0 | 49 | 30 | 0 | 0 | 30 | 86 | 0 | 199 | 0 | 0 | 0 | 290 | 11 | 2 | 0 | 15 | 0 | 0 | 104 | 0 | 17 | 0 | 2 | 1 | 0 | 336 | 70 | 35 | 0 | 3 | 20 | 0 | 17 | 0 | 3 | 12 | 346 | 0 | 51 | 72 | 0 | 0 | 0 | 12 | 20 | 0 | 320 | 5 | 0 | 545 | 18 | 758 | 0 | 0 | 15 | 0 |  | 876 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 210 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 75 | 0 | 34 | 0 | 0 | 50 | 940 | 220 | 0 | 0 | 4 | 54 | 70 | 0 | 0 | 1010 | 36 | 230 | 1016 | 185 | 0 | 0 | 59 | 30 |  | 12198 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 130 | 80 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 6 | 40 | 34 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 345 | 0 | 211 | 142 | 50 | 37 | 52 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 62 | 10 | 0 | 0 | 0 | 39 | 0 | 53 | 35 | 0 | 0 | 31 | 86 | 0 | 212 | 0 | 0 | 0 | 265 | 12 | 2 | 0 | 125 | 0 | 0 | 55 | 0 | 96 | 0 | 12 | 120 | 0 | 372 | 62 | 70 | 17 | 0 | 15 | 0 | 17 | 34 | 96 | 12 | 338 | 16 | 0 | 90 | 0 | 0 | 17 | 0 | 96 | 17 | 355 | 0 | 0 | 540 | 0 | 756 | 0 | 0 | 0 | 0 |  | 756 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 0 | 15 | 70 | 0 | 0 | 0 | 1060 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 1054 | 0 | 200 | 1074 | 0 | 0 | 0 | 0 | 0 |  | 12841 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 97 | 143 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 21 | 33 | 18 | 25 | 0 | 134 | 80 | 0 | 0 | 25 | 149 | 0 | 0 | 0 |  | 18 | 75 | 84 | 0 | 50 | 50 | 0 | 35 | 0 | 0 |  | 350 | 0 | 215 | 185 | 50 | 34 | 51 | 0 | 51 | 0 | 35 | 41 | 0 | 0 |  | 18 | 70 | 15 | 0 | 0 | 0 | 40 | 0 | 51 | 35 | 0 | 0 | 30 | 86 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 145 | 0 | 0 | 160 | 0 | 135 | 0 | 12 | 200 | 120 | 350 | 74 | 105 | 17 | 0 | 50 | 54 | 110 | 106 | 96 | 100 | 350 | 68 | 0 | 162 | 108 | 0 | 54 | 0 | 95 | 17 | 360 | 163 | 0 | 612 | 60 | 750 | 0 | 0 |  |  |  | 450 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 24 | 90 | 0 | 0 | 46 | 0 | 30 | 0 | 0 | 8 | 60 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 72 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 1230 | 0 | 307 | 1100 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 16 | 21 | 33 | 18 | 16 | 0 | 134 | 80 | 0 | 0 | 8 | 149 |  | 0 | 0 | 0 | 6 | 65 | 51 | 0 | 38 | 50 | 0 | 35 | 0 | 0 | 0 | 310 | 0 | 215 | 185 | 50 | 34 | 51 | 0 | 51 | 0 | 35 | 24 | 0 | 0 |  | 18 | 60 | 10 | 0 | 0 | 1.6 | 38 | 0 | 51 | 35 | 0 | 0 | 30 | 86 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 95 | 0 | 0 | 125 | 0 | 35 | 20 | 12 | 100 | 50 | 350 | 74 | 50 | 17 | 5 | 50 | 54 | 100 | 106 | 84 | 90 | 350 | 52 | 50 | 162 | 105 | 0 | 17 | 35 | 65 | 17 | 360 | 35 | 0 | 612 | 42 | 750 | 0 | 0 | 70 |  |  | 450 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 130 | 10 | 64 | 0 | 0 | 0 | 30 | 0 | 50 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 70 | 0 | 113 | 0 | 70 | 0 | 8 | 95 | 1244 | 220 |  | 17 | 6 | 100 | 115 | 0 | 0 | 1200 | 30 | 307 | 1000 | 170 | 0 |  | 29 | 14 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 16 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 21 | 30 | 12 | 8 | 0 | 130 | 80 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 280 | 0 | 215 | 189 | 50 | 36 | 52 | 0 | 51 | 0 | 0 | 1 | 0 | 0 | 0 | 18 | 48 | 5 | 0 | 0 | 1 | 40 | 0 | 53 | 36 | 0 | 0 | 31 | 88 | 0 | 210 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 15 | 0 | 0 | 125 | 0 | 35 | 10 | 12 | 68 | 2 | 354 | 74 | 17 | 17 | 3 | 50 | 0 | 72 | 0 | 65 | 12 | 346 | 15 | 23 | 54 | 0 | 0 | 0 | 16 | 53 | 0 | 290 | 0 | 0 | 530 | 0 | 756 | 0 | 0 | 39 | 0 | 0 | 440 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 177 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 10 | 1040 | 220 | 0 | 0 | 2 | 41 | 35 | 0 | 0 | 909 | 7 | 200 | 1015 | 87 | 0 | 0 | 24 | 14 | 0 |  |  |  | 121890847 | 20344727 | 0 | 91904387 | 34382477 | 1452480 | 3185828 | 175200 | 4472015 |  |  |  | 277807961
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [6 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 121.8908 | 20.3447 | 0 | 91.9044 | 34.3825 | 1.4525 | 3.1858 | 0.1752 | 4.472
| Minimum Generation |  | 11396 | 8:00
| Highest Generation |  | 13417 | 24:00 | [129 empty] | 0 | [75 empty] | 277.808
| Day Peak Generation |  | 12198 | 12:00
| Evening Peak Generation |  | 12841 | 21:00 | [205 empty] | 202699852
| HVDC Max Flow |  | 883 | 1:00 | [205 empty] | 202.6999
| HVDC EvPeak Flow |  | 756 | 21:00
| Load factor L.F |  | 93.87% | [168 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-09-22
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-09-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12198 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11543
Evening Peak Generation : |  |  | 12841 | MW Hour : | 21:00 | Available Max Generation : |  | 15760
E.P. Demand (at gen end) : |  |  | 12880 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15900
Maximum Generation : |  |  | 13417 | MW Hour : | 24:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 302.2717 | System Load Factor : | 93.87% | Load Shed : |  | 132
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 420 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-09-22
Actual : |  | 107.61 | Ft.(MSL) , | Rule curve : | 103.84 | Ft.( MSL )
Gas Consumed : |  | Total = | 885.54 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 372565655.306 | Adani : | 161705076.83
: |  |  | Coal : | 631138120.84 | Oil : | 630681857.85 | Total : | 1796090710.826
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 37 | 888:00 | 5309.637 |  |  | 30 | -0.7401%
Chittagong Area |  | 0 | 0:00 | 1463.5928 |  |  | 19 | 1.142%
Khulna Area |  | 0 | 0:00 | 2051.5561 |  |  | 19 | 1.543%
Rajshahi Area |  | 0 | 0:00 | 1784.4161 |  |  | 15 | 1.968%
Cumilla Area |  | 0 | 0:00 | 1467.6227 |  |  | 15 | 1.705%
Mymensingh Area |  | 0 | 0:00 | 1092.2058 |  |  | 15 | 2.074%
Sylhet Area |  | 0 | 0:00 | 611.5045 |  |  | 5 | 1.369%
Barisal Area |  | 0 | 0:00 | 510.265 |  |  | 0 | 2.141%
Rangpur Area |  | 0 | 0:00 | 997.9738 |  |  | 14 | 2.132%
Total |  | 37 |  | 15288.7739 |  |  | 132
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Ashuganj south
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
09:00 | 10:59 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to Pbs switching station redhot |  |  |  |  | 45.0MW load interrup.
maintenance.
09:18 | 13:18 | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D
09:18 | 13:15 | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D
| 09:25 | Bogura 132/33kV S/S Transformer-4 LT is restored.
| 09:25 | Bogura 132/33kV S/S Transformer-4 HT is restored.
09:31 | 13:15 | Faridpur 132/33kV S/S 33 KV Bus Scheduled S/D
| 09:40 | Siddhirganj-Siddhirganj (Orion)132kV Ckt-1 is restored.
09:43 | 16:29 | Munshiganj 132/33kV S/S Transformer-2 HT Forced S/D Due to Y-Ph HT Bushing Cap Maintenance at 132/33kV Power
Transformer-2
| 09:45 | Purbasadipur 132/33kV S/S Single Bus is restored.
10:35 | 10:56 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH Y, Z1, Dist. Send. relays Due to Heavy |  |  |  |  | 20.0MW load interrup.
rainfall.
11:56 | 12:06 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Tripped showing FBCPU relays Due to buchholz Trip |  |  |  |  | 55.0MW load interrup.
12:00 |  | Day Peak Generation: 12198 MW
12:06 | 12:06 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Project Work S/D Due to Maintenance of PTR-02
12:18 | 13:32 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to Red hot Removed. |  |  |  |  | 16.0MW load interrup.
| 12:38 | Panchagar-Thakurgaon 132kV Ckt-1 is restored.
13:20 | 13:31 | Chattak-Sylhet 132 kV Ckt-1 Tripped from Sylhet 132/33kV end showing Distance, Zone-2, Phase-B relays. |  |  |  |  | 27.0MW load interrup.
Sylhet 132/33kV end.
| 14:34 | Kushtia 132/33kV S/S T-3 HT is restored.
| 14:34 | Kushtia 132/33kV S/S T-3 LT is restored.
15:23 | 16:26 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Forced S/D Due to To carrying new transformer |  |  |  |  | 30.0MW load interrup.
15:24 | 16:24 | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT Forced S/D Due to To carrying new transformer
15:36 | 15:38 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing OC/EF, Phase B and C relays Due to None
15:40 | 15:51 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Tripped showing O/C relays Due to O/C
15:57 | 16:20 | Gulsan-Rampura 132kV Ckt-2 Tripped from Rampura 230/132kV end showing 1. Distance protection 21 , Distance 1.2
kM. 2. Z1 operate 3. Y-ph pick Up relays Due to Unknown
16:57 | 17:20 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Forced S/D Due to To carrying new transformer |  |  |  |  | 30.0MW load interrup.
16:59 | 17:19 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Forced S/D Due to To carrying new transformer |  |  |  |  | 30.0MW load interrup.
17:20 | 19:35 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Over Voltage relays Due to Rain & Strom.
18:10 | 18:15 | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Tripped showing MCGG relays Due to Due to Talaimari 33 KV feeder |  |  |  |  | 17.0MW load interrup.
fault.
19:32 | 20:22 | Borhanuddin 230/33kV S/S Tr-Load HT Forced S/D Due to Red Hot Maintenance. |  |  |  |  | 35.0MW load interrup.
| 19:32 | Chowmuhani 132/33kV S/S TR2 is restored.
19:34 | 21:51 | Bogura 132/33kV S/S Transformer-4 LT Tripped showing Micom relays Due to Transformer-4 33 kv incomer CB Trip due to |  |  |  |  | 24.0MW load interrup.
Dupchacia PBS-1 33kv feeder loop broken Fault .
19:34 | 20:34 | Bogura 132/33kV S/S Transformer-3 LT Tripped showing Micom relays Due to Transformer-3 33 kv incomer CB Trip due to |  |  |  |  | 24.0MW load interrup.
Dupchacia PBS-1 33kv feeder loop broken Fault .
19:40 | 19:57 | Bhaluka 132/33kV S/S Transformer- 01 LT Tripped showing O/C E/F relays Due to 33kv BPDB Beacon feeder CT brust |  |  |  |  | 98.0MW load interrup.
19:40 | 20:32 | Bhaluka 132/33kV S/S Transformer- 02 LT Tripped showing O/C and E/F relays Due to 33kv Breacon feeder CT Brust |  |  |  |  | 98.0MW load interrup.
19:40 | 20:47 | Palashbari 132/33kV S/S TR2-404T LT Forced S/D Due to Gaibandha 2 nesco feeder trouble in our 33KV incomer loop |  |  |  |  | 10.0MW load interrup.
19:41 | 20:46 | Palashbari 132/33kV S/S TR2-404T HT Forced S/D |  |  |  |  | 10.0MW load interrup.
21:00 |  | Evening Peak Generation = 12,841MW
| 23:05 | Chowmuhani-Ramganj 132 kV Ckt-2 is restored.
| 23:05 | Chowmuhani-Ramganj 132 kV Ckt-2 is restored.
00:50 |  | Shikalbaha 225 MW ST was shutdown.
06:35 |  | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Forced S/D Due to Red hot |  |  |  |  | 30.0MW load interrup.
06:35 |  | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Forced S/D Due to Red hot
07:00 |  | Minimum Generation is 11543 MW
07:14 |  | Bhaluka 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to 33 kv incomeing isolator redhot |  |  |  |  | 30.0MW load interrup.
07:15 |  | Bhaluka 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to 33 kv incomeing isolator redhot |  |  |  |  | 30.0MW load interrup.
07:30 |  | Kushtia 132/33kV S/S T2 LT Forced S/D Due to 33 kv koburkat feeder red hot maintenance |  |  |  |  | 20.0MW load interrup.
07:30 |  | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to 33 KV Bisic(Chunarughat) feeder red hot Maintenece |  |  |  |  | 43.0MW load interrup.
07:30 |  | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to 33 KV Bisic(Chunarughat) feeder red hot Maintenece |  |  |  |  | 43.0MW load interrup.
07:31 |  | Kushtia 132/33kV S/S T2 HT Forced S/D Due to 33 kv koburkat feeder red hot maintenance |  |  |  |  | 20.0MW load interrup.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-09-21
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 411 | 9489600
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9966500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 389215 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 65000 | Reserve NENP
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 236 | 6414703 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 254736 | low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 701640 | low demand
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 1863840 | low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 400531 | low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 669391
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 37 | 789120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 729900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 11 | 368600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 264000 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 125 | 1952073 | low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 96 | 1046160 | low demand
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 909120 | low demand
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 16 | 674880 | low demand
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 1569600 | low demand
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 97895
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 118800 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5915 | 1811 | 38735304
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 1900000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 12024 | Reserve
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 54000
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 210 | 4472015
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 214 | 936182
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 645672 | low demand
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 270976 | low demand
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 203435 | low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 423360 | low demand
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 470400
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 114240 | Reserve
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 15719
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 935891 | low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 389268 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 1333158 | low demand
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 420480 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 278509 | Reserve
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 327854 | Reserve
60 | SS Power I |  | SS Power | 2*612 | 1224 | 540 | 13325453 | Unit-2 S/D due to coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 175200
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 756 | 18276363 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1891 | 44980199
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 5138000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7926200 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 355 | 7723000 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 824832 | Engine problem
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 52 | 1150560 | Engine problem
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 142 | 3830545 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 975364 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 1005309 | reserve
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 427152 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1552430 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 1950720 | low demand
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 62 | 1452480
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 666950 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 347430 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 579120 | low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1606920 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 1416960 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 131936
| Cumilla Area Total |  |  |  | 2917 | 1739 | 38705908
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 10 | 238080 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12900
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 55 | 2109600 | Bad weather
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 62 | 1437600 | Bad weather
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 248160
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 128160 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 323640 | Bad weather
| Mymensingh Area Total |  |  |  | 646 | 150 | 4498140
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 39 | 920000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1135200
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 35 | 762048 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 46368 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 31 | 732192 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1966080
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 212 | 5179080 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 238512 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 265 | 6931500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 372 | 8755000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 338 | 8255800 | FGMO
| Sylhet Area Total |  |  |  | 2417 | 1445 | 34921780
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 756 | 20344727
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 210 | 5120640 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 637440 | low demand
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 144864 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 475920
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 1054 | 23338180 | Low demand due to bad weather
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 2088 | 50061771
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 218496
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 137741
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 134 | 2580000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 25800300 | Low demand due to bad weather
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5069220
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 200 | 5040000 | Low demand due to bad weather
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 2439
| Barisal Area Total |  |  |  | 2236 | 1640 | 38848196
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 293723 | Reserve
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 92039 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 175751 | Reserve
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 181 | 4194364 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8984218
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 158833 | Reserve
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 111438 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 146064 | Reserve
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 1039200 | Reserve
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 820608 | Reserve
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31380
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1074 | 24463703
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 339000
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 208910
| Rajshahi Area Total |  |  |  | 3449 | 1669 | 41059231
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 63 | 1405091
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4719000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 1220227 | low demand
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 15693
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 1549248 | low demand
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 245796
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1306080
| Rangpur Area Total |  |  |  | 950 | 408 | 10461135
| Total |  |  |  | 27086 | 12841 | 302271664
| Eastern Grid Total |  |  |  | 16752 | 7036 | 161841331
| Western Grid Total |  |  |  | 10334 | 5805 | 140430333
| National Grid Total |  |  |  | 27086 | 12841 | 302271664
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-09-2024
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10093.57 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4982.9 | MW
i) Dhaka area |  |  | 5440.57 |  | MW | i) Khulna area |  |  |  | 1853.5 | MW
ii) Chattogram area |  |  | 1431 |  | MW | ii) Barishal area |  |  |  | 499 | MW
iii) Cumilla area |  |  | 1444 |  | MW | iii) Rajshahi area |  |  |  | 1645.4 | MW
iv) Mymensingh area |  |  | 1083 |  | MW | iv) Rangpur area |  |  |  | 985 | MW
v) Sylhet area |  |  | 695 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15076.47 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 24 | 12:00 | 67 | Jamalpur | 101 | 00:00 | 133 | Rahim | 44 | 02:00
2 | AKSML | 107.1 | 09:00 | 68 | Jashore | 161 | 18:30 | 134 | Rajbari | 90 | 00:00
3 | Aftabnagar | 58 | 00:00 | 69 | Jhenaidah | 135 | 18:30 | 135 | Rajendrapur | 98 | 19:00
4 | Agargaon | 128 | 00:00 | 70 | Joydebpur | 204 | 19:00 | 136 | Rajshahi | 136 | 00:00
5 | Agrabad | 82 | 00:00 | 71 | Joypurhat | 69 | 04:00 | 137 | Rajshahi-230 | 88 | 15:00
6 | Amnura | 68 | 22:00 | 72 | Juldah | 18 | 23:00 | 138 | Ramganj | 124 | 20:00
7 | Ashuganj | 108 | 00:00 | 73 | KSRM | 36 | 14:00 | 139 | Rampur | 41 | 00:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 283 | 18:00 | 140 | Rangamati | 17 | 18:30
9 | BSRM | 103 | 03:00 | 75 | Kachua | 92 | 00:00 | 141 | Rangpur | 152 | 13:00
10 | Bagerhat | 62 | 18:30 | 76 | Kallyanpur | 141 | 00:00 | 142 | Ruppur | 5.6 | 10:00
11 | Bakulia | 105 | 15:00 | 77 | Kalurghat | 36 | 18:00 | 143 | SSM | 0 | 00:00
12 | Banani | 60.6 | 13:00 | 78 | Kamrangirchar | 57 | 13:00 | 144 | Saidpur | 120 | 12:00
13 | Bangabhaban | 10 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 132 | 21:00
14 | Barapukuria | 68 | 13:00 | 80 | Kazla | 113 | 16:00 | 146 | Satmasjid | 111 | 14:00
15 | Barguna | 22 | 21:00 | 81 | Keranigonj | 63 | 02:00 | 147 | Savar | 204 | 15:00
16 | Barishal | 106 | 19:00 | 82 | Khagrachori | 28 | 19:00 | 148 | SevenRings | 7.52 | 18:30
17 | Barishal-230 | 90 | 19:00 | 83 | Khulna | 91 | 20:00 | 149 | ShahCement | 26 | 00:00
18 | Baroaulia | 73 | 10:00 | 84 | Khulshi | 167 | 18:00 | 150 | Shahjadpur | 78 | 03:00
19 | Baroirhat | 65 | 18:30 | 85 | Kishoreganj | 142 | 00:00 | 151 | Shahjibazar | 138 | 04:00
20 | Bashundhara | 189 | 00:00 | 86 | Kodda | 300 | 18:30 | 152 | Shahmirpur | 46 | 18:00
21 | BashundharaCement | 1 | 00:00 | 87 | Kulaura | 50 | 04:00 | 153 | Shariatpur | 81 | 02:00
22 | Beanibazar | 86 | 04:00 | 88 | Kurigram | 68 | 07:00 | 154 | Sherpur | 128 | 00:00
23 | Benapole | 68 | 00:00 | 89 | Kushtia | 156 | 00:00 | 155 | Shikalbaha | 31 | 18:30
24 | Bhaluka | 136 | 18:30 | 90 | Lalbag | 83 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 54 | 20:00 | 91 | Lalmonirhat | 62 | 21:00 | 157 | Shitalakhya | 81 | 16:00
26 | Bhangura | 44 | 04:00 | 92 | MI_Cement | 10 | 09:00 | 158 | Sholosohor | 46 | 18:30
27 | Bheramara(GK) | 69 | 00:00 | 93 | Madanganj | 34 | 00:00 | 159 | Shyampur | 152 | 00:00
28 | Bhulta | 249 | 23:00 | 94 | Madaripur | 102 | 01:00 | 160 | Siddhirganj | 116 | 12:00
29 | Bog-Sherpur | 66 | 04:00 | 95 | Madartek | 104.92 | 00:00 | 161 | Sirajganj | 108 | 02:00
30 | Bogura | 178 | 15:00 | 96 | Madunaghat | 57 | 18:00 | 162 | Sonargaon | 93 | 18:30
31 | Borhanuddin | 37 | 18:00 | 97 | Magura | 74 | 00:00 | 163 | Sreemongol | 71 | 18:30
32 | Brahmanbaria | 185 | 01:00 | 98 | Mahasthangarh | 78 | 04:00 | 164 | Sreepur | 105 | 10:00
33 | Cantonment | 128 | 00:00 | 99 | Manikganj | 126 | 19:30 | 165 | Srinagar | 45.2 | 04:00
34 | Chandpur | 70 | 01:00 | 100 | Maniknagar | 74 | 15:00 | 166 | Sunamganj | 60 | 05:00
35 | Chandraghona | 39 | 18:30 | 101 | Matarbari | 46 | 18:30 | 167 | Sylhet | 52 | 02:00
36 | Chapai | 72 | 22:00 | 102 | Matuail | 58 | 00:00 | 168 | Sylhet-132 | 145 | 11:00
37 | Charsaidpur | 38 | 16:00 | 103 | Millgate | 133 | 15:00 | 169 | TK | 32.5 | 19:00
38 | Chauddagram | 69 | 00:00 | 104 | Mirpur | 160 | 00:00 | 170 | Tangail | 174 | 00:00
39 | Chhatak | 38 | 04:00 | 105 | Mirsorai | 5 | 18:30 | 171 | Thakurgaon | 117 | 22:00
40 | Chowmuhani | 182 | 22:00 | 106 | Mirzapur | 39 | 20:00 | 172 | Tongi | 137 | 08:00
41 | Chuadanga | 120 | 00:00 | 107 | Mithapukur | 62 | 07:00 | 173 | Ullahpara | 27 | 02:00
42 | Coxsbazar | 107 | 15:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 64 | 00:00
43 | Cumilla(N) | 172 | 04:00 | 109 | Mogbazar | 108 | 15:00 | 175 | Uttara | 76 | 00:00
44 | Cumilla(S) | 159 | 01:00 | 110 | Mongla | 44 | 19:30 | 176 | UttaraNew | 72 | 00:00
45 | Daudkandi | 151 | 19:00 | 111 | Motijheel | 43 | 00:00 | 177 | Zigatola | 119 | 00:00
46 | Dhaka | 38 | 13:00 | 112 | Munshiganj | 103 | 03:00
47 | Dhamrai | 138 | 10:00 | 113 | Mymensingh | 249 | 02:00
48 | Dhanmondi | 131.6 | 13:00 | 114 | Naogaon | 135 | 13:00
49 | Dohazari | 98 | 20:00 | 115 | Narail | 59 | 21:00
50 | Faridpur | 175 | 00:00 | 116 | Narinda | 69 | 13:00
51 | Fatullah | 104 | 16:00 | 117 | Narshingdi | 153 | 19:30
52 | Fenchuganj | 46 | 03:00 | 118 | Natore | 137 | 03:00
53 | Feni | 101 | 01:00 | 119 | Nawabganj | 45.9 | 21:00
54 | GPH | 77 | 19:00 | 120 | Netrakona | 109 | 00:00
55 | Ghatail | 46 | 00:00 | 121 | New | 54.5 | 15:00
56 | Ghorashal | 53 | 10:00 | 122 | Niamatpur | 71 | 04:00
57 | Goalpara | 42 | 20:00 | 123 | Noapara | 48 | 19:30

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-09-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 380 | 17:00 | 369 | 12:00 | Kaliakoir | 394 | 14:00 | 353 | 12:00
| Ashuganj | 406 | 16:00 | 388 | 19:30 | Madunaghat | 395 | 05:00 | 388 | 22:00
| Bhulta | 394 | 03:00 | 383 | 12:00 | Meghnaghat | 376 | 03:00 | 365 | 12:00
| Bibiana | 397 | 16:00 | 384 | 12:00 | Payra | 409 | 06:00 | 402 | 22:00
| BIPTC | 401 | 08:00 | 393 | 00:00 | Rahanpur | 407 | 18:00 | 393 | 04:00
| Bogura | 398 | 18:00 | 378 | 05:00 | Rampal | 399 | 09:00 | 387 | 22:00
| Gopalganj | 394 | 17:00 | 382 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 225 | 04:00 | 216 | 12:00 | Haripur | 227 | 16:00 | 220 | 12:00
| AKSML | 239 | 07:00 | 229 | 12:00 | Hasnabad | 225 | 05:00 | 217 | 12:00
| Aminbazar | 233 | 10:00 | 217 | 12:00 | Hathazari | 236 | 01:00 | 229 | 23:00
| Ashuganj | 236 | 16:00 | 192 | 04:00 | Ishurdi | 237 | 17:00 | 228 | 12:00
| Ashuganj-400 | 235 | 7:00 | 222 | 20:00 | Jhenaidah | 228 | 00:00 | 214 | 23:00
| Baghabari | 235 | 17:00 | 225 | 12:00 | Kaliakoir | 228 | 16:00 | 218 | 12:00
| Barapukuria | 223 | 18:00 | 212 | 11:00 | Keranigonj | 224 | 03:00 | 216 | 12:00
| Barapukuria-230 | 223 | 18:00 | 212 | 11:00 | Khulna(S) | 229 | 08:00 | 216 | 21:00
| Barishal | 235 | 09:00 | 226 | 23:00 | Madunaghat | 239 | 07:00 | 232 | 22:00
| Bheramara | 235 | 17:00 | 222 | 23:00 | Maniknagar | 227 | 06:00 | 219 | 12:00
| Bhulta | 229 | 07:00 | 220 | 12:00 | Meghnaghat | 233 | 11:00 | 228 | 12:00
| Bibiana | 225 | 16:00 | 218 | 12:00 | Meghnaghat-400 | 230 | 04:00 | 222 | 12:00
| BIPTC | 236 | 00:00 | 225 | 21:00 | Mirsorai | 234 | 04:00 | 226 | 12:00
| Bogura | 233 | 18:00 | 221 | 10:00 | Rajshahi | 236 | 17:00 | 223 | 23:00
| Bogura-400 | 235 | 18:00 | 222 | 04:00 | Rampal | 229 | 00:00 | 217 | 22:00
| Borhanuddin | 239 | 09:00 | 236 | 11:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 235 | 04:00 | 227 | 12:00 | Rampura | 227 | 05:00 | 219 | 12:00
| Cumilla(N) | 228 | 07:00 | 221 | 12:00 | Shikalbaha | 238 | 04:00 | 229 | 21:00
| Faridpur | 231 | 07:00 | 222 | 23:00 | Shyampur | 226 | 03:00 | 218 | 12:00
| Fenchuganj | 227 | 16:00 | 218 | 08:00 | Siddhirganj | 227 | 11:00 | 221 | 12:00
| Ghorashal | 232 | 01:00 | 230 | 00:00 | Sirajgonj | 240 | 17:00 | 232 | 10:00
| Ghorashal-230 | 229 | 16:00 | 218 | 12:00 | Sreepur | 232 | 16:00 | 221 | 09:00
| Gopalganj | 232 | 06:00 | 225 | 22:00 | Tongi | 226 | 04:00 | 216 | 12:00
| GPH | 236 | 04:00 | 229 | 12:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 132 | 03:00 | 125 | 12:00 | Kushtia | 135 | 09:00 | 126 | 23:00
| Agargaon | 130 | 04:00 | 124 | 12:00 | Lalbag | 131 | 04:00 | 124 | 13:00
| Agrabad | 134 | 04:00 | 130 | 11:00 | Lalmonirhat | 132 | 18:00 | 116 | 21:00
| AKS | 133 | 07:00 | 128 | 21:00 | Madanganj | 129 | 11:00 | 123 | 12:00
| Aminbazar | 135 | 11:00 | 126 | 12:00 | Madaripur | 131 | 04:00 | 126 | 21:00
| Amnura | 141 | 18:30 | 124 | 04:00 | Madartek | 132 | 04:00 | 125 | 12:00
| Ashuganj | 138 | 17:00 | 135 | 00:00 | Madunaghat | 136 | 04:00 | 131 | 21:00
| Bagerhat | 139 | 00:00 | 122 | 23:00 | Magura | 135 | 09:00 | 122 | 23:00
| Bakulia | 134 | 01:00 | 130 | 21:00 | Mahasthangarh | 140 | 18:00 | 126 | 04:00
| Banani | 132 | 16:00 | 124 | 12:00 | Manikganj | 125 | 16:00 | 117 | 12:00
| Bangabhaban | 128 | 04:00 | 122 | 12:00 | Maniknagar | 128 | 04:00 | 122 | 12:00
| Barapukuria | 138 | 18:00 | 128 | 11:00 | Matarbari | 126 | 07:00 | 116 | 19:30
| Barguna | 136 | 03:00 | 130 | 23:00 | Matuail | 130 | 11:00 | 124 | 12:00
| Barishal | 132 | 05:00 | 124 | 22:00 | Millgate | 130 | 03:00 | 122 | 12:00
| Barishal-230 | 133 | 06:00 | 125 | 23:00 | Mirpur | 133 | 03:00 | 127 | 12:00
| Baroaulia | 135 | 03:00 | 130 | 12:00 | Mirzapur | 131 | 16:00 | 117 | 12:00
| Baroirhat | 131 | 02:00 | 120 | 23:00 | Mithapukur | 137 | 18:00 | 120 | 04:00
| Bashundhara | 132 | 03:00 | 120 | 14:00 | MI_Cement | 132 | 04:00 | 125 | 12:00
| BashundharaCement | 129 | 11:00 | 123 | 12:00 | Modern | 134 | 03:00 | 130 | 18:00
| Beanibazar | 132 | 14:00 | 118 | 04:00 | Mogbazar | 133 | 06:00 | 127 | 10:00
| Benapole | 131 | 08:00 | 119 | 18:30 | Mongla | 138 | 00:00 | 121 | 22:00
| Bhaluka | 133 | 16:00 | 119 | 12:00 | Motijheel | 128 | 04:00 | 122 | 12:00
| Bhandaria | 132 | 07:00 | 118 | 21:00 | Munshiganj | 129 | 11:00 | 123 | 23:00
| Bhangura | 140 | 18:00 | 131 | 11:00 | Mymensingh | 137 | 16:00 | 116 | 01:00
| Bheramara | 135 | 00:00 | 129 | 23:00 | Naogaon | 140 | 18:00 | 122 | 11:00
| Bheramara(GK) | 136 | 17:00 | 130 | 23:00 | Narail | 135 | 07:00 | 122 | 23:00
| Bhulta | 122 | 11:00 | 115 | 15:00 | Narinda | 128 | 04:00 | 122 | 12:00
| Bog-Sherpur | 141 | 17:00 | 129 | 04:00 | Narshingdi | 121 | 03:00 | 115 | 12:00
| Bogura | 143 | 18:00 | 130 | 11:00 | Natore | 139 | 18:00 | 128 | 12:00
| Bogura-230 | 141 | 18:00 | 130 | 11:00 | Nawabganj | 131 | 11:00 | 125 | 12:00
| Brahmanbaria | 135 | 16:00 | 126 | 04:00 | Netrakona | 137 | 16:00 | 117 | 12:00
| Cantonment | 131 | 07:00 | 124 | 12:00 | New | 130 | 04:00 | 123 | 14:00
| Chandpur | 136 | 01:00 | 127 | 23:00 | Niamatpur | 138 | 18:30 | 130 | 04:00
| Chandraghona | 136 | 02:00 | 133 | 12:00 | Noapara | 135 | 00:00 | 122 | 22:00
| Chapai | 138 | 18:30 | 125 | 22:00 | Pabna | 138 | 18:30 | 129 | 23:00
| Charsaidpur | 130 | 11:00 | 123 | 12:00 | Palashbari | 139 | 18:00 | 118 | 05:00
| Chauddagram | 132 | 01:00 | 122 | 23:00 | Panchagarh | 133 | 07:00 | 113 | 21:00
| Chhatak | 132 | 14:00 | 121 | 04:00 | Patuakhali | 136 | 04:00 | 132 | 09:00
| Chowmuhani | 135 | 01:00 | 120 | 18:00 | Payra | 136 | 00:00 | 133 | 07:00
| Chuadanga | 128 | 09:00 | 114 | 22:00 | PHP | 131 | 01:00 | 120 | 23:00
| Coxsbazar | 126 | 08:00 | 116 | 21:00 | Postogola | 134 | 07:00 | 127 | 13:00
| Cumilla(N) | 132 | 07:00 | 127 | 23:00 | Purbachal | 132 | 05:00 | 123 | 09:00
| Cumilla(S) | 132 | 05:00 | 127 | 14:00 | Purbasadipur | 130 | 18:30 | 114 | 21:00
| Daudkandi | 130 | 11:00 | 121 | 12:00 | Rahanpur | 138 | 18:00 | 132 | 04:00
| Dhaka | 133 | 07:00 | 126 | 12:00 | Rahim | 135 | 21:00 | 124 | 12:00
| Dhamrai | 131 | 16:00 | 121 | 12:00 | Rajbari | 127 | 06:00 | 121 | 22:00
| Dhanmondi | 135 | 06:00 | 126 | 12:00 | Rajendrapur | 127 | 17:00 | 115 | 13:00
| Dohazari | 132 | 08:00 | 124 | 21:00 | Rajshahi | 138 | 18:00 | 128 | 23:00
| Faridpur | 130 | 07:00 | 124 | 23:00 | Rajshahi-230 | 139 | 18:30 | 119 | 15:00
| Fatullah | 132 | 04:00 | 126 | 12:00 | Ramganj | 135 | 02:00 | 121 | 23:00
| Fenchuganj | 136 | 15:00 | 129 | 07:00 | Rampur | 134 | 02:00 | 131 | 12:00
| Feni | 132 | 01:00 | 122 | 23:00 | Rampura | 131 | 05:00 | 125 | 12:00
| Ghatail | 134 | 16:00 | 114 | 12:00 | Rangamati | 135 | 02:00 | 131 | 21:00
| Ghorashal | 135 | 04:00 | 134 | 00:00 | Rangpur | 135 | 18:00 | 118 | 03:00
| Goalpara | 140 | 00:00 | 126 | 23:00 | Ruppur | 138 | 18:30 | 130 | 23:00
| Gollamari | 137 | 00:00 | 127 | 22:00 | Saidpur | 135 | 18:00 | 119 | 03:00
| Gopalganj | 132 | 00:00 | 125 | 22:00 | Satkhira | 140 | 00:00 | 120 | 21:00
| Gopalganj-400 | 131 | 06:00 | 126 | 22:00 | Satmasjid | 129 | 04:00 | 123 | 12:00
| Gulshan | 131 | 04:00 | 125 | 12:00 | Savar | 133 | 03:00 | 126 | 08:00
| Halishahar | 134 | 02:00 | 129 | 21:00 | SevenRings | 139 | 16:00 | 129 | 12:00
| Haripur | 130 | 11:00 | 124 | 12:00 | ShahCement | 130 | 11:00 | 123 | 12:00
| HaripurSBU | 135 | 21:00 | 124 | 12:00 | Shahjadpur | 140 | 18:00 | 133 | 22:00
| Hasnabad | 133 | 03:00 | 127 | 11:00 | Shahjibazar | 136 | 16:00 | 126 | 05:00
| Hathazari | 138 | 01:00 | 133 | 23:00 | Shahmirpur | 135 | 03:00 | 131 | 18:00
| Ishurdi | 138 | 18:00 | 133 | 12:00 | Shariatpur | 131 | 07:00 | 123 | 23:00
| Jaldhaka | 130 | 18:00 | 115 | 21:00 | Sherpur | 140 | 18:30 | 118 | 12:00
| Jamalpur | 139 | 18:30 | 122 | 12:00 | Shikalbaha | 122 | 17:00 | 119 | 19:30
| Jashore | 132 | 00:00 | 120 | 23:00 | Shikalbaha-230 | 136 | 06:00 | 128 | 23:00
| Jhenaidah | 135 | 08:00 | 124 | 23:00 | Shitalakhya | 132 | 04:00 | 125 | 12:00
| Jhenaidah-230 | 135 | 08:00 | 125 | 23:00 | Sholosohor | 135 | 04:00 | 129 | 23:00
| Joydebpur | 134 | 16:00 | 122 | 12:00 | Shyampur | 130 | 08:00 | 125 | 12:00
| Joypurhat | 138 | 18:00 | 119 | 11:00 | Shyampur-230 | 131 | 03:00 | 125 | 12:00
| Juldah | 135 | 02:00 | 130 | 19:30 | Siddhirganj | 129 | 05:00 | 124 | 12:00
| Kabirpur | 130 | 16:00 | 118 | 13:00 | Sirajganj | 140 | 17:00 | 126 | 01:00
| Kachua | 133 | 01:00 | 127 | 18:00 | Sonargaon | 129 | 03:00 | 122 | 12:00
| Kaliakoir | 132 | 16:00 | 120 | 12:00 | Sreemongol | 135 | 16:00 | 126 | 23:00
| Kallyanpur | 128 | 05:00 | 124 | 00:00 | Sreepur | 131 | 16:00 | 124 | 09:00
| Kalurghat | 135 | 06:00 | 131 | 23:00 | Srinagar | 131 | 11:00 | 125 | 12:00
| Kamrangirchar | 130 | 06:00 | 123 | 00:00 | SSM | 140 | 00:00 | 137 | 15:00
| Kaptai | 134 | 7:00 | 128 | 19:00 | Sunamganj | 130 | 14:00 | 119 | 11:00
| Kazla | 127 | 04:00 | 122 | 13:00 | Sylhet | 132 | 15:00 | 124 | 04:00
| Keranigonj | 131 | 03:00 | 126 | 12:00 | Sylhet-132 | 131 | 15:00 | 125 | 12:00
| Khagrachori | 135 | 01:00 | 131 | 19:00 | Tangail | 131 | 16:00 | 114 | 12:00
| Khulna | 138 | 00:00 | 125 | 22:00 | Thakurgaon | 130 | 17:00 | 109 | 11:00
| Khulna(S) | 137 | 00:00 | 127 | 21:00 | TK | 135 | 04:00 | 129 | 23:00
| Khulshi | 134 | 07:00 | 128 | 23:00 | Tongi | 132 | 04:00 | 126 | 08:00
| Kishoreganj | 135 | 16:00 | 124 | 10:00 | Ullahpara | 142 | 17:00 | 132 | 10:00
| Kodda | 130 | 16:00 | 116 | 12:00 | Ullon | 131 | 05:00 | 125 | 12:00
| KSRM | 135 | 03:00 | 130 | 12:00 | Uttara | 135 | 06:00 | 127 | 10:00
| Kulaura | 135 | 16:00 | 128 | 11:00 | UttaraNew | 134 | 05:00 | 127 | 12:00
| Kurigram | 132 | 17:00 | 115 | 05:00 | Zigatola | 131 | 05:00 | 125 | 12:00

## L-Curve
Date | 2024-09-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 962 | 7273 | 6144 | 13417 |  |  |  | QF-LDC-11
0:30 | 884 | 7283.5 | 6070 | 13353.5 | Date: | 2024-09-21
1:00 | 806 | 7294 | 5996 | 13290
1:30 | 787 | 7306.5 | 5981 | 13287.5
2:00 | 768 | 7319 | 5966 | 13285
2:30 | 744 | 7237.5 | 5947 | 13184.5 | [5 empty] | Gen. at Eve. Peak | 12841 | 12841 MW (21:00 )
3:00 | 720 | 7156 | 5928 | 13084 | [6 empty] | 21:00
3:30 | 705 | 7166 | 5918 | 13084 | [5 empty] | Gen. at Day Peak | 12198 | 12198 MW (12:00 )
4:00 | 690 | 7176 | 5908 | 13084 | [6 empty] | 12:00
4:30 | 692 | 7051 | 5871 | 12922 | [5 empty] | Highest Generation | 13417
5:00 | 694 | 6926 | 5834 | 12760 | [6 empty] | 24:00
5:30 | 730 | 6730.5 | 5685.5 | 12416
6:00 | 766 | 6535 | 5537 | 12072
6:30 | 788 | 6416.5 | 5516 | 11932.5
7:00 | 810 | 6298 | 5495 | 11793
7:30 | 885 | 6173.5 | 5421 | 11594.5
8:00 | 960 | 6049 | 5347 | 11396
8:30 | 1023 | 6096 | 5405 | 11501
9:00 | 1086 | 6143 | 5463 | 11606
9:30 | 1130 | 6128 | 5436.5 | 11564.5
10:00 | 1174 | 6113 | 5410 | 11523
10:30 | 1194 | 5992.5 | 5432 | 11424.5
11:00 | 1214 | 5872 | 5454 | 11326
11:30 | 1176 | 6007 | 5755 | 11762
12:00 | 1138 | 6142 | 6056 | 12198
12:30 | 1107 | 6303.5 | 6081 | 12384.5
13:00 | 1076 | 6465 | 6106 | 12571
13:30 | 1050 | 6552 | 5993.5 | 12545.5
14:00 | 1024 | 6639 | 5881 | 12520
14:30 | 1024 | 6736.5 | 5845 | 12581.5
15:00 | 1024 | 6834 | 5809 | 12643
15:30 | 1033 | 6529.5 | 5622.5 | 12152
16:00 | 1042 | 6225 | 5436 | 11661
16:30 | 1037 | 6074.5 | 5313.5 | 11388
17:00 | 1032 | 5924 | 5191 | 11115
17:30 | 1020 | 5987.5 | 5038 | 11025.5
18:00 | 1008 | 6051 | 4885 | 10936
18:30 | 719 | 6437 | 5007.5 | 11444.5
19:00 | 430 | 6823 | 5130 | 11953
19:30 | 482 | 6808 | 5442 | 12250
20:00 | 624 | 6854 | 5669 | 12523 |  |  |  | Executive Engineer
20:30 | 522 | 6945 | 5737 | 12682 |  |  |  | Network Operation Division
21:00 | 420 | 7036 | 5805 | 12841
21:30 | 440 | 7040.5 | 5928 | 12968.5
22:00 | 460 | 7045 | 6051 | 13096 |  |  |  |  | Page 6 of 7
22:30 | 568 | 7085.5 | 6118 | 13203.5
23:00 | 676 | 7126 | 6185 | 13311
23:30 | 819 | 7199.5 | 6164.5 | 13364
24:00 | 962 | 7273 | 6144 | 13417
12841 MW (21:00 )
12198 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-09-21 |  | Energy |  | 302271664
[16 empty] | 2024-09-21 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3505 | 446 | 1880 | 0 | 1604 | 4419 | 170 | 0 | 226 | 68 | 1099 | 0 | 0 | 79.265
0:30 | 3433.5 | 664.5 | 1854 | 0 | 1638.5 | 4186.5 | 170 | 0 | 274 | 69 | 1057.5 | 0 | 6 | 498.0325 |  |  | Date: | 44094
1:00 | 3362 | 883 | 1828 | 0 | 1673 | 3954 | 170 | 0 | 322 | 70 | 1016 | 0 | 12 | 916.8
1:30 | 3351.5 | 883 | 1833.5 | 0 | 1687 | 3947.5 | 170 | 0 | 317 | 70 | 1017.5 | 0 | 10.5 | 833.2375 | [8 empty] | Total Energy | 302.2717 | 302.2717 | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 3341 | 883 | 1839 | 0 | 1701 | 3941 | 170 | 0 | 312 | 70 | 1019 | 0 | 9 | 749.675 | [8 empty] | Energy not Served | 7.1092 | 7.1092
2:30 | 3349.5 | 879.5 | 1816.5 | 0 | 1663 | 3934.5 | 169 | 0 | 276 | 69 | 1019.5 | 0 | 8 | 716.7275 | [8 empty] | Energy Requirement | 309.3809 | 309.3809
3:00 | 3358 | 876 | 1794 | 0 | 1625 | 3928 | 168 | 0 | 240 | 68 | 1020 | 0 | 7 | 683.78
3:30 | 3362.5 | 876.5 | 1809 | 0 | 1620 | 3933.5 | 167.5 | 0 | 223 | 67 | 1020.5 | 0 | 4.5 | 612.155 | [7 empty] | Shortage
4:00 | 3367 | 877 | 1824 | 0 | 1615 | 3939 | 167 | 0 | 206 | 66 | 1021 | 0 | 2 | 540.53
4:30 | 3362.5 | 876.5 | 1824.5 | 0 | 1502 | 3924 | 166.5 | 0 | 184.5 | 60 | 1020.5 | 0 | 1 | 494.69
5:00 | 3358 | 876 | 1825 | 0 | 1389 | 3909 | 166 | 0 | 163 | 54 | 1020 | 0 | 0 | 448.85
5:30 | 3373.5 | 876.5 | 1805.5 | 0 | 1161 | 3831.5 | 166 | 0 | 122 | 58 | 1017.5 | 1 | 3.5 | 419.245
6:00 | 3389 | 877 | 1786 | 0 | 933 | 3754 | 166 | 0 | 81 | 62 | 1015 | 2 | 7 | 389.64
6:30 | 3333 | 877 | 1767 | 0 | 900 | 3683 | 166.5 | 0 | 81 | 60 | 1014.5 | 38 | 12.5 | 350.9625 | [6 empty] | Coal
7:00 | 3277 | 877 | 1748 | 0 | 867 | 3612 | 167 | 0 | 81 | 58 | 1014 | 74 | 18 | 312.285
7:30 | 3268.5 | 877.5 | 1645.5 | 0 | 818.5 | 3515.5 | 168 | 0 | 81 | 57 | 1013.5 | 129 | 20.5 | 315.6425 | [5 empty] | Oil
8:00 | 3260 | 878 | 1543 | 0 | 770 | 3419 | 169 | 0 | 81 | 56 | 1013 | 184 | 23 | 319
8:30 | 3259 | 877.5 | 1598 | 0 | 784.5 | 3416.5 | 169 | 0 | 72.5 | 50 | 1014.5 | 239.5 | 20 | 338
9:00 | 3258 | 877 | 1653 | 0 | 799 | 3414 | 169 | 0 | 64 | 44 | 1016 | 295 | 17 | 357
9:30 | 3272 | 876.5 | 1630 | 0 | 736.5 | 3386 | 169.5 | 0 | 64 | 43 | 1016.5 | 355.5 | 15 | 334.6425
10:00 | 3286 | 876 | 1607 | 0 | 674 | 3358 | 170 | 0 | 64 | 42 | 1017 | 416 | 13 | 312.285
10:30 | 3226 | 876 | 1596.5 | 0 | 606.5 | 3404.5 | 170 | 0 | 64 | 43 | 1016.5 | 408.5 | 13 | 287.1425
11:00 | 3166 | 876 | 1586 | 0 | 539 | 3451 | 170 | 0 | 64 | 44 | 1016 | 401 | 13 | 262
11:30 | 3214 | 876 | 1688.5 | 0 | 635.5 | 3602 | 170 | 0 | 66.5 | 52 | 1016 | 426 | 15.5 | 261
12:00 | 3262 | 876 | 1791 | 0 | 732 | 3753 | 170 | 0 | 69 | 60 | 1016 | 451 | 18 | 260
12:30 | 3202.5 | 876.5 | 1772.5 | 0 | 907 | 3803 | 190 | 0 | 75 | 63 | 1015.5 | 461 | 18.5 | 330.5
13:00 | 3143 | 877 | 1754 | 0 | 1082 | 3853 | 210 | 0 | 81 | 66 | 1015 | 471 | 19 | 401
13:30 | 3143 | 877 | 1754 | 0 | 1082 | 3853 | 210 | 0 | 81 | 66 | 1015 | 471 | 19 | 401
14:00 | 3143 | 877 | 1754 | 0 | 1082 | 3853 | 210 | 0 | 81 | 66 | 1015 | 471 | 19 | 401
14:30 | 3184 | 876.5 | 1712.5 | 0 | 1286.5 | 3749 | 209 | 0 | 110.5 | 66 | 1017.5 | 383 | 12.5 | 371
15:00 | 3225 | 876 | 1671 | 0 | 1491 | 3645 | 208 | 0 | 140 | 66 | 1020 | 295 | 6 | 341
15:30 | 3150.5 | 874.5 | 1601.5 | 0 | 1291.5 | 3546 | 208 | 0 | 168 | 63 | 1015 | 231 | 3 | 237
16:00 | 3076 | 873 | 1532 | 0 | 1092 | 3447 | 208 | 0 | 196 | 60 | 1010 | 167 | 0 | 133
16:30 | 3054 | 873 | 1459 | 0 | 1058 | 3375.5 | 208 | 0 | 197 | 59 | 1001 | 102 | 1.5 | 121.5
17:00 | 3032 | 873 | 1386 | 0 | 1024 | 3304 | 208 | 0 | 198 | 58 | 992 | 37 | 3 | 110
17:30 | 3090 | 873 | 1280.5 | 0 | 1072 | 3267 | 208.5 | 0 | 203 | 60 | 948.5 | 19 | 4 | 73.5
18:00 | 3148 | 873 | 1175 | 0 | 1120 | 3230 | 209 | 0 | 208 | 62 | 905 | 1 | 5 | 37
18:30 | 3176.5 | 802 | 1361 | 0 | 1286.5 | 3429.5 | 209.5 | 0 | 233.5 | 61 | 882 | 0.5 | 2.5 | 65
19:00 | 3205 | 731 | 1547 | 0 | 1453 | 3629 | 210 | 0 | 259 | 60 | 859 | 0 | 0 | 93
19:30 | 3252 | 731 | 1769 | 0 | 1395 | 3720 | 210 | 0 | 209 | 58 | 906 | 0 | 0 | 81
20:00 | 3314 | 756 | 1786 | 0 | 1395 | 3784 | 210 | 0 | 209 | 62 | 1007 | 0 | 0 | 69
20:30 | 3405 | 756 | 1790 | 0 | 1389.5 | 3828.5 | 210 | 0 | 200.5 | 62 | 1040.5 | 0 | 0 | 53
21:00 | 3496 | 756 | 1794 | 0 | 1384 | 3873 | 210 | 0 | 192 | 62 | 1074 | 0 | 0 | 37
21:30 | 3454 | 756.5 | 1825.5 | 0 | 1400 | 3978 | 210 | 0 | 192 | 63 | 1089.5 | 0 | 0 | 39.51
22:00 | 3412 | 757 | 1857 | 0 | 1416 | 4083 | 210 | 0 | 192 | 64 | 1105 | 0 | 0 | 42.02
22:30 | 3458 | 756.5 | 1861 | 0 | 1408 | 4141 | 210 | 0 | 192 | 64 | 1113 | 0 | 0 | 56.345
23:00 | 3504 | 756 | 1865 | 0 | 1400 | 4199 | 210 | 0 | 192 | 64 | 1121 | 0 | 0 | 70.67
23:30 | 3504.5 | 601 | 1872.5 | 0 | 1502 | 4309 | 190 | 0 | 209 | 66 | 1110 | 0 | 0 | 74.9675 |  |  | Max Temp. in Dhaka |  | 33.8°C
24:00 | 3505 | 446 | 1880 | 0 | 1604 | 4419 | 170 | 0 | 226 | 68 | 1099 | 0 | 0 | 79.265
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on X13: Author:

## Generation
2024-09-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 130 | 130 | 128 | 127 | 126 | 126 | 127 | 129 | 129 | 130 | 130 | 130 | 130 | 129 | 128 | 128 | 128 | 129 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3088015
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 40 | 1384000
3 | Chattogram TPP-1 | 105 | 107 | 105 | 110 | 110 | 110 | 108 | 106 | 105 | 110 | 110 | 111 | 110 | 109 | 110 | 110 | 110 | 75 | [8 empty] | 1900000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 2 | [16 empty] | 1 | [7 empty] | 0 | 12024
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 |  |  | 18 |  |  |  |  | 13 | 8 | 2 | [9 empty] | 54000
6 | Sikalbaha 225MW CCPP (Gas) | [12 empty] | 31 | 31 | 31 | 32 | 34 | 56 |  | 72 | 83 | 145 | 214 | 185 | 147 | 134 | 936182
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 27 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 203435
12 | Hathazari 100 MW peaking PP | 8 | 8 | 8 | 8 | [13 empty] | 16 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 270976
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 68 | 85 | 85 | 85 | 34 | 17 | 17 | 17 | 17 | [6 empty] | 11 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 645672
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 28 | 28 | [11 empty] | 23 | 29 | 29 | 32 | 34 |  | 38 | 36 | 36 | 36 | 36 | 36 | 37 | 427152
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 290 | 298 | 294 | 290 | 272 | 264 | 270 | 277 | 278 | 278 | 240 | 241 | 262 | 272 | 285 | 280 | 240 | 240 |  | 265 | 252 | 235 | 236 | 221 | 227 | 260 | 6414703
18 | Kodda 300 MW PP Unit-2 (Summit) | 99 | 95 | 95 | 95 | 95 | 45 | 45 | 15 | 15 | 85 | 15 | 15 | 40 | 62 | 97 | 45 | 45 | 48 |  | 102 | 125 | 125 | 125 | 125 | 125 | 125 | 1952073
19 | Ashuganj 195 MW PP (APSCL-United) | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 137 | 137 | 137 | 163 | 185 | 185 | 158 | 160 | 160 | 108 | 45 |  | 100 | 117 | 138 | 142 | 185 | 189 | 190 | 3830545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 610 | 610 | 612 | 608 | 590 | 555 | 500 | 500 | 502 | 490 | 545 | 590 | 612 | 603 | 512 | 450 | 438 |  | 500 | 500 | 500 | 540 | 608 | 612 | 612 | 13325453
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 34 | 34 | 34 | 34 | 34 | 35 | 35 | 35 | 32 | 31 | 31 | 33 | 32 | 35 | 33 | 35 | 35 | 35 |  | 35 | 35 | 36 | 37 | 37 | 37 | 37 | 824832
33 | Ashuganj 225 MW CCPP | 208 | 210 | 210 | 211 | 210 | 212 | 212 | 210 | 211 | 210 | 207 | 213 | 215 | 205 | 212 | 217 | 216 | 209 |  | 212 | 213 | 216 | 211 | 212 | 210 | 212 | 5138000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 330 | 310 | 310 | 310 | 310 | 350 | 305 | 295 | 290 | 300 | 335 | 305 | 305 | 340 | 305 | 280 | 295 | 335 |  | 320 | 310 | 310 | 345 | 320 | 350 | 350 | 7926200
| Ashuganj 420 MW CCPP(East) | 330 | 320 | 320 | 320 | 320 | 320 | 295 | 290 | 285 | 290 | 290 | 320 | 290 | 340 | 325 | 305 | 285 | 315 |  | 290 | 310 | 325 | 355 | 325 | 365 | 370 | 7723000
35 | Ashuganj 55 MW PP (Precision) | 48 | 49 | 49 | 50 | 51 | 51 | 49 | 49 | 46 | 46 | 46 | 47 | 48 | 49 | 51 | 51 | 49 | 22 |  | 41 | 41 | 50 | 52 | 52 | 52 | 53 | 1150560
36 | Chandpur 150 MW CCPP | 75 | 75 | 75 | 75 | 80 | 90 | 80 | 75 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 71 | 70 | 50 | 1552430
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 402 | 402 | 404 | 404 | 404 | 401 | 360 | 400 | 405 | 407 | 380 | 400 | 411 | 405 | 389 | 327 | 301 | 301 |  | 410 | 411 | 410 | 411 | 409 | 409 | 407 | 9489600
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 380 | 340 | 420 | 420 | 450 | 450 | 450 | 370 | 400 | 350 | 320 | 300 |  | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 9966500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 11 | 11 | 8 | 6 | 5 | 4 | 5 | 5 | 5 | 6 | 5 |  | 5 | 6 | 7 | 10 | 10 | 11 | 11 | 238080
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 10 | 23 | 37 | 41 | 40 | 51 | 49 | 30 | 0 | 0 | 0 | [9 empty] | 248160
44 | Fenchugonj CCPP Phase-1 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 38 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 40 | 920000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 29 | 30 | 29 | 20 | 30 | 32 | 30 | 31 | 32 | 32 | 30 |  | 31 | 31 | 32 | 31 | 31 | 31 | 30 | 732192
48 | Shahjibazar 86 MW PP (Shahjibazar) | 84 | 84 | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 51 | 86 | 86 | 86 | 85 | 85 | 86 | 41 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1966080
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 200 | 202 | 203 | 203 | 206 | 206 | 206 | 207 | 203 | 202 | 201 | 199 | 201 | 209 | 208 | 210 | 211 | 212 |  | 212 | 212 | 212 | 212 | 212 | 210 | 210 | 5179080
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 46368
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 11 | 50 | 49 | 49 | 49 | 49 | 50 | 50 | 51 | 52 | 22 |  | 53 | 53 | 52 | 53 | 53 | 53 | 53 | 1135200
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 |  |  |  | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 238512
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 295 | 290 | 285 | 285 | 290 | 290 | 285 | 295 | 290 | 285 | 290 | 290 | 285 | 285 | 270 | 280 | 270 |  | 275 | 290 | 270 | 265 | 280 | 280 | 280 | 6931500
| Bibiyana South 400 MW | 346 | 346 | 346 | 346 | 356 | 346 | 316 | 316 | 346 | 370 | 356 | 346 | 346 | 370 | 340 | 316 | 300 | 340 |  | 320 | 327 | 320 | 338 | 328 | 378 | 378 | 8255800
58 | Nababganj 55 MW PP (Southern power ) |  | 35 | 35 | 35 | 35 | 17 | 17 | [5 empty] | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 669391
59 | Tangail Palli Power Gen 22 MW | 4 | 6 | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 6 |  | 0 | 2 | 3 | 6 | 6 | 6 | 6 | 128160
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 70 | 70 | 68 | 66 | 54 | 62 | 58 | 56 | 44 | 42 | 44 | 60 | 66 | 64 | 66 | 60 | 58 | 62 |  | 60 | 58 | 62 | 62 | 64 | 64 | 68 | 1452480
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 0 | 42 | 42 | 42 | 36 | 10 | 2 | 3 | 3 | 5 | 2 | 2 | 2 | 0 | 0 | 5 |  | 11 | 11 | 21 | 24 | 28 | 32 | 38 | 470400
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 347430
69 | Summit Ashulia | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 |  | 16 | 16 |  | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 403200
70 | Summit Madhabdi |  |  | 21 | 21 | 21 | 21 | 18 | 21 | 21 | 21 | 15 | 20 | 20 | 21 | 21 | 21 |  | 21 |  | 21 | 21 | 14 | 21 | 21 | 21 | 21 | 385920
71 | Maona 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 729900
72 | Rupganj 33 MW PP(Summit) | 21 | 21 | 21 | 23 | 23 | 23 | 20 | 18 | 16 | 15 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 368600
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 52 | 52 | 52 | 52 | 17 | 17 | 17 | 17 | [6 empty] | 17 | 17 | 17 | 17 |  | 34 | 34 | 34 | 34 | 34 | 34 | 67 | 579120
| Chowmuhani 113 MW | 96 | 96 | 96 | 96 | 96 | 44 | 44 | 26 | 8 | 8 |  | 3 | 34 | 57 | 58 | 57 | 63 | 66 |  | 80 | 97 | 95 | 96 | 97 | 97 | 97 | 1606920
| Manikgonj 162MW PP(MPGL) | 72 | 72 | 72 | 72 | 72 | 35 | 35 | 17 | 54 | 54 | 72 | 72 | 72 | 72 | 90 | 54 | 17 | 17 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1569600
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 25 |  | 25 | 25 | 25 | 25 | 25 | 16 | 8 | 264000
79 | Kodda 150 MW PP | 142 | 142 | 98 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 48 | 64 | 69 | 48 | 82 |  | 98 | 82 | 82 | 82 | 82 | 82 | 98 | 1863840
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 41 | 41 | 41 | 42 | 24 | 24 | 24 | 24 | [5 empty] | 5 | 24 | 42 | 39 | 35 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 666950
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 35 | 35 |  | 105 | 105 | 88 | 70 | 70 | 70 | 35 | 909120
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 2 | 1 | 3 | 1 | 2 | 2 | 1 | 0 | [9 empty] | 15719
| Jodiac Power | 24 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 |  |  | 0 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | [5 empty] | 0 | 389268
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 51 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 56 | 70 | 73 | 73 | 34 | 34 |  | 34 | 17 | 17 | 17 | 17 | 17 | 48 | 1333158
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 13 | 13 | 13 | 13 | 13 | [20 empty] | 0 | 65000
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 51 | 51 | 53 | 52 | 52 | 52 | 52 | 52 | 52 | 17 |  |  | 17 | 17 | 17 | 16 | 17 | 17 |  | 16 | 16 | 16 | 16 | 16 |  | 0 | 674880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 10 | 30 | 35 | 35 | 25 | 35 | 33 | 10 |  | 35 | 35 | 32 | 35 | 36 | 36 | 36 | 762048
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 43 | 10 | 10 |  | 36 | 43 | 43 | 43 | 43 | 43 | 51 | 975364
94 | Gagnagar 102 MW PP (Digital Power) | 40 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 32 | 254736
95 | Patenga 50MW PP (Baraka) | [25 empty] | 0 | 0
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 10 | 12 | 12 | 12 | 12 | 12 | [11 empty] | 6 | [6 empty] | 114240
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | [5 empty] | 0 | 389215
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | [7 empty] | 9 | 17 | 35 | 35 | 35 | 35 | 35 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 400531
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [11 empty] | 12900
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 35 | 17 | 17 | 17 | 701640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 95 | 95 | 95 | 96 | 96 | 96 | 123 | 123 | 123 | 124 | 113 | 104 | 111 | 120 | 123 | 9 | 9 | 14 |  | 32 | 32 | 37 | 55 | 56 | 80 | 80 | 2109600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 40 | 61 | 70 | 78 |  | 95 | 96 | 95 | 96 | 96 | 82 | 79 | 1046160
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 12 | 12 | 12 | 12 |  |  |  | 2 | 25 | 25 | 25 | 25 | 37 | 37 |  | 12 | 12 | 12 | 12 | 12 | 12 | 20 | 423360
116 | Chandpur 200 MW (Desh energy) | 136 | 136 | 136 | 136 | 100 | 17 | 17 | 17 | 17 |  |  | 1 | 25 | 42 | 78 | 111 | 85 | 85 |  | 102 | 120 | 120 | 120 | 120 | 120 | 120 | 1950720
117 | Ashuganj 150 MW PP (Midland) | 103 | 102 | 105 | 105 | 107 | 50 | 10 | 10 | 28 | 30 |  |  |  | 5 | 28 | 30 | 30 | 37 |  | 53 | [5 empty] | 0 | 1005309
118 | Bibiyana-III 400 MW CCPP | 361 | 361 | 361 | 368 | 354 | 353 | 347 | 350 | 350 | 350 | 337 | 336 | 223 | 296 | 300 | 337 | 366 | 372 |  | 371 | 371 | 370 | 372 | 372 | 379 | 374 | 8755000
| Jamalpur 115 MW PP (United) | 54 | 54 | 54 | 54 | 55 | 55 | 73 | 73 | 72 | 72 | 72 | 70 | 69 | 70 | 70 | 8 | 8 | 32 |  | 52 | 52 | 52 | 62 | 62 | 82 | 82 | 1437600
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 49 | 49 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 45 | 45 | 132 | 50 | 50 | 50 |  | 50 | 15 | 15 | 15 | 15 | 15 | 100 | 935891
| Juldah unit-2 (Acorn) | 24 | 24 | 24 | 24 | 24 | 12 | 12 | 12 |  |  |  | 12 | 24 | 24 | 24 | 24 | 24 | 37 |  | 12 | 12 | 12 | 12 | 12 | 12 | 24 | 420480
| Anlima Energy Ltd. | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 15 | 17 | 17 | 17 | 17 | 17 |  | 17 | [5 empty] | 0 | 278509
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 0 |  |  |  | 7 |  | 17 | 35 | 24 | 17 | 17 | 17 | 17 | 323640
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 8 |  |  |  | 12 | 33 | 22 | 11 | 2 | 3 | 0 | [8 empty] | 97895
| Chandpur 115(Doreen) | 52 | 53 | 50 | 51 | 50 | 52 | 51 | 51 | 52 | 33 | 17 | 20 | 48 | 59 | 59 | 59 | 59 | 67 |  | 95 | 95 | 95 | 96 | 96 | 67 | 54 | 1416960
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 118800
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 5 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  |  |  | 17 | 327854
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 12 | 9 | 7 | 2 | 0 | 7 | 18 | 23 | 17 | 13 | 13 | 18 | 19 | 15 | 6 | 0 | 3 | 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175200
| Sonagazi 75 MW Solar Plant | [5 empty] | 0 | 1 | 6 | 2 | 1 | 6 | 15 | 16 | 21 | 38 | 19 | 7 | [9 empty] | 131936
| Matarbari 2*600 MW (CPGCL) | 763 | 755 | 754 | 759 | 760 | 755 | 756 | 758 | 756 | 757 | 758 | 758 | 757 | 755 | 753 | 750 | 738 | 756 |  | 757 | 755 | 756 | 756 | 756 | 758 | 759 | 18276363
Meghnaghat (Reliance) 718MW CCPP
120
121 | Eastern Zone Total | 7294 | 7319 | 7156 | 7176 | 6926 | 6535 | 6298 | 6049 | 6143 | 6113 | 5872 | 6142 | 6465 | 6639 | 6834 | 6225 | 5924 | 6051 |  | 6823 | 6808 | 6854 | 7036 | 7045 | 7126 | 7273 | 161841331
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | 53 | 53 | 53 | 53 | 53 | 17 | [10 empty] | 12 | 17 |  | 30 | 53 | 53 | 53 | 53 | 53 | 53 | 637440
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 2 | 33 | 72 | 64 | 54 | 85 | 59 | 40 | 25 | 9 | 1 | [8 empty] | 475920
132 | Rampal 1320 MW (BIFPCL) | 1009 | 1006 | 1014 | 1018 | 1011 | 959 | 890 | 870 | 868 | 824 | 858 | 1010 | 1016 | 980 | 980 | 906 | 909 | 863 |  | 990 | 982 | 1035 | 1054 | 1065 | 1115 | 1247 | 23338180
133 | United Payra Power Ltd. | [25 empty] | 0 | 0
| Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 180 | 220 | 180 | 220 | 220 | 180 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5069220
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | [11 empty] | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 218496
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 230 | 230 | 197 | 180 | 180 | 168 | 164 |  | 200 | 200 | 200 | 200 | 250 | 250 | 307 | 5040000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2439
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 130 | 90 | 90 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 100 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 2580000
141 | Bhola 33 MW PP (Venture) | 2 | 7 | 9 | 0 | 0 | 0 | 0 | 3 | 3 | 2 | 6 | 6 | 6 | 9 | 8 | 7 | 8 | 10 |  | 10 | 9 | 10 | 10 | 10 | 10 | 9 | 137741
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP | [17 empty] | 15 |  | 32 | 32 | 32 | 15 | 15 | 15 | 15 | 144864
147 | Bheramara HVDC | 883 | 883 | 876 | 877 | 876 | 877 | 877 | 878 | 877 | 876 | 876 | 876 | 877 | 876 | 876 | 873 | 873 | 873 |  | 731 | 731 | 756 | 756 | 757 | 756 | 446 | 20344727
148 | Bheramara 410 MW CCPP | 218 | 214 | 213 | 214 | 219 | 218 | 218 | 218 | 217 | 218 | 212 | 212 | 203 | 201 | 194 | 191 | 191 | 190 |  | 190 | 208 | 208 | 210 | 214 | 214 | 215 | 5120640
149 | Payra 1320 MW | 1100 | 1100 | 1080 | 1080 | 1060 | 980 | 940 | 860 | 860 | 850 | 920 | 940 | 990 | 940 | 920 | 860 | 800 | 750 |  | 920 | 1020 | 1030 | 1060 | 1140 | 1200 | 1230 | 25800300
150
151 | Barapukuria TPP Unit-1 | 60 | 60 | 60 | 60 | 60 | 60 | 61 | 61 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 59 | 59 |  | 62 | 63 | 63 | 63 | 64 | 64 | 64 | 1405091
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 170 | 170 | 165 | 165 | 210 | 210 | 165 | 150 | 180 | 180 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4719000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 37 | 37 | 37 | 37 | 37 | [9 empty] | 20 | 28 | 34 | [8 empty] | 0 | 293723
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 3 | 1 | 4 | 4 | 6 | 1 | 1 | 0 | 0 | [9 empty] | 31380
157 | Sirajganj 68 MW Solar Park | [5 empty] | 0 | 13 | 28 | 43 | 48 | 32 | 59 | 64 | 34 | 9 | 5 | [10 empty] | 339000
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 182 | 181 | 181 | 181 | 182 | 182 | 181 | 150 | 176 | 182 | 140 | 164 | 182 | 160 | 171 | 160 | 140 | 140 |  | 140 | 150 | 162 | 181 | 181 | 182 | 182 | 4194364
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 370 | 370 | 320 | 360 | 320 | 300 | 380 | 380 | 320 | 350 | 300 | 260 | 260 |  | 260 | 414 | 414 | 414 | 414 | 414 | 414 | 8984218
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | 22 | 22 | 22 | 22 | [22 empty] | 92039
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | [9 empty] | 0 | 111438
166 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | 38 | 28 | 28 | 28 | 15 | [9 empty] | 10 | 21 | 35 | [9 empty] | 175751
169 | Santahar 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | [21 empty] | 158833
170 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
171 | Chapainawabganj 100 MW Peaking PP | [15 empty] | 32 | 32 | 32 |  | 32 | [6 empty] | 146064
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 60 | 35 | 35 | 75 | 98 | 113 | 113 | 50 | 35 | [8 empty] | 22 | 1039200
173 | Confidence Power Bogura Unit-1 113 MW | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 50 | 75 | 95 | 95 | 35 | 35 | [8 empty] | 50 | 820608
175 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | Rangpur 113 MW PP (Confidence) | 70 | 70 | 49 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 32 | 33 | 75 |  | 49 | 49 | 59 | 70 | 98 | 106 | 106 | 1220227
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | [6 empty] | 6 | 3 | 2 | 1 | 0 | [8 empty] | 15693
| Energypac Power Venture Thakurgaon Ltd. | 75 | 75 | 75 | 75 | 75 | 75 | 14 |  |  |  |  | 70 | 75 | 75 | 75 | 74 | 74 | 35 |  | 55 | 55 | 70 | 75 | 115 | 115 | 115 | 1549248
| Intraco Solar 30 MW | [5 empty] | 0 | 6 | 14 | 24 | 31 | 34 | 36 | 34 | 19 | 23 | 13 | 7 | 0 | [8 empty] | 245796
178 | Adani Power Jharkhanda Ltd | 1016 | 1019 | 1020 | 1021 | 1020 | 1015 | 1014 | 1013 | 1016 | 1017 | 1016 | 1016 | 1015 | 1013 | 1020 | 1010 | 992 | 905 |  | 859 | 906 | 1007 | 1074 | 1105 | 1121 | 1099 | 24463703
| Teesta Solar Limited | [5 empty] | 2 | 35 | 88 | 136 | 176 | 185 | 185 | 155 | 168 | 134 | 83 | 0 | [9 empty] | 1306080