## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-09-25 | Wednesday
|  | Date (day): | 2024-09-25 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15032.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16474 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-09-24 | 2024-09-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 401 | 410 | 400 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 180 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 18 | 150 | 150 | 185 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 13 | 13 | 13 | 13 | 62 |  | Fuel shortage
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 291 | 290 | 0 | 0 |  | 335 | Under maint |  | 2024-09-27
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 82 | 8 | 102
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 8 | 54 | 17 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 133 | 64 | 132 |  | 17 | Engine problem
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 35 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 37 | 37 | 40 |  | 40 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 30 | 33 | 33
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 11 | 11 | 18 | 18 |  | 15 | Engine problem
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 17 | 25 | 16 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 64 | 278 | 80 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 112 | 132 | 115 | 132 |  | 17 | Engine problem
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 34 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 50 | 17 | 53 | 51 |  | Lub Oil problem
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 35 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem.
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1739 | 2170 | 1682 | 2349 | 2285 | 1224
35 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
36 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 16 | 25 | 8 | 25
37 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
38 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 28 | 0 | 50 | 50
39 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 213 | 212 | 214 | 214
40 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 217 | 224 | 224
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
42 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 19 | 17 | 105 | 105
43 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 65 | 65 | 33 |  | Fuel shortage
44 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 51 | 51 | 84 |  | 18 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
45 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 37 | 25 | 37 | 63 |  | fuel shortage.
46 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 23 | 7 | 20
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 31 | 51 | 38 | 50 | 58 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 50 | 15 | 50 | 50 | 250 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 37 | 34 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 24 | 24 | 24
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 108 | 108
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 72 | 35 | 163
55 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 612 | 570 | 612 | 612 |  | 612 | Unit-2 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 24 | 17 | 42 | 60 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 757 | 708 | 750 | 750 |  |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 2168 | 2147 | 2597 | 2805 | 584 | 960
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 208 | 216 | 210 | 210
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 305 | 310 | 310 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 350 | 320 | 330 | 330 | 70 |  | FGMO
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 37 | 34 | 34 | 11 |  | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 50 | 54 | 53 | 53
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 177 | 108 | 140 | 140 | 55 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 65 | 95 | 125 | 125 |  | 25 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 35 | 35 | 35 |  | 17 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 50 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 103 | 195 | 17 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 60 | 70 | 60 | 70
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 17 | 52 | 16 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 106 | 34 | 106 |  | 8 | Engine problem
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 60 | 94 | 95 | 113
76 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 92 | 50 | 90 |  | 25 | Fuel shortag
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 59 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1731 | 1890 | 1698 | 1987 | 249 | 442
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 4 | 10 | 5 | 15 | 187 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 125 | 162 | 125 | 160 | 40 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 72 | 89 | 74 | 90 | 25 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 26 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 1 | 18 | 6 | 18 |  | 4 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 16 | 17 | 54
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 230 | 295 | 278.6 | 337 | 187 | 4
84 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 28 | 28 | 30 | 30 |  | 40 | Machine problem.
85 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | under maint
86 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
87 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
88 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 11 | 11 | 11 | 40 |  | Gas shortage
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 10 | 35 | 35 | 15 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 2 | 5 | 5 |  | 6 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 28 | 30 | 30 | 30 | 36 |  | Gas shortage
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 61 | 61 | 86 | 86
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 206 | 210 | 210 | 210 |  | 21 | Machine problem
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 11 | 11 | 12 | 12 |  | 13 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 275 | 300 | 300 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 362 | 360 | 366 | 366 |  |  | FGMO
99 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 346 | 346 | 350 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1521 | 1507 | 1598 | 1598 | 111 | 500
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 886 | 888 | 908 | 908
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 30 | 35 |  | 19 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 55 |  | 54 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 217 | 179 | 215 | 215 | 195 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 53 | 70 | 90 | 15 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 100 | 100 | 5
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 85 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 950 | 1122 | 1200 | 1230
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 2155 | 2300 | 2623 | 2633 | 797 | 73
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 7 | 10 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 134 | 130 | 130 |  | 64 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 920 | 1080 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 54 | 96 |  | Fuel shortage
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 200 | 307 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1477 | 1784 | 2038 | 2075 | 96 | 64
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 37 | 30 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 23 | 0 | 24 |  | 47 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
122 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 25 | 46
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 156 | 181 | 180 | 180 | 30 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 400 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 8 | 5 | 8 |  | 3 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52 | 0 |  | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 95 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 55 | 113 | 70 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 95 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1020 | 1114 | 1000 | 1100
135 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 61 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 35 | 0 | 14 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1901 | 2218 | 1981 | 2210 | 641 | 96
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 62 | 62 | 60 | 60 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 200 | 200 |  | 74
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 106 | 34 | 105 |  | 8 | Engine problem
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 95 | 35 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 126 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 506 | 473 | 537 | 480 | 40 | 192
| Total |  |  |  |  | 27791 | 27086 | 13428 | 14784 | 15032.6 | 16474 | 4990 | 3555
A. |  | 2024-09-24 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 14784 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11903 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15050 | MW
3 | Day peak Generation : |  |  | 13428 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14486.59 | MW
4 | Evening peak Generation : |  |  | 14784 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 254 | MW
5 | Total Energy Generation : |  | 321.6004 | MKWHr | By Solar | 3.2322 | MKWHr
| By Gas : | 121.2397 | MKWHr |  | By Oil: | 49.8024 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 95.9942 | MKWHr |  | By Hydro: | 5.1547 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 24.6164 | MKWHr |  | By Wind: | 0.57168 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4990 | MW | Dhaka | 5371.04 | 5276.04 |  | 95 |  | 18:00 |  | 779.28
|  |  | For Plants S/D or M/C prob = |  |  | 3555 | MW | Chittagong | 1334.2 | 1334.2 |  | 0 |  | 19:00 |  | 431.66
|  |  | Total = |  |  | 8545 | MW | Khulna | 1720 | 1720 |  | 0 |  | 19:30 |  | 337.115
7 | Total Gas Supplied : |  | 875.22 | MMCFD | **Import Adani: | Taka | 162714159.43 | Rajshahi | 1438.85 | 1438.85 |  | 0 |  | 20:00 |  | 335.205
8 | Fuel Cost : | i) Gas : | Taka | 364997673.024 | ii) Oil : | Taka | 908682015.68 | Comilla | 1418 | 1393 |  | 25 |  | 21:00 |  | 254.03
|  | iii) Coal : | Taka | 660940348.57 | Total | Taka | 2097334196.704 | Mymensingh | 1239 | 1105 |  | 134 |  | 22:00 |  | 256.895
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 8226.9 | MKWHr. | Sylhet | 597 | 597 |  | 0 |  | 23:00 |  | 252.12
| ii) During Peak Demand : |  |  | 1010 | MW (W to E) at | 21:00 | hrs | Barisal | 449.5 | 449.5 |  | 0 |  | 24:00 |  | 741.08
| iii) Maximum : |  |  | 216 | MW at | 1:00 | hrs | Rangpur | 919 | 919 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.2°C |  |  | Total | 14486.59 | 14232.59 |  | 254
B. |  | 2024-09-25 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 35.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16474 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12500 | MW
4 | Reserve(Generation end) |  |  |  | 2474 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 304.5458 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11447 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.4291 | MKWHr. | ii) HVDC Flow at Peak Time |  | 888 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.56 | MKWHr. | iii) Maximum HVDC Flow : |  | 889 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 107.18 |  | (b) Today: | 107.02 |  | (c) Rule Curve: |  | 104.56
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-09-24 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 240 | 0 | 0 | 0 | 8 | 82 | 13 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 21 | 0 | 12 | 0 | 0 | 131 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 81 | 84 | 0 | 30 | 26 | 0 | 27 | 0 | 0 | 0 | 25 | 0 | 218 | 172 | 50 | 32 | 53 | 0 | 51 | 0 | 36 | 43 | 0 | 0 | 0 | 18 | 68 | 10 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 204 | 0 | 0 | 0 | 280 | 10 | 5 | 0 | 77 | 0 | 0 | 67 | 0 | 114 | 0 | 25 | 103 | 102 | 335 | 36 | 17 | 85 | 0 | 52 | 54 | 110 | 88 | 62 | 24 | 346 | 17 | 0 | 17 | 108 | 0 | 0 | 0 | 54 | 23 | 335 | 17 | 0 | 612 | 18 | 744 | 0 | 0 | 0 | 0 |  | 447 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 35 | 15 | 60 | 0 | 0 | 28 | 8 | 30 | 0 | 0 | 0 | 59 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 35 | 67 | 55 | 0 | 0 | 113 | 1220 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 1242 | 0 | 307 | 1013 | 0 | 0 | 0 | 0 | 0 |  | 7239 | 6207 | 13446 | 3064 | 447 | 1922 | 0 | 1828 | 4384 | 211 | 0 | 491 | 68 | 1013 | 0 | 18 | 242.57 | 107.23
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 234 | 0 | 0 | 0 | 8 | 82 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 3 | 12 | 0 | 0 | 131 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 81 | 34 | 0 | 25 | 26 | 0 | 27 | 0 | 0 | 0 | 25 | 0 | 214 | 177 | 50 | 32 | 53 | 0 | 51 | 0 | 36 | 43 | 0 | 0 | 0 | 18 | 66 | 11 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 205 | 0 | 0 | 0 | 280 | 10 | 5 | 0 | 64 | 0 | 0 | 45 | 0 | 65 | 0 | 25 | 103 | 103 | 335 | 35 | 17 | 85 | 0 | 52 | 54 | 110 | 88 | 60 | 24 | 346 | 17 | 0 | 17 | 108 | 0 | 14 | 0 | 53 | 35 | 335 | 17 | 0 | 612 | 15 | 758 | 0 | 0 | 0 | 0 |  | 447 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 35 | 5 | 0 | 0 | 0 | 28 | 8 | 30 | 0 | 0 | 0 | 62 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 35 | 15 | 56 | 0 | 0 | 113 | 1160 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 1176 | 0 | 260 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 7101 | 5855 | 12956 | 3062 | 447 | 1887 | 0 | 1676 | 4228 | 211 | 0 | 348 | 66 | 1016 | 0 | 15 | 137.52 | 107.22
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 220 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 12 | 12 | 0 | 0 | 131 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 81 | 34 | 0 | 25 | 15 | 0 | 32 | 0 | 0 | 0 | 60 | 0 | 215 | 180 | 70 | 29 | 52 | 0 | 51 | 0 | 36 | 43 | 0 | 0 | 0 | 18 | 64 | 12 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 204 | 0 | 0 | 0 | 285 | 10 | 5 | 0 | 64 | 0 | 0 | 45 | 0 | 33 | 0 | 25 | 103 | 97 | 335 | 35 | 17 | 85 | 0 | 52 | 54 | 97 | 88 | 57 | 12 | 346 | 0 | 0 | 17 | 108 | 0 | 17 | 0 | 55 | 35 | 335 | 17 | 0 | 612 | 20 | 756 | 0 | 0 | 0 | 0 |  | 487 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 63 | 0 | 177 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 53 | 0 | 35 | 15 | 56 | 0 | 0 | 113 | 1060 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 1171 | 0 | 260 | 1017 | 0 | 0 | 0 | 0 | 0 |  | 7042 | 5618 | 12660 | 3114 | 487 | 1845 | 0 | 1587 | 4099 | 211 | 0 | 216 | 64 | 1017 | 0 | 20 | 28.65 | 107.21
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 221 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 25 | 13 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 36 | 0 | 0 | 0 | 55 | 0 | 215 | 158 | 59 | 29 | 52 | 0 | 51 | 0 | 36 | 43 | 0 | 0 | 0 | 18 | 62 | 12 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 207 | 0 | 0 | 0 | 280 | 10 | 5 | 0 | 64 | 0 | 0 | 45 | 0 | 40 | 0 | 25 | 103 | 98 | 353 | 35 | 17 | 85 | 0 | 52 | 54 | 97 | 34 | 58 | 24 | 346 | 0 | 0 | 17 | 108 | 0 | 17 | 0 | 54 | 35 | 335 | 17 | 0 | 612 | 20 | 756 | 0 | 0 | 0 | 0 |  | 560 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 63 | 0 | 178 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 53 | 0 | 35 | 15 | 56 | 0 | 0 | 35 | 1060 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 1174 | 0 | 260 | 1015 | 0 | 0 | 0 | 0 | 0 |  | 6874 | 5599 | 12473 | 3135 | 560 | 1821 | 0 | 1444 | 4103 | 212 | 0 | 101 | 62 | 1015 | 0 | 20 | 25.785 | 107.2
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 221 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 25 | 13 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 38 | 0 | 0 | 0 | 55 | 0 | 214 | 158 | 70 | 33 | 51 | 0 | 51 | 0 | 36 | 43 | 0 | 0 | 0 | 18 | 62 | 12 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 207 | 0 | 0 | 0 | 285 | 10 | 5 | 0 | 64 | 0 | 0 | 45 | 0 | 35 | 0 | 12 | 103 | 0 | 363 | 35 | 17 | 85 | 0 | 52 | 54 | 110 | 34 | 57 | 24 | 346 | 0 | 0 | 17 | 53 | 0 | 17 | 0 | 53 | 35 | 335 | 17 | 0 | 612 | 13 | 754 | 0 | 0 | 0 | 0 |  | 704 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 63 | 0 | 200 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 17 | 0 | 35 | 0 | 56 | 0 | 0 | 35 | 1060 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 1167 | 0 | 260 | 1021 | 0 | 0 | 0 | 0 | 0 |  | 6734 | 5714 | 12448 | 3158 | 704 | 1828 | 0 | 1233 | 4116 | 212 | 0 | 101 | 62 | 1021 | 0 | 13 | 16.235 | 107.19
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 224 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 25 | 13 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 38 | 0 | 0 | 0 | 20 | 0 | 216 | 158 | 70 | 32 | 51 | 0 | 51 | 0 | 36 | 19 | 0 | 0 | 0 | 18 | 56 | 12 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 130 | 0 | 30 | 61 | 0 | 206 | 0 | 0 | 0 | 280 | 10 | 5 | 0 | 64 | 0 | 0 | 45 | 0 | 35 | 1 | 12 | 103 | 0 | 365 | 35 | 17 | 85 | 0 | 52 | 54 | 110 | 34 | 58 | 24 | 346 | 3 | 0 | 17 | 45 | 0 | 17 | 0 | 54 | 35 | 335 | 17 | 0 | 580 | 32 | 757 | 0 | 0 | 0 | 0 |  | 770 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 63 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1020 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 1057 | 0 | 238 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 6626 | 5539 | 12165 | 3129 | 770 | 1749 | 0 | 1184 | 3915 | 212 | 0 | 101 | 56 | 1016 | 1 | 32 | 14.325 | 107.18
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 227 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 21 | 25 | 13 | 8 | 0 | 131 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 33 | 0 | 0 | 0 | 105 | 0 | 214 | 158 | 50 | 31 | 53 | 0 | 51 | 0 | 30 | 17 | 0 | 0 | 0 | 18 | 56 | 5 | 0 | 0 | 0 | 26 | 0 | 11 | 10 | 130 | 0 | 30 | 61 | 0 | 207 | 0 | 0 | 0 | 275 | 11 | 5 | 0 | 64 | 0 | 0 | 45 | 0 | 35 | 4 | 12 | 103 | 0 | 366 | 35 | 17 | 17 | 0 | 30 | 17 | 34 | 34 | 58 | 24 | 346 | 17 | 2 | 17 | 17 | 0 | 17 | 3 | 53 | 35 | 335 | 17 | 0 | 500 | 12 | 757 | 0 | 0 | 17 | 0 |  | 881 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 62 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 960 | 180 | 0 | 0 | 0 | 6 | 36 | 0 | 0 | 974 | 4 | 200 | 1016 | 24 | 0 | 0 | 4 | 0 |  | 6381 | 5522 | 11903 | 3204 | 881 | 1739 | 0 | 972 | 3653 | 211 | 0 | 95 | 56 | 1016 | 64 | 12 | 9.55 | 107.17
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 253 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 21 | 25 | 11 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 212 | 158 | 50 | 30 | 53 | 0 | 51 | 0 | 36 | 17 | 0 | 0 | 0 | 18 | 56 | 5 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 130 | 0 | 30 | 61 | 0 | 208 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 64 | 0 | 0 | 45 | 0 | 35 | 6 | 12 | 103 | 0 | 366 | 35 | 17 | 17 | 2 | 30 | 17 | 34 | 34 | 52 | 24 | 348 | 17 | 4 | 17 | 17 | 0 | 17 | 4 | 53 | 35 | 335 | 17 | 0 | 500 | 28 | 757 | 0 | 0 | 46 | 0 |  | 881 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 63 | 0 | 200 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 900 | 180 | 0 | 0 | 1 | 15 | 36 | 0 | 0 | 903 | 9 | 200 | 1017 | 10 | 0 | 0 | 13 | 0 |  | 6605 | 5368 | 11973 | 3362 | 881 | 1716 | 0 | 965 | 3523 | 212 | 0 | 101 | 56 | 1017 | 112 | 28 | 0 | 107.16
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 265 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 21 | 25 | 11 | 17 | 0 | 131 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 0 | 0 | 0 | 357 | 0 | 212 | 158 | 50 | 32 | 53 | 0 | 43 | 0 | 36 | 17 | 0 | 0 | 0 | 18 | 62 | 4 | 0 | 0 | 1 | 28 | 0 | 11 | 10 | 130 | 0 | 30 | 61 | 0 | 208 | 0 | 0 | 0 | 275 | 11 | 5 | 0 | 64 | 0 | 0 | 62 | 0 | 74 | 10 | 12 | 103 | 2 | 360 | 55 | 35 | 17 | 2 | 30 | 17 | 34 | 34 | 56 | 24 | 346 | 17 | 13 | 17 | 17 | 0 | 17 | 11 | 53 | 35 | 335 | 17 | 0 | 612 | 32 | 758 | 0 | 0 | 44 | 0 |  | 886 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 63 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 50 | 0 | 34 | 0 | 4 | 55 | 880 | 180 | 0 | 0 | 1 | 63 | 35 | 0 | 0 | 912 | 15 | 200 | 1016 | 53 | 0 | 0 | 22 | 5 |  | 6928 | 5495 | 12423 | 3434 | 886 | 1700 | 0 | 1096 | 3625 | 211 | 0 | 117 | 62 | 1016 | 244 | 32 | 121 | 107.15
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 272 | 0 | 0 | 0 | 8 | 64 | 10 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 21 | 25 | 11 | 17 | 0 | 131 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 0 | 0 | 0 | 350 | 0 | 210 | 158 | 50 | 35 | 51 | 0 | 43 | 0 | 36 | 17 | 0 | 0 | 0 | 18 | 60 | 4 | 0 | 0 | 1 | 28 | 0 | 11 | 10 | 130 | 0 | 30 | 61 | 0 | 207 | 0 | 0 | 0 | 285 | 11 | 5 | 0 | 64 | 0 | 0 | 95 | 0 | 95 | 16 | 12 | 103 | 20 | 360 | 74 | 35 | 17 | 3 | 30 | 17 | 34 | 34 | 57 | 24 | 346 | 17 | 20 | 35 | 17 | 0 | 17 | 22 | 53 | 35 | 340 | 36 | 0 | 612 | 16 | 757 | 0 | 0 | 50 | 0 |  | 885 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 62 | 0 | 190 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 55 | 0 | 34 | 0 | 4 | 75 | 880 | 180 | 0 | 0 | 5 | 76 | 35 | 0 | 0 | 907 | 26 | 200 | 1010 | 94 | 0 | 0 | 35 | 18 |  | 7107 | 5590 | 12697 | 3437 | 885 | 1706 | 0 | 1258 | 3608 | 211 | 0 | 136 | 60 | 1010 | 370 | 16 | 194 | 107.14
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 283 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 21 | 25 | 11 | 17 | 0 | 133 | 80 | 0 | 0 | 5 | 220 | 0 | 0 | 0 |  | 0 | 4 | 0 | 0 | 29 | 4 | 0 | 2 | 0 | 0 | 0 | 345 | 0 | 210 | 158 | 40 | 34 | 49 | 0 | 43 | 0 | 36 | 17 | 0 | 0 | 0 | 18 | 68 | 4 | 0 | 0 | 1 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 206 | 0 | 0 | 0 | 285 | 11 | 5 | 0 | 64 | 0 | 0 | 96 | 0 | 107 | 18 | 25 | 103 | 60 | 362 | 73 | 35 | 17 | 5 | 30 | 17 | 34 | 34 | 57 | 24 | 346 | 17 | 39 | 35 | 17 | 0 | 17 | 25 | 51 | 35 | 335 | 36 | 0 | 612 | 34 | 759 | 0 | 0 | 79 | 0 |  | 886 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 62 | 0 | 210 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 55 | 0 | 34 | 0 | 6 | 95 | 880 | 180 | 0 | 0 | 5 | 60 | 35 | 0 | 0 | 905 | 23 | 200 | 1027 | 121 | 0 | 0 | 67 | 35 |  | 7278 | 5741 | 13019 | 3425 | 886 | 1739 | 0 | 1357 | 3628 | 213 | 0 | 158 | 68 | 1027 | 484 | 34 | 211 | 107.13
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 291 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 8 | 35 | 17 | 0 | 15 | 21 | 17 | 11 | 17 | 0 | 133 | 80 | 0 | 0 | 16 | 216 | 0 | 0 | 0 |  | 1 | 0 | 17 | 0 | 31 | 28 | 0 | 4 | 0 | 0 | 0 | 345 | 0 | 208 | 177 | 40 | 32 | 50 | 0 | 43 | 0 | 36 | 17 | 0 | 0 | 0 | 18 | 60 | 4 | 0 | 0 | 2 | 28 | 0 | 11 | 10 | 163 | 0 | 28 | 61 | 0 | 206 | 0 | 0 | 0 | 290 | 11 | 5 | 0 | 64 | 0 | 0 | 125 | 0 | 112 | 20 | 25 | 103 | 65 | 362 | 72 | 35 | 19 | 5 | 50 | 17 | 37 | 17 | 60 | 24 | 346 | 17 | 26 | 35 | 17 | 0 | 0 | 34 | 51 | 35 | 350 | 36 | 0 | 612 | 24 | 757 | 0 | 0 | 59 | 0 |  | 886 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 62 | 0 | 210 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 55 | 0 | 34 | 0 | 3 | 95 | 920 | 220 | 0 | 0 | 5 | 85 | 35 | 0 | 0 | 950 | 36 | 200 | 1020 | 126 | 0 | 0 | 61 | 35 |  | 7389 | 6039 | 13428 | 3460 | 886 | 1900 | 0 | 1470 | 3711 | 213 | 0 | 187 | 60 | 1020 | 497 | 24 | 260 | 107.12
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 20 | 21 | 17 | 11 | 17 | 0 | 134 | 80 | 0 | 0 | 16 | 218 | 0 | 0 | 0 |  | 6 | 3 | 29 | 0 | 31 | 32 | 0 | 7 | 0 | 0 | 0 | 345 | 0 | 210 | 178 | 40 | 30 | 51 | 0 | 43 | 0 | 36 | 17 | 0 | 0 | 0 | 18 | 78 | 4 | 0 | 0 | 2 | 27 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 204 | 0 | 0 | 0 | 285 | 11 | 5 | 0 | 64 | 0 | 0 | 116 | 0 | 96 | 20 | 25 | 103 | 75 | 363 | 72 | 35 | 34 | 4 | 50 | 17 | 68 | 17 | 70 | 24 | 346 | 17 | 31 | 35 | 17 | 0 | 0 | 24 | 51 | 35 | 325 | 36 | 0 | 612 | 26 | 756 | 0 | 0 | 43 | 0 |  | 886 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 62 | 0 | 210 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 57 | 0 | 34 | 0 | 5 | 95 | 950 | 220 | 0 | 0 | 5 | 19 | 35 | 0 | 0 | 953 | 23 | 200 | 1008 | 162 | 0 | 0 | 42 | 45 |  | 6951 | 6044 | 12995 | 3483 | 886 | 1450 | 0 | 1476 | 3743 | 214 | 0 | 206 | 78 | 1008 | 425 | 26 | 768.775 | 107.11
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 0 | 0 | 0 | 0 | 10 | 303 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 20 | 21 | 30 | 11 | 17 | 0 | 134 | 80 | 0 | 0 | 16 | 218 | 0 | 0 | 0 |  | 6 | 42 | 17 | 0 | 31 | 33 | 0 | 3 | 0 | 0 | 0 | 354 | 0 | 210 | 178 | 40 | 30 | 51 | 0 | 43 | 0 | 43 | 17 | 0 | 0 | 0 | 18 | 74 | 4 | 0 | 0 | 1 | 28 | 0 | 10 | 10 | 163 | 0 | 30 | 61 | 0 | 203 | 0 | 0 | 0 | 290 | 11 | 5 | 0 | 75 | 0 | 0 | 125 | 0 | 100 | 13 | 25 | 103 | 78 | 362 | 71 | 35 | 34 | 0 | 50 | 17 | 68 | 17 | 73 | 24 | 346 | 17 | 15 | 35 | 17 | 0 | 0 | 31 | 51 | 35 | 325 | 36 | 0 | 612 | 16 | 758 | 0 | 0 | 64 | 0 |  | 886 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 0 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 0 | 12 | 17 | 22 | 0 | 0 | 2 | 62 | 0 | 210 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 70 | 0 | 34 | 0 | 5 | 95 | 970 | 220 | 0 | 0 | 2 | 33 | 35 | 0 | 0 | 960 | 25 | 200 | 1022 | 169 | 0 | 0 | 37 | 32 |  | 7033 | 6135 | 13168 | 3493 | 886 | 1451 | 0 | 1538 | 3772 | 214 | 0 | 275 | 74 | 1022 | 427 | 16 | 890.06 | 107.13
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 |  | 0 | 0 | 0 | 0 | 0 | 55 | 311 | 0 | 0 | 0 | 17 | 48 | 13 | 0 | 0 | 0 | 17 | 35 | 30 | 0 | 20 | 21 | 30 | 11 | 17 | 0 | 134 | 80 | 0 | 0 | 10 | 216 | 0 | 0 | 0 |  | 6 | 53 | 17 | 0 | 31 | 20 | 0 | 2 | 0 | 0 | 0 | 341 | 0 | 205 | 168 | 40 | 32 | 50 | 0 | 43 | 0 | 41 | 16 | 0 | 0 | 0 | 18 | 84 | 5 | 0 | 0 | 2 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 203 | 0 | 0 | 0 | 290 | 11 | 5 | 0 | 97 | 0 | 0 | 124 | 0 | 96 | 3 | 25 | 98 | 77 | 363 | 71 | 35 | 34 | 1 | 52 | 17 | 74 | 17 | 69 | 24 | 365 | 26 | 16 | 35 | 17 | 0 | 0 | 23 | 51 | 35 | 320 | 17 | 0 | 612 | 49 | 756 | 0 | 0 | 52 | 0 |  | 886 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 0 | 0 | 0 | 0 | 14 | 5 | 50 | 0 | 0 | 19 | 17 | 22 | 0 | 0 | 2 | 62 | 0 | 210 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 70 | 0 | 33 | 0 | 1 | 95 | 990 | 220 | 0 | 0 | 3 | 2 | 35 | 0 | 0 | 960 | 5 | 200 | 1019 | 138 | 0 | 0 | 39 | 28 |  | 7097 | 6073 | 13170 | 3481 | 886 | 1440 | 0 | 1608 | 3790 | 214 | 0 | 286 | 84 | 1019 | 313 | 49 | 1031.4 | 107.09
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 0 |  | 0 | 0 | 0 | 0 | 0 | 55 | 310 | 0 | 0 | 0 | 17 | 48 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 20 | 21 | 30 | 11 | 17 | 0 | 134 | 80 | 0 | 0 | 16 | 218 | 0 | 0 | 0 |  | 6 | 46 | 16 | 0 | 31 | 20 | 0 | 7 | 0 | 0 | 0 | 344 | 0 | 201 | 158 | 45 | 35 | 49 | 0 | 43 | 0 | 41 | 16 | 0 | 0 | 0 | 18 | 76 | 5 | 0 | 0 | 1 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 201 | 0 | 0 | 0 | 285 | 11 | 5 | 0 | 97 | 0 | 0 | 124 | 0 | 102 | 6 | 25 | 20 | 78 | 362 | 71 | 35 | 34 | 0 | 80 | 17 | 75 | 17 | 68 | 24 | 347 | 34 | 14 | 35 | 17 | 0 | 0 | 13 | 51 | 35 | 300 | 17 | 0 | 612 | 43 | 758 | 0 | 0 | 10 | 0 |  | 886 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 0 | 0 | 0 | 0 | 22 | 7 | 50 | 0 | 0 | 19 | 16 | 22 | 0 | 0 | 5 | 62 | 0 | 210 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 70 | 0 | 33 | 0 | 1 | 113 | 990 | 220 | 0 | 0 | 1 | 10 | 35 | 0 | 0 | 964 | 0 | 200 | 1026 | 22 | 0 | 0 | 21 | 10 |  | 6956 | 5959 | 12915 | 3447 | 886 | 1429 | 0 | 1601 | 3796 | 214 | 0 | 288 | 76 | 1026 | 109 | 43 | 1083.925 | 107.08
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 55 | 310 | 0 | 0 | 0 | 17 | 48 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 21 | 30 | 11 | 17 | 0 | 134 | 80 | 0 | 0 | 16 | 217 | 0 | 0 | 0 |  | 8 | 54 | 17 | 0 | 31 | 19 | 0 | 13 | 0 | 0 | 0 | 320 | 0 | 195 | 152 | 50 | 33 | 49 | 0 | 43 | 0 | 35 | 16 | 0 | 0 | 0 | 15 | 72 | 6 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 120 | 0 | 30 | 61 | 0 | 200 | 0 | 0 | 0 | 280 | 11 | 2 | 0 | 97 | 0 | 0 | 124 | 0 | 114 | 3 | 37 | 48 | 80 | 360 | 71 | 35 | 34 | 0 | 85 | 17 | 91 | 72 | 73 | 24 | 316 | 34 | 8 | 35 | 17 | 0 | 0 | 5 | 51 | 35 | 285 | 17 | 0 | 505 | 40 | 757 | 0 | 0 | 6 | 0 |  | 886 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 37 | 8 | 50 | 0 | 0 | 26 | 16 | 22 | 0 | 0 | 5 | 61 | 0 | 210 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 90 | 15 | 66 | 0 | 0 | 113 | 940 | 180 | 0 | 6 | 0 | 4 | 35 | 0 | 0 | 968 | 0 | 192 | 1016 | 6 | 0 | 0 | 1 | 9 |  | 6870 | 5852 | 12722 | 3364 | 886 | 1275 | 0 | 1864 | 3633 | 214 | 0 | 316 | 72 | 1016 | 42 | 40 | 933.99 | 107.08
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 |  | 0 | 0 | 0 | 0 | 0 | 55 | 310 | 0 | 0 | 0 | 42 | 48 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 21 | 30 | 11 | 25 | 0 | 133 | 80 | 0 | 0 | 18 | 218 | 0 | 0 | 0 |  | 18 | 64 | 65 | 0 | 44 | 19 | 0 | 13 | 0 | 0 | 0 | 335 | 0 | 208 | 128 | 50 | 36 | 50 | 0 | 43 | 0 | 41 | 31 | 0 | 0 | 0 | 18 | 66 | 6 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 120 | 0 | 30 | 61 | 0 | 202 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 97 | 0 | 0 | 124 | 0 | 107 | 0 | 37 | 195 | 87 | 362 | 63 | 35 | 34 | 0 | 85 | 17 | 98 | 88 | 92 | 24 | 365 | 34 | 0 | 90 | 17 | 0 | 0 | 0 | 63 | 35 | 270 | 17 | 0 | 550 | 14 | 759 | 0 | 0 | 0 | 0 |  | 889 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 35 | 8 | 0 | 130 | 8 | 16 | 0 | 0 | 0 | 37 | 15 | 89 | 0 | 0 | 35 | 52 | 22 | 0 | 0 | 5 | 60 | 0 | 210 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 23 | 0 | 90 | 15 | 98 | 0 | 0 | 113 | 880 | 220 | 0 | 17 | 0 | 0 | 55 | 0 | 0 | 958 | 0 | 210 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 7266 | 6068 | 13334 | 3385 | 889 | 1358 | 0 | 2290 | 3627 | 213 | 0 | 476 | 66 | 1016 | 0 | 14 | 779.28 | 107.07
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 0 | 10 | 0 | 0 | 55 | 303 | 0 | 0 | 0 | 97 | 120 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 131 | 80 | 0 | 0 | 25 | 218 | 0 | 0 | 0 |  | 18 | 83 | 68 | 0 | 51 | 19 | 0 | 13 | 0 | 0 | 0 | 320 | 0 | 217 | 108 | 50 | 37 | 53 | 0 | 43 | 0 | 35 | 52 | 0 | 0 | 0 | 18 | 54 | 5 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 202 | 0 | 0 | 0 | 275 | 11 | 2 | 0 | 125 | 0 | 0 | 162 | 0 | 106 | 0 | 37 | 200 | 90 | 362 | 89 | 70 | 34 | 0 | 85 | 17 | 110 | 88 | 94 | 24 | 346 | 40 | 0 | 162 | 17 | 0 | 0 | 0 | 80 | 35 | 290 | 90 | 0 | 600 | 17 | 755 | 0 | 0 | 0 | 0 |  | 888 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 46 | 15 | 0 | 100 | 10 | 16 | 0 | 0 | 0 | 37 | 16 | 94 | 0 | 0 | 45 | 52 | 22 | 0 | 0 | 5 | 61 | 0 | 210 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 42 | 0 | 100 | 32 | 105 | 0 | 0 | 113 | 980 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 1106 | 0 | 307 | 1094 | 0 | 0 | 0 | 0 | 0 |  | 7842 | 6506 | 14348 | 3363 | 888 | 1277 | 0 | 2754 | 4019 | 211 | 0 | 671 | 54 | 1094 | 0 | 17 | 431.66 | 107.06
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 0 | 15 | 0 | 0 | 55 | 305 | 0 | 0 | 0 | 97 | 117 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 131 | 80 | 0 | 0 | 25 | 218 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 51 | 0 | 0 | 13 | 0 | 0 | 0 | 330 | 0 | 212 | 108 | 50 | 36 | 53 | 0 | 43 | 0 | 35 | 52 | 0 | 0 | 0 | 18 | 60 | 6 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 209 | 0 | 0 | 0 | 290 | 11 | 2 | 0 | 278 | 0 | 0 | 162 | 0 | 133 | 0 | 37 | 200 | 96 | 362 | 89 | 105 | 17 | 0 | 50 | 17 | 68 | 106 | 94 | 24 | 371 | 44 | 0 | 162 | 17 | 0 | 0 | 0 | 92 | 35 | 325 | 126 | 0 | 570 | 12 | 708 | 0 | 0 | 0 | 0 |  | 889 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 100 | 10 | 16 | 0 | 0 | 0 | 37 | 16 | 94 | 0 | 0 | 45 | 52 | 23 | 0 | 0 | 8 | 61 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 51 | 0 | 113 | 15 | 105 | 0 | 0 | 113 | 1100 | 180 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 1114 | 0 | 307 | 1115 | 0 | 0 | 0 | 0 | 0 |  | 7978 | 6619 | 14597 | 3423 | 889 | 1307 | 0 | 2883 | 4070 | 211 | 0 | 627 | 60 | 1115 | 0 | 12 | 337.115 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 80 | 16 | 0 | 0 | 55 | 303 | 0 | 0 | 0 | 97 | 133 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 131 | 80 | 0 | 0 | 25 | 217 | 0 | 0 | 0 |  | 18 | 41 | 51 | 0 | 51 | 0 | 0 | 15 | 0 | 0 | 0 | 290 | 0 | 213 | 108 | 50 | 37 | 53 | 0 | 43 | 0 | 35 | 52 | 0 | 0 | 0 | 18 | 66 | 7 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 209 | 0 | 0 | 0 | 270 | 11 | 2 | 0 | 270 | 0 | 0 | 162 | 0 | 133 | 0 | 37 | 200 | 95 | 360 | 89 | 105 | 17 | 0 | 50 | 17 | 68 | 106 | 94 | 24 | 346 | 50 | 0 | 162 | 17 | 0 | 0 | 0 | 92 | 35 | 285 | 126 | 0 | 570 | 7 | 705 | 0 | 0 | 0 | 0 |  | 889 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 37 | 17 | 95 | 0 | 0 | 45 | 52 | 23 | 0 | 0 | 8 | 60 | 0 | 210 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 53 | 0 | 113 | 15 | 106 | 0 | 0 | 113 | 1100 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 1113 | 0 | 307 | 1114 | 0 | 0 | 0 | 0 | 0 |  | 7945 | 6704 | 14649 | 3359 | 889 | 1410 | 0 | 2883 | 4065 | 211 | 0 | 645 | 66 | 1114 | 0 | 7 | 335.205 | 107.06
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 180 | 18 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 82 | 133 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 132 | 80 | 0 | 0 | 25 | 217 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 51 | 0 | 0 | 23 | 0 | 0 | 0 | 305 | 0 | 216 | 108 | 50 | 37 | 54 | 0 | 43 | 0 | 35 | 52 | 0 | 0 | 0 | 18 | 70 | 10 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 210 | 0 | 0 | 0 | 275 | 11 | 2 | 0 | 278 | 0 | 0 | 162 | 0 | 132 | 0 | 37 | 195 | 95 | 360 | 89 | 105 | 17 | 0 | 15 | 17 | 34 | 106 | 94 | 24 | 346 | 50 | 0 | 162 | 17 | 0 | 16 | 0 | 92 | 35 | 320 | 72 | 0 | 570 | 17 | 708 | 0 | 0 | 0 | 0 |  | 888 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 37 | 23 | 95 | 0 | 0 | 45 | 52 | 23 | 0 | 0 | 8 | 62 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 15 | 106 | 0 | 0 | 113 | 1080 | 220 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 1122 | 0 | 307 | 1114 | 0 | 0 | 0 | 0 | 0 |  | 8009 | 6775 | 14784 | 3440 | 888 | 1590 | 0 | 2797 | 4059 | 212 | 0 | 597 | 70 | 1114 | 0 | 17 | 254.03 | 107.06
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 300 | 27 | 0 | 0 | 55 | 241 | 0 | 0 | 0 | 89 | 131 | 13 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 15 | 21 | 30 | 11 | 25 | 0 | 133 | 80 | 0 | 0 | 25 | 218 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 51 | 0 | 0 | 26 | 0 | 0 | 0 | 315 | 0 | 213 | 108 | 50 | 33 | 53 | 0 | 43 | 0 | 35 | 52 | 0 | 0 | 0 | 18 | 62 | 11 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 212 | 0 | 0 | 0 | 270 | 11 | 2 | 0 | 183 | 0 | 0 | 162 | 0 | 132 | 0 | 30 | 199 | 95 | 360 | 90 | 105 | 17 | 0 | 15 | 17 | 34 | 106 | 94 | 24 | 346 | 57 | 0 | 108 | 17 | 0 | 17 | 0 | 83 | 35 | 320 | 72 | 0 | 612 | 24 | 712 | 0 | 0 | 0 | 0 |  | 888 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 37 | 23 | 95 | 0 | 0 | 45 | 8 | 23 | 0 | 0 | 8 | 62 | 0 | 210 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 15 | 106 | 0 | 0 | 113 | 1080 | 220 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 1114 | 0 | 307 | 1116 | 0 | 0 | 0 | 0 | 0 |  | 7955 | 6726 | 14681 | 3397 | 888 | 1716 | 0 | 2573 | 4097 | 213 | 0 | 595 | 62 | 1116 | 0 | 24 | 256.895 | 107.06
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 420 | 128 | 0 | 0 | 55 | 233 | 0 | 0 | 0 | 73 | 131 | 13 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 16 | 20 | 30 | 11 | 16 | 0 | 133 | 80 | 0 | 0 | 25 | 223 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 50 | 0 | 0 | 27 | 0 | 0 | 0 | 310 | 0 | 216 | 127 | 70 | 36 | 53 | 0 | 51 | 0 | 36 | 52 | 0 | 0 | 0 | 18 | 66 | 10 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 25 | 61 | 0 | 212 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 117 | 0 | 0 | 162 | 0 | 134 | 0 | 25 | 200 | 95 | 360 | 90 | 88 | 22 | 0 | 30 | 17 | 43 | 106 | 94 | 24 | 346 | 65 | 0 | 54 | 17 | 0 | 17 | 0 | 60 | 35 | 335 | 17 | 0 | 612 | 23 | 709 | 0 | 0 | 0 | 0 |  | 889 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 37 | 18 | 96 | 0 | 0 | 45 | 8 | 23 | 0 | 0 | 8 | 61 | 0 | 210 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 15 | 106 | 0 | 0 | 113 | 1140 | 220 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 1108 | 0 | 307 | 1112 | 0 | 0 | 0 | 0 | 0 |  | 7983 | 6743 | 14726 | 3421 | 889 | 1975 | 0 | 2368 | 4147 | 213 | 0 | 512 | 66 | 1112 | 0 | 23 | 252.12 | 107.05
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 150 | 0 | 0 | 55 | 144 | 0 | 0 | 0 | 66 | 82 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 11 | 8 | 0 | 134 | 80 | 0 | 0 | 25 | 223 | 0 | 0 | 0 |  | 15 | 40 | 51 | 0 | 51 | 0 | 0 | 27 | 0 | 0 | 0 | 290 | 0 | 216 | 165 | 50 | 36 | 53 | 0 | 51 | 0 | 36 | 52 | 0 | 0 | 0 | 18 | 78 | 10 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 212 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 97 | 0 | 0 | 152 | 0 | 132 | 0 | 25 | 97 | 97 | 360 | 90 | 35 | 61 | 0 | 50 | 20 | 80 | 48 | 94 | 24 | 346 | 63 | 0 | 17 | 17 | 0 | 17 | 0 | 54 | 35 | 290 | 17 | 0 | 612 | 27 | 621 | 0 | 0 | 0 | 0 |  | 888 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 36 | 17 | 96 | 0 | 0 | 45 | 8 | 23 | 0 | 0 | 8 | 62 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 55 | 15 | 70 | 0 | 0 | 113 | 1160 | 220 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 1121 | 0 | 307 | 1070 | 0 | 0 | 0 | 0 | 0 |  | 7540 | 6584 | 14124 | 3247 | 888 | 2065 | 0 | 1999 | 4093 | 214 | 0 | 443 | 78 | 1070 | 0 | 27 | 741.08 | 107.05
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9874800 | 0 |  | 0 | 6316000 | 195375 | 0 | 0 | 1239777 | 6345075 | 0 | 0 | 0 | 684432 | 1665120 | 274000 | 0 | 0 | 0 | 394200 | 398448 | 399607 | 0 | 406800 | 491400 | 560520 | 266500 | 310080 | 0 | 3222698 | 1932000 | 0 | 0 | 265928 | 5240128 | 0 | 0 | 0 |  | 159840 | 770736 | 636907 | 0 | 822720 | 275040 | 0 | 440160 | 0 | 0 | 0 | 6179000 | 0 | 5145000 | 3663273 | 1217840 | 783792 | 1237440 | 0 | 1011184 | 0 | 893008 | 758117 | 0 | 0 | 0 | 421320 | 1560000 | 161280 | 0 | 0 | 10950 | 667000 | 0 | 261600 | 336888 | 3609327 | 0 | 708288 | 1473600 | 0 | 5146970 | 0 | 0 | 0 | 6878000 | 266880 | 110544 | 0 | 2406218 | 0 | 0 | 2484000 | 0 | 2164608 | 90585 | 583680 | 2936640 | 1612509 | 8957000 | 1503600 | 1000320 | 1051309 | 22078 | 1201855 | 690933 | 1810727 | 1340640 | 1708560 | 579840 | 8365400 | 616320 | 237340 | 1183680 | 876927 | 0 | 255600 | 191402 | 1432320 | 851760 | 7962700 | 806255 | 0 | 14187271 | 571680 | 18000000 | 0 | 0 | 461464 | 0 |  | 19429090 | 0 | 4799520 | 0 | 0 | 0 | 0 | 0 | 242400 | 15360 | 0 | 2997000 | 207852 | 160512 | 0 | 0 | 0 | 400725 | 166527 | 1015344 | 0 | 0 | 348923 | 386765 | 311168 | 0 | 0 | 79992 | 1405090 | 0 | 4945000 | 0 | 0 | 4248727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9102981 | 755520 | 0 | 1652640 | 281664 | 1427971 | 0 | 35456 | 2161056 | 26460400 | 5102590 | 0 | 133200 | 29280 | 403200 | 1296384 | 0 | 0 | 25105450 | 159544 | 5891000 | 24616363 | 1052640 | 0 | 3432 | 309000 | 225810 |  | 174234813 | 147365576 | 321600389 | 81403476 | 19429090 | 39836270 | 0 | 42529947 | 95994211 | 5154698 | 0 | 7272473 | 1560000 | 24616363 | 3232181 | 571680 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28439424 | 0 |  | 0 | 20084880 | 668182.5 | 0 | 0 | 21844870.74 | 19352478.75 | 0 | 0 | 0 | 12285554.4 | 32336630.4 | 5110100 | 0 | 0 | 0 | 7198092 | 6279540.48 | 7308812.03 | 0 | 305100 | 0 | 0 | 0 | 5553532.8 | 0 | 0 | 0 | 0 | 0 | 5036676.32 | 16716008.32 | 0 | 0 | 0 |  | 2811585.6 | 13572660.96 | 11407004.37 | 0 | 16100630.4 | 4527158.4 | 0 | 0 | 0 | 0 | 0 | 17239410 | 0 | 17081400 | 12271964.55 | 3933623.2 | 2641379.04 | 5419987.2 | 0 | 4054847.84 | 0 | 15993773.28 | 13691593.02 | 0 | 0 | 0 | 315990 | 10233600 | 501580.8 | 0 | 0 | 0 | 2601300 | 0 | 1190280 | 1532840.4 | 12343898.34 | 0 | 3930998.4 | 7692192 | 0 | 14360046.3 | 0 | 0 | 0 | 21253020 | 200160 | 84013.44 | 0 | 49086847.2 | 0 | 0 | 47717640 | 0 | 38118746.88 | 0 | 10395340.8 | 50950704 | 26735399.22 | 23736050 | 28658616 | 18766003.2 | 18860483.46 | 0 | 19650329.25 | 13431737.52 | 32484442.38 | 25619630.4 | 33163149.6 | 10326950.4 | 22251964 | 10520582.4 | 0 | 21649507.2 | 14714835.06 | 0 | 4567572 | 0 | 25810406.4 | 14428814.4 | 23649219 | 11352070.4 | 0 | 98885278.87 | 0 | 106200000 | 0 | 0 | 0 | 0 |  | 54595742.9 | 0 | 14158584 | 0 | 0 | 0 | 0 | 0 | 4559544 | 288921.6 | 0 | 9470520 | 985218.48 | 2767226.88 | 0 | 0 | 0 | 7176984.75 | 3055770.45 | 17067932.64 | 0 | 0 | 6249210.93 | 6845740.5 | 5573018.88 | 0 | 0 | 60553.944 | 15498142.7 | 0 | 41735800 | 0 | 0 | 14020799.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26580704.52 | 12904281.6 | 0 | 32755324.8 | 4979819.52 | 28445182.32 | 0 | 0 | 42875351.04 | 171463392 | 15869054.9 | 0 | 2577420 | 0 | 0 | 22492262.4 | 0 | 0 | 183269785 | 0 | 43887950 | 162714159.43 | 0 | 0 | 0 | 0 | 0 |  | 1207239140.32 | 954924399.284 | 2162163539.604 | 235050602.294 | 54595742.9 | 129947070.73 | 0 | 780048493.02 | 660940348.57 | 0 | 0 | 128633522.66 | 10233600 | 162714159.43 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 291 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 8 | 35 | 17 | 0 | 15 | 21 | 17 | 11 | 17 | 0 | 133 | 80 | 0 | 0 | 16 | 216 | 0 | 0 | 0 |  | 1 | 0 | 17 | 0 | 31 | 28 | 0 | 4 | 0 | 0 | 0 | 345 | 0 | 208 | 177 | 40 | 32 | 50 | 0 | 43 | 0 | 36 | 17 | 0 | 0 | 0 | 18 | 60 | 4 | 0 | 0 | 2 | 28 | 0 | 11 | 10 | 163 | 0 | 28 | 61 | 0 | 206 | 0 | 0 | 0 | 290 | 11 | 5 | 0 | 64 | 0 | 0 | 125 | 0 | 112 | 20 | 25 | 103 | 65 | 362 | 72 | 35 | 19 | 5 | 50 | 17 | 37 | 17 | 60 | 24 | 346 | 17 | 26 | 35 | 17 | 0 | 0 | 34 | 51 | 35 | 350 | 36 | 0 | 612 | 24 | 757 | 0 | 0 | 59 | 0 |  | 886 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 62 | 0 | 210 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 55 | 0 | 34 | 0 | 3 | 95 | 920 | 220 | 0 | 0 | 5 | 85 | 35 | 0 | 0 | 950 | 36 | 200 | 1020 | 126 | 0 | 0 | 61 | 35 |  | 13428 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 180 | 18 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 82 | 133 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 16 | 21 | 30 | 11 | 25 | 0 | 132 | 80 | 0 | 0 | 25 | 217 | 0 | 0 | 0 | 0 | 18 | 40 | 51 | 0 | 51 | 0 | 0 | 23 | 0 | 0 | 0 | 305 | 0 | 216 | 108 | 50 | 37 | 54 | 0 | 43 | 0 | 35 | 52 | 0 | 0 | 0 | 18 | 70 | 10 | 0 | 0 | 0 | 28 | 0 | 11 | 10 | 163 | 0 | 30 | 61 | 0 | 210 | 0 | 0 | 0 | 275 | 11 | 2 | 0 | 278 | 0 | 0 | 162 | 0 | 132 | 0 | 37 | 195 | 95 | 360 | 89 | 105 | 17 | 0 | 15 | 17 | 34 | 106 | 94 | 24 | 346 | 50 | 0 | 162 | 17 | 0 | 16 | 0 | 92 | 35 | 320 | 72 | 0 | 570 | 17 | 708 | 0 | 0 | 0 | 0 |  | 888 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 37 | 23 | 95 | 0 | 0 | 45 | 52 | 23 | 0 | 0 | 8 | 62 | 0 | 210 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 15 | 106 | 0 | 0 | 113 | 1080 | 220 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 1122 | 0 | 307 | 1114 | 0 | 0 | 0 | 0 | 0 |  | 14784 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 132 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 21 | 33 | 18 | 25 | 0 | 134 | 80 | 0 | 0 | 25 | 224 | 0 | 0 | 0 |  | 18 | 65 | 84 | 0 | 50 | 50 | 0 | 20 | 0 | 0 |  | 310 | 0 | 210 | 140 | 50 | 34 | 53 | 0 | 51 | 0 | 35 | 52 | 0 | 0 |  | 18 | 70 | 15 | 0 | 0 | 0 | 30 | 0 | 11 | 35 | 163 | 0 | 30 | 86 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 280 | 0 | 0 | 160 | 0 | 132 | 0 | 37 | 200 | 125 | 366 | 90 | 105 | 105 | 0 | 50 | 54 | 110 | 106 | 113 | 24 | 350 | 53 | 0 | 162 | 108 | 0 | 54 | 0 | 90 | 35 | 330 | 163 | 0 | 612 | 60 | 750 | 0 | 0 |  |  |  | 908 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 24 | 90 | 0 | 0 | 46 | 52 | 30 | 0 | 0 | 8 | 60 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 113 | 100 | 105 | 0 | 0 | 113 | 1244 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 1230 | 0 | 307 | 1100 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 8 | 64 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 16 | 21 | 33 | 18 | 16 | 0 | 134 | 80 | 0 | 0 | 8 | 224 |  | 0 | 0 | 0 | 6 | 65 | 51 | 0 | 38 | 50 | 0 | 7 | 0 | 0 | 0 | 310 | 0 | 210 | 140 | 50 | 34 | 53 | 0 | 51 | 0 | 35 | 16 | 0 | 0 |  | 18 | 60 | 5 | 0 | 0 | 1.6 | 30 | 0 | 11 | 35 | 163 | 0 | 30 | 86 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 80 | 0 | 0 | 125 | 0 | 115 | 20 | 25 | 17 | 125 | 366 | 74 | 34 | 105 | 5 | 50 | 54 | 110 | 34 | 95 | 24 | 350 | 17 | 50 | 35 | 108 | 0 | 17 | 35 | 50 | 35 | 330 | 35 | 0 | 612 | 42 | 750 | 0 | 0 | 70 |  |  | 908 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 30 | 0 | 50 | 0 | 0 | 25 | 52 | 25 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 70 | 0 | 70 | 100 | 34 | 0 | 8 | 95 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 1200 | 30 | 307 | 1000 | 170 | 0 |  | 29 | 14 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 0 | 350 | 151 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 20 | 30 | 11 | 8 | 0 | 131 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 310 | 0 | 215 | 138 | 50 | 30 | 53 | 0 | 51 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 54 | 4 | 0 | 0 | 1 | 28 | 0 | 11 | 10 | 120 | 0 | 33 | 61 | 0 | 211 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 15 | 0 | 0 | 125 | 0 | 35 | 7 | 0 | 17 | 0 | 335 | 74 | 17 | 17 | 2 | 52 | 54 | 51 | 17 | 53 | 0 | 315 | 0 | 12 | 17 | 0 | 0 | 0 | 6 | 51 | 35 | 325 | 0 | 0 | 550 | 33 | 622 | 0 | 0 | 31 | 0 | 0 | 889 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 184 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 180 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 918 | 1 | 200 | 1018 | 21 | 0 | 0 | 6 | 21 | 0 |  |  |  | 121239746 | 19429090 | 0 | 95994211 | 49802420 | 1560000 | 3232181 | 571680 | 5154698 |  |  |  | 296984026
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [6 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 121.2397 | 19.4291 | 0 | 95.9942 | 49.8024 | 1.56 | 3.2322 | 0.57168 | 5.1547
| Minimum Generation |  | 11903 | 7:00
| Highest Generation |  | 14784 | 21:00 | [129 empty] | 0 | [75 empty] | 296.984
| Day Peak Generation |  | 13428 | 12:00
| Evening Peak Generation |  | 14784 | 21:00 | [205 empty] | 202699852
| HVDC Max Flow |  | 889 | 18:00 | [205 empty] | 202.6999
| HVDC EvPeak Flow |  | 888 | 21:00
| Load factor L.F |  | 90.64% | [168 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-09-25
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-09-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13428 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 11447
Evening Peak Generation : |  |  | 14784 | MW Hour : | 21:00 | Available Max Generation : |  | 16474
E.P. Demand (at gen end) : |  |  | 15050 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 14784 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2474
Total Gen. (MKWH) : |  |  | 321.6004 | System Load Factor : | 90.64% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 216 | MW at | 1:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-09-25
Actual : |  | 107.02 | Ft.(MSL) , | Rule curve : | 104.56 | Ft.( MSL )
Gas Consumed : |  | Total = | 875.22 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 364997673.024 | Adani : | 162714159.43
: |  |  | Coal : | 660940348.57 | Oil : | 908682015.68 | Total : | 2097334196.704
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 95 | 2280:00 | 4695.4665 |  |  | 0 | -18.83%
Chittagong Area |  | 0 | 0:00 | 1291.088 |  |  | 0 | -17.09%
Khulna Area |  | 0 | 0:00 | 1808.7915 |  |  | 0 | -16.71%
Rajshahi Area |  | 0 | 0:00 | 1572.379 |  |  | 0 | -16.32%
Cumilla Area |  | 25 | 600:00 | 1293.6804 |  |  | 0 | -16.56%
Mymensingh Area |  | 134 | 3216:00 | 962.2882 |  |  | 0 | -16.22%
Sylhet Area |  | 0 | 0:00 | 539.2681 |  |  | 0 | -16.88%
Barisal Area |  | 0 | 0:00 | 449.5289 |  |  | 0 | -16.16%
Rangpur Area |  | 0 | 0:00 | 879.1971 |  |  | 0 | -16.17%
Total |  | 254 |  | 13491.6877 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
- | 8:48 | Madaripur 132/33kV S/S T3-426T HT is restored.
- | 8:50 | Madaripur 132/33kV S/S T3-426T LT is restored.
- | 9:23 | Chattak-Sylhet 132 kV Ckt-1 is restored.
- | 9:23 | Chattak-Sylhet 132 kV Ckt-1 is restored.
- | 9:26 | Jhenaidah 132/33kV S/S Transformer T-2 HT is restored.
9:32 | 16:00 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Project Work S/D Due to Development work
- | 9:35 | Ghatail 132/33kV S/S T-1 HT is restored.
- | 9:37 | Ghatail 132/33kV S/S T-1 LT is restored.
9:58 | 15:09 | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to Under Frequency relay testing |  |  |  |  | 12.0MW load interrup.
9:58 | 15:11 | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to Under Frequency relay testing |  |  |  |  | 12.0MW load interrup.
10:25 | 11:42 | Khulna(C )-Khulna (S) 132kV Ckt-2 Forced S/D from Khulna (C) end Due to CB to DS loop chang due to Temperature Rise.
- | 10:33 | Chhatak 132/33kV S/S T-1 HT is restored.
- | 10:34 | Chhatak 132/33kV S/S T-1 LT is restored.
12:00 | - | Day Peak Generation = 13,431MW and Loadshed = 260MW
12:10 | 13:26 | Khulna(C )-Noapara 132kV Ckt-2 Forced S/D from Khulna (C) end Due to Temperature reduce and from Noapara 132/33kV end Due to Instructed by ALDC
- | 12:15 | Jamalpur United(20MW)-Sherpur 132kV Ckt-1 is restored.
12:34 | 13:04 | Joypurhat-Naogaon 132kV Ckt-1 Forced S/D from Naogaon 132/33kV end Due to Finger contact (male-female) maintenance of line DS |  |  |  |  | 50.0MW load interrup. Naogaon 132/33kV end
12:37 | - | Meghnaghat 450 MW CCPP (MPL) Tripped
12:37 | - | Meghnaghat 450 MW CCPP tripped. |  |  |  |  | 450MW generation interrup.
- | 13:56 | Aminbazar 400/230/132kV S/S 230 kv Bus 01 is restored.
14:53 | 17:15 | Barishal-Barishal(N) 132 kV Ckt-1 Forced S/D from Barishal 230/132kV end Due to TCS1 Fail and from Barishal 132/33kV end Due to Order by ALDC
17:22 | - | Jamalpur United(20MW)-Sherpur 132kV Ckt-1 Tripped from Sherpur 132/33kV end showing Distance protection, P443. relays Due to Stormy weather.
18:08 | 18:25 | Gopalganj 132/33kV S/S T2 LT Tripped showing Definite O/c + e/f relays Due to Gopalganj reb5&8 feeder fault |  |  |  |  | 53.0MW load interrup.
18:29 | - | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2
18:29 | - | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- None
18:29 | - | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- GT-2 synchronized as per NLDC request.
19:44 | - | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT-2
19:44 | - | Meghnaghat 450 MW CCPP GT-2 was sync.
21:00 | - | peak generation 14784 MW
21:00 | - | Evening peak Generation is 14784 MW
21:24 | - | Meghnaghat 450 MW CCPP (MPL) Synchronized with remarks:- GT1
21:43 | - | Meghnaghat CCPP(Summit) Synchronized with remarks:- ST
21:43 | - | Meghnaghat CCPP(Summit) ST Synchronized with remarks:- None
23:01 | - | Cumilla (North)- BSRM 230kV ckt-1 tripped from Cumilla(N) end showing distance relay.
23:59 | - | BSRM-Cumilla(N) 230 kV Ckt-1 Forced S/D from BSRM 230/33kV end Due to Emergency Shutdown according NLDC 299725
2:22 | - | Siddhirganj 335 MW CCPP Shutdown with remarks:- ST
2:30 | - | Siddhirganj 335 MW CCPP Shutdown with remarks:- GT
4:02 | 4:29 | Chowmuhani-Ramganj 132 kV Ckt-2 Tripped from Chowmuhani 132/33kV end showing Distance Relay A,B,C, 3Phase. Zone-1 relays Due to 132KV Ramgonj Line-2 Tripped by Distance Relay A,B,C, 3Phase. Zone-1
7:00 | - | Minimum Generation: 11702 MW .
7:01 | - | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D Due to Red hot maintenance
7:02 | - | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D Due to Red hot maintenance
7:07 | - | Bhaluka 132/33kV S/S Transformer- 01 LT Forced S/D Due to 33kv bus coupler-2, Y-phase Red hot |  |  |  |  | 60.0MW load interrup.
7:07 | - | Bhaluka 132/33kV S/S Transformer- 01 HT Forced S/D Due to 33kv bus coupler-2, Y-phase Red hot |  |  |  |  | 60.0MW load interrup.
7:08 | - | Bhaluka 132/33kV S/S Capacitor Bank- 01 Forced S/D Due to 33kv bus coupler-2, Y-phase Red hot |  |  |  |  | 60.0MW load interrup.
7:14 | - | Ghatail 132/33kV S/S T-1 LT Forced S/D |  |  |  |  | 30.0MW load interrup.
7:15 | - | Ghatail 132/33kV S/S T-1 HT Forced S/D Due to Red Hot Maintenance work |  |  |  |  | 30.0MW load interrup.
7:17 | - | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D Due to Hasnabad-Shitalakhya line overload
7:26 | - | Bhaluka 132/33kV S/S Bus Section- 01 Forced S/D Due to 33kv bus coupler-2, Y-phase Red hot |  |  |  |  | 60.0MW load interrup.
7:26 | - | Bhaluka 132/33kV S/S Bus Section- 03 Forced S/D Due to 33kv bus coupler-2, Y-phase Red hot |  |  |  |  | 60.0MW load interrup.
7:32 | - | Khulna (S)-Rampal Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to Red hot maintenance work
7:43 | - | Mirzapur 132/33kV S/S Transformer-02(E07) LT Scheduled S/D Due to 33kV outgoing feeder loop out. Shutdown taken by PBS. |  |  |  |  | 25.0MW load interrup.
7:47 | - | Mirzapur 132/33kV S/S Transformer-02(E07) HT Scheduled S/D Due to 33 kV outgoing loop damage .S/D taken by PBS. |  |  |  |  | 25.0MW load interrup.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-09-24
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 410 | 9874800
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 180 | 6316000 | GT2 was sync. at 19:44 hrs.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 18 | 195375 | GT2 was sync. at 18:29 hrs.
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1239777
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 274000 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 290 | 6345075 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 82 | 684432 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 394200
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 1665120 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 398448 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 399607 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 37 | 898200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 560520
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 11 | 266500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 310080 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 2406218 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2164608 | Engine problem
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1000320
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 50 | 616320 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1183680
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 191402
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 851760 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 2170 | 38236442
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 265928
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 90585
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 275040 | Meghnaghat transformer limitation
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 212 | 5154698
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 217 | 5240128
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 1051309 | Meghnaghat transformer limitation
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 770736 | Meghnaghat transformer limitation
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 636907 | Meghnaghat transformer limitation
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 583680 | Meghnaghat transformer limitation
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 440160
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 822720 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22078
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 1201855 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 690933 | Meghnaghat transformer limitation
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 1810727 | Meghnaghat transformer limitation
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 579840 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 876927 | Meghnaghat transformer limitation
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 72 | 806255 | Meghnaghat transformer limitation
60 | SS Power I |  | SS Power | 2*612 | 1224 | 570 | 14187271 | Unit-2 S/D due to coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 60 | 17 | 571680
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 708 | 18000000 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 2147 | 54079457
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 5145000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 6179000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 320 | 7962700 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 783792 | Engine problem
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 54 | 1237440 | Engine problem
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 108 | 3663273 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1011184 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 95 | 1612509 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 893008 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1217840 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 195 | 2936640
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 70 | 1560000
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 758117
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 421320 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1340640 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 94 | 1708560 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 1432320 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 461464
| Cumilla Area Total |  |  |  | 2917 | 1890 | 40324807
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 10 | 161280 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10950
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 162 | 2484000 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 89 | 1503600 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 237340
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 159840 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 16 | 255600 | BPDB Line fault
| Mymensingh Area Total |  |  |  | 646 | 295 | 4812610
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 28 | 667000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3609327
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 11 | 261600 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 336888 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 110544 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 708288 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 61 | 1473600 | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 210 | 5146970
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 11 | 266880 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 6878000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 360 | 8957000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 346 | 8365400 | FGMO
| Sylhet Area Total |  |  |  | 2417 | 1507 | 36781497
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 888 | 19429090
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 43 | 242400
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 15360 | Aminbazar transformer limitation
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 179 | 4799520 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 755520 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 281664 | Aminbazar transformer limitation
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 403200
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 1122 | 25105450 | Aminbazar transformer limitation
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 2300 | 51032204
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 160512 | Meghnaghat transformer limitation
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 207852
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 134 | 2997000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 26460400 | Aminbazar transformer limitation
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5102590
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 133200 | Aminbazar transformer limitation
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 5891000
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 3432
| Barisal Area Total |  |  |  | 2236 | 1784 | 40955986
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 37 | 400725
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 23 | 166527 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 348923 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 181 | 4248727 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9102981
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 311168 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 79992 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 386765
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 1015344 | Fuel shortage
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1652640
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2161056
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29280
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1114 | 24616363
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 309000
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 225810
| Rajshahi Area Total |  |  |  | 3449 | 2218 | 45055301
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 62 | 1405090
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4945000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1427971 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35456
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 95 | 1296384
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 159544
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1052640
| Rangpur Area Total |  |  |  | 950 | 473 | 10322085
| Total |  |  |  | 27086 | 14784 | 321600389
| Eastern Grid Total |  |  |  | 16752 | 8009 | 174234813
| Western Grid Total |  |  |  | 10334 | 6775 | 147365576
| National Grid Total |  |  |  | 27086 | 14784 | 321600389
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-09-24
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9705.24 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4528.3 | MW
i) Dhaka area |  |  | 5276.04 |  | MW | i) Khulna area |  |  |  | 1720 | MW
ii) Chattogram area |  |  | 1334.2 |  | MW | ii) Barishal area |  |  |  | 449.5 | MW
iii) Cumilla area |  |  | 1393 |  | MW | iii) Rajshahi area |  |  |  | 1439.8 | MW
iv) Mymensingh area |  |  | 1105 |  | MW | iv) Rangpur area |  |  |  | 919 | MW
v) Sylhet area |  |  | 597 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14233.54 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 6 | 12:00 | 67 | Jamalpur | 104 | 19:30 | 133 | Rahim | 59 | 05:00
2 | AKSML | 18.4 | 13:00 | 68 | Jashore | 144 | 13:00 | 134 | Rajbari | 90 | 00:00
3 | Aftabnagar | 68 | 15:00 | 69 | Jhenaidah | 139 | 00:00 | 135 | Rajendrapur | 86 | 21:00
4 | Agargaon | 129 | 17:00 | 70 | Joydebpur | 218 | 20:00 | 136 | Rajshahi | 147 | 21:00
5 | Agrabad | 102 | 15:00 | 71 | Joypurhat | 78 | 01:00 | 137 | Rajshahi-230 | 69 | 01:00
6 | Amnura | 67 | 01:00 | 72 | Juldah | 17 | 00:00 | 138 | Ramganj | 120 | 21:00
7 | Ashuganj | 83 | 23:00 | 73 | KSRM | 36 | 11:00 | 139 | Rampur | 42 | 00:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 285 | 11:00 | 140 | Rangamati | 17 | 13:00
9 | BSRM | 134 | 15:00 | 75 | Kachua | 98 | 22:00 | 141 | Rangpur | 157 | 19:00
10 | Bagerhat | 60 | 01:00 | 76 | Kallyanpur | 123 | 00:00 | 142 | Ruppur | 7 | 16:00
11 | Bakulia | 103 | 19:00 | 77 | Kalurghat | 64 | 17:00 | 143 | SSM | 10 | 01:00
12 | Banani | 81 | 13:00 | 78 | Kamrangirchar | 59.32 | 18:30 | 144 | Saidpur | 111 | 08:00
13 | Bangabhaban | 25 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 133 | 01:00
14 | Barapukuria | 71 | 18:30 | 80 | Kazla | 120 | 13:00 | 146 | Satmasjid | 125 | 00:00
15 | Barguna | 22 | 00:00 | 81 | Keranigonj | 78 | 09:00 | 147 | Savar | 220 | 19:00
16 | Barishal | 110 | 22:00 | 82 | Khagrachori | 32 | 21:00 | 148 | SevenRings | 18.87 | 12:00
17 | Barishal-230 | 108 | 19:00 | 83 | Khulna | 76 | 00:00 | 149 | ShahCement | 30 | 12:00
18 | Baroaulia | 75 | 11:00 | 84 | Khulshi | 180 | 14:00 | 150 | Shahjadpur | 97 | 19:30
19 | Baroirhat | 75 | 18:30 | 85 | Kishoreganj | 128 | 22:00 | 151 | Shahjibazar | 135 | 00:00
20 | Bashundhara | 198 | 19:00 | 86 | Kodda | 306 | 21:00 | 152 | Shahmirpur | 62.5 | 01:00
21 | BashundharaCement | 12 | 00:00 | 87 | Kulaura | 58 | 00:00 | 153 | Shariatpur | 88 | 00:00
22 | Beanibazar | 88 | 00:00 | 88 | Kurigram | 67 | 23:00 | 154 | Sherpur | 138 | 00:00
23 | Benapole | 67 | 00:00 | 89 | Kushtia | 160 | 00:00 | 155 | Shikalbaha | 31 | 19:30
24 | Bhaluka | 114 | 21:00 | 90 | Lalbag | 88 | 18:30 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 56 | 00:00 | 91 | Lalmonirhat | 60 | 03:00 | 157 | Shitalakhya | 85.8 | 12:00
26 | Bhangura | 46 | 01:00 | 92 | MI_Cement | 9.1 | 15:00 | 158 | Sholosohor | 46 | 15:00
27 | Bheramara(GK) | 68 | 00:00 | 93 | Madanganj | 38 | 00:00 | 159 | Shyampur | 164 | 12:00
28 | Bhulta | 261 | 07:00 | 94 | Madaripur | 114 | 21:00 | 160 | Siddhirganj | 128 | 14:00
29 | Bog-Sherpur | 62 | 18:00 | 95 | Madartek | 96.9 | 00:00 | 161 | Sirajganj | 124 | 19:30
30 | Bogura | 157 | 18:30 | 96 | Madunaghat | 53 | 15:00 | 162 | Sonargaon | 94 | 00:00
31 | Borhanuddin | 84 | 01:00 | 97 | Magura | 71 | 00:00 | 163 | Sreemongol | 84 | 00:00
32 | Brahmanbaria | 183 | 20:00 | 98 | Mahasthangarh | 74 | 19:00 | 164 | Sreepur | 82 | 21:00
33 | Cantonment | 128 | 15:00 | 99 | Manikganj | 143 | 00:00 | 165 | Srinagar | 48.66 | 00:00
34 | Chandpur | 71 | 20:00 | 100 | Maniknagar | 90 | 13:00 | 166 | Sunamganj | 62 | 01:00
35 | Chandraghona | 39 | 19:00 | 101 | Matarbari | 47 | 19:00 | 167 | Sylhet | 56 | 00:00
36 | Chapai | 72 | 01:00 | 102 | Matuail | 58.5 | 10:00 | 168 | Sylhet-132 | 145 | 18:00
37 | Charsaidpur | 33 | 01:00 | 103 | Millgate | 125 | 10:00 | 169 | TK | 32.7 | 23:00
38 | Chauddagram | 75 | 19:30 | 104 | Mirpur | 157 | 18:30 | 170 | Tangail | 210 | 19:00
39 | Chhatak | 36 | 19:00 | 105 | Mirsorai | 5 | 00:00 | 171 | Thakurgaon | 101 | 00:00
40 | Chowmuhani | 231 | 21:00 | 106 | Mirzapur | 50 | 21:00 | 172 | Tongi | 140 | 15:00
41 | Chuadanga | 111 | 18:30 | 107 | Mithapukur | 64 | 19:00 | 173 | Ullahpara | 36 | 00:00
42 | Coxsbazar | 115 | 14:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 56 | 00:00
43 | Cumilla(N) | 168 | 22:00 | 109 | Mogbazar | 120.4 | 11:00 | 175 | Uttara | 91 | 18:30
44 | Cumilla(S) | 157 | 15:00 | 110 | Mongla | 48 | 23:00 | 176 | UttaraNew | 65 | 00:00
45 | Daudkandi | 152 | 20:00 | 111 | Motijheel | 47 | 13:00 | 177 | Zigatola | 106 | 00:00
46 | Dhaka | 46 | 13:00 | 112 | Munshiganj | 120 | 00:00
47 | Dhamrai | 138 | 07:00 | 113 | Mymensingh | 238 | 14:00
48 | Dhanmondi | 131 | 13:00 | 114 | Naogaon | 137 | 00:00
49 | Dohazari | 100 | 00:00 | 115 | Narail | 65 | 00:00
50 | Faridpur | 173 | 00:00 | 116 | Narinda | 79 | 18:00
51 | Fatullah | 105 | 10:00 | 117 | Narshingdi | 159 | 22:00
52 | Fenchuganj | 49 | 00:00 | 118 | Natore | 156 | 21:00
53 | Feni | 108 | 19:30 | 119 | Nawabganj | 53 | 21:00
54 | GPH | 84 | 12:00 | 120 | Netrakona | 117 | 20:00
55 | Ghatail | 46 | 19:00 | 121 | New | 55 | 12:00
56 | Ghorashal | 50 | 20:00 | 122 | Niamatpur | 80 | 02:00
57 | Goalpara | 42 | 00:00 | 123 | Noapara | 48 | 00:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-09-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 375 | 06:00 | 365 | 12:00 | Kaliakoir | 366 | 01:00 | 350 | 12:00
| Ashuganj | 406 | 22:00 | 384 | 11:00 | Madunaghat | 395 | 08:00 | 387 | 14:00
| Bhulta | 386 | 03:00 | 372 | 12:00 | Meghnaghat | 370 | 04:00 | 360 | 12:00
| Bibiana | 392 | 01:00 | 383 | 12:00 | Payra | 406 | 07:00 | 400 | 00:00
| BIPTC | 406 | 06:00 | 390 | 13:00 | Rahanpur | 401 | 17:00 | 393 | 01:00
| Bogura | 389 | 02:00 | 380 | 01:00 | Rampal | 397 | 17:00 | 387 | 01:00
| Gopalganj | 389 | 07:00 | 380 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 221 | 06:00 | 211 | 12:00 | Haripur | 224 | 00:00 | 213 | 12:00
| AKSML | 238 | 17:00 | 229 | 09:00 | Hasnabad | 221 | 20:00 | 211 | 12:00
| Aminbazar | 221 | 06:00 | 213 | 13:00 | Hathazari | 238 | 17:00 | 233 | 07:00
| Ashuganj | 234 | 15:00 | 222 | 12:00 | Ishurdi | 232 | 00:00 | 223 | 20:00
| Ashuganj-400 | 235 | 10:00 | 224 | 7:00 | Jhenaidah | 225 | 09:00 | 215 | 23:00
| Baghabari | 230 | 02:00 | 223 | 12:00 | Kaliakoir | 225 | 01:00 | 215 | 12:00
| Barapukuria | 220 | 17:00 | 212 | 05:00 | Keranigonj | 220 | 03:00 | 211 | 12:00
| Barapukuria-230 | 222 | 18:30 | 212 | 05:00 | Khulna(S) | 227 | 09:00 | 217 | 23:00
| Barishal | 233 | 17:00 | 226 | 23:00 | Madunaghat | 240 | 00:00 | 233 | 12:00
| Bheramara | 231 | 00:00 | 222 | 18:30 | Maniknagar | 223 | 04:00 | 213 | 12:00
| Bhulta | 225 | 01:00 | 214 | 12:00 | Meghnaghat | 232 | 05:00 | 222 | 15:00
| Bibiana | 223 | 05:00 | 218 | 12:00 | Meghnaghat-400 | 225 | 04:00 | 217 | 12:00
| BIPTC | 230 | 00:00 | 221 | 19:30 | Mirsorai | 234 | 18:30 | 225 | 16:00
| Bogura | 229 | 02:00 | 222 | 12:00 | Rajshahi | 230 | 04:00 | 223 | 18:30
| Bogura-400 | 229 | 00:00 | 223 | 01:00 | Rampal | 226 | 09:00 | 217 | 01:00
| Borhanuddin | 238 | 12:00 | 233 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 233 | 17:00 | 226 | 12:00 | Rampura | 224 | 05:00 | 211 | 12:00
| Cumilla(N) | 224 | 17:00 | 216 | 12:00 | Shikalbaha | 237 | 00:00 | 230 | 14:00
| Faridpur | 229 | 09:00 | 221 | 23:00 | Shyampur | 222 | 04:00 | 213 | 12:00
| Fenchuganj | 225 | 09:00 | 219 | 23:00 | Siddhirganj | 224 | 02:00 | 215 | 12:00
| Ghorashal | 230 | 00:00 | 228 | 04:00 | Sirajgonj | 237 | 00:00 | 231 | 12:00
| Ghorashal-230 | 225 | 00:00 | 214 | 12:00 | Sreepur | 232 | 00:00 | 220 | 16:00
| Gopalganj | 230 | 08:00 | 224 | 00:00 | Tongi | 224 | 03:00 | 213 | 11:00
| GPH | 235 | 00:00 | 230 | 10:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 130 | 03:00 | 119 | 12:00 | Kushtia | 132 | 06:00 | 127 | 18:30
| Agargaon | 129 | 03:00 | 122 | 12:00 | Lalbag | 128 | 03:00 | 121 | 12:00
| Agrabad | 135 | 19:00 | 130 | 10:00 | Lalmonirhat | 132 | 18:00 | 117 | 05:00
| AKS | 133 | 00:00 | 129 | 12:00 | Madanganj | 126 | 21:00 | 119 | 12:00
| Aminbazar | 133 | 19:00 | 123 | 00:00 | Madaripur | 131 | 09:00 | 125 | 22:00
| Amnura | 136 | 00:00 | 123 | 01:00 | Madartek | 130 | 04:00 | 119 | 12:00
| Ashuganj | 140 | 00:00 | 133 | 15:00 | Madunaghat | 136 | 02:00 | 131 | 12:00
| Bagerhat | 135 | 17:00 | 124 | 01:00 | Magura | 133 | 09:00 | 123 | 19:00
| Bakulia | 136 | 19:00 | 131 | 11:00 | Mahasthangarh | 134 | 17:00 | 129 | 01:00
| Banani | 130 | 03:00 | 119 | 12:00 | Manikganj | 125 | 01:00 | 117 | 18:00
| Bangabhaban | 125 | 02:00 | 116 | 12:00 | Maniknagar | 125 | 03:00 | 117 | 12:00
| Barapukuria | 136 | 17:00 | 127 | 05:00 | Matarbari | 126 | 15:00 | 118 | 23:00
| Barguna | 134 | 17:00 | 129 | 00:00 | Matuail | 127 | 00:00 | 120 | 12:00
| Barishal | 130 | 17:00 | 123 | 00:00 | Millgate | 129 | 03:00 | 120 | 12:00
| Barishal-230 | 132 | 17:00 | 126 | 00:00 | Mirpur | 130 | 02:00 | 124 | 12:00
| Baroaulia | 136 | 17:00 | 132 | 15:00 | Mirzapur | 130 | 01:00 | 119 | 18:00
| Baroirhat | 130 | 17:00 | 118 | 04:00 | Mithapukur | 133 | 18:00 | 122 | 08:00
| Bashundhara | 130 | 02:00 | 119 | 12:00 | MI_Cement | 128 | 19:00 | 120 | 12:00
| BashundharaCement | 126 | 00:00 | 119 | 12:00 | Modern | 135 | 00:00 | 131 | 10:00
| Beanibazar | 128 | 04:00 | 118 | 00:00 | Mogbazar | 132 | 05:00 | 120 | 12:00
| Benapole | 132 | 09:00 | 121 | 18:30 | Mongla | 131 | 09:00 | 124 | 23:00
| Bhaluka | 133 | 00:00 | 116 | 16:00 | Motijheel | 125 | 02:00 | 116 | 12:00
| Bhandaria | 130 | 17:00 | 115 | 01:00 | Munshiganj | 127 | 21:00 | 119 | 12:00
| Bhangura | 135 | 07:00 | 130 | 12:00 | Mymensingh | 134 | 10:00 | 113 | 14:00
| Bheramara | 133 | 00:00 | 130 | 15:00 | Naogaon | 134 | 03:00 | 126 | 12:00
| Bheramara(GK) | 134 | 03:00 | 129 | 18:30 | Narail | 132 | 10:00 | 123 | 20:00
| Bhulta | 118 | 00:00 | 110 | 12:00 | Narinda | 125 | 03:00 | 117 | 12:00
| Bog-Sherpur | 138 | 02:00 | 130 | 12:00 | Narshingdi | 122 | 00:00 | 110 | 15:00
| Bogura | 140 | 02:00 | 132 | 12:00 | Natore | 133 | 00:00 | 129 | 01:00
| Bogura-230 | 139 | 02:00 | 132 | 01:00 | Nawabganj | 129 | 05:00 | 122 | 12:00
| Brahmanbaria | 127 | 06:00 | 122 | 22:00 | Netrakona | 134 | 10:00 | 120 | 07:00
| Cantonment | 129 | 03:00 | 121 | 12:00 | New | 129 | 01:00 | 120 | 12:00
| Chandpur | 135 | 17:00 | 120 | 16:00 | Niamatpur | 134 | 06:00 | 131 | 01:00
| Chandraghona | 137 | 17:00 | 133 | 10:00 | Noapara | 133 | 09:00 | 126 | 01:00
| Chapai | 131 | 17:00 | 126 | 01:00 | Pabna | 135 | 07:00 | 128 | 18:30
| Charsaidpur | 126 | 00:00 | 120 | 12:00 | Palashbari | 132 | 02:00 | 121 | 01:00
| Chauddagram | 130 | 17:00 | 119 | 04:00 | Panchagarh | 136 | 17:00 | 113 | 04:00
| Chhatak | 125 | 06:00 | 120 | 00:00 | Patuakhali | 133 | 19:00 | 129 | 00:00
| Chowmuhani | 130 | 17:00 | 113 | 03:00 | Payra | 136 | 17:00 | 132 | 00:00
| Chuadanga | 128 | 09:00 | 114 | 18:30 | PHP | 129 | 17:00 | 118 | 04:00
| Coxsbazar | 125 | 15:00 | 118 | 23:00 | Postogola | 131 | 05:00 | 123 | 12:00
| Cumilla(N) | 131 | 17:00 | 124 | 12:00 | Purbachal | 130 | 03:00 | 119 | 12:00
| Cumilla(S) | 131 | 04:00 | 122 | 12:00 | Purbasadipur | 131 | 17:00 | 114 | 05:00
| Daudkandi | 125 | 17:00 | 118 | 12:00 | Rahanpur | 136 | 17:00 | 132 | 01:00
| Dhaka | 131 | 03:00 | 120 | 12:00 | Rahim | 126 | 00:00 | 120 | 12:00
| Dhamrai | 126 | 00:00 | 120 | 12:00 | Rajbari | 126 | 08:00 | 121 | 00:00
| Dhanmondi | 131.5 | 04:00 | 120 | 12:00 | Rajendrapur | 131 | 00:00 | 117 | 13:00
| Dohazari | 132 | 17:00 | 127 | 14:00 | Rajshahi | 133 | 09:00 | 129 | 18:30
| Faridpur | 129 | 17:00 | 124 | 00:00 | Rajshahi-230 | 134 | 00:00 | 119 | 01:00
| Fatullah | 129 | 06:00 | 122 | 12:00 | Ramganj | 132 | 17:00 | 116 | 03:00
| Fenchuganj | 132 | 06:00 | 129 | 12:00 | Rampur | 135 | 16:00 | 130 | 11:00
| Feni | 128 | 17:00 | 120 | 03:00 | Rampura | 130 | 03:00 | 119 | 12:00
| Ghatail | 131 | 00:00 | 116 | 19:30 | Rangamati | 136 | 17:00 | 132 | 10:00
| Ghorashal | 134 | 00:00 | 127 | 13:00 | Rangpur | 131 | 18:00 | 118 | 07:00
| Goalpara | 134 | 08:00 | 128 | 19:30 | Ruppur | 135 | 07:00 | 131 | 18:00
| Gollamari | 135 | 17:00 | 128 | 01:00 | Saidpur | 132 | 18:00 | 117 | 04:00
| Gopalganj | 132 | 17:00 | 125 | 23:00 | Satkhira | 133 | 17:00 | 121 | 01:00
| Gopalganj-400 | 130 | 08:00 | 126 | 00:00 | Satmasjid | 129 | 04:00 | 121 | 12:00
| Gulshan | 129 | 05:00 | 120 | 12:00 | Savar | 130 | 17:00 | 124 | 23:00
| Halishahar | 136 | 00:00 | 130 | 10:00 | SevenRings | 137 | 00:00 | 128 | 12:00
| Haripur | 126 | 00:00 | 120 | 12:00 | ShahCement | 126 | 00:00 | 120 | 12:00
| HaripurSBU | 126 | 00:00 | 120 | 12:00 | Shahjadpur | 138 | 00:00 | 134 | 12:00
| Hasnabad | 129 | 06:00 | 123 | 12:00 | Shahjibazar | 128 | 07:00 | 123 | 22:00
| Hathazari | 138 | 00:00 | 133 | 10:00 | Shahmirpur | 136 | 00:00 | 131 | 12:00
| Ishurdi | 135 | 00:00 | 131 | 19:30 | Shariatpur | 129 | 08:00 | 123 | 00:00
| Jaldhaka | 131 | 18:00 | 115 | 04:00 | Sherpur | 140 | 01:00 | 121 | 19:30
| Jamalpur | 140 | 01:00 | 126 | 06:00 | Shikalbaha | 127 | 00:00 | 121 | 09:00
| Jashore | 132 | 09:00 | 122 | 18:30 | Shikalbaha-230 | 137 | 17:00 | 131 | 14:00
| Jhenaidah | 134 | 09:00 | 125 | 18:30 | Shitalakhya | 128 | 21:00 | 120 | 12:00
| Jhenaidah-230 | 134 | 09:00 | 126 | 01:00 | Sholosohor | 136 | 00:00 | 131 | 10:00
| Joydebpur | 134 | 00:00 | 120 | 12:00 | Shyampur | 127 | 06:00 | 122 | 12:00
| Joypurhat | 133 | 02:00 | 122 | 01:00 | Shyampur-230 | 128 | 06:00 | 122 | 12:00
| Juldah | 136 | 00:00 | 131 | 10:00 | Siddhirganj | 127 | 21:00 | 120 | 12:00
| Kabirpur | 130 | 18:30 | 119 | 12:00 | Sirajganj | 137 | 02:00 | 128 | 12:00
| Kachua | 132 | 17:00 | 121 | 04:00 | Sonargaon | 125 | 00:00 | 121 | 16:00
| Kaliakoir | 131 | 01:00 | 121 | 12:00 | Sreemongol | 128 | 07:00 | 124 | 21:00
| Kallyanpur | 127 | 03:00 | 122 | 12:00 | Sreepur | 133 | 00:00 | 122 | 16:00
| Kalurghat | 138 | 19:00 | 132 | 10:00 | Srinagar | 131 | 04:00 | 122 | 12:00
| Kamrangirchar | 128 | 05:00 | 120 | 12:00 | SSM | 140 | 00:00 | 136 | 10:00
| Kaptai | 137 | 19:00 | 128 | 2:00 | Sunamganj | 124 | 20:00 | 119 | 01:00
| Kazla | 129 | 06:00 | 115 | 13:00 | Sylhet | 130 | 03:00 | 123 | 00:00
| Keranigonj | 129 | 06:00 | 122 | 12:00 | Sylhet-132 | 126 | 06:00 | 125 | 00:00
| Khagrachori | 135 | 18:30 | 130 | 11:00 | Tangail | 130 | 01:00 | 114 | 19:30
| Khulna | 135 | 09:00 | 127 | 22:00 | Thakurgaon | 136 | 19:00 | 110 | 04:00
| Khulna(S) | 136 | 09:00 | 129 | 01:00 | TK | 136 | 01:00 | 131 | 11:00
| Khulshi | 134 | 00:00 | 129 | 10:00 | Tongi | 131 | 03:00 | 124 | 11:00
| Kishoreganj | 136 | 00:00 | 122 | 15:00 | Ullahpara | 137 | 02:00 | 130 | 12:00
| Kodda | 133 | 00:00 | 116 | 08:00 | Ullon | 131 | 06:00 | 121 | 12:00
| KSRM | 138 | 17:00 | 132 | 10:00 | Uttara | 131 | 04:00 | 124 | 12:00
| Kulaura | 130 | 07:00 | 127 | 00:00 | UttaraNew | 130 | 03:00 | 124 | 12:00
| Kurigram | 130 | 17:00 | 115 | 07:00 | Zigatola | 129 | 07:00 | 123 | 11:00

## L-Curve
Date | 2024-09-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1098 | 7540 | 6584 | 14124 |  |  |  | QF-LDC-11
0:30 | 657 | 7389.5 | 6395.5 | 13785 | Date: | 2024-09-24
1:00 | 216 | 7239 | 6207 | 13446
1:30 | 345 | 7170 | 6031 | 13201
2:00 | 474 | 7101 | 5855 | 12956
2:30 | 467 | 7071.5 | 5736.5 | 12808 | [5 empty] | Gen. at Eve. Peak | 14784 | 14784 MW (21:00 )
3:00 | 460 | 7042 | 5618 | 12660 | [6 empty] | 21:00
3:30 | 484 | 6958 | 5608.5 | 12566.5 | [5 empty] | Gen. at Day Peak | 13428 | 13428 MW (12:00 )
4:00 | 508 | 6874 | 5599 | 12473 | [6 empty] | 12:00
4:30 | 544 | 6804 | 5656.5 | 12460.5 | [5 empty] | Highest Generation | 14784
5:00 | 580 | 6734 | 5714 | 12448 | [6 empty] | 21:00
5:30 | 643 | 6680 | 5626.5 | 12306.5
6:00 | 706 | 6626 | 5539 | 12165
6:30 | 813 | 6503.5 | 5530.5 | 12034
7:00 | 920 | 6381 | 5522 | 11903
7:30 | 940 | 6493 | 5445 | 11938
8:00 | 960 | 6605 | 5368 | 11973
8:30 | 1035 | 6766.5 | 5431.5 | 12198
9:00 | 1110 | 6928 | 5495 | 12423
9:30 | 1127 | 7017.5 | 5542.5 | 12560
10:00 | 1144 | 7107 | 5590 | 12697
10:30 | 1212 | 7192.5 | 5665.5 | 12858
11:00 | 1280 | 7278 | 5741 | 13019
11:30 | 1278 | 7333.5 | 5890 | 13223.5
12:00 | 1276 | 7389 | 6039 | 13428
12:30 | 1293 | 7170 | 6041.5 | 13211.5
13:00 | 1310 | 6951 | 6044 | 12995
13:30 | 1304 | 6992 | 6089.5 | 13081.5
14:00 | 1298 | 7033 | 6135 | 13168
14:30 | 1257 | 7065 | 6104 | 13169
15:00 | 1216 | 7097 | 6073 | 13170
15:30 | 1261 | 7026.5 | 6016 | 13042.5
16:00 | 1306 | 6956 | 5959 | 12915
16:30 | 1305 | 6913 | 5905.5 | 12818.5
17:00 | 1304 | 6870 | 5852 | 12722
17:30 | 1345 | 7068 | 5960 | 13028
18:00 | 1386 | 7266 | 6068 | 13334
18:30 | 1123 | 7554 | 6287 | 13841
19:00 | 860 | 7842 | 6506 | 14348
19:30 | 914 | 7978 | 6619 | 14597
20:00 | 950 | 7945 | 6704 | 14649 |  |  |  | Executive Engineer
20:30 | 980 | 7977 | 6739.5 | 14716.5 |  |  |  | Network Operation Division
21:00 | 1010 | 8009 | 6775 | 14784
21:30 | 1000 | 7982 | 6750.5 | 14732.5
22:00 | 990 | 7955 | 6726 | 14681 |  |  |  |  | Page 6 of 7
22:30 | 1026 | 7969 | 6734.5 | 14703.5
23:00 | 1062 | 7983 | 6743 | 14726
23:30 | 1080 | 7761.5 | 6663.5 | 14425
24:00 | 1098 | 7540 | 6584 | 14124
14784 MW (21:00 )
13428 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-09-24 |  | Energy |  | 321600389
[15 empty] | Date: | 2024-09-24 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3247 | 888 | 2065 | 0 | 1999 | 4093 | 214 | 0 | 443 | 78 | 1070 | 0 | 27 | 741.08
0:30 | 3155.5 | 667.5 | 1993.5 | 0 | 1913.5 | 4238.5 | 212.5 | 0 | 467 | 73 | 1041.5 | 0 | 22.5 | 491.825 |  |  | Date: | 44097
1:00 | 3064 | 447 | 1922 | 0 | 1828 | 4384 | 211 | 0 | 491 | 68 | 1013 | 0 | 18 | 242.57
1:30 | 3063 | 447 | 1904.5 | 0 | 1752 | 4306 | 211 | 0 | 419.5 | 67 | 1014.5 | 0 | 16.5 | 190.045 | [8 empty] | Total Energy | 321.6004 | 321.6004 | Total Energy Gen 321.600 MKWHr Energy Not Served 9.130 MKWHr Energy Requirement 330.731 MKWHr
2:00 | 3062 | 447 | 1887 | 0 | 1676 | 4228 | 211 | 0 | 348 | 66 | 1016 | 0 | 15 | 137.52 | [8 empty] | Energy not Served | 9.1304 | 9.1304
2:30 | 3088 | 467 | 1866 | 0 | 1631.5 | 4163.5 | 211 | 0 | 282 | 65 | 1016.5 | 0 | 17.5 | 83.085 | [8 empty] | Energy Requirement | 330.7308 | 330.7308
3:00 | 3114 | 487 | 1845 | 0 | 1587 | 4099 | 211 | 0 | 216 | 64 | 1017 | 0 | 20 | 28.65
3:30 | 3124.5 | 523.5 | 1833 | 0 | 1515.5 | 4101 | 211.5 | 0 | 158.5 | 63 | 1016 | 0 | 20 | 27.2175 | [7 empty] | Shortage
4:00 | 3135 | 560 | 1821 | 0 | 1444 | 4103 | 212 | 0 | 101 | 62 | 1015 | 0 | 20 | 25.785
4:30 | 3146.5 | 632 | 1824.5 | 0 | 1338.5 | 4109.5 | 212 | 0 | 101 | 62 | 1018 | 0 | 16.5 | 21.01
5:00 | 3158 | 704 | 1828 | 0 | 1233 | 4116 | 212 | 0 | 101 | 62 | 1021 | 0 | 13 | 16.235
5:30 | 3143.5 | 737 | 1788.5 | 0 | 1208.5 | 4015.5 | 212 | 0 | 101 | 59 | 1018.5 | 0.5 | 22.5 | 15.28
6:00 | 3129 | 770 | 1749 | 0 | 1184 | 3915 | 212 | 0 | 101 | 56 | 1016 | 1 | 32 | 14.325
6:30 | 3166.5 | 825.5 | 1744 | 0 | 1078 | 3784 | 211.5 | 0 | 98 | 56 | 1016 | 32.5 | 22 | 11.9375 | [6 empty] | Coal
7:00 | 3204 | 881 | 1739 | 0 | 972 | 3653 | 211 | 0 | 95 | 56 | 1016 | 64 | 12 | 9.55
7:30 | 3283 | 881 | 1727.5 | 0 | 968.5 | 3588 | 211.5 | 0 | 98 | 56 | 1016.5 | 88 | 20 | 4.775 | [5 empty] | Oil
8:00 | 3362 | 881 | 1716 | 0 | 965 | 3523 | 212 | 0 | 101 | 56 | 1017 | 112 | 28 | 0
8:30 | 3398 | 883.5 | 1708 | 0 | 1030.5 | 3574 | 211.5 | 0 | 109 | 59 | 1016.5 | 178 | 30 | 60.5
9:00 | 3434 | 886 | 1700 | 0 | 1096 | 3625 | 211 | 0 | 117 | 62 | 1016 | 244 | 32 | 121
9:30 | 3435.5 | 885.5 | 1703 | 0 | 1177 | 3616.5 | 211 | 0 | 126.5 | 61 | 1013 | 307 | 24 | 157.5
10:00 | 3437 | 885 | 1706 | 0 | 1258 | 3608 | 211 | 0 | 136 | 60 | 1010 | 370 | 16 | 194
10:30 | 3431 | 885.5 | 1722.5 | 0 | 1307.5 | 3618 | 212 | 0 | 147 | 64 | 1018.5 | 427 | 25 | 202.5
11:00 | 3425 | 886 | 1739 | 0 | 1357 | 3628 | 213 | 0 | 158 | 68 | 1027 | 484 | 34 | 211
11:30 | 3442.5 | 886 | 1819.5 | 0 | 1413.5 | 3669.5 | 213 | 0 | 172.5 | 64 | 1023.5 | 490.5 | 29 | 235.5
12:00 | 3460 | 886 | 1900 | 0 | 1470 | 3711 | 213 | 0 | 187 | 60 | 1020 | 497 | 24 | 260
12:30 | 3471.5 | 886 | 1675 | 0 | 1473 | 3727 | 213.5 | 0 | 196.5 | 69 | 1014 | 461 | 25 | 575.03
13:00 | 3483 | 886 | 1450 | 0 | 1476 | 3743 | 214 | 0 | 206 | 78 | 1008 | 425 | 26 | 890.06
13:30 | 3483 | 886 | 1450 | 0 | 1476 | 3743 | 214 | 0 | 206 | 78 | 1008 | 425 | 26 | 890.06
14:00 | 3483 | 886 | 1450 | 0 | 1476 | 3743 | 214 | 0 | 206 | 78 | 1008 | 425 | 26 | 890.06
14:30 | 3482 | 886 | 1445 | 0 | 1542 | 3766.5 | 214 | 0 | 246 | 81 | 1013.5 | 369 | 37.5 | 960.73
15:00 | 3481 | 886 | 1440 | 0 | 1608 | 3790 | 214 | 0 | 286 | 84 | 1019 | 313 | 49 | 1031.4
15:30 | 3464 | 886 | 1434.5 | 0 | 1604.5 | 3793 | 214 | 0 | 287 | 80 | 1022.5 | 211 | 46 | 1057.6625
16:00 | 3447 | 886 | 1429 | 0 | 1601 | 3796 | 214 | 0 | 288 | 76 | 1026 | 109 | 43 | 1083.925
16:30 | 3405.5 | 886 | 1352 | 0 | 1732.5 | 3714.5 | 214 | 0 | 302 | 74 | 1021 | 75.5 | 41.5 | 1008.9575
17:00 | 3364 | 886 | 1275 | 0 | 1864 | 3633 | 214 | 0 | 316 | 72 | 1016 | 42 | 40 | 933.99
17:30 | 3374.5 | 887.5 | 1316.5 | 0 | 2077 | 3630 | 213.5 | 0 | 396 | 69 | 1016 | 21 | 27 | 856.635
18:00 | 3385 | 889 | 1358 | 0 | 2290 | 3627 | 213 | 0 | 476 | 66 | 1016 | 0 | 14 | 779.28
18:30 | 3374 | 888.5 | 1317.5 | 0 | 2522 | 3823 | 212 | 0 | 573.5 | 60 | 1055 | 0 | 15.5 | 605.47
19:00 | 3363 | 888 | 1277 | 0 | 2754 | 4019 | 211 | 0 | 671 | 54 | 1094 | 0 | 17 | 431.66
19:30 | 3423 | 889 | 1307 | 0 | 2883 | 4070 | 211 | 0 | 627 | 60 | 1115 | 0 | 12 | 383.4325
20:00 | 3359 | 889 | 1410 | 0 | 2883 | 4065 | 211 | 0 | 645 | 66 | 1114 | 0 | 7 | 335.205
20:30 | 3399.5 | 888.5 | 1500 | 0 | 2840 | 4062 | 211.5 | 0 | 621 | 68 | 1114 | 0 | 12 | 294.6175
21:00 | 3440 | 888 | 1590 | 0 | 2797 | 4059 | 212 | 0 | 597 | 70 | 1114 | 0 | 17 | 254.03
21:30 | 3418.5 | 888 | 1653 | 0 | 2685 | 4078 | 212.5 | 0 | 596 | 66 | 1115 | 0 | 20.5 | 255.4625
22:00 | 3397 | 888 | 1716 | 0 | 2573 | 4097 | 213 | 0 | 595 | 62 | 1116 | 0 | 24 | 256.895
22:30 | 3409 | 888.5 | 1845.5 | 0 | 2470.5 | 4122 | 213 | 0 | 553.5 | 64 | 1114 | 0 | 23.5 | 254.5075
23:00 | 3421 | 889 | 1975 | 0 | 2368 | 4147 | 213 | 0 | 512 | 66 | 1112 | 0 | 23 | 252.12
23:30 | 3334 | 888.5 | 2020 | 0 | 2183.5 | 4120 | 213.5 | 0 | 477.5 | 72 | 1091 | 0 | 25 | 496.6 |  |  | Max Temp. in Dhaka |  | 35.2°C
24:00 | 3247 | 888 | 2065 | 0 | 1999 | 4093 | 214 | 0 | 443 | 78 | 1070 | 0 | 27 | 741.08
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 321.600 MKWHr Energy Not Served 9.130 MKWHr Energy Requirement 330.731 MKWHr
Note on X13: Author:

## Generation
2024-09-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 131 | 131 | 131 | 132 | 132 | 132 | 131 | 132 | 131 | 131 | 133 | 133 | 134 | 134 | 134 | 134 | 134 | 133 |  | 131 | 131 | 131 | 132 | 133 | 133 | 134 | 3222698
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1932000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 5 | 16 | 16 | 16 | 10 | 16 | 16 | 18 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 265928
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 6 | 10 | 16 | 18 | 20 | 20 | 13 | 3 | 6 | 3 | [9 empty] | 90585
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 224 | 226 | 226 | 226 | 226 | 227 | 224 | 223 | 222 | 220 | 216 | 218 | 218 | 216 | 218 | 217 | 218 |  | 218 | 218 | 217 | 217 | 218 | 223 | 223 | 5240128
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 84 | 34 | 34 | 0 | [7 empty] | 17 | 29 | 17 | 17 | 16 | 17 | 65 |  | 68 | 51 | 51 | 51 | 51 | 51 | 51 | 636907
12 | Hathazari 100 MW peaking PP | 81 | 81 | 81 | 0 | [6 empty] | 4 |  | 3 | 42 | 53 | 46 | 54 | 64 |  | 83 | 40 | 41 | 40 | 40 | 40 | 40 | 770736
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 85 | 85 | 85 | 85 | 85 | 85 | 17 | 17 | 17 | 17 | 17 | 19 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 17 | 17 | 17 | 17 | 22 | 61 | 1051309
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 36 | 36 | 36 | 36 | 36 | 36 | 30 | 36 | 36 | 36 | 36 | 36 | 36 | 43 | 41 | 41 | 35 | 41 |  | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 893008
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 240 | 234 | 220 | 221 | 221 | 224 | 227 | 253 | 265 | 272 | 283 | 291 | 304 | 303 | 311 | 310 | 310 | 310 |  | 303 | 305 | 303 | 290 | 241 | 233 | 144 | 6345075
18 | Kodda 300 MW PP Unit-2 (Summit) | 77 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 75 | 97 | 97 | 97 | 97 |  | 125 | 278 | 270 | 278 | 183 | 117 | 97 | 2406218
19 | Ashuganj 195 MW PP (APSCL-United) | 172 | 177 | 180 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 177 | 178 | 178 | 168 | 158 | 152 | 128 |  | 108 | 108 | 108 | 108 | 108 | 127 | 165 | 3663273
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 612 | 612 | 612 | 612 | 580 | 500 | 500 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 505 | 550 |  | 600 | 570 | 570 | 570 | 612 | 612 | 612 | 14187271
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 32 | 32 | 29 | 29 | 33 | 32 | 31 | 30 | 32 | 35 | 34 | 32 | 30 | 30 | 32 | 35 | 33 | 36 |  | 37 | 36 | 37 | 37 | 33 | 36 | 36 | 783792
33 | Ashuganj 225 MW CCPP | 218 | 214 | 215 | 215 | 214 | 216 | 214 | 212 | 212 | 210 | 210 | 208 | 210 | 210 | 205 | 201 | 195 | 208 |  | 217 | 212 | 213 | 216 | 213 | 216 | 216 | 5145000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 25 | 25 | 60 | 55 | 55 | 20 | 105 | 275 | 357 | 350 | 345 | 345 | 345 | 354 | 341 | 344 | 320 | 335 |  | 320 | 330 | 290 | 305 | 315 | 310 | 290 | 6179000
| Ashuganj 420 MW CCPP(East) | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 340 | 335 | 350 | 325 | 325 | 320 | 300 | 285 | 270 |  | 290 | 325 | 285 | 320 | 320 | 335 | 290 | 7962700
35 | Ashuganj 55 MW PP (Precision) | 53 | 53 | 52 | 52 | 51 | 51 | 53 | 53 | 53 | 51 | 49 | 50 | 51 | 51 | 50 | 49 | 49 | 50 |  | 53 | 53 | 53 | 54 | 53 | 53 | 53 | 1237440
36 | Chandpur 150 MW CCPP | 50 | 50 | 70 | 59 | 70 | 70 | 50 | 50 | 50 | 50 | 40 | 40 | 40 | 40 | 40 | 45 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 70 | 50 | 1217840
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 403 | 407 | 408 | 408 | 407 | 408 | 407 | 408 | 408 | 407 | 407 | 401 | 401 | 401 | 395 | 395 | 400 | 368 |  | 401 | 404 | 403 | 410 | 409 | 409 | 407 | 9874800
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | [9 empty] | 80 | 180 | 300 | 420 | 450 | 6316000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 10 | 11 | 12 | 12 | 12 | 12 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 6 | 6 |  | 5 | 6 | 7 | 10 | 11 | 10 | 10 | 161280
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 2 | 4 | 13 | 20 | 39 | 26 | 31 | 15 | 16 | 14 | 8 | [9 empty] | 237340
44 | Fenchugonj CCPP Phase-1 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 28 | 28 | 28 | 28 | 28 | 27 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 667000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 25 | 30 | 708288
48 | Shahjibazar 86 MW PP (Shahjibazar) | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 |  | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1473600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 204 | 205 | 204 | 207 | 207 | 206 | 207 | 208 | 208 | 207 | 206 | 206 | 204 | 203 | 203 | 201 | 200 | 202 |  | 202 | 209 | 209 | 210 | 212 | 212 | 212 | 5146970
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 110544
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 261600
56 | Shahjahanulla 25 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 |  | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 266880
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 285 | 280 | 285 | 280 | 275 | 285 | 275 | 285 | 285 | 290 | 285 | 290 | 290 | 285 | 280 | 280 |  | 275 | 290 | 270 | 275 | 270 | 280 | 280 | 6878000
| Bibiyana South 400 MW | 346 | 346 | 346 | 346 | 346 | 346 | 346 | 348 | 346 | 346 | 346 | 346 | 346 | 346 | 365 | 347 | 316 | 365 |  | 346 | 371 | 346 | 346 | 346 | 346 | 346 | 8365400
58 | Nababganj 55 MW PP (Southern power ) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 30 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 399607
59 | Tangail Palli Power Gen 22 MW | [11 empty] | 1 | 6 | 6 | 6 | 6 | 8 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 159840
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 68 | 66 | 64 | 62 | 62 | 56 | 56 | 56 | 62 | 60 | 68 | 60 | 78 | 74 | 84 | 76 | 72 | 66 |  | 54 | 60 | 66 | 70 | 62 | 66 | 78 | 1560000
64 | Malancha, Ctg. EPZ (United) | 27 | 27 | 32 | 36 | 38 | 38 | 33 | 0 | 2 | 2 | 2 | 4 | 7 | 3 | 2 | 7 | 13 | 13 |  | 13 | 13 | 15 | 23 | 26 | 27 | 27 | 440160
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 421320
69 | Summit Ashulia | 17 | 17 | 17 | 17 | 17 | 18 | 16 | 16 | 16 | 16 | 15 | 15 | 20 | 20 | 20 | 20 | 20 | 20 |  | 16 | 16 | 16 | 16 | 15 | 16 | 16 | 406800
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 491400
71 | Maona 33 MW PP(Summit) | 0 | 3 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 560520
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 13 | 13 | 13 | 13 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 266500
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 88 | 88 | 88 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 72 | 88 |  | 88 | 106 | 106 | 106 | 106 | 106 | 48 | 1340640
| Chowmuhani 113 MW | 62 | 60 | 57 | 58 | 57 | 58 | 58 | 52 | 56 | 57 | 57 | 60 | 70 | 73 | 69 | 68 | 73 | 92 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1708560
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 90 |  | 162 | 162 | 162 | 162 | 108 | 54 | 17 | 1183680
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 |  | 25 | 25 | 25 | 25 | 25 | 16 | 8 | 310080
79 | Kodda 150 MW PP | 82 | 82 | 48 | 48 | 48 | 48 | 48 | 48 | 64 | 64 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 120 | 117 | 133 | 133 | 131 | 131 | 82 | 1665120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 31 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 758117
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 70 | 105 | 105 | 105 | 105 | 88 | 35 | 1000320
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 2 | 2 | 3 | 5 | 5 | 4 | 0 | 1 | 0 | [10 empty] | 22078
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 690933
| Karnaphuli Power Ltd. | 110 | 110 | 97 | 97 | 110 | 110 | 34 | 34 | 34 | 34 | 34 | 37 | 68 | 68 | 74 | 75 | 91 | 98 |  | 110 | 68 | 68 | 34 | 34 | 43 | 80 | 1810727
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 10 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 274000
86 | Meghnaghat CCPP ( Summit) | [19 empty] | 10 | 15 | 16 | 18 | 27 | 128 | 150 | 195375
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 0 |  | 0 | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 34 | 34 | 34 |  | 40 | 44 | 50 | 50 | 57 | 65 | 63 | 616320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 336888
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 51 | 51 | 1011184
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 17 | 17 | 42 |  | 97 | 97 | 97 | 82 | 89 | 73 | 66 | 684432
95 | Patenga 50MW PP (Baraka) | 26 | 26 | 15 | 0 | [6 empty] | 4 | 28 | 32 | 33 | 20 | 20 | 19 | 19 |  | 19 | [5 empty] | 0 | 275040
96 | Chattogram 108 MW PP (ECPV) | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 25 | 25 | 29 | 31 | 31 | 31 | 31 | 31 | 31 | 44 |  | 51 | 51 | 51 | 51 | 51 | 50 | 51 | 822720
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 10 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1239777
100 | Manikganj 55 MW PP (Northern) | 35 | 0 | [9 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 |  |  | 0 | 398448
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 120 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3609327
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 1 | 0 | [9 empty] | 10950
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 8 | 17 | 17 | 17 | 17 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 |  | 0 | 394200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 67 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 62 | 95 | 96 | 125 | 116 | 125 | 124 | 124 | 124 | 124 |  | 162 | 162 | 162 | 162 | 162 | 162 | 152 | 2484000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 114 | 65 | 33 | 40 | 35 | 35 | 35 | 35 | 74 | 95 | 107 | 112 | 96 | 100 | 96 | 102 | 114 | 107 |  | 106 | 133 | 133 | 132 | 132 | 134 | 132 | 2164608
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 37 | 37 |  | 37 | 37 | 37 | 37 | 30 | 25 | 25 | 583680
116 | Chandpur 200 MW (Desh energy) | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 98 | 20 | 48 | 195 |  | 200 | 200 | 200 | 195 | 199 | 200 | 97 | 2936640
117 | Ashuganj 150 MW PP (Midland) | 102 | 103 | 97 | 98 | 0 |  |  |  | 2 | 20 | 60 | 65 | 75 | 78 | 77 | 78 | 80 | 87 |  | 90 | 96 | 95 | 95 | 95 | 95 | 97 | 1612509
118 | Bibiyana-III 400 MW CCPP | 335 | 335 | 335 | 353 | 363 | 365 | 366 | 366 | 360 | 360 | 362 | 362 | 363 | 362 | 363 | 362 | 360 | 362 |  | 362 | 362 | 360 | 360 | 360 | 360 | 360 | 8957000
| Jamalpur 115 MW PP (United) | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 74 | 73 | 72 | 72 | 71 | 71 | 71 | 71 | 63 |  | 89 | 89 | 89 | 89 | 90 | 90 | 90 | 1503600
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 30 | 30 | 30 | 30 | 30 | 50 | 50 | 50 | 52 | 80 | 85 | 85 |  | 85 | 50 | 50 | 15 | 15 | 30 | 50 | 1201855
| Juldah unit-2 (Acorn) | 24 | 24 | 12 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 579840
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 53 | 45 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 876927
| Bhairob 54.5 MW | 0 | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 16 | 17 | 17 | 17 | 255600
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 4 | 11 | 22 | 25 | 34 | 24 | 31 | 23 | 13 | 5 | [9 empty] | 191402
| Chandpur 115(Doreen) | 54 | 53 | 55 | 54 | 53 | 54 | 53 | 53 | 53 | 53 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 63 |  | 80 | 92 | 92 | 92 | 83 | 60 | 54 | 1432320
| Kanchan Purbachal Power Generation Ltd. | 23 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 851760
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 |  | 90 | 126 | 126 | 72 | 72 | 17 | 17 | 806255
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 18 | 15 | 20 | 20 | 13 | 32 | 12 | 28 | 32 | 16 | 34 | 24 | 26 | 16 | 49 | 43 | 40 | 14 |  | 17 | 12 | 7 | 17 | 24 | 23 | 27 | 571680
| Sonagazi 75 MW Solar Plant | [5 empty] | 0 | 17 | 46 | 44 | 50 | 79 | 59 | 43 | 64 | 52 | 10 | 6 | [9 empty] | 461464
| Matarbari 2*600 MW (CPGCL) | 744 | 758 | 756 | 756 | 754 | 757 | 757 | 757 | 758 | 757 | 759 | 757 | 756 | 758 | 756 | 758 | 757 | 759 |  | 755 | 708 | 705 | 708 | 712 | 709 | 621 | 18000000
Meghnaghat (Reliance) 718MW CCPP
120
121 | Eastern Zone Total | 7239 | 7101 | 7042 | 6874 | 6734 | 6626 | 6381 | 6605 | 6928 | 7107 | 7278 | 7389 | 6951 | 7033 | 7097 | 6956 | 6870 | 7266 |  | 7842 | 7978 | 7945 | 8009 | 7955 | 7983 | 7540 | 174234813
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2) | [26 empty] | 0
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | 23 | 0 | [15 empty] | 35 |  | 46 | 43 | 42 | 43 | 43 | 18 | 0 | 242400
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | 53 | 53 | 53 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 |  | 42 | 51 | 53 | 53 | 53 | 53 | 53 | 755520
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 6 | 15 | 63 | 76 | 60 | 85 | 19 | 33 | 2 | 10 | 4 | [9 empty] | 403200
132 | Rampal 1320 MW (BIFPCL) | 1242 | 1176 | 1171 | 1174 | 1167 | 1057 | 974 | 903 | 912 | 907 | 905 | 950 | 953 | 960 | 960 | 964 | 968 | 958 |  | 1106 | 1114 | 1113 | 1122 | 1114 | 1108 | 1121 | 25105450
133 | United Payra Power Ltd. | [16 empty] | 6 | 17 |  | 35 | 17 | 17 | 17 | 17 | 17 | 0 | 133200
| Bhola Nutan Biddut BD LTD (GAS) | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 180 | 220 |  | 220 | 180 | 220 | 220 | 220 | 220 | 220 | 5102590
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 0 | [12 empty] | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 160512
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 260 | 260 | 260 | 260 | 238 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 192 | 210 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 5891000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3432
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 100 | 100 | 134 | 134 | 134 | 134 | 134 | 2997000
141 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 9 | 10 | 9 | 7 | 7 | 7 | 5 | 7 | 7 | 7 | 8 | 8 | 8 | 6 | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 207852
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP | [16 empty] | 2 | 8 |  | 15 | [6 empty] | 15360
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP | 67 | 15 | 15 | 15 | 0 | [11 empty] | 15 | 15 |  | 32 | 15 | 15 | 15 | 15 | 15 | 15 | 281664
147 | Bheramara HVDC | 447 | 447 | 487 | 560 | 704 | 770 | 881 | 881 | 886 | 885 | 886 | 886 | 886 | 886 | 886 | 886 | 886 | 889 |  | 888 | 889 | 889 | 888 | 888 | 889 | 888 | 19429090
148 | Bheramara 410 MW CCPP | 186 | 186 | 187 | 187 | 187 | 187 | 205 | 217 | 217 | 217 | 217 | 217 | 209 | 206 | 194 | 190 | 186 | 185 |  | 180 | 180 | 180 | 179 | 179 | 175 | 173 | 4799520
149 | Payra 1320 MW | 1220 | 1160 | 1060 | 1060 | 1060 | 1020 | 960 | 900 | 880 | 880 | 880 | 920 | 950 | 970 | 990 | 990 | 940 | 880 |  | 980 | 1100 | 1100 | 1080 | 1080 | 1140 | 1160 | 26460400
150
151 | Barapukuria TPP Unit-1 | 59 | 62 | 63 | 63 | 63 | 63 | 62 | 63 | 63 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 60 |  | 61 | 61 | 60 | 62 | 62 | 61 | 62 | 1405090
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 177 | 178 | 200 | 200 | 200 | 200 | 200 | 190 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 4945000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 35 | 35 | 0 | [11 empty] | 14 | 22 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 400725
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 1 | 5 | 5 | 5 | 5 | 2 | 3 | 1 | 0 | [9 empty] | 29280
157 | Sirajganj 68 MW Solar Park | [6 empty] | 4 | 13 | 22 | 35 | 67 | 61 | 42 | 37 | 39 | 21 | 1 | [9 empty] | 309000
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 181 | 180 | 180 | 181 | 181 | 180 | 180 | 165 | 150 | 150 | 150 | 156 | 192 | 185 | 185 | 185 | 183 | 163 |  | 160 | 140 | 150 | 181 | 182 | 182 | 181 | 4248727
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 360 | 360 | 360 | 320 | 320 | 320 | 320 | 320 | 320 | 414 | 414 | 414 | 414 | 414 | 350 | 414 |  | 300 | 350 | 350 | 414 | 414 | 414 | 414 | 9102981
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | 15 | 5 | 0 | [9 empty] | 4 | 5 | 5 | 7 | 8 | 15 |  | 16 | 16 | 17 | 23 | 23 | 18 | 17 | 166527
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | [8 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 |  | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 79992
166 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | 28 | 28 | 0 | [10 empty] | 12 | 19 | 19 | 26 | 35 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 348923
169 | Santahar 50 MW Peaking PP | 30 | 30 | 0 | [10 empty] | 22 | 22 | 22 | 22 | 22 |  | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 311168
170 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 17 | 16 | 16 | 52 |  | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 386765
171 | Chapainawabganj 100 MW Peaking PP | 60 | 0 | [8 empty] | 34 | 50 | 50 | 50 | 50 | 50 | 50 | 89 |  | 94 | 94 | 95 | 95 | 95 | 96 | 96 | 1015344
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 55 | 55 | 55 | 57 | 70 | 70 | 70 | 90 | 90 |  | 100 | 113 | 113 | 113 | 113 | 113 | 55 | 1652640
173 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 35 | 55 | 75 | 95 | 95 | 95 | 95 | 95 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2161056
175 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
176 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | Rangpur 113 MW PP (Confidence) | 55 | 56 | 56 | 56 | 56 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 66 | 98 |  | 105 | 105 | 106 | 106 | 106 | 106 | 70 | 1427971
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 2 | 4 | 4 | 6 | 3 | 5 | 5 | 1 | 1 | 0 | 0 | [8 empty] | 35456
| Energypac Power Venture Thakurgaon Ltd. | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 115 | 115 | 115 | 95 | 95 | 95 | 95 | 1296384
| Intraco Solar 30 MW | [5 empty] | 0 | 4 | 9 | 15 | 26 | 23 | 36 | 23 | 25 | 5 | 0 | 0 | [9 empty] | 159544
178 | Adani Power Jharkhanda Ltd | 1013 | 1016 | 1017 | 1015 | 1021 | 1016 | 1016 | 1017 | 1016 | 1010 | 1027 | 1020 | 1008 | 1022 | 1019 | 1026 | 1016 | 1016 |  | 1094 | 1115 | 1114 | 1114 | 1116 | 1112 | 1070 | 24616363
| Teesta Solar Limited | [6 empty] | 24 | 10 | 53 | 94 | 121 | 126 | 162 | 169 | 138 | 22 | 6 | [9 empty] | 1052640