## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-09-27 | Friday
|  | Date (day): | 2024-09-27 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14707.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16228 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-09-26 | 2024-09-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 412 | 350 | 400 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 295 | 285 | 300 | 300 | 35 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 13 | 13 | 62 |  | Fuel shortage
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint |  | 2024-09-27
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 66 | 16 | 98
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 98 | 64 | 132 |  | 17 | Engine problem
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 30 | 29 | 37 | 40 |  | 40 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 30 | 30 | 30
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 10 | 10 | 18 | 18 |  | 15 | Engine problem
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 17 | 25 | 16 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 42 | 95 | 80 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 80 | 115 | 115 | 132 |  | 17 | Engine problem
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 70 | 34 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 25 | 50 | 17 | 60 | 44 |  | Lub Oil problem
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 108 | 35 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 7 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 35 | 35 |  | 20 | Engine problem.
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1532 | 1887 | 1837 | 2499 | 2128 | 1224
35 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
36 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 8 | 25
37 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 7 | 0 | 20 | 0
38 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 50 | 50
39 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 212 | 214 | 214 | 214
40 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 225 | 225 | 225
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
42 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 34 | 105 | 105
43 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 65 | 65 | 33 |  | Fuel shortage
44 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 51 | 84 |  | 18 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
45 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 4 | 37 | 25 | 37 | 63 |  | fuel shortage.
46 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 23 | 15 | 30
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 43 | 38 | 50 | 58 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 50 | 50 | 50 | 250 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 20 | 68 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 24 | 24 | 24 |  |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 108 | 108
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 35 | 35 | 163
55 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 550 | 609 | 612 | 612 |  | 612 | Unit-2 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 8 | 0 | 42 | 60 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 619 | 318 | 750 | 750 |  |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1726 | 1802 | 2606 | 2816 | 584 | 960
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 216 | 217 | 210 | 210
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 285 | 330 | 330 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 320 | 295 | 350 | 350 | 50 |  | FGMO
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 34 | 43 | 43 | 43 | 2 |  | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 50 | 55 | 53 | 53
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 35 | 140 | 140 | 55 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 40 | 125 | 125 |  | 25 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 28 | 35 | 35 |  | 17 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 30 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 170 | 17 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 48 | 50 | 60 | 70
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 16 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 34 | 106 |  | 8 | Engine problem
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 53 | 95 | 95 | 113
76 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 92 | 50 | 90 |  | 25 | Fuel shortag
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 34 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1350 | 1563 | 1747 | 2036 | 220 | 442
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 3 | 0 | 11 | 15 | 187 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 95 | 115 | 125 | 160 | 40 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 73 | 92 | 74 | 92 | 23 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 10 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 18 | 6 | 18 |  | 4 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 3 | 17 | 17 | 54
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 190 | 242 | 284.6 | 339 | 187 | 4
84 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 28 | 28 | 30 | 30 |  | 40 | Machine problem.
85 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | under maint
86 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 120 | 163 | 163
87 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
88 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 10 | 10 | 11 | 11 | 40 |  | Gas shortage
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 10 | 35 | 35 | 15 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 62 | 62 | 62 | 4
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 61 | 31 | 31 | 86
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 212 | 212 | 210 | 210 |  | 21
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 300 | 300 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 366 | 365 | 366 | 366 |  |  | FGMO
99 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 346 | 346 | 350 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1500 | 1486 | 1575 | 1630 | 79 | 500
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 886 | 890 | 908 | 908
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 48 |  | 6 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 55 |  | 54 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 228 | 214 | 250 | 250 | 160 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 70 | 90 | 15 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 100 | 100 | 5
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 12 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 561 | 620 | 600 | 600 |  |  | Unit-1 under maint
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1687 | 1756 | 2058 | 2051 | 762 | 60
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 9 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 134 | 100 | 130 | 130 |  | 64 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1080 | 1244 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 180 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 116 | 34 |  | Fuel shortage
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 180 | 307 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1620 | 1840 | 2038 | 2137 | 34 | 64
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 30 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 24 |  | 47 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
122 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 46
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 198 | 160 | 180 | 180 | 30 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 320 | 414 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 8 |  | 3 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52 | 0 |  | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 33 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 70 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 95 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1008 | 1019 | 1000 | 1100
135 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 5 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 33 | 0 | 14 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1661 | 1534 | 1995 | 2210 | 641 | 96
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 61 | 66 | 60 | 60 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230 |  | 44
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 34 | 105 |  | 8 | Engine problem
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 35 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 1 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 21 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 313 | 365 | 567 | 510 | 40 | 162
| Total |  |  |  |  | 27791 | 27086 | 11579 | 12475 | 14707.6 | 16228 | 4675 | 3512
A. |  | 2024-09-26 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 12475 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 10371 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12475 | MW
3 | Day peak Generation : |  |  | 11579 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12103.4 | MW
4 | Evening peak Generation : |  |  | 12475 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 285.869 | MKWHr | By Solar | 1.1102 | MKWHr
| By Gas : | 123.6016 | MKWHr |  | By Oil: | 24.3933 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 78.4441 | MKWHr |  | By Hydro: | 11.1059 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 24.417 | MKWHr |  | By Wind: | 0.4248 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4675 | MW | Dhaka | 4641.4 | 4641.4 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3512 | MW | Chittagong | 1361.5 | 1361.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 8187 | MW | Khulna | 1372 | 1372 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 876.51 | MMCFD | **Import Adani: | Taka | 161396515.42 | Rajshahi | 1063.4 | 1063.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 373839177.512 | ii) Oil : | Taka | 447363722.45 | Comilla | 1189 | 1189 |  | 0 |  | 21:00 |  | 20
|  | iii) Coal : | Taka | 541659535.12 | Total | Taka | 1524258950.502 | Mymensingh | 942 | 942 |  | 0 |  | 22:00 |  | 20
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 11003.85 | MKWHr. | Sylhet | 534 | 534 |  | 0 |  | 23:00 |  | 18
| ii) During Peak Demand : |  |  | 968 | MW (W to E) at | 19:30 | hrs | Barisal | 364 | 364 |  | 0 |  | 24:00 |  | 17
| iii) Maximum : |  |  | 930 | MW at | 19:00 | hrs | Rangpur | 636.1 | 636.1 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.2°C |  |  | Total | 12103.4 | 12103.4 |  | 0
B. |  | 2024-09-27 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 28.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16228 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11200 | MW
4 | Reserve(Generation end) |  |  |  | 3028 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 302.4827 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9747 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.1789 | MKWHr. | ii) HVDC Flow at Peak Time |  | 890 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.1933 | MKWHr. | iii) Maximum HVDC Flow : |  | 892 | MW at | 16:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 0 |  | (b) Today: | 106.68 |  | (c) Rule Curve: |  | 105.04
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-09-26 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 |  | 0 | 420 | 282 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 25 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 10 | 0 | 0 | 133 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 285 | 0 | 217 | 108 | 50 | 37 | 54 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 54 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 31 | 61 | 0 | 212 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 45 | 0 | 0 | 97 | 0 | 58 | 0 | 0 | 51 | 0 | 348 | 55 | 17 | 17 | 0 | 15 | 0 | 51 | 0 | 97 | 0 | 316 | 17 | 0 | 17 | 0 | 0 | 20 | 0 | 40 | 19 | 290 | 0 | 0 | 612 | 25 | 617 | 0 | 0 | 0 | 0 |  | 887 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 53 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 1100 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 627 | 0 | 221 | 1009 | 0 | 0 | 0 | 0 | 0 |  | 6331 | 5440 | 11771 | 3063 | 887 | 2056 | 0 | 913 | 3469 | 213 | 0 | 82 | 54 | 1009 | 0 | 25 | 133 | 0
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 |  | 0 | 420 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 11 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 285 | 0 | 217 | 108 | 50 | 37 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 31 | 61 | 0 | 213 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 96 | 0 | 35 | 0 | 0 | 51 | 0 | 348 | 55 | 17 | 17 | 0 | 15 | 0 | 17 | 0 | 87 | 0 | 316 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 40 | 17 | 290 | 0 | 0 | 612 | 27 | 620 | 0 | 0 | 0 | 0 |  | 887 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 230 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1100 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624 | 0 | 200 | 1011 | 0 | 0 | 0 | 0 | 0 |  | 6162 | 5183 | 11345 | 3064 | 887 | 2021 | 0 | 537 | 3450 | 214 | 0 | 82 | 52 | 1011 | 0 | 27 | 100.275 | 0
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 |  | 0 | 420 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 10 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 295 | 0 | 216 | 108 | 50 | 37 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 12 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 32 | 61 | 0 | 213 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 0 | 0 | 0 | 96 | 0 | 34 | 0 | 0 | 51 | 0 | 348 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 40 | 17 | 290 | 0 | 0 | 550 | 37 | 622 | 0 | 0 | 0 | 0 |  | 887 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566 | 0 | 150 | 1013 | 0 | 0 | 0 | 0 | 0 |  | 5994 | 5047 | 11041 | 3084 | 887 | 2096 | 0 | 408 | 3220 | 214 | 0 | 32 | 50 | 1013 | 0 | 37 | 51.57 | 0
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 420 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 11 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 285 | 0 | 218 | 108 | 50 | 37 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 12 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 32 | 61 | 0 | 213 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 96 | 0 | 35 | 0 | 0 | 34 | 0 | 348 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 17 | 285 | 0 | 0 | 551 | 37 | 621 | 0 | 0 | 0 | 0 |  | 886 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 230 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 513 | 0 | 150 | 1007 | 0 | 0 | 0 | 0 | 0 |  | 5956 | 4909 | 10865 | 3072 | 886 | 2081 | 0 | 397 | 3089 | 214 | 0 | 32 | 50 | 1007 | 0 | 37 | 52.525 | 0
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 |  | 0 | 420 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 12 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 320 | 0 | 216 | 108 | 70 | 37 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 12 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 32 | 61 | 0 | 213 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 0 | 0 | 0 | 96 | 0 | 35 | 0 | 0 | 17 | 0 | 348 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 17 | 315 | 0 | 0 | 450 | 30 | 623 | 0 | 0 | 0 | 0 |  | 886 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 230 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 0 | 150 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 5955 | 4718 | 10673 | 3196 | 886 | 2105 | 0 | 363 | 2781 | 214 | 0 | 32 | 50 | 1016 | 0 | 30 | 49.66 | 0
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 420 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 12 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 285 | 0 | 218 | 108 | 51 | 37 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | 18 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 32 | 61 | 0 | 213 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 96 | 0 | 34 | 1 | 0 | 17 | 0 | 348 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 17 | 285 | 0 | 0 | 450 | 13 | 618 | 0 | 0 | 1 | 0 |  | 886 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 150 | 1007 | 0 | 0 | 0 | 0 | 0 |  | 5736 | 4635 | 10371 | 3101 | 886 | 1976 | 0 | 339 | 2755 | 214 | 0 | 32 | 46 | 1007 | 2 | 13 | 46.795 | 0
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 |  | 0 | 420 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 21 | 30 | 12 | 3 | 0 | 133 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 345 | 0 | 217 | 78 | 50 | 38 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 44 | 12 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 31 | 61 | 0 | 213 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 0 | 0 | 0 | 124 | 0 | 35 | 4 | 0 | 17 | 0 | 348 | 73 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 63 | 0 | 316 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 34 | 17 | 335 | 0 | 0 | 450 | 8 | 622 | 0 | 0 | 24 | 0 |  | 887 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 467 | 1 | 150 | 1008 | 12 | 0 | 0 | 0 | 2 |  | 5909 | 4573 | 10482 | 3165 | 887 | 1968 | 0 | 389 | 2721 | 213 | 0 | 32 | 44 | 1008 | 47 | 8 | 0 | 0
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 |  | 0 | 420 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 21 | 25 | 10 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 330 | 0 | 215 | 78 | 50 | 32 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 44 | 11 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 31 | 61 | 0 | 213 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 0 | 0 | 0 | 125 | 0 | 36 | 5 | 0 | 17 | 0 | 348 | 73 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 53 | 0 | 346 | 0 | 2 | 0 | 0 | 0 | 0 | 3 | 34 | 17 | 320 | 0 | 0 | 500 | 10 | 621 | 0 | 0 | 30 | 0 |  | 887 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 230 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 463 | 1 | 150 | 1010 | 2 | 0 | 0 | 3 | 10 |  | 5915 | 4721 | 10636 | 3199 | 887 | 1972 | 0 | 386 | 2826 | 212 | 0 | 32 | 44 | 1010 | 58 | 10 | 0 | 106.82
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 420 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 30 | 10 | 17 | 0 | 131 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 310 | 0 | 218 | 78 | 50 | 30 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | 5 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 32 | 61 | 0 | 211 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 0 | 0 | 0 | 125 | 0 | 40 | 14 | 0 | 17 | 0 | 359 | 73 | 35 | 2 | 3 | 15 | 2 | 0 | 0 | 53 | 0 | 346 | 0 | 1 | 17 | 1 | 0 | 0 | 12 | 34 | 17 | 290 | 0 | 0 | 550 | 21 | 618 | 0 | 0 | 15 | 0 |  | 887 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 230 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 2 | 150 | 1008 | 10 | 0 | 0 | 4 | 31 |  | 5974 | 4954 | 10928 | 3149 | 887 | 1960 | 0 | 454 | 3070 | 211 | 0 | 32 | 44 | 1008 | 92 | 21 | 0 | 106.81
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 |  | 0 | 420 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 4 | 17 | 0 | 0 | 15 | 18 | 30 | 10 | 17 | 0 | 132 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 325 | 0 | 216 | 78 | 45 | 32 | 52 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 3 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 130 | 0 | 31 | 61 | 0 | 212 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 5 | 0 | 0 | 95 | 0 | 79 | 20 | 0 | 17 | 0 | 360 | 73 | 35 | 17 | 3 | 15 | 17 | 15 | 0 | 53 | 0 | 346 | 16 | 8 | 35 | 17 | 0 | 0 | 4 | 35 | 17 | 290 | 0 | 0 | 551 | 19 | 621 | 0 | 0 | 24 | 0 |  | 887 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 220 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 505 | 1 | 150 | 1006 | 15 | 0 | 0 | 16 | 24 |  | 6136 | 4980 | 11116 | 3168 | 887 | 1945 | 0 | 593 | 3089 | 212 | 0 | 32 | 48 | 1006 | 117 | 19 | 51.57 | 106.81
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 420 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 13 | 21 | 30 | 10 | 17 | 0 | 132 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 325 | 0 | 216 | 78 | 45 | 30 | 50 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 4 | 0 | 0 | 1 | 28 | 0 | 10 | 10 | 130 | 0 | 30 | 61 | 0 | 211 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 30 | 0 | 0 | 95 | 0 | 80 | 20 | 0 | 26 | 0 | 361 | 73 | 35 | 17 | 2 | 15 | 17 | 17 | 0 | 53 | 0 | 353 | 16 | 8 | 35 | 17 | 0 | 0 | 13 | 34 | 17 | 320 | 0 | 0 | 551 | 13 | 620 | 0 | 0 | 39 | 0 |  | 887 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 220 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 555 | 1 | 150 | 1009 | 20 | 0 | 0 | 6 | 27 |  | 6260 | 5098 | 11358 | 3228 | 887 | 1969 | 0 | 642 | 3178 | 212 | 0 | 32 | 48 | 1009 | 140 | 13 | 40.11 | 106.8
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 420 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 13 | 17 | 30 | 10 | 17 | 0 | 132 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 325 | 0 | 216 | 78 | 40 | 34 | 50 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 3 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 130 | 0 | 30 | 61 | 0 | 212 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 42 | 0 | 0 | 95 | 0 | 80 | 7 | 4 | 51 | 0 | 366 | 73 | 35 | 17 | 2 | 15 | 17 | 20 | 0 | 53 | 12 | 346 | 25 | 10 | 54 | 17 | 0 | 3 | 7 | 34 | 17 | 320 | 0 | 0 | 550 | 8 | 619 | 0 | 0 | 34 | 0 |  | 886 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 230 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 1 | 12 | 0 | 0 | 0 | 561 | 1 | 180 | 1008 | 21 | 0 | 0 | 5 | 33 |  | 6298 | 5281 | 11579 | 3217 | 886 | 2041 | 0 | 729 | 3281 | 212 | 0 | 16 | 48 | 1008 | 133 | 8 | 39.155 | 106.8
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 420 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 13 | 14 | 30 | 10 | 17 | 0 | 132 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 220 | 97 | 40 | 38 | 51 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 46 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 31 | 61 | 0 | 209 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 45 | 0 | 0 | 95 | 0 | 80 | 10 | 18 | 51 | 0 | 365 | 73 | 35 | 20 | 2 | 50 | 19 | 34 | 0 | 53 | 24 | 346 | 33 | 7 | 72 | 18 | 0 | 17 | 2 | 34 | 17 | 330 | 17 | 0 | 578 | 31 | 573 | 0 | 0 | 22 | 0 |  | 887 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 230 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 220 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 618 | 5 | 180 | 1018 | 39 | 0 | 0 | 22 | 36 |  | 6435 | 5458 | 11893 | 3209 | 887 | 2040 | 0 | 853 | 3400 | 212 | 0 | 49 | 46 | 1018 | 148 | 31 | 54 | 106.79
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 420 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 0 | 20 | 30 | 10 | 17 | 0 | 133 | 80 | 0 | 0 | 3 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 8 | 0 | 0 | 0 | 285 | 0 | 219 | 97 | 35 | 36 | 53 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 1 | 28 | 0 | 10 | 10 | 163 | 0 | 31 | 61 | 0 | 209 | 0 | 0 | 0 | 270 | 12 | 5 | 0 | 58 | 0 | 0 | 85 | 0 | 80 | 13 | 25 | 51 | 0 | 370 | 73 | 35 | 51 | 4 | 50 | 35 | 42 | 0 | 53 | 24 | 325 | 50 | 3 | 90 | 35 | 0 | 17 | 10 | 34 | 17 | 290 | 17 | 0 | 599 | 37 | 406 | 0 | 0 | 16 | 0 |  | 886 | 0 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1080 | 180 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 618 | 5 | 150 | 1008 | 26 | 0 | 0 | 13 | 27 |  | 6369 | 5129 | 11498 | 3039 | 886 | 1952 | 0 | 1000 | 3145 | 213 | 0 | 49 | 48 | 1008 | 121 | 37 | 31 | 106.8
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 420 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 0 | 20 | 30 | 10 | 17 | 0 | 133 | 80 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 21 | 0 | 0 | 3 | 0 | 0 | 0 | 310 | 0 | 218 | 97 | 35 | 40 | 51 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 32 | 61 | 0 | 208 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 60 | 0 | 0 | 105 | 0 | 80 | 11 | 25 | 51 | 0 | 370 | 73 | 35 | 51 | 3 | 50 | 35 | 51 | 0 | 53 | 24 | 346 | 50 | 9 | 90 | 35 | 0 | 17 | 9 | 34 | 17 | 320 | 17 | 0 | 595 | 31 | 372 | 0 | 0 | 16 | 0 |  | 887 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 631 | 4 | 150 | 1018 | 15 | 0 | 0 | 9 | 36 |  | 6481 | 5180 | 11661 | 3144 | 887 | 2001 | 0 | 1055 | 3080 | 213 | 0 | 65 | 48 | 1018 | 119 | 31 | 0 | 106.78
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 |  | 0 | 420 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 13 | 0 | 0 | 20 | 30 | 10 | 17 | 0 | 133 | 80 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 25 | 0 | 0 | 3 | 0 | 0 | 0 | 335 | 0 | 216 | 97 | 35 | 40 | 51 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 50 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 31 | 61 | 0 | 210 | 0 | 0 | 0 | 275 | 12 | 5 | 0 | 60 | 0 | 0 | 105 | 0 | 86 | 5 | 25 | 51 | 0 | 367 | 73 | 35 | 17 | 1 | 15 | 17 | 34 | 0 | 53 | 12 | 346 | 50 | 3 | 90 | 17 | 0 | 17 | 2 | 34 | 17 | 345 | 17 | 0 | 554 | 23 | 320 | 0 | 0 | 12 | 0 |  | 892 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 180 | 0 | 0 | 1 | 14 | 0 | 0 | 0 | 566 | 1 | 150 | 930 | 4 | 0 | 0 | 13 | 8 |  | 6298 | 4812 | 11110 | 3116 | 892 | 1930 | 0 | 945 | 2882 | 213 | 0 | 65 | 50 | 930 | 64 | 23 | 0 | 106.78
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 420 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 10 | 20 | 30 | 10 | 17 | 0 | 134 | 80 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 25 | 0 | 0 | 11 | 0 | 0 | 0 | 325 | 0 | 216 | 97 | 35 | 39 | 52 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 56 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 31 | 61 | 0 | 210 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 60 | 0 | 0 | 96 | 0 | 97 | 1 | 37 | 51 | 3 | 368 | 73 | 52 | 17 | 0 | 15 | 17 | 34 | 0 | 53 | 24 | 346 | 50 | 0 | 90 | 17 | 0 | 17 | 3 | 35 | 17 | 330 | 17 | 0 | 551 | 18 | 315 | 0 | 0 | 4 | 0 |  | 891 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 1000 | 180 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 571 | 0 | 150 | 919 | 1 | 0 | 0 | 0 | 4 |  | 6324 | 4810 | 11134 | 3085 | 891 | 1948 | 0 | 1042 | 2879 | 214 | 0 | 65 | 56 | 919 | 17 | 18 | 0 | 106.77
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 400 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 98 | 0 | 0 | 0 | 0 | 54 | 17 | 22 | 0 | 14 | 15 | 30 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 8 | 3 | 34 | 0 | 25 | 0 | 0 | 15 | 0 | 0 | 0 | 330 | 0 | 215 | 53 | 35 | 39 | 55 | 0 | 51 | 0 | 0 | 9 | 0 | 0 | 0 | 16 | 66 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 163 | 0 | 60 | 31 | 0 | 209 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 90 | 0 | 0 | 122 | 0 | 97 | 0 | 32 | 63 | 23 | 367 | 74 | 52 | 17 | 0 | 23 | 17 | 36 | 23 | 58 | 24 | 346 | 50 | 0 | 120 | 17 | 0 | 17 | 0 | 48 | 26 | 300 | 17 | 0 | 580 | 5 | 316 | 0 | 0 | 0 | 0 |  | 892 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 230 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 1 | 15 | 30 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 596 | 0 | 241 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 6611 | 5303 | 11914 | 3176 | 892 | 1956 | 0 | 1351 | 3068 | 214 | 0 | 170 | 66 | 1016 | 0 | 5 | 0 | 106.77
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 400 | 254 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 66 | 98 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 0 | 14 | 30 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 19 | 224 | 0 | 0 | 0 |  | 11 | 32 | 34 | 0 | 43 | 14 | 0 | 20 | 0 | 0 | 0 | 285 | 0 | 218 | 35 | 30 | 41 | 55 | 0 | 51 | 0 | 0 | 36 | 0 | 0 | 0 | 18 | 48 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 62 | 31 | 0 | 212 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 145 | 0 | 0 | 115 | 0 | 110 | 0 | 25 | 167 | 80 | 365 | 92 | 70 | 34 | 0 | 50 | 17 | 60 | 34 | 84 | 24 | 325 | 48 | 0 | 150 | 17 | 0 | 17 | 0 | 54 | 35 | 290 | 35 | 0 | 604 | 2 | 317 | 0 | 0 | 0 | 0 |  | 890 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 15 | 67 | 0 | 0 | 0 | 1220 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 620 | 0 | 307 | 1015 | 0 | 0 | 0 | 0 | 0 |  | 6949 | 5515 | 12464 | 2995 | 890 | 1775 | 0 | 1930 | 3363 | 214 | 0 | 232 | 48 | 1015 | 0 | 2 | 0 | 106.75
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 400 | 285 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 66 | 98 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 15 | 14 | 30 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 18 | 40 | 34 | 0 | 43 | 6 | 0 | 23 | 0 | 0 | 0 | 285 | 0 | 217 | 35 | 30 | 43 | 55 | 0 | 51 | 0 | 28 | 25 | 0 | 0 | 0 | 18 | 50 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 62 | 31 | 0 | 212 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 95 | 0 | 0 | 115 | 0 | 115 | 0 | 37 | 170 | 40 | 365 | 92 | 70 | 34 | 0 | 50 | 17 | 68 | 34 | 95 | 24 | 346 | 50 | 0 | 108 | 17 | 0 | 17 | 0 | 92 | 35 | 295 | 35 | 0 | 609 | 0 | 318 | 0 | 0 | 0 | 0 |  | 890 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 1244 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 620 | 0 | 307 | 1019 | 0 | 0 | 0 | 0 | 0 |  | 6980 | 5495 | 12475 | 3038 | 890 | 1814 | 0 | 1788 | 3394 | 214 | 0 | 268 | 50 | 1019 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 400 | 306 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 66 | 98 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 15 | 14 | 30 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 18 | 39 | 34 | 0 | 37 | 6 | 0 | 23 | 0 | 0 | 0 | 305 | 0 | 216 | 35 | 30 | 43 | 55 | 0 | 51 | 0 | 38 | 25 | 0 | 0 | 0 | 18 | 50 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 55 | 31 | 0 | 212 | 0 | 0 | 0 | 275 | 12 | 5 | 0 | 95 | 0 | 0 | 115 | 0 | 116 | 0 | 37 | 170 | 40 | 368 | 92 | 50 | 34 | 0 | 50 | 17 | 68 | 26 | 94 | 24 | 370 | 50 | 0 | 54 | 17 | 0 | 21 | 0 | 90 | 35 | 310 | 35 | 0 | 606 | 3 | 317 | 0 | 0 | 0 | 0 |  | 889 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 1244 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 618 | 0 | 307 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 6976 | 5487 | 12463 | 3091 | 889 | 1825 | 0 | 1711 | 3387 | 214 | 0 | 277 | 50 | 1016 | 0 | 3 | 0 | 106.76
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 400 | 290 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 65 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 15 | 20 | 30 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 19 | 39 | 34 | 0 | 22 | 6 | 0 | 32 | 0 | 0 | 0 | 285 | 0 | 217 | 36 | 35 | 43 | 55 | 0 | 51 | 0 | 38 | 25 | 0 | 0 | 0 | 18 | 52 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 55 | 31 | 0 | 212 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 95 | 0 | 0 | 115 | 0 | 110 | 0 | 37 | 136 | 10 | 368 | 92 | 52 | 17 | 0 | 15 | 17 | 34 | 17 | 99 | 24 | 346 | 50 | 0 | 54 | 17 | 0 | 35 | 0 | 92 | 35 | 320 | 35 | 0 | 605 | 7 | 316 | 0 | 0 | 0 | 0 |  | 890 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 1244 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 618 | 0 | 307 | 1018 | 0 | 0 | 0 | 0 | 0 |  | 6773 | 5461 | 12234 | 3070 | 890 | 1825 | 0 | 1545 | 3385 | 214 | 0 | 228 | 52 | 1018 | 0 | 7 | 20 | 106.75
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 400 | 282 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 40 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 15 | 20 | 30 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 24 | 39 | 34 | 0 | 24 | 6 | 0 | 34 | 0 | 0 | 0 | 280 | 0 | 217 | 36 | 40 | 42 | 55 | 0 | 51 | 0 | 38 | 25 | 0 | 0 | 0 | 18 | 54 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 55 | 31 | 0 | 211 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 45 | 0 | 0 | 115 | 0 | 98 | 0 | 37 | 100 | 10 | 368 | 73 | 52 | 17 | 0 | 15 | 17 | 34 | 17 | 105 | 24 | 346 | 50 | 0 | 54 | 17 | 0 | 35 | 0 | 91 | 35 | 320 | 0 | 0 | 612 | 4 | 316 | 0 | 0 | 0 | 0 |  | 891 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1244 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 307 | 1125 | 0 | 0 | 0 | 0 | 0 |  | 6540 | 5499 | 12039 | 3077 | 891 | 1824 | 0 | 1311 | 3380 | 214 | 0 | 159 | 54 | 1125 | 0 | 4 | 20 | 106.75
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 400 | 262 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 20 | 30 | 10 | 17 | 0 | 132 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 24 | 39 | 34 | 0 | 25 | 6 | 0 | 36 | 0 | 0 | 0 | 285 | 0 | 219 | 36 | 50 | 42 | 55 | 0 | 51 | 0 | 38 | 25 | 0 | 0 | 0 | 18 | 58 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 56 | 31 | 0 | 211 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 45 | 0 | 0 | 115 | 0 | 97 | 0 | 25 | 100 | 10 | 347 | 73 | 52 | 17 | 0 | 15 | 17 | 34 | 17 | 105 | 24 | 346 | 31 | 0 | 54 | 17 | 0 | 19 | 0 | 74 | 35 | 325 | 0 | 0 | 612 | 1 | 316 | 0 | 0 | 0 | 0 |  | 889 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 307 | 1124 | 0 | 0 | 0 | 0 | 0 |  | 6399 | 5487 | 11886 | 3092 | 889 | 1806 | 0 | 1153 | 3392 | 212 | 0 | 159 | 58 | 1124 | 0 | 1 | 18 | 106.74
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 400 | 285 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 40 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 15 | 20 | 30 | 10 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 24 | 39 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 285 | 0 | 217 | 36 | 50 | 40 | 55 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 56 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 55 | 31 | 0 | 211 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 45 | 0 | 0 | 115 | 0 | 98 | 0 | 0 | 100 | 0 | 353 | 73 | 17 | 17 | 0 | 15 | 17 | 34 | 17 | 105 | 0 | 346 | 17 | 0 | 54 | 17 | 0 | 17 | 0 | 48 | 35 | 325 | 0 | 0 | 604 | 5 | 315 | 0 | 0 | 0 | 0 |  | 891 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 307 | 1093 | 0 | 0 | 0 | 0 | 0 |  | 6175 | 5457 | 11632 | 3092 | 891 | 1825 | 0 | 988 | 3383 | 212 | 0 | 87 | 56 | 1093 | 0 | 5 | 17 | 106.74
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9626400 | 0 |  | 0 | 8649500 | 6949178 | 0 | 0 | 152797 | 0 | 0 | 0 | 0 | 446976 | 1202880 | 43000 | 0 | 0 | 0 | 415080 | 245515 | 285869 | 0 | 309000 | 455760 | 809600 | 247400 | 314400 | 0 | 9173853 | 1932000 | 0 | 0 | 105120 | 5263377 | 0 | 0 | 0 |  | 231840 | 239136 | 184337 | 0 | 285120 | 43200 | 0 | 532320 | 0 | 0 | 0 | 7694800 | 0 | 5280000 | 1923636 | 1051940 | 903384 | 1283520 | 0 | 1205547 | 0 | 165744 | 225830 | 0 | 0 | 0 | 415100 | 1193280 | 72960 | 0 | 0 | 0 | 669000 | 0 | 259200 | 342792 | 3677073 | 0 | 913824 | 1286400 | 0 | 5238770 | 0 | 0 | 0 | 6904500 | 282480 | 120960 | 0 | 1116545 | 0 | 0 | 2546400 | 0 | 1754640 | 131490 | 332160 | 1573920 | 207418 | 8977000 | 1700400 | 848640 | 450799 | 26281 | 466691 | 332818 | 754400 | 156180 | 1823640 | 273600 | 8286500 | 613440 | 57750 | 1169280 | 309873 | 0 | 334080 | 65707 | 1105920 | 550800 | 7585300 | 234181 | 0 | 13499998 | 424800 | 11898181 | 0 | 0 | 235227 | 0 |  | 21178909 | 0 | 5474304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2659000 | 184914 | 33792 | 0 | 0 | 0 | 0 | 0 | 112320 | 0 | 0 | 0 | 7901 | 0 | 0 | 0 | 59796 | 1455272 | 0 | 5576000 | 0 | 0 | 4217364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8718254 | 158400 | 0 | 97344 | 87552 | 317510 | 0 | 5589 | 67968 | 27302200 | 5070760 | 0 | 0 | 8160 | 52560 | 267840 | 0 | 0 | 13825450 | 25976 | 4887000 | 24417022 | 190800 | 0 | 1275 | 90750 | 218600 |  | 159098457 | 126770582 | 285869039 | 76614019 | 21178909 | 46987594 | 0 | 22254698 | 78444101 | 11105853 | 0 | 2138598 | 1193280 | 24417022 | 1110165 | 424800 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27724032 | 0 |  | 0 | 27505410 | 23766188.76 | 0 | 0 | 2692283.14 | 0 | 0 | 0 | 0 | 8023219.2 | 23359929.6 | 801950 | 0 | 0 | 0 | 7579360.8 | 3869316.4 | 5228544.01 | 0 | 231750 | 0 | 0 | 0 | 5630904 | 0 | 0 | 0 | 0 | 0 | 1990972.8 | 16790172.63 | 0 | 0 | 0 |  | 4078065.6 | 4211184.96 | 3301475.67 | 0 | 5579798.4 | 711072 | 0 | 0 | 0 | 0 | 0 | 21468492 | 0 | 17529600 | 6444180.6 | 3397766.2 | 3044404.08 | 5621817.6 | 0 | 4834243.47 | 0 | 2968475.04 | 4078489.8 | 0 | 0 | 0 | 311325 | 7827916.8 | 226905.6 | 0 | 0 | 0 | 2609100 | 0 | 1179360 | 1559703.6 | 12575589.66 | 0 | 5071723.2 | 6715008 | 0 | 14616168.3 | 0 | 0 | 0 | 21334905 | 211860 | 91929.6 | 0 | 22777518 | 0 | 0 | 48916344 | 0 | 30899210.4 | 0 | 5915769.6 | 27307512 | 3438990.44 | 23789050 | 32409624 | 15920486.4 | 8087334.06 | 0 | 7630397.85 | 6469981.92 | 13533936 | 2984599.8 | 35396852.4 | 4872816 | 22042090 | 10471420.8 | 0 | 21386131.2 | 5199668.94 | 0 | 5970009.6 | 0 | 19928678.4 | 9330552 | 22528341 | 3297268.48 | 0 | 94094986.06 | 0 | 70199267.9 | 0 | 0 | 0 | 0 |  | 59512734.29 | 0 | 16149196.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8402440 | 876492.36 | 582574.08 | 0 | 0 | 0 | 0 | 0 | 1888099.2 | 0 | 0 | 0 | 139847.7 | 0 | 0 | 0 | 45265.572 | 16051650.16 | 0 | 47061440 | 0 | 0 | 13917301.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25457301.68 | 2705472 | 0 | 1929358.08 | 1547919.36 | 6324799.2 | 0 | 0 | 1348485.12 | 176918256 | 15770063.6 | 0 | 0 | 0 | 0 | 4647024 | 0 | 0 | 100925785 | 0 | 36408150 | 161396515.42 | 0 | 0 | 0 | 0 | 0 |  | 891593430.77 | 700006170.822 | 1591599601.592 | 220198913.182 | 59512734.29 | 153640264.33 | 0 | 408337289.5 | 541659535.12 | 0 | 0 | 39026432.95 | 7827916.8 | 161396515.42 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 420 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 13 | 17 | 30 | 10 | 17 | 0 | 132 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 325 | 0 | 216 | 78 | 40 | 34 | 50 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 3 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 130 | 0 | 30 | 61 | 0 | 212 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 42 | 0 | 0 | 95 | 0 | 80 | 7 | 4 | 51 | 0 | 366 | 73 | 35 | 17 | 2 | 15 | 17 | 20 | 0 | 53 | 12 | 346 | 25 | 10 | 54 | 17 | 0 | 3 | 7 | 34 | 17 | 320 | 0 | 0 | 550 | 8 | 619 | 0 | 0 | 34 | 0 |  | 886 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 230 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 1 | 12 | 0 | 0 | 0 | 561 | 1 | 180 | 1008 | 21 | 0 | 0 | 5 | 33 |  | 11579 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 400 | 285 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 66 | 98 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 15 | 14 | 30 | 10 | 25 | 0 | 134 | 80 | 0 | 0 | 8 | 225 | 0 | 0 | 0 | 0 | 18 | 40 | 34 | 0 | 43 | 6 | 0 | 23 | 0 | 0 | 0 | 285 | 0 | 217 | 35 | 30 | 43 | 55 | 0 | 51 | 0 | 28 | 25 | 0 | 0 | 0 | 18 | 50 | 0 | 0 | 0 | 0 | 28 | 0 | 10 | 10 | 120 | 0 | 62 | 31 | 0 | 212 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 95 | 0 | 0 | 115 | 0 | 115 | 0 | 37 | 170 | 40 | 365 | 92 | 70 | 34 | 0 | 50 | 17 | 68 | 34 | 95 | 24 | 346 | 50 | 0 | 108 | 17 | 0 | 17 | 0 | 92 | 35 | 295 | 35 | 0 | 609 | 0 | 318 | 0 | 0 | 0 | 0 |  | 890 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 1244 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 620 | 0 | 307 | 1019 | 0 | 0 | 0 | 0 | 0 |  | 12475 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 300 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 98 | 132 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 21 | 30 | 18 | 25 | 0 | 134 | 80 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 18 | 65 | 84 | 0 | 50 | 50 | 0 | 30 | 0 | 0 |  | 330 | 0 | 210 | 140 | 50 | 43 | 53 | 0 | 51 | 0 | 35 | 52 | 0 | 0 |  | 18 | 70 | 15 | 0 | 0 | 0 | 30 | 0 | 11 | 35 | 163 | 0 | 62 | 86 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 280 | 0 | 0 | 160 | 0 | 132 | 0 | 37 | 200 | 125 | 366 | 92 | 105 | 105 | 0 | 50 | 54 | 110 | 106 | 113 | 24 | 350 | 60 | 0 | 162 | 108 | 0 | 54 | 0 | 90 | 35 | 350 | 163 | 0 | 612 | 60 | 750 | 0 | 0 |  |  |  | 908 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 48 | 55 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 24 | 90 | 0 | 0 | 46 | 52 | 30 | 0 | 0 | 8 | 60 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 113 | 100 | 105 | 0 | 0 | 113 | 1244 | 220 | 0 | 116 | 0 | 0 | 115 | 0 | 0 | 600 | 0 | 307 | 1100 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 300 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 16 | 64 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 16 | 21 | 30 | 18 | 16 | 0 | 134 | 80 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 65 | 51 | 0 | 38 | 50 | 0 | 15 | 0 | 0 | 0 | 330 | 0 | 210 | 140 | 50 | 43 | 53 | 0 | 51 | 0 | 35 | 16 | 0 | 0 |  | 18 | 60 | 11 | 0 | 0 | 1.6 | 30 | 0 | 11 | 35 | 163 | 0 | 62 | 31 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 80 | 0 | 0 | 125 | 0 | 115 | 20 | 25 | 17 | 125 | 366 | 74 | 34 | 105 | 5 | 50 | 54 | 110 | 34 | 95 | 24 | 350 | 17 | 50 | 35 | 108 | 0 | 17 | 35 | 50 | 35 | 350 | 35 | 0 | 612 | 42 | 750 | 0 | 0 | 70 |  |  | 908 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 30 | 0 | 50 | 0 | 0 | 25 | 52 | 25 | 0 | 0 | 5 | 60 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 70 | 0 | 70 | 100 | 34 | 0 | 8 | 95 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 600 | 30 | 307 | 1000 | 170 | 0 |  | 29 | 14 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 340 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 30 | 12 | 8 | 0 | 134 | 40 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 280 | 0 | 221 | 36 | 50 | 41 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 44 | 8 | 0 | 0 | 1 | 28 | 0 | 10 | 10 | 163 | 0 | 62 | 31 | 0 | 211 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 75 | 0 | 35 | 10 | 0 | 17 | 0 | 361 | 72 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 53 | 0 | 320 | 0 | 12 | 0 | 0 | 0 | 0 | 7 | 17 | 17 | 393 | 0 | 0 | 440 | 0 | 316 | 0 | 0 | 41 | 0 | 0 | 886 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 1 | 46 | 0 | 0 | 0 | 403 | 1 | 150 | 818 | 22 | 0 | 0 | 14 | 20 | 0 |  |  |  | 123601613 | 21178909 | 0 | 78444101 | 24393296 | 1193280 | 1110165 | 424800 | 11105853 |  |  |  | 261452017
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [6 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 123.6016 | 21.1789 | 0 | 78.4441 | 24.3933 | 1.1933 | 1.1102 | 0.4248 | 11.1059
| Minimum Generation |  | 10371 | 6:00
| Highest Generation |  | 12475 | 19:30 | [129 empty] | 0 | [75 empty] | 261.452
| Day Peak Generation |  | 11579 | 12:00
| Evening Peak Generation |  | 12475 | 19:30 | [205 empty] | 202699852
| HVDC Max Flow |  | 892 | 16:00 | [205 empty] | 202.6999
| HVDC EvPeak Flow |  | 890 | 19:30
| Load factor L.F |  | 95.48% | [168 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-09-27
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-09-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11579 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9747
Evening Peak Generation : |  |  | 12475 | MW Hour : | 19:30 | Available Max Generation : |  | 16228
E.P. Demand (at gen end) : |  |  | 12475 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13200
Maximum Generation : |  |  | 12475 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3028
Total Gen. (MKWH) : |  |  | 285.869 | System Load Factor : | 95.48% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 930 | MW at | 19:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-09-27
Actual : |  | 106.68 | Ft.(MSL) , | Rule curve : | 105.04 | Ft.( MSL )
Gas Consumed : |  | Total = | 876.51 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 373839177.512 | Adani : | 161396515.42
: |  |  | Coal : | 541659535.12 | Oil : | 447363722.45 | Total : | 1524258950.502
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4695.4665 |  |  | 0 | -18.83%
Chittagong Area |  | 0 | 0:00 | 1291.088 |  |  | 0 | -17.09%
Khulna Area |  | 0 | 0:00 | 1808.7915 |  |  | 0 | -16.71%
Rajshahi Area |  | 0 | 0:00 | 1572.379 |  |  | 0 | -16.32%
Cumilla Area |  | 0 | 0:00 | 1293.6804 |  |  | 0 | -16.56%
Mymensingh Area |  | 0 | 0:00 | 962.2882 |  |  | 0 | -16.22%
Sylhet Area |  | 0 | 0:00 | 539.2681 |  |  | 0 | -16.88%
Barisal Area |  | 0 | 0:00 | 449.5289 |  |  | 0 | -16.16%
Rangpur Area |  | 0 | 0:00 | 879.1971 |  |  | 0 | -16.17%
Total |  | 0 |  | 13491.6877 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
09:07 | 10:36 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to Due to Maintenance in Kish
SS end and from Kishoreganj 132/33kVend.
09:08 | 11:23 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Forced S/D from BIPTC end.
09:21 | 09:30 | Mongla 132/33kV S/S T-2 LT Scheduled S/D Due to Ordered by ALDC |  |  |  |  | 24.0MW load interrup.
| 09:23 | Bagerhat-Goalpara 132 kV Ckt-1 is restored.
| 09:24 | Bagerhat 132/33kV S/S 132 kV BUS is restored.
| 09:27 | Bagerhat-Mongla 132 kV Ckt-1 is restored.
| 09:30 | Mongla 132/33kV S/S T-1 LT is restored.
| 09:37 | Bagerhat-Mongla 132 kV Ckt-2 is restored.
| 09:38 | Mongla 132/33kV S/S 100MW ERBL Solar PS is restored.
10:01 | 15:40 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to SPMD Relay Testing.
10:02 | 15:02 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to SPMD Relay Testing
10:05 | 11:35 | BIPTC S/S Baharampur-1 Forced S/D
| 10:36 | Kishoreganj-Mymensingh 132kV Ckt-1 is restored.
12:00 |  | Day peak generation 11579 MW
12:27 | 13:08 | BIPTC S/S 10CF13 Scheduled S/D Due to None
14:16 | 14:55 | Bogura 230/132kV S/S T-01 LT Scheduled S/D Due to Auxuliary Transformer oil Filling.
14:16 | 14:55 | Bogura 230/132kV S/S T-01 HT Scheduled S/D Due to Auxuliary Transformer oil Filling.
15:06 | 15:55 | BIPTC S/S 20DF11 Scheduled S/D Due to Schedule Shutdown (Weeds and bushes cleaning)
16:07 | 16:40 | BIPTC S/S 20DF12 Scheduled S/D Due to Schedule shutdown( Weeds and bushes cleaning)
| 17:50 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt is restored.
18:36 |  | Aminbazar 400/230kV, 520MVA ATR-01 was switched on (loaded).
19:30 |  | Evening Peak Generation = 12,477MW and Loadshed = 0MW
20:07 | 20:23 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Tripped showing Over current relays Due to 33 kv Zinzira ckt-3 fault |  |  |  |  | 17.0MW load interrup.
20:07 | 20:23 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Tripped showing Over current relays Due to 33 kv Zinzira ckt-3 fault |  |  |  |  | 17.0MW load interrup.
01:03 |  | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D Due to Ordered by NLDC
07:00 |  | Minimum Generation is 9747 MW
07:23 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Project Work S/D Due to 33kV on 33kV Busbar by Ozopadiko Jhenaidah-2
"Kaliganj And new isolator connection work of 33KV Butyl feeder. "
07:23 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Project Work S/D Due to 33kV on 33kV Busbar by Ozopadiko Jhenaidah-2 |  |  |  |  | 50.0MW load interrup.
"Kaliganj And new isolator connection work of 33KV Butyl feeder. "
07:38 |  | Faridpur 132/33kV S/S Transformer-2 HT Forced S/D Due to Section bus Red hot |  |  |  |  | 30.0MW load interrup.
07:38 |  | Faridpur 132/33kV S/S Transformer-2 LT Forced S/D Due to Section bus red-hot |  |  |  |  | 30.0MW load interrup.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-09-26
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 350 | 9626400 | frequency control
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8649500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 285 | 6949178 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 152797 | Low Demand D/T Bad weather
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 43000 | Reserve NENP
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 66 | 446976 | Low Demand D/T Bad weather
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 415080
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 1202880 | Low Demand D/T Bad weather
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 245515 | Low Demand D/T Bad weather
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 285869 | Low Demand D/T Bad weather
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 29 | 764760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 809600
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 10 | 247400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 314400 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 95 | 1116545 | Low Demand D/T Bad weather
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1754640 | Low Demand D/T Bad weather
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 848640 | Low Demand D/T Bad weather
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 50 | 613440 | Low Demand D/T Bad weather
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1169280 | Low Demand D/T Bad weather
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 65707
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 550800 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 1887 | 36272407
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 105120 | Low Demand D/T Bad weather
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 131490
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 43200 | Low Demand D/T Bad weather
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 214 | 11105853
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5263377
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 34 | 450799 | Low Demand D/T Bad weather
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 239136 | Low Demand D/T Bad weather
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 184337 | Low Demand D/T Bad weather
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 332160 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 532320
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 43 | 285120 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26281
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 50 | 466691 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 332818 | Low Demand D/T Bad weather
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 68 | 754400 | Low Demand D/T Bad weather
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 273600 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 309873 | Low Demand D/T Bad weather
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 35 | 234181 | Low Demand D/T Bad weather
60 | SS Power I |  | SS Power | 2*612 | 1224 | 609 | 13499998 | Unit-2 S/D due to coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 424800
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 318 | 11898181 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1802 | 46893735
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 5280000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7694800
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 295 | 7585300 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 43 | 903384 | Engine problem
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 55 | 1283520
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 35 | 1923636 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1205547
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 40 | 207418 | Low Demand D/T Bad weather
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 165744 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 30 | 1051940 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 1573920 | Low Demand D/T Bad weather
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 50 | 1193280
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 225830 | Low Demand D/T Bad weather
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 415100 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 156180 | Low Demand D/T Bad weather
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 1823640 | Low Demand D/T Bad weather
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 1105920 | Engine problem
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 235227
| Cumilla Area Total |  |  |  | 2917 | 1563 | 34030386
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 0 | 72960 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 0
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 115 | 2546400 | Low Demand D/T Bad weather
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 92 | 1700400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 57750
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 231840 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 334080 | Low Demand D/T Bad weather
| Mymensingh Area Total |  |  |  | 646 | 242 | 4943430
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 28 | 669000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3677073 | frequency control
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 10 | 259200 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 342792 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 120960 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 913824
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 31 | 1286400
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 212 | 5238770 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 282480 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6904500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 365 | 8977000 | Machine problem.
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 346 | 8286500 | FGMO
| Sylhet Area Total |  |  |  | 2417 | 1486 | 36958499
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 890 | 21178909
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 214 | 5474304 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 158400 | Low Demand D/T Bad weather
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 87552 | Low Demand D/T Bad weather
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 52560
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 620 | 13825450 | Unit-1 Problem
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1756 | 40777175
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 33792 | Low Demand D/T Bad weather
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 9 | 184914 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 100 | 2659000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27302200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 180 | 5070760 | frequency control
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 4887000
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 1275
| Barisal Area Total |  |  |  | 2236 | 1840 | 40138941
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 160 | 4217364 | frequency control
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 320 | 8718254 | frequency control
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 2 | 59796 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 7901 | Reserve
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 33 | 112320 | Low Demand D/T Bad weather
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 97344 | Reserve
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 67968 | Reserve
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 8160
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1019 | 24417022
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 90750
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 218600
| Rajshahi Area Total |  |  |  | 3449 | 1534 | 38015479
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 66 | 1455272
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5576000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 317510 | Low Demand D/T Bad weather
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 5589
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 267840 | Low Demand D/T Bad weather
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 25976
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 190800
| Rangpur Area Total |  |  |  | 950 | 365 | 7838987
| Total |  |  |  | 27086 | 12475 | 285869039
| Eastern Grid Total |  |  |  | 16752 | 6980 | 159098457
| Western Grid Total |  |  |  | 10334 | 5495 | 126770582
| National Grid Total |  |  |  | 27086 | 12475 | 285869039
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-09-26
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9705.24 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4528.3 | MW
i) Dhaka area |  |  | 5276.04 |  | MW | i) Khulna area |  |  |  | 1720 | MW
ii) Chattogram area |  |  | 1334.2 |  | MW | ii) Barishal area |  |  |  | 449.5 | MW
iii) Cumilla area |  |  | 1393 |  | MW | iii) Rajshahi area |  |  |  | 1439.8 | MW
iv) Mymensingh area |  |  | 1105 |  | MW | iv) Rangpur area |  |  |  | 919 | MW
v) Sylhet area |  |  | 597 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14233.54 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 5 | 12:00 | 67 | Jamalpur | 86 | 18:30 | 133 | Rahim | 50 | 09:00
2 | AKSML | 11 | 12:00 | 68 | Jashore | 110 | 19:00 | 134 | Rajbari | 66 | 19:00
3 | Aftabnagar | 54 | 13:00 | 69 | Jhenaidah | 112 | 19:00 | 135 | Rajendrapur | 94 | 18:30
4 | Agargaon | 106 | 13:00 | 70 | Joydebpur | 190 | 18:00 | 136 | Rajshahi | 127 | 20:00
5 | Agrabad | 96 | 19:00 | 71 | Joypurhat | 49 | 00:00 | 137 | Rajshahi-230 | 59 | 13:00
6 | Amnura | 46 | 20:00 | 72 | Juldah | 17 | 23:00 | 138 | Ramganj | 104 | 21:00
7 | Ashuganj | 82 | 04:00 | 73 | KSRM | 24 | 15:00 | 139 | Rampur | 41 | 00:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 286 | 08:00 | 140 | Rangamati | 15 | 18:30
9 | BSRM | 112 | 02:00 | 75 | Kachua | 60 | 18:30 | 141 | Rangpur | 120 | 00:00
10 | Bagerhat | 60 | 00:00 | 76 | Kallyanpur | 93 | 00:00 | 142 | Ruppur | 6 | 09:00
11 | Bakulia | 101 | 18:30 | 77 | Kalurghat | 38 | 10:00 | 143 | SSM | 6 | 08:00
12 | Banani | 62 | 13:00 | 78 | Kamrangirchar | 59 | 13:00 | 144 | Saidpur | 88 | 18:30
13 | Bangabhaban | 18 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 92 | 19:00
14 | Barapukuria | 48 | 18:30 | 80 | Kazla | 103 | 13:00 | 146 | Satmasjid | 104 | 13:00
15 | Barguna | 18 | 00:00 | 81 | Keranigonj | 69 | 13:00 | 147 | Savar | 210 | 11:00
16 | Barishal | 98 | 22:00 | 82 | Khagrachori | 32 | 19:00 | 148 | SevenRings | 13 | 18:30
17 | Barishal-230 | 86 | 13:00 | 83 | Khulna | 83 | 13:00 | 149 | ShahCement | 30 | 03:00
18 | Baroaulia | 72 | 08:00 | 84 | Khulshi | 167 | 19:00 | 150 | Shahjadpur | 64 | 12:00
19 | Baroirhat | 66 | 21:00 | 85 | Kishoreganj | 140 | 00:00 | 151 | Shahjibazar | 123 | 22:00
20 | Bashundhara | 159 | 13:00 | 86 | Kodda | 312 | 18:00 | 152 | Shahmirpur | 54 | 00:00
21 | BashundharaCement | 1 | 00:00 | 87 | Kulaura | 40 | 18:00 | 153 | Shariatpur | 68 | 21:00
22 | Beanibazar | 68 | 21:00 | 88 | Kurigram | 50 | 00:00 | 154 | Sherpur | 102 | 19:30
23 | Benapole | 48 | 00:00 | 89 | Kushtia | 126 | 18:30 | 155 | Shikalbaha | 28 | 18:30
24 | Bhaluka | 124 | 15:00 | 90 | Lalbag | 85 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 46 | 00:00 | 91 | Lalmonirhat | 46 | 00:00 | 157 | Shitalakhya | 75 | 14:00
26 | Bhangura | 28 | 18:30 | 92 | MI_Cement | 11 | 13:00 | 158 | Sholosohor | 45 | 15:00
27 | Bheramara(GK) | 52 | 19:00 | 93 | Madanganj | 33 | 11:00 | 159 | Shyampur | 160 | 10:00
28 | Bhulta | 259 | 22:00 | 94 | Madaripur | 78 | 01:00 | 160 | Siddhirganj | 108 | 12:00
29 | Bog-Sherpur | 48 | 00:00 | 95 | Madartek | 70 | 00:00 | 161 | Sirajganj | 82 | 00:00
30 | Bogura | 129 | 18:30 | 96 | Madunaghat | 51 | 19:30 | 162 | Sonargaon | 90 | 10:00
31 | Borhanuddin | 78 | 21:00 | 97 | Magura | 55 | 18:30 | 163 | Sreemongol | 65 | 20:00
32 | Brahmanbaria | 148 | 00:00 | 98 | Mahasthangarh | 54 | 00:00 | 164 | Sreepur | 86 | 17:00
33 | Cantonment | 110 | 13:00 | 99 | Manikganj | 102 | 20:00 | 165 | Srinagar | 37 | 20:00
34 | Chandpur | 63 | 19:30 | 100 | Maniknagar | 76 | 13:00 | 166 | Sunamganj | 46 | 00:00
35 | Chandraghona | 40 | 18:30 | 101 | Matarbari | 47 | 18:30 | 167 | Sylhet | 42 | 23:00
36 | Chapai | 56 | 22:00 | 102 | Matuail | 53 | 11:00 | 168 | Sylhet-132 | 109 | 13:00
37 | Charsaidpur | 26 | 10:00 | 103 | Millgate | 118 | 15:00 | 169 | TK | 33 | 18:30
38 | Chauddagram | 60 | 19:30 | 104 | Mirpur | 131 | 13:00 | 170 | Tangail | 164 | 00:00
39 | Chhatak | 31 | 00:00 | 105 | Mirsorai | 5 | 18:00 | 171 | Thakurgaon | 74 | 00:00
40 | Chowmuhani | 201 | 18:30 | 106 | Mirzapur | 60 | 18:30 | 172 | Tongi | 130 | 12:00
41 | Chuadanga | 94 | 18:30 | 107 | Mithapukur | 44 | 00:00 | 173 | Ullahpara | 22 | 18:30
42 | Coxsbazar | 108 | 18:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 46 | 14:00
43 | Cumilla(N) | 153 | 21:00 | 109 | Mogbazar | 104 | 15:00 | 175 | Uttara | 76 | 14:00
44 | Cumilla(S) | 140 | 18:00 | 110 | Mongla | 36 | 00:00 | 176 | UttaraNew | 51 | 13:00
45 | Daudkandi | 135 | 20:00 | 111 | Motijheel | 34 | 12:00 | 177 | Zigatola | 90 | 13:00
46 | Dhaka | 36 | 13:00 | 112 | Munshiganj | 90 | 23:00
47 | Dhamrai | 134 | 15:00 | 113 | Mymensingh | 193 | 00:00
48 | Dhanmondi | 131 | 13:00 | 114 | Naogaon | 108 | 00:00
49 | Dohazari | 96 | 18:00 | 115 | Narail | 47 | 18:30
50 | Faridpur | 134 | 19:00 | 116 | Narinda | 70 | 13:00
51 | Fatullah | 105 | 12:00 | 117 | Narshingdi | 181 | 00:00
52 | Fenchuganj | 38 | 19:00 | 118 | Natore | 111 | 18:30
53 | Feni | 92 | 19:30 | 119 | Nawabganj | 39 | 21:00
54 | GPH | 80 | 20:00 | 120 | Netrakona | 109 | 18:30
55 | Ghatail | 50 | 00:00 | 121 | New | 52 | 12:00
56 | Ghorashal | 59 | 00:00 | 122 | Niamatpur | 50 | 00:00
57 | Goalpara | 34 | 21:00 | 123 | Noapara | 37 | 19:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-09-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 387 | 05:00 | 375 | 11:00 | Kaliakoir | 375 | 18:30 | 359 | 12:00
| Ashuganj | 404 | 6:00 | 392 | 12:00 | Madunaghat | 400 | 19:30 | 391 | 13:00
| Bhulta | 398 | 05:00 | 384 | 12:00 | Meghnaghat | 383 | 19:00 | 370 | 12:00
| Bibiana | 396 | 18:00 | 380 | 14:00 | Payra | 411 | 06:00 | 404 | 13:00
| BIPTC | 402 | 03:00 | 394 | 13:00 | Rahanpur | 404 | 17:00 | 398 | 23:00
| Bogura | 393 | 19:00 | 385 | 13:00 | Rampal | 403 | 06:00 | 390 | 13:00
| Gopalganj | 399 | 06:00 | 387 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 230 | 19:00 | 221 | 10:00 | Haripur | 232 | 19:00 | 221 | 12:00
| AKSML | 240 | 19:00 | 231 | 10:00 | Hasnabad | 230 | 19:00 | 218 | 18:00
| Aminbazar | 230 | 05:00 | 220 | 12:00 | Hathazari | 240 | 19:00 | 234 | 11:00
| Ashuganj | 234 | 18:30 | 226 | 12:00 | Ishurdi | 236 | 06:00 | 229 | 22:00
| Ashuganj-400 | 232 | 18:00 | 222 | 11:00 | Jhenaidah | 230 | 06:00 | 221 | 22:00
| Baghabari | 232 | 05:00 | 220 | 18:00 | Kaliakoir | 234 | 18:30 | 221 | 12:00
| Barapukuria | 221 | 16:00 | 217 | 01:00 | Keranigonj | 230 | 19:00 | 220 | 11:00
| Barapukuria-230 | 220 | 5:00 | 215 | 1:00 | Khulna(S) | 232 | 06:00 | 222 | 22:00
| Barishal | 236 | 05:00 | 230 | 13:00 | Madunaghat | 241 | 20:00 | 234 | 12:00
| Bheramara | 234 | 04:00 | 227 | 22:00 | Maniknagar | 232 | 19:00 | 220 | 12:00
| Bhulta | 233 | 19:00 | 222 | 12:00 | Meghnaghat | 240 | 04:00 | 230 | 12:00
| Bibiana | 226 | 19:00 | 220 | 12:00 | Meghnaghat-400 | 234 | 19:30 | 226 | 10:00
| BIPTC | 236 | 05:00 | 226 | 22:00 | Mirsorai | 240 | 19:00 | 228 | 12:00
| Bogura | 229 | 09:00 | 226 | 12:00 | Rajshahi | 236 | 06:00 | 226 | 22:00
| Bogura-400 | 232 | 19:00 | 227 | 02:00 | Rampal | 231 | 06:00 | 222 | 12:00
| Borhanuddin | 241 | 08:00 | 235 | 17:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 238 | 19:00 | 228 | 11:00 | Rampura | 231 | 19:00 | 221 | 12:00
| Cumilla(N) | 231 | 19:00 | 221 | 12:00 | Shikalbaha | 239 | 18:30 | 231 | 11:00
| Faridpur | 235 | 06:00 | 229 | 11:00 | Shyampur | 232 | 19:00 | 223 | 10:00
| Fenchuganj | 229 | 18:30 | 222 | 07:00 | Siddhirganj | 233 | 19:00 | 222 | 12:00
| Ghorashal | 235 | 00:00 | 230 | 07:00 | Sirajgonj | 237 | 04:00 | 233 | 12:00
| Ghorashal-230 | 231 | 19:00 | 220 | 12:00 | Sreepur | 230 | 19:00 | 224 | 11:00
| Gopalganj | 236 | 06:00 | 229 | 12:00 | Tongi | 232 | 18:30 | 218 | 10:00
| GPH | 238 | 19:00 | 230 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 136 | 04:00 | 128 | 11:00 | Kushtia | 136 | 09:00 | 131 | 23:00
| Agargaon | 135 | 04:00 | 129 | 11:00 | Lalbag | 133 | 04:00 | 127 | 12:00
| Agrabad | 136 | 19:00 | 130 | 10:00 | Lalmonirhat | 130 | 19:00 | 124 | 02:00
| AKS | 133 | 04:00 | 130 | 08:00 | Madanganj | 132 | 19:00 | 123 | 11:00
| Aminbazar | 139 | 05:00 | 129 | 11:00 | Madaripur | 132 | 06:00 | 130 | 00:00
| Amnura | 136 | 00:00 | 130 | 00:00 | Madartek | 135 | 19:00 | 127 | 12:00
| Ashuganj | 139 | 19:00 | 135 | 10:00 | Madunaghat | 137 | 19:30 | 132 | 13:00
| Bagerhat | 137 | 06:00 | 126 | 22:00 | Magura | 137 | 06:00 | 131 | 18:30
| Bakulia | 136 | 18:30 | 131 | 11:00 | Mahasthangarh | 136 | 18:30 | 132 | 02:00
| Banani | 135 | 04:00 | 126 | 13:00 | Manikganj | 127 | 18:30 | 118 | 12:00
| Bangabhaban | 138 | 00:00 | 123 | 11:00 | Maniknagar | 131 | 19:00 | 122 | 12:00
| Barapukuria | 138 | 18:30 | 133 | 01:00 | Matarbari | 125 | 14:00 | 119 | 20:00
| Barguna | 135 | 09:00 | 131 | 00:00 | Matuail | 132 | 19:00 | 124 | 12:00
| Barishal | 133 | 06:00 | 128 | 23:00 | Millgate | 134 | 19:00 | 124 | 11:00
| Barishal-230 | 134 | 07:00 | 130 | 12:00 | Mirpur | 137 | 18:30 | 130 | 11:00
| Baroaulia | 137 | 18:30 | 132 | 05:00 | Mirzapur | 128 | 19:00 | 123 | 01:00
| Baroirhat | 128 | 18:30 | 119 | 00:00 | Mithapukur | 133 | 18:30 | 127 | 03:00
| Bashundhara | 135 | 18:30 | 123 | 10:00 | MI_Cement | 134 | 01:00 | 127 | 13:00
| BashundharaCement | 132 | 19:00 | 123 | 11:00 | Modern | 136 | 18:30 | 131 | 11:00
| Beanibazar | 126 | 07:00 | 122 | 20:00 | Mogbazar | 136 | 21:00 | 128 | 11:00
| Benapole | 134 | 06:00 | 126 | 22:00 | Mongla | 135 | 06:00 | 124 | 18:30
| Bhaluka | 137 | 07:00 | 124 | 10:00 | Motijheel | 131 | 19:00 | 123 | 11:00
| Bhandaria | 130 | 09:00 | 124 | 00:00 | Munshiganj | 132 | 18:30 | 123 | 11:00
| Bhangura | 138 | 05:00 | 134 | 12:00 | Mymensingh | 136 | 09:00 | 121 | 00:00
| Bheramara | 137 | 06:00 | 133 | 13:00 | Naogaon | 134 | 09:00 | 130 | 00:00
| Bheramara(GK) | 137 | 06:00 | 133 | 13:00 | Narail | 137 | 06:00 | 131 | 21:00
| Bhulta | 123 | 19:00 | 116 | 12:00 | Narinda | 131 | 19:00 | 122 | 12:00
| Bog-Sherpur | 136 | 06:00 | 132 | 11:00 | Narshingdi | 124 | 06:00 | 117 | 01:00
| Bogura | 137 | 06:00 | 135 | 12:00 | Natore | 136 | 06:00 | 132 | 19:00
| Bogura-230 | 138 | 09:00 | 135 | 12:00 | Nawabganj | 134 | 06:00 | 127 | 12:00
| Brahmanbaria | 128 | 17:00 | 124 | 00:00 | Netrakona | 135 | 17:00 | 126 | 01:00
| Cantonment | 135 | 06:00 | 128 | 12:00 | New | 133 | 19:30 | 125 | 11:00
| Chandpur | 135 | 18:30 | 121 | 03:00 | Niamatpur | 136 | 09:00 | 133 | 00:00
| Chandraghona | 137 | 19:00 | 133 | 11:00 | Noapara | 136 | 05:00 | 129 | 22:00
| Chapai | 135 | 17:00 | 131 | 00:00 | Pabna | 137 | 06:00 | 132 | 00:00
| Charsaidpur | 133 | 18:30 | 123 | 12:00 | Palashbari | 133 | 18:30 | 129 | 11:00
| Chauddagram | 130 | 19:00 | 121 | 00:00 | Panchagarh | 137 | 18:30 | 125 | 02:00
| Chhatak | 127 | 06:00 | 122 | 22:00 | Patuakhali | 134 | 06:00 | 132 | 00:00
| Chowmuhani | 127 | 23:00 | 119 | 02:00 | Payra | 137 | 07:00 | 133 | 22:00
| Chuadanga | 132 | 06:00 | 124 | 22:00 | PHP | 129 | 19:00 | 120 | 00:00
| Coxsbazar | 125 | 13:00 | 117 | 22:00 | Postogola | 136 | 03:00 | 128 | 12:00
| Cumilla(N) | 133 | 18:30 | 126 | 11:00 | Purbachal | 135 | 03:00 | 124 | 10:00
| Cumilla(S) | 132 | 19:00 | 124 | 10:00 | Purbasadipur | 132 | 18:30 | 124 | 08:00
| Daudkandi | 129 | 19:00 | 121 | 11:00 | Rahanpur | 137 | 06:00 | 135 | 00:00
| Dhaka | 135 | 04:00 | 127 | 12:00 | Rahim | 132 | 19:00 | 125 | 11:00
| Dhamrai | 132 | 19:00 | 124 | 10:00 | Rajbari | 131 | 06:00 | 126 | 12:00
| Dhanmondi | 135 | 22:00 | 128 | 12:00 | Rajendrapur | 129 | 19:00 | 117 | 13:00
| Dohazari | 132 | 18:30 | 127 | 11:00 | Rajshahi | 135 | 06:00 | 130 | 23:00
| Faridpur | 132 | 05:00 | 128 | 12:00 | Rajshahi-230 | 136 | 06:00 | 126 | 12:00
| Fatullah | 135 | 19:00 | 128 | 12:00 | Ramganj | 129 | 19:00 | 118 | 00:00
| Fenchuganj | 134 | 19:00 | 131 | 01:00 | Rampur | 135 | 05:00 | 129 | 11:00
| Feni | 129 | 18:30 | 120 | 01:00 | Rampura | 134 | 04:00 | 128 | 11:00
| Ghatail | 132 | 09:00 | 121 | 01:00 | Rangamati | 136 | 19:00 | 132 | 10:00
| Ghorashal | 137 | 19:00 | 131 | 08:00 | Rangpur | 132 | 18:30 | 124 | 03:00
| Goalpara | 137 | 06:00 | 130 | 13:00 | Ruppur | 137 | 01:00 | 133 | 23:00
| Gollamari | 138 | 06:00 | 131 | 12:00 | Saidpur | 133 | 18:30 | 124 | 02:00
| Gopalganj | 134 | 06:00 | 129 | 22:00 | Satkhira | 138 | 17:00 | 128 | 22:00
| Gopalganj-400 | 133 | 05:00 | 129 | 12:00 | Satmasjid | 135 | 19:00 | 127 | 13:00
| Gulshan | 134 | 04:00 | 127 | 12:00 | Savar | 139 | 18:30 | 129 | 08:00
| Halishahar | 136 | 19:00 | 130 | 11:00 | SevenRings | 138 | 19:00 | 131 | 12:00
| Haripur | 132 | 19:00 | 125 | 11:00 | ShahCement | 133 | 18:30 | 123 | 12:00
| HaripurSBU | 132 | 19:00 | 125 | 11:00 | Shahjadpur | 142 | 04:00 | 136 | 12:00
| Hasnabad | 136 | 19:30 | 130 | 11:00 | Shahjibazar | 130 | 16:00 | 124 | 23:00
| Hathazari | 140 | 19:00 | 135 | 11:00 | Shahmirpur | 137 | 19:00 | 131 | 11:00
| Ishurdi | 139 | 06:00 | 134 | 23:00 | Shariatpur | 132 | 06:00 | 127 | 12:00
| Jaldhaka | 130 | 18:30 | 121 | 03:00 | Sherpur | 137 | 13:00 | 123 | 01:00
| Jamalpur | 140 | 09:00 | 125 | 01:00 | Shikalbaha | 126 | 18:30 | 120 | 10:00
| Jashore | 135 | 06:00 | 128 | 13:00 | Shikalbaha-230 | 137 | 18:30 | 132 | 09:00
| Jhenaidah | 137 | 05:00 | 131 | 22:00 | Shitalakhya | 134 | 01:00 | 127 | 13:00
| Jhenaidah-230 | 137 | 05:00 | 131 | 22:00 | Sholosohor | 136 | 19:00 | 131 | 10:00
| Joydebpur | 135 | 18:30 | 128 | 08:00 | Shyampur | 134 | 19:30 | 128 | 11:00
| Joypurhat | 134 | 09:00 | 129 | 00:00 | Shyampur-230 | 134 | 04:00 | 128 | 10:00
| Juldah | 135 | 22:00 | 133 | 04:00 | Siddhirganj | 132 | 18:30 | 125 | 11:00
| Kabirpur | 131 | 19:00 | 120 | 08:00 | Sirajganj | 134 | 01:00 | 131 | 11:00
| Kachua | 134 | 19:30 | 123 | 01:00 | Sonargaon | 131 | 19:00 | 123 | 08:00
| Kaliakoir | 133 | 04:00 | 124 | 12:00 | Sreemongol | 130 | 05:00 | 125 | 23:00
| Kallyanpur | 132 | 02:00 | 126 | 12:00 | Sreepur | 130 | 04:00 | 127 | 00:00
| Kalurghat | 137 | 18:30 | 132 | 13:00 | Srinagar | 134 | 19:00 | 126 | 12:00
| Kamrangirchar | 134 | 19:00 | 125 | 11:00 | SSM | 140 | 14:00 | 138 | 01:00
| Kaptai | 136 | 18:00 | 130 | 12:00 | Sunamganj | 125 | 07:00 | 122 | 12:00
| Kazla | 130 | 04:00 | 121 | 13:00 | Sylhet | 128 | 05:00 | 125 | 23:00
| Keranigonj | 134 | 06:00 | 128 | 11:00 | Sylhet-132 | 128 | 05:00 | 126 | 00:00
| Khagrachori | 135 | 19:00 | 131 | 11:00 | Tangail | 128 | 05:00 | 124 | 08:00
| Khulna | 137 | 06:00 | 131 | 12:00 | Thakurgaon | 136 | 18:30 | 122 | 02:00
| Khulna(S) | 139 | 06:00 | 132 | 13:00 | TK | 137 | 18:30 | 132 | 11:00
| Khulshi | 135 | 19:00 | 129 | 11:00 | Tongi | 134 | 04:00 | 127 | 10:00
| Kishoreganj | 130 | 05:00 | 127 | 00:00 | Ullahpara | 137 | 02:00 | 133 | 12:00
| Kodda | 132 | 18:30 | 118 | 12:00 | Ullon | 135 | 19:00 | 125 | 06:00
| KSRM | 137 | 19:30 | 132 | 10:00 | Uttara | 138 | 19:00 | 129 | 12:00
| Kulaura | 132 | 08:00 | 130 | 00:00 | UttaraNew | 137 | 19:00 | 131 | 11:00
| Kurigram | 130 | 09:00 | 126 | 07:00 | Zigatola | 134 | 19:00 | 128 | 11:00

## L-Curve
Date | 2024-09-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1274 | 6175 | 5457 | 11632 |  |  |  | QF-LDC-11
0:30 | 1206 | 6253 | 5448.5 | 11701.5 | Date: | 2024-09-26
1:00 | 1138 | 6331 | 5440 | 11771
1:30 | 1113 | 6246.5 | 5311.5 | 11558
2:00 | 1088 | 6162 | 5183 | 11345
2:30 | 1111 | 6078 | 5115 | 11193 | [5 empty] | Gen. at Eve. Peak | 12475 | 12475 MW (19:30 )
3:00 | 1134 | 5994 | 5047 | 11041 | [6 empty] | 19:30
3:30 | 1153 | 5975 | 4978 | 10953 | [5 empty] | Gen. at Day Peak | 11579 | 11579 MW (12:00 )
4:00 | 1172 | 5956 | 4909 | 10865 | [6 empty] | 12:00
4:30 | 1213 | 5955.5 | 4813.5 | 10769 | [5 empty] | Highest Generation | 12475
5:00 | 1254 | 5955 | 4718 | 10673 | [6 empty] | 19:30
5:30 | 1297 | 5845.5 | 4676.5 | 10522
6:00 | 1340 | 5736 | 4635 | 10371
6:30 | 1282 | 5822.5 | 4604 | 10426.5
7:00 | 1224 | 5909 | 4573 | 10482
7:30 | 1233 | 5912 | 4647 | 10559
8:00 | 1242 | 5915 | 4721 | 10636
8:30 | 1346 | 5944.5 | 4837.5 | 10782
9:00 | 1450 | 5974 | 4954 | 10928
9:30 | 1463 | 6055 | 4967 | 11022
10:00 | 1476 | 6136 | 4980 | 11116
10:30 | 1474 | 6198 | 5039 | 11237
11:00 | 1472 | 6260 | 5098 | 11358
11:30 | 1427 | 6279 | 5189.5 | 11468.5
12:00 | 1382 | 6298 | 5281 | 11579
12:30 | 1363 | 6366.5 | 5369.5 | 11736
13:00 | 1344 | 6435 | 5458 | 11893
13:30 | 1314 | 6402 | 5293.5 | 11695.5
14:00 | 1284 | 6369 | 5129 | 11498
14:30 | 1342 | 6425 | 5154.5 | 11579.5
15:00 | 1400 | 6481 | 5180 | 11661
15:30 | 1325 | 6389.5 | 4996 | 11385.5
16:00 | 1250 | 6298 | 4812 | 11110
16:30 | 1237 | 6311 | 4811 | 11122
17:00 | 1224 | 6324 | 4810 | 11134
17:30 | 1196 | 6467.5 | 5056.5 | 11524
18:00 | 1168 | 6611 | 5303 | 11914
18:30 | 1049 | 6780 | 5409 | 12189
19:00 | 930 | 6949 | 5515 | 12464
19:30 | 968 | 6980 | 5495 | 12475
20:00 | 990 | 6976 | 5487 | 12463 |  |  |  | Executive Engineer
20:30 | 999 | 6874.5 | 5474 | 12348.5 |  |  |  | Network Operation Division
21:00 | 1008 | 6773 | 5461 | 12234
21:30 | 1083 | 6656.5 | 5480 | 12136.5
22:00 | 1158 | 6540 | 5499 | 12039 |  |  |  |  | Page 6 of 7
22:30 | 1200 | 6469.5 | 5493 | 11962.5
23:00 | 1242 | 6399 | 5487 | 11886
23:30 | 1258 | 6287 | 5472 | 11759
24:00 | 1274 | 6175 | 5457 | 11632
12475 MW (19:30 )
11579 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-09-26 |  | Energy |  | 285869039
[16 empty] | 2024-09-26 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3092 | 891 | 1825 | 0 | 988 | 3383 | 212 | 0 | 87 | 56 | 1093 | 0 | 5 | 17
0:30 | 3077.5 | 889 | 1940.5 | 0 | 950.5 | 3426 | 212.5 | 0 | 84.5 | 55 | 1051 | 0 | 15 | 75 |  |  | Date: | 44099
1:00 | 3063 | 887 | 2056 | 0 | 913 | 3469 | 213 | 0 | 82 | 54 | 1009 | 0 | 25 | 133
1:30 | 3063.5 | 887 | 2038.5 | 0 | 725 | 3459.5 | 213.5 | 0 | 82 | 53 | 1010 | 0 | 26 | 116.6375 | [8 empty] | Total Energy | 285.869 | 285.869 | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 3064 | 887 | 2021 | 0 | 537 | 3450 | 214 | 0 | 82 | 52 | 1011 | 0 | 27 | 100.275 | [8 empty] | Energy not Served | 0.68175 | 0.68175
2:30 | 3074 | 887 | 2058.5 | 0 | 472.5 | 3335 | 214 | 0 | 57 | 51 | 1012 | 0 | 32 | 75.9225 | [8 empty] | Energy Requirement | 286.5508 | 286.5508
3:00 | 3084 | 887 | 2096 | 0 | 408 | 3220 | 214 | 0 | 32 | 50 | 1013 | 0 | 37 | 51.57
3:30 | 3078 | 886.5 | 2088.5 | 0 | 402.5 | 3154.5 | 214 | 0 | 32 | 50 | 1010 | 0 | 37 | 52.0475 | [7 empty] | Shortage
4:00 | 3072 | 886 | 2081 | 0 | 397 | 3089 | 214 | 0 | 32 | 50 | 1007 | 0 | 37 | 52.525
4:30 | 3134 | 886 | 2093 | 0 | 380 | 2935 | 214 | 0 | 32 | 50 | 1011.5 | 0 | 33.5 | 51.0925
5:00 | 3196 | 886 | 2105 | 0 | 363 | 2781 | 214 | 0 | 32 | 50 | 1016 | 0 | 30 | 49.66
5:30 | 3148.5 | 886 | 2040.5 | 0 | 351 | 2768 | 214 | 0 | 32 | 48 | 1011.5 | 1 | 21.5 | 48.2275
6:00 | 3101 | 886 | 1976 | 0 | 339 | 2755 | 214 | 0 | 32 | 46 | 1007 | 2 | 13 | 46.795
6:30 | 3133 | 886.5 | 1972 | 0 | 364 | 2738 | 213.5 | 0 | 32 | 45 | 1007.5 | 24.5 | 10.5 | 23.3975 | [6 empty] | Coal
7:00 | 3165 | 887 | 1968 | 0 | 389 | 2721 | 213 | 0 | 32 | 44 | 1008 | 47 | 8 | 0
7:30 | 3182 | 887 | 1970 | 0 | 387.5 | 2773.5 | 212.5 | 0 | 32 | 44 | 1009 | 52.5 | 9 | 0 | [5 empty] | Oil
8:00 | 3199 | 887 | 1972 | 0 | 386 | 2826 | 212 | 0 | 32 | 44 | 1010 | 58 | 10 | 0
8:30 | 3174 | 887 | 1966 | 0 | 420 | 2948 | 211.5 | 0 | 32 | 44 | 1009 | 75 | 15.5 | 0
9:00 | 3149 | 887 | 1960 | 0 | 454 | 3070 | 211 | 0 | 32 | 44 | 1008 | 92 | 21 | 0
9:30 | 3158.5 | 887 | 1952.5 | 0 | 523.5 | 3079.5 | 211.5 | 0 | 32 | 46 | 1007 | 104.5 | 20 | 25.785
10:00 | 3168 | 887 | 1945 | 0 | 593 | 3089 | 212 | 0 | 32 | 48 | 1006 | 117 | 19 | 51.57
10:30 | 3198 | 887 | 1957 | 0 | 617.5 | 3133.5 | 212 | 0 | 32 | 48 | 1007.5 | 128.5 | 16 | 45.84
11:00 | 3228 | 887 | 1969 | 0 | 642 | 3178 | 212 | 0 | 32 | 48 | 1009 | 140 | 13 | 40.11
11:30 | 3222.5 | 886.5 | 2005 | 0 | 685.5 | 3229.5 | 212 | 0 | 24 | 48 | 1008.5 | 136.5 | 10.5 | 39.6325
12:00 | 3217 | 886 | 2041 | 0 | 729 | 3281 | 212 | 0 | 16 | 48 | 1008 | 133 | 8 | 39.155
12:30 | 3213 | 886.5 | 2040.5 | 0 | 791 | 3340.5 | 212 | 0 | 32.5 | 47 | 1013 | 140.5 | 19.5 | 35.0775
13:00 | 3209 | 887 | 2040 | 0 | 853 | 3400 | 212 | 0 | 49 | 46 | 1018 | 148 | 31 | 31
13:30 | 3209 | 887 | 2040 | 0 | 853 | 3400 | 212 | 0 | 49 | 46 | 1018 | 148 | 31 | 31
14:00 | 3209 | 887 | 2040 | 0 | 853 | 3400 | 212 | 0 | 49 | 46 | 1018 | 148 | 31 | 31
14:30 | 3176.5 | 887 | 2020.5 | 0 | 954 | 3240 | 212.5 | 0 | 57 | 47 | 1018 | 133.5 | 31 | 15.5
15:00 | 3144 | 887 | 2001 | 0 | 1055 | 3080 | 213 | 0 | 65 | 48 | 1018 | 119 | 31 | 0
15:30 | 3130 | 889.5 | 1965.5 | 0 | 1000 | 2981 | 213 | 0 | 65 | 49 | 974 | 91.5 | 27 | 0
16:00 | 3116 | 892 | 1930 | 0 | 945 | 2882 | 213 | 0 | 65 | 50 | 930 | 64 | 23 | 0
16:30 | 3100.5 | 891.5 | 1939 | 0 | 993.5 | 2880.5 | 213.5 | 0 | 65 | 53 | 924.5 | 40.5 | 20.5 | 0
17:00 | 3085 | 891 | 1948 | 0 | 1042 | 2879 | 214 | 0 | 65 | 56 | 919 | 17 | 18 | 0
17:30 | 3130.5 | 891.5 | 1952 | 0 | 1196.5 | 2973.5 | 214 | 0 | 117.5 | 61 | 967.5 | 8.5 | 11.5 | 0
18:00 | 3176 | 892 | 1956 | 0 | 1351 | 3068 | 214 | 0 | 170 | 66 | 1016 | 0 | 5 | 0
18:30 | 3085.5 | 891 | 1865.5 | 0 | 1640.5 | 3215.5 | 214 | 0 | 201 | 57 | 1015.5 | 0 | 3.5 | 0
19:00 | 2995 | 890 | 1775 | 0 | 1930 | 3363 | 214 | 0 | 232 | 48 | 1015 | 0 | 2 | 0
19:30 | 3038 | 890 | 1814 | 0 | 1788 | 3394 | 214 | 0 | 268 | 50 | 1019 | 0 | 0 | 0
20:00 | 3091 | 889 | 1825 | 0 | 1711 | 3387 | 214 | 0 | 277 | 50 | 1016 | 0 | 3 | 0
20:30 | 3080.5 | 889.5 | 1825 | 0 | 1628 | 3386 | 214 | 0 | 252.5 | 51 | 1017 | 0 | 5 | 10
21:00 | 3070 | 890 | 1825 | 0 | 1545 | 3385 | 214 | 0 | 228 | 52 | 1018 | 0 | 7 | 20
21:30 | 3073.5 | 890.5 | 1824.5 | 0 | 1428 | 3382.5 | 214 | 0 | 193.5 | 53 | 1071.5 | 0 | 5.5 | 20
22:00 | 3077 | 891 | 1824 | 0 | 1311 | 3380 | 214 | 0 | 159 | 54 | 1125 | 0 | 4 | 20
22:30 | 3084.5 | 890 | 1815 | 0 | 1232 | 3386 | 213 | 0 | 159 | 56 | 1124.5 | 0 | 2.5 | 19
23:00 | 3092 | 889 | 1806 | 0 | 1153 | 3392 | 212 | 0 | 159 | 58 | 1124 | 0 | 1 | 18
23:30 | 3092 | 890 | 1815.5 | 0 | 1070.5 | 3387.5 | 212 | 0 | 123 | 57 | 1108.5 | 0 | 3 | 17.5 |  |  | Max Temp. in Dhaka |  | 28.2°C
24:00 | 3092 | 891 | 1825 | 0 | 988 | 3383 | 212 | 0 | 87 | 56 | 1093 | 0 | 5 | 17
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on X13: Author:

## Generation
2024-09-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 133 | 134 | 134 | 134 | 134 | 134 | 133 | 132 | 131 | 132 | 132 | 132 | 132 | 133 | 133 | 133 | 134 | 134 |  | 134 | 134 | 134 | 134 | 134 | 132 | 132 | 9173853
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1932000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [13 empty] | 3 | 8 | 8 | 8 | 8 |  | 19 | 8 | 17 | 8 | 8 | 8 | 0 | 105120
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 5 | 14 | 20 | 20 | 7 | 10 | 13 | 11 | 5 | 1 | [9 empty] | 131490
6 | Sikalbaha 225MW CCPP (Gas) | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 226 | 222 | 222 | 222 | 220 | 220 | 220 | 218 | 218 | 219 | 220 |  | 224 | 225 | 225 | 223 | 223 | 223 | 223 | 5263377
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 |  | 184337
12 | Hathazari 100 MW peaking PP | [17 empty] | 3 |  | 32 | 40 | 39 | 39 | 39 | 39 | 39 | 239136
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | [6 empty] | 2 | 17 | 17 | 17 | 20 | 51 | 51 | 17 | 17 | 17 |  | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 450799
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [20 empty] | 28 | 38 | 38 | 38 | 38 |  | 165744
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 45 | [8 empty] | 5 | 30 | 42 | 45 | 58 | 60 | 60 | 60 | 90 |  | 145 | 95 | 95 | 95 | 45 | 45 | 45 | 1116545
19 | Ashuganj 195 MW PP (APSCL-United) | 108 | 108 | 108 | 108 | 108 | 108 | 78 | 78 | 78 | 78 | 78 | 78 | 97 | 97 | 97 | 97 | 97 | 53 |  | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 1923636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 612 | 550 | 551 | 450 | 450 | 450 | 500 | 550 | 551 | 551 | 550 | 578 | 599 | 595 | 554 | 551 | 580 |  | 604 | 609 | 606 | 605 | 612 | 612 | 604 | 13499998
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 37 | 38 | 32 | 30 | 32 | 30 | 34 | 38 | 36 | 40 | 40 | 39 | 39 |  | 41 | 43 | 43 | 43 | 42 | 42 | 40 | 903384
33 | Ashuganj 225 MW CCPP | 217 | 217 | 216 | 218 | 216 | 218 | 217 | 215 | 218 | 216 | 216 | 216 | 220 | 219 | 218 | 216 | 216 | 215 |  | 218 | 217 | 216 | 217 | 217 | 219 | 217 | 5280000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 295 | 285 | 320 | 285 | 345 | 330 | 310 | 325 | 325 | 325 | 310 | 285 | 310 | 335 | 325 | 330 |  | 285 | 285 | 305 | 285 | 280 | 285 | 285 | 7694800
| Ashuganj 420 MW CCPP(East) | 290 | 290 | 290 | 285 | 315 | 285 | 335 | 320 | 290 | 290 | 320 | 320 | 330 | 290 | 320 | 345 | 330 | 300 |  | 290 | 295 | 310 | 320 | 320 | 325 | 325 | 7585300
35 | Ashuganj 55 MW PP (Precision) | 54 | 54 | 54 | 55 | 55 | 55 | 55 | 55 | 55 | 52 | 50 | 50 | 51 | 53 | 51 | 51 | 52 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1283520
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 70 | 51 | 50 | 50 | 50 | 45 | 45 | 40 | 40 | 35 | 35 | 35 | 35 | 35 |  | 30 | 30 | 30 | 35 | 40 | 50 | 50 | 1051940
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 415 | 415 | 414 | 413 | 414 | 413 | 414 | 414 | 411 | 415 | 412 | 412 | 412 | 413 | 411 | 396 | 370 | 412 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 9626400
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8649500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 0 | 0 | 12 | 12 | 12 | 18 | 12 | 11 | 5 | 3 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72960
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 2 | 1 | 8 | 8 | 10 | 7 | 3 | 9 | 3 | 0 | [9 empty] | 57750
44 | Fenchugonj CCPP Phase-1 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 669000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 31 | 31 | 32 | 32 | 32 | 32 | 31 | 31 | 32 | 31 | 30 | 30 | 31 | 31 | 32 | 31 | 31 | 60 |  | 62 | 62 | 55 | 55 | 55 | 56 | 55 | 913824
48 | Shahjibazar 86 MW PP (Shahjibazar) | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 1286400
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 212 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 211 | 212 | 211 | 212 | 209 | 209 | 208 | 210 | 210 | 209 |  | 212 | 212 | 212 | 212 | 211 | 211 | 211 | 5238770
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120960
55 | Fenchugonj 51 MW PP (Barakatullah) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 259200
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 282480
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 290 | 285 | 290 | 285 | 290 | 295 | 285 | 280 | 280 | 285 | 290 | 280 | 270 | 285 | 275 | 285 | 290 |  | 280 | 285 | 275 | 280 | 285 | 285 | 280 | 6904500
| Bibiyana South 400 MW | 316 | 316 | 316 | 316 | 346 | 316 | 316 | 346 | 346 | 346 | 353 | 346 | 346 | 325 | 346 | 346 | 346 | 346 |  | 325 | 346 | 370 | 346 | 346 | 346 | 346 | 8286500
58 | Nababganj 55 MW PP (Southern power ) | [13 empty] | 17 | 17 | 13 | 17 | 22 |  | 35 | 35 | 35 | 35 | 35 | 17 | 35 | 285869
59 | Tangail Palli Power Gen 22 MW | 6 | 5 | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 |  | 11 | 18 | 18 | 19 | 24 | 24 | 24 | 231840
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 54 | 52 | 50 | 50 | 50 | 46 | 44 | 44 | 44 | 48 | 48 | 48 | 46 | 48 | 48 | 50 | 56 | 66 |  | 48 | 50 | 50 | 52 | 54 | 58 | 56 | 1193280
64 | Malancha, Ctg. EPZ (United) | 32 | 36 | 37 | 37 | 39 | 38 | 37 | 9 | 4 | 4 | 6 | 6 | 10 | 8 | 3 | 3 | 11 | 15 |  | 20 | 23 | 23 | 32 | 34 | 36 | 37 | 532320
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 415100
69 | Summit Ashulia | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 13 | 13 | 13 |  |  |  | 10 | 14 |  |  | 15 | 15 | 15 | 15 | 15 | 15 | 309000
70 | Summit Madhabdi | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 14 | 18 | 21 | 17 | 14 | 20 | 20 | 20 | 20 | 15 |  | 14 | 14 | 14 | 20 | 20 | 20 | 20 | 455760
71 | Maona 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 25 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 809600
72 | Rupganj 33 MW PP(Summit) | 10 | 11 | 10 | 11 | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 247400
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [17 empty] | 23 |  | 34 | 34 | 26 | 17 | 17 | 17 | 17 | 156180
| Chowmuhani 113 MW | 97 | 87 | 79 | 85 | 86 | 63 | 63 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 58 |  | 84 | 95 | 94 | 99 | 105 | 105 | 105 | 1823640
| Manikgonj 162MW PP(MPGL) | 17 | 17 | [6 empty] | 17 | 35 | 35 | 54 | 72 | 90 | 90 | 90 | 90 | 120 |  | 150 | 108 | 54 | 54 | 54 | 54 | 54 | 1169280
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 3 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 |  | 25 | 25 | 25 | 25 | 25 | 17 | 8 | 314400
79 | Kodda 150 MW PP | 82 | 82 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 32 | 32 | 48 | 48 | 48 | 98 |  | 98 | 98 | 98 | 82 | 48 | 48 | 48 | 1202880
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | [12 empty] | 8 | 8 | 8 | 8 | 9 |  | 36 | 25 | 25 | 25 | 25 | 25 | 25 | 225830
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 52 | 52 |  | 70 | 70 | 50 | 52 | 52 | 52 | 17 | 848640
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 3 | 2 | 2 | 2 | 4 | 3 | 1 | 0 | [9 empty] | 26281
| Jodiac Power | [8 empty] | 2 | 17 | 17 | 17 | 19 | 35 | 35 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 332818
| Karnaphuli Power Ltd. | 51 | 17 | [7 empty] | 15 | 17 | 20 | 34 | 42 | 51 | 34 | 34 | 36 |  | 60 | 68 | 68 | 34 | 34 | 34 | 34 | 754400
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 43000
86 | Meghnaghat CCPP ( Summit) | 282 | 280 | 293 | 273 | 300 | 275 | 294 | 298 | 253 | 274 | 294 | 295 | 248 | 273 | 274 | 304 | 302 | 300 |  | 254 | 285 | 306 | 290 | 282 | 262 | 285 | 6949178
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | [7 empty] | 16 | 16 | 25 | 33 | 50 | 50 | 50 | 50 | 50 |  | 48 | 50 | 50 | 50 | 50 | 31 | 17 | 613440
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 342792
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1205547
94 | Gagnagar 102 MW PP (Digital Power) | 25 | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 40 |  | 66 | 66 | 66 | 65 | 40 | 40 | 40 | 446976
95 | Patenga 50MW PP (Baraka) | [19 empty] | 14 | 6 | 6 | 6 | 6 | 6 | 0 | 43200
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 2 | 21 | 25 | 25 | 25 |  | 43 | 43 | 37 | 22 | 24 | 25 | 0 | 285120
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | [18 empty] | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 152797
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 17 | 17 | 17 | 17 |  | 0 | 245515
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 163 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3677073
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 0 | 0 | 0 | [9 empty] | 0
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 17 |  | 0 | 415080
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 96 | 96 | 96 | 96 | 96 | 124 | 125 | 125 | 95 | 95 | 95 | 95 | 85 | 105 | 105 | 96 | 122 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2546400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 58 | 35 | 34 | 35 | 35 | 34 | 35 | 36 | 40 | 79 | 80 | 80 | 80 | 80 | 80 | 86 | 97 | 97 |  | 110 | 115 | 116 | 110 | 98 | 97 | 98 | 1754640
115 | Juldah 100 MW PP Unit-3 (Acorn) | [11 empty] | 4 | 18 | 25 | 25 | 25 | 37 | 32 |  | 25 | 37 | 37 | 37 | 37 | 25 | 0 | 332160
116 | Chandpur 200 MW (Desh energy) | 51 | 51 | 51 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 51 | 51 | 51 | 51 | 51 | 51 | 63 |  | 167 | 170 | 170 | 136 | 100 | 100 | 100 | 1573920
117 | Ashuganj 150 MW PP (Midland) | [16 empty] | 3 | 23 |  | 80 | 40 | 40 | 10 | 10 | 10 | 0 | 207418
118 | Bibiyana-III 400 MW CCPP | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 348 | 359 | 360 | 361 | 366 | 365 | 370 | 370 | 367 | 368 | 367 |  | 365 | 365 | 368 | 368 | 368 | 347 | 353 | 8977000
| Jamalpur 115 MW PP (United) | 55 | 55 | 55 | 55 | 55 | 55 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 74 |  | 92 | 92 | 92 | 92 | 73 | 73 | 73 | 1700400
| Anwara 300 MW PP (United) | 15 | 15 | [6 empty] | 15 | 15 | 15 | 15 | 50 | 50 | 50 | 15 | 15 | 23 |  | 50 | 50 | 50 | 15 | 15 | 15 | 15 | 466691
| Juldah unit-2 (Acorn) | [11 empty] | 12 | 24 | 24 | 24 | 12 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 273600
| Anlima Energy Ltd. | [8 empty] | 1 | 17 | 17 | 17 | 18 | 35 | 35 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 309873
| Bhairob 54.5 MW | 20 | 17 | 17 | 17 | [7 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 21 | 35 | 35 | 19 | 17 | 334080
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 3 | 12 | 4 | 13 | 7 | 2 | 10 | 9 | 2 | 3 | [9 empty] | 65707
| Chandpur 115(Doreen) | 40 | 40 | 40 | 35 | 34 | 34 | 34 | 34 | 34 | 35 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 48 |  | 54 | 92 | 90 | 92 | 91 | 74 | 48 | 1105920
| Kanchan Purbachal Power Generation Ltd. | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 550800
| Mirsharai 150 MW (Oil) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 |  |  | 0 | 234181
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 25 | 27 | 37 | 37 | 30 | 13 | 8 | 10 | 21 | 19 | 13 | 8 | 31 | 37 | 31 | 23 | 18 | 5 |  | 2 | 0 | 3 | 7 | 4 | 1 | 5 | 424800
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 24 | 30 | 15 | 24 | 39 | 34 | 22 | 16 | 16 | 12 | 4 | [9 empty] | 235227
| Matarbari 2*600 MW (CPGCL) | 617 | 620 | 622 | 621 | 623 | 618 | 622 | 621 | 618 | 621 | 620 | 619 | 573 | 406 | 372 | 320 | 315 | 316 |  | 317 | 318 | 317 | 316 | 316 | 316 | 315 | 11898181
Meghnaghat (Reliance) 718MW CCPP
120
121 | Eastern Zone Total | 6331 | 6162 | 5994 | 5956 | 5955 | 5736 | 5909 | 5915 | 5974 | 6136 | 6260 | 6298 | 6435 | 6369 | 6481 | 6298 | 6324 | 6611 |  | 6949 | 6980 | 6976 | 6773 | 6540 | 6399 | 6175 | 159098457
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | 53 | [15 empty] | 12 | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 158400
131 | Mongla Orion 100 MW Solar PP | [9 empty] | 1 | 3 | 12 | 2 | 1 | 6 | 14 | 4 | [9 empty] | 52560
132 | Rampal 1320 MW (BIFPCL) | 627 | 624 | 566 | 513 | 464 | 465 | 467 | 463 | 510 | 505 | 555 | 561 | 618 | 618 | 631 | 566 | 571 | 596 |  | 620 | 620 | 618 | 618 | 606 | 618 | 618 | 13825450
133 | United Payra Power Ltd. | [25 empty] | 0 | 0
| Bhola Nutan Biddut BD LTD (GAS) | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 220 | 180 | 180 | 220 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 5070760
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | [5 empty] | 0 | 33792
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 221 | 200 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 180 | 180 | 150 | 150 | 150 | 150 | 241 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 4887000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 1275
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 127 | 127 | 127 | 134 | 134 | 134 | 100 | 136 | 80 | 90 | 136 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2659000
141 | Bhola 33 MW PP (Venture) | 10 | 8 | 10 | 9 | 9 | 8 | 7 | 5 | 5 | 5 | 4 | 6 | 5 | 6 | 6 | 5 | 6 | 8 |  | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 184914
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP | [16 empty] | 15 | 15 |  | 15 | 15 | 15 | 15 |  |  | 0 | 87552
147 | Bheramara HVDC | 887 | 887 | 887 | 886 | 886 | 886 | 887 | 887 | 887 | 887 | 887 | 886 | 887 | 886 | 887 | 892 | 891 | 892 |  | 890 | 890 | 889 | 890 | 891 | 889 | 891 | 21178909
148 | Bheramara 410 MW CCPP | 206 | 205 | 205 | 206 | 215 | 227 | 227 | 236 | 243 | 243 | 243 | 228 | 226 | 223 | 217 | 214 | 213 | 213 |  | 214 | 214 | 213 | 216 | 225 | 238 | 237 | 5474304
149 | Payra 1320 MW | 1100 | 1100 | 1040 | 960 | 800 | 780 | 740 | 800 | 950 | 970 | 1010 | 1080 | 1160 | 1080 | 1040 | 1000 | 1000 | 1040 |  | 1220 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 27302200
150
151 | Barapukuria TPP Unit-1 | 62 | 64 | 62 | 64 | 64 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 62 | 62 | 62 | 62 | 65 |  | 65 | 66 | 65 | 65 | 65 | 65 | 65 | 1455272
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5576000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | [9 empty] | 8160
157 | Sirajganj 68 MW Solar Park | [7 empty] | 3 | 4 | 16 | 6 | 5 | 22 | 13 | 9 | 13 | [10 empty] | 90750
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 188 | 188 | 188 | 188 | 188 | 188 | 150 | 165 | 165 | 165 | 185 | 198 | 198 | 160 | 160 | 160 | 160 | 162 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 4217364
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 350 | 350 | 414 | 414 | 414 | 350 | 350 | 350 | 350 | 350 | 350 | 414 | 414 | 350 | 350 | 300 | 300 | 350 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 8718254
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 59796
166 | Amnura 50 MW PP(Sinha)
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP
169 | Santahar 50 MW Peaking PP | [26 empty] | 0
170 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 7901
171 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 18 |  | 33 | 33 | 33 |  |  |  | 0 | 112320
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | 35 | [16 empty] | 1 | [7 empty] | 0 | 97344
173 | Confidence Power Bogura Unit-1 113 MW | 35 | [24 empty] | 0 | 67968
175 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | Rangpur 113 MW PP (Confidence) | 70 | 34 | [15 empty] | 30 |  | 67 | 34 | 34 | 34 | 34 |  | 0 | 317510
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 5589
| Energypac Power Venture Thakurgaon Ltd. | 35 | [16 empty] | 35 |  | 35 | 35 | 35 | 35 |  |  | 0 | 267840
| Intraco Solar 30 MW | [5 empty] | 0 | 1 | 1 | 2 | 1 | 1 | 1 | 5 | 5 | 4 | 1 | 0 | [9 empty] | 25976
178 | Adani Power Jharkhanda Ltd | 1009 | 1011 | 1013 | 1007 | 1016 | 1007 | 1008 | 1010 | 1008 | 1006 | 1009 | 1008 | 1018 | 1008 | 1018 | 930 | 919 | 1016 |  | 1015 | 1019 | 1016 | 1018 | 1125 | 1124 | 1093 | 24417022
| Teesta Solar Limited | [6 empty] | 12 | 2 | 10 | 15 | 20 | 21 | 39 | 26 | 15 | 4 | 1 | [9 empty] | 190800