## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month: July 2024
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2024-07-01 |  | 2024-06-01 |  | 2023-07-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 15223 | 2024-07-28 | 15798 | 2024-06-11 | 15164 | 2023-07-26 | 16477 | 2024-04-30
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 10542 | 2024-07-23 | 8396 | 2024-06-20 | 8071 | 2023-07-01 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | - | HVDC
3 | Maximum Evening Peak Generation (MW) | 15223 | 2024-07-28 | 16067 | 2024-05-23 | 14655 | 2023-06-08 | 16477 | 2024-04-30 | 746(13.02)23:00
|  |  | 21:00 |  | 21:00 |  | 20:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 13868 | 2024-07-28 | 14167 | 2024-06-11 | 13419 | 2023-07-24 | 14488 | 2024-05-16
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 16000 | 2024-07-30 | 16700 | 2024-06-30 | 15700 | 2023-07-30 | 17200 | 2024-04-29
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14431 |  | 14053.0333 |  | 14160.6129 |  | - | -
7 | Average Generation (MW) at Day Peak | 12793.5806 |  | 12257.2667 |  | 12085.4516 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 970 | 2024-07-06 | 938 | 2024-06-07 | 927 | 2023-07-02 | 970 | 2024-07-06
|  |  | 14:30 |  | 3:30 |  | 21:00 |  | 14:30
9 | Maximum Power Import from Tripura, India (MW) | 106 | 2024-07-18 | 100 | 2024-06-05 | 182 | 2023-07-13 | 194 | 12/06/19
|  |  | 15:00 |  | 20:00 |  | 15:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1341 | 2024-07-10 | 1727 | 2024-06-25 | 1100 | 2023-07-19 | 4395 | 04/10/2022
|  |  | 21:00 |  | 19:30 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14096 | 2024-07-10 | 13792 | 2024-06-25 | 14448 | 45126 | 14965 | 2024-05-16
|  | - | 21:00 | - | 19:30 |  | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2024-07-05 | 0 | 2024-06-15 | 0 | 45110 | - | -
|  |  | 21:00 |  | 21:00 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 13229 | 2024-07-05 | 13723 | 2024-06-15 | 12454 | 2023-07-03 | - | -
|  |  | 21:00 |  | 21:00 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 1795 | 2024-07-11 | 1808 | 2024-06-25 | 1806 | 45127 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 12870 | 2024-07-11 | 12757 | 2024-06-25 | 12359 | 45127 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2024-07-05 | 0 | 2024-06-15 | 0 | 45110 | - | -
|  |  | 12:00 |  | 12:00 |  | 21:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 11167 | 2024-07-05 | 11757 | 2024-06-15 | 9951 | 45110 | - | -
|  |  | 12:00 |  | 12:00 |  | 21:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 29 |  | 22 |  | 24 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 17 |  | 19 |  | 24 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1553.74 |  | 2340.8823 |  | 1774.0473 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 63.1342 |  | 125.5183 |  | 45.3987 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1490.6058 |  | 2215.364 |  | 1728.6486 |  | - | -
23 | Net Generation of IPP (MKWH) | 6375.85 |  | 5237.2842 |  | 5413.9228 |  | - | -
24 | Net Generation of REB (MKWH) | 72.09 |  | 69.9332 |  | 119.8463 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 224.06 |  | 239.9504 |  | 406.1896 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 8162.6058 |  | 7762.5318 |  | 7668.6073 |  | 8063.07 | July'24
26 | Energy Generation by Gas (MKWH) | 3964.7401 |  | 4103.364 |  | 4793.0721 |  | 4771.06 | May-24
27 | Energy Generation by Diesel (MKWH) | 18.1087 |  | 23.2046 |  | 254.4028 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1371.0357 |  | 1429.8415 |  | 1645.587 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 138.7193 |  | 80.8001 |  | 45.1338 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 59.6045 |  | 44.0204 |  | 40.6725 |  | 59.6 | July'24
31 | Energy Generation by Coal (MKWH) | 1206.4395 |  | 988.7654 |  | 935.1378 |  | 1206.44 | July'24
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 739.9666 |  | 700.4526 |  | 773.3438 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 81.3292 |  | 76.6243 |  | 84.9085 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: July 2024
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 15223 | 2024-07-28 | 21:00
Generation Period
| Dhaka | MW | 5163.71
| Chattogram | MW | 1458.5
| Cumilla | MW | 1384
| Mymensingh | MW | 1003
| Sylhet | MW | 563
a) | Total supply in East zone | MW | 9572.21
| Khulna | MW | 1858.4
| Barisal | MW | 485.5
| Rajshahi | MW | 1638.6
| Rangpur | MW | 969
b) | Total supply in West zone | MW | 4951.5
c) | Total supply in both zone ( a+b) | MW | 14523.71
Ref: | 27.21.0000.603.16.087.20.831 | Date: 18/07/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:July 2024
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 90 | 2024-07-02 | 5:00
| b) Ishurdi end | MW | 258 | 2024-07-26 | 13:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 932 | 2024-07-25 | 10:00
| b) Ishurdi end | MW | 42 | 2024-07-02 | 400:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.14658
| b) Ishurdi end | MKWH | 149.1989
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 144.7229
| b) Ishurdi end | MKWH | 0.14231
23 | Transmission loss of EWI/ NO-1 | % | 3 |  |  | 5.91
24 | Daily Maximum power Export through EWI/ NO-2 |  |  |  |  | 2.955
| a) Ashuganj end | MW | 360 | 2024-07-01 | 24:00
| b)Serajganj end | MW | 740 | 2024-07-10 | 9:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 440 | 2024-07-25 | 10:00
| b)Sirajganj end | MW | 140 | 2024-07-02 | 5:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.5667
| b)Sirajganj end | MKWH | 323.994
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 313.7107
| b)Sirajganj end | MKWH | 0.566
30 | Transmission loss of EWI /NO-2 | % | 3.169'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2252 | 2024-07-31 | 20:00
|  | MW | 1520
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2146 | 2024-07-31 | 20:00
|  | MW | 1412
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 26032 | 2024-07-31 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 25600 | 2024-07-31
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 754.851
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 752.7399
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.27967
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 HT | 2024-07-07 14:27 | 2024-07-07 14:47 | 0:20 | T | Unknown | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 HT | 2024-07-07 14:27 | 2024-07-07 14:47 | 0:20 | T | Unknown | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 HT | 2024-07-07 14:27 | 2024-07-07 14:47 | 0:20 | T | Unknown | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Bus A | 2024-07-15 07:20 | 2024-07-15 09:44 | 2:24 | E/O | High temperature maintenance. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-07-02 02:11 | 2024-07-02 02:21 | 0:10 | T | 33 kV pbs feeder no 13 don't trip | 55 | 9.1667 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-07-02 14:28 | 2024-07-02 16:19 | 1:51 | E/O | 33KV TR-1 bus coupler red hot maintenance | 50 | 92.5 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-07-02 02:11 | 2024-07-02 02:21 | 0:10 | T | 33kV pbs feeder no 13 don't trip | 55 | 9.1667 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-07-12 03:38 | 2024-07-12 04:12 | 0:34 | T | Tripped showing O/C & 86 Relay relays. | 100 | 56.6667 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-07-12 03:38 | 2024-07-12 08:20 | 4:42 | T | Tripped showing O/C & 86 Relay relays. | 55 | 258.5 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-07-12 05:00 | 2024-07-12 08:20 | 3:20 | E/O | Work at 33 kV bus DS. | 50 | 166.6667 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2024-07-28 04:58 | 2024-07-28 10:36 | 5:38 | T | 33kV Outgoing cable Y-phase blast | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2024-07-15 22:15 | 2024-07-16 00:15 | 2:00 | E/O | Red hot maintenance | 60 | 120 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2024-07-03 10:51 | 2024-07-03 10:51 | 0:00 | T | PRD | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2024-07-03 19:58 | 2024-07-03 20:32 | 0:34 | T | PRD Showing Trip | 15 | 8.5 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2024-07-03 22:51 | 2024-07-03 22:51 | 0:00 | T | PRD | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2024-07-04 09:25 | 2024-07-04 14:38 | 5:13 | E/O | PRD maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2024-07-15 07:31 | 2024-07-15 10:29 | 2:58 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-07-29 07:20 | 2024-07-29 08:44 | 1:24 | E/O | Due to emergency maint.work | 20 | 28 | Power interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2024-07-18 11:02 | 2024-07-18 11:16 | 0:14 | T | 33kV Fault in DESCO GIS | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2024-07-18 11:35 | 2024-07-18 11:53 | 0:18 | T | Over current due to overload by DESCO | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2024-07-18 12:10 | 2024-07-18 12:34 | 0:24 | T | Over current for Over load by DESCO 33kV | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) HT | 2024-07-12 17:40 | 2024-07-12 19:47 | 2:07 | E/O | 33kv side bushing cleam repair | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2024-07-25 10:47 | 2024-07-25 11:38 | 0:51 | T | Tripped showing Earth fault relays. | 65 | 55.25 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2024-07-25 10:47 | 2024-07-25 11:06 | 0:19 | T | Tripped showing Earth fault relays. | 65 | 20.5833 | Power interruption
Satmasjid 132/33kV Grid Sub-Station | 132/33 KV Transformer-1 HT | 2024-07-13 07:26 | 2024-07-13 09:14 | 1:48 | E/O | PRD Preventive Maintenance | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | 132/33 KV Transformer-2 HT | 2024-07-13 09:27 | 2024-07-13 10:45 | 1:18 | E/O | PRD preventive Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2024-07-09 02:15 | 2024-07-09 03:09 | 0:54 | E/O | Red hot Maintenance PBS Feeder_1 | 35 | 31.5 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 HT | 2024-07-12 10:29 | 2024-07-12 11:15 | 0:46 | E/O | for PRD check | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2024-07-06 22:18 | 2024-07-06 22:37 | 0:19 | T | Earth Fault | 65 | 20.5833 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2024-07-06 23:00 | 2024-07-06 23:10 | 0:10 | T | Not Found | 65 | 10.8333 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2024-07-27 10:05 | 2024-07-27 12:17 | 2:12 | E/O | 33kv ghatail feeder bus isolator red hot | 80 | 176 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-07-06 17:48 | 2024-07-06 18:07 | 0:19 | T | Not Found | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-07-06 22:18 | 2024-07-06 22:38 | 0:20 | T | 86x Relay | 65 | 21.6667 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-07-06 23:00 | 2024-07-07 02:21 | 3:21 | T | 86x Relay | 65 | 217.75 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 LT | 2024-07-27 10:04 | 2024-07-27 12:18 | 2:14 | E/O | 33kv ghatail feeder bus isolator red hot | 80 | 178.6667 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 HT | 2024-07-07 14:27 | 2024-07-07 14:36 | 0:09 | T | N/A | 195 | 29.25 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-02 HT | 2024-07-07 14:27 | 2024-07-07 14:36 | 0:09 | T | N/A | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 LT | 2024-07-07 14:27 | 2024-07-07 14:58 | 0:31 | T |  | 0 | 0 | No interruption
|  |  | Total : | 50:41 |  | Unserved Energy: |  | 1511.25
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2024-07-06 12:24 | 2024-07-06 12:52 | 0:28 | T | OTI TRIP | 200 | 93.3333 | Power interruption
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2024-07-07 04:50 | 2024-07-07 07:10 | 2:20 | E/O | OTI Maintenance purpose | 80 | 186.6667 | Power interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2024-07-16 10:08 | 2024-07-16 10:27 | 0:19 | T | PBS 33kV feeder fault. | 16 | 5.0667 | Power interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2024-07-12 20:35 | 2024-07-12 22:55 | 2:20 | T | LT Tripped showing N/A relays. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) HT | 2024-07-18 18:04 | 2024-07-18 18:11 | 0:07 | E/O | siddirganj s/s has taken this S/D. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 HT | 2024-07-17 02:37 | 2024-07-17 02:37 | 0:00 | T | 132kV(Interim) CT (B-ph) explodes. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2024-07-17 02:37 | 2024-07-17 02:37 | 0:00 | T | 132kV(Interim) CT (B-ph) explodes. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | NLDC Trafo HT | 2024-07-31 21:02 | 2024-07-31 22:15 | 1:13 | T | Trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 LT | 2024-07-14 09:13 | 2024-07-14 09:53 | 0:40 | T | Physical stroke on Demra Line underground cable by Excavator under G2G project work. | 58 | 38.6667 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | T-2 LT | 2024-07-14 09:13 | 2024-07-14 13:34 | 4:21 | T | Physical stroke on Demra Line underground cable by Excavator under G2G project work.. | 58 | 252.3 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 HT | 2024-07-11 20:13 | 2024-07-11 22:08 | 1:55 | E/O | 33kv bushing B phase red hot maintenance works | 0 | 0 | No interruption
|  |  | Total : | 13:43 |  | Unserved Energy: |  | 576.0333
Chattogram Grid Circle :
Bakulia 132/33kV Grid Sub-Station | T-3 (422T) LT | 2024-07-06 22:27 | 2024-07-06 23:09 | 0:42 | E/O | Red Hot maintenance. | 12 | 8.4 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | Bus-A | 2024-07-24 10:55 | 2024-07-24 16:38 | 5:43 | E/O | Red hot maintenance work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T HT | 2024-07-24 10:12 | 2024-07-24 12:21 | 2:09 | E/O | Red hot maintenance work | 10 | 21.5 | Power interruption
Chandraghona 132/33kV Grid Sub-Station | TR-02(416T) LT | 2024-07-01 07:24 | 2024-07-01 12:28 | 5:04 | E/O | 33kv bushing spark. | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | 415T-T2 HT | 2024-07-02 15:22 | 2024-07-02 16:24 | 1:02 | E/O | Ukhiya (REB SADAR) 33 kV side | 41 | 42.3667 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | 415T-T2 HT | 2024-07-31 17:38 | 2024-07-31 18:38 | 1:00 | E/O | T-02(80/120MVA) Open due to burst of 33KV Ukhiya feeder | 30 | 30 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2024-07-10 09:16 | 2024-07-10 10:37 | 1:21 | E/O | Due to 33kv bus DS of chokariy pdb red hot maintenance. | 12 | 16.2 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2024-07-26 17:46 | 2024-07-26 17:58 | 0:12 | T | Special O/C protection Operated at Hatazari SS (T02 sec.+Lohagara PBS+Chandanaish PBS tripped) | 46 | 9.2 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-04 HT | 2024-07-26 16:00 | 2024-07-26 19:41 | 3:41 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 LT | 2024-07-26 17:55 | 2024-07-26 18:03 | 0:08 | T | Tripped showing lockout | 39 | 5.2 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | T-02 LT | 2024-07-26 17:55 | 2024-07-26 18:03 | 0:08 | T | Tripped showing lockout | 9 | 1.2 | Power interruption
Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T HT | 2024-07-31 00:40 | 2024-07-31 08:44 | 8:04 | E/O | Urgent spark maintenance work of line DS(B-phase). | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) HT | 2024-07-28 16:37 | 2024-07-28 17:25 | 0:48 | E/O | OLTC OIL LEVEL LOW ALARM | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) LT | 2024-07-10 13:01 | 2024-07-10 15:11 | 2:10 | E/O | BPDB 33 KV feeder FIDC inc-2, Bus-1 incommer B-phase( red hot) maintenance. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) LT | 2024-07-04 13:32 | 2024-07-04 14:49 | 1:17 | E/O | Feeder name : 33 KV PDB incomer-1, (R-ph) redhot, spark in bus section -2. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-07-04 15:32 | 2024-07-04 16:50 | 1:18 | E/O | Red-hot Maintenance By BPDB | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-07-04 21:22 | 2024-07-04 22:19 | 0:57 | E/O | Maintenance work by BPDB | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-07-14 16:32 | 2024-07-14 18:15 | 1:43 | E/O | BPDB Maintenance work | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | 50/75 MVA T-1(405T) HT | 2024-07-06 20:48 | 2024-07-07 13:03 | 16:15 | T | O/C | 0.6 | 9.75 | Power interruption
TK chemical 132kV Grid Sub-Station | 50/75 MVA T-1(405T) HT | 2024-07-07 18:16 | 2024-07-09 16:50 | 46:34 | T | Internal problem in TK Factory | 0.6 | 27.94 | Power interruption
|  |  | Total : | 100:16 |  | Unserved Energy: |  | 171.7567
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2024-07-01 21:55 | 2024-07-01 23:24 | 1:29 | E/O | 33 kv incomer-02 red hot | 25 | 37.0833 | Power interruption
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2024-07-17 08:25 | 2024-07-17 10:50 | 2:25 | E/O | Red hot maintenance | 30 | 72.5 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1-415T LT | 2024-07-10 00:28 | 2024-07-10 10:33 | 10:05 | T | Tripped By Instt. E/F | 58 | 584.8333 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3 | 2024-07-04 07:34 | 2024-07-04 09:10 | 1:36 | E/O | 33 KV T-3 Bus red hot maintenance. | 20 | 32 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3 | 2024-07-14 19:32 | 2024-07-14 22:10 | 2:38 | E/O | 132 kv HT side bushing red-hot. | 30 | 79 | Power interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 HT | 2024-07-05 17:02 | 2024-07-05 17:46 | 0:44 | T | WTI | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 HT | 2024-07-18 11:20 | 2024-07-18 11:44 | 0:24 | E/O | Tr-3 33kV GCB Gas refill work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-07-06 01:17 | 2024-07-06 05:13 | 3:56 | T | unknown | 25 | 98.3333 | Power interruption
|  |  | Total : | 23:17 |  | Unserved Energy: |  | 903.75
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) LT | 2024-07-07 15:50 | 2024-07-07 16:06 | 0:16 | T | 33kV TR-03 Incomers tripped due to 33kV BSCIC feeder CB fault. | 41 | 10.9333 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-07-08 23:10 | 2024-07-08 23:26 | 0:16 | T | Trip circuit not healthy | 38 | 10.1333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-07-16 13:28 | 2024-07-16 13:45 | 0:17 | T | 33 KV Bhandaria PBS feeder fault. Bus DS flashing. | 37 | 10.4833 | Power interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2024-07-18 10:36 | 2024-07-18 13:15 | 2:39 | E/O | Hot Spot Maintenance of 33kV Bushing Blue phase of Transformer | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-07-15 17:32 | 2024-07-15 19:12 | 1:40 | E/O | Red hot maintenance of Gpbs | 12 | 20 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2024-07-28 17:01 | 2024-07-28 18:52 | 1:51 | E/O | Due to red hot reduce of 33 kv bus section # 1(Isoletor) | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 2 | 2024-07-24 11:32 | 2024-07-24 16:16 | 4:44 | E/O | Due to Gas leakage on NWPGCL new GIS230KV bay. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2024-07-20 07:40 | 2024-07-20 10:02 | 2:22 | E/O | Due to emergency maint.work | 16 | 37.8667 | Power interruption
Mongla 132/33kV Grid Sub-Station | Main Bus | 2024-07-08 16:44 | 2024-07-08 19:20 | 2:36 | E/O | Red hot of main bus DS. | 22 | 57.2 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2024-07-08 16:34 | 2024-07-08 19:24 | 2:50 | E/O | Red hot of main bus DS. | 22 | 62.3333 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2024-07-08 16:34 | 2024-07-08 19:25 | 2:51 | E/O | Red hot of main bus DS. | 22 | 62.7 | Power interruption
Mongla 132/33kV Grid Sub-Station | Transfer Bus | 2024-07-08 16:44 | 2024-07-08 18:20 | 1:36 | E/O | Red hot of main bus DS. | 22 | 35.2 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) HT | 2024-07-26 07:14 | 2024-07-26 08:07 | 0:53 | E/O | Auxiliary transformer -2 fuse wire change work | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2024-07-26 07:14 | 2024-07-26 08:07 | 0:53 | E/O | Auxiliary transformer -2 fuse wire change work | 12 | 10.6 | Power interruption
|  |  | Total : | 25:44 |  | Unserved Energy: |  | 317.45
HVDC Grid Circle :
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T1(416T) LT | 2024-07-18 07:35 | 2024-07-18 08:04 | 0:29 | E/O | Due to Monkey climbed on the gantry structure | 47 | 22.7167 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T2(426T) LT | 2024-07-18 07:36 | 2024-07-18 08:05 | 0:29 | E/O | Due to Monkey climbed on the gantry structure | 35 | 16.9167 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T3 LT | 2024-07-18 07:38 | 2024-07-18 08:05 | 0:27 | E/O | Due to Monkey climbed on the gantry structure | 19 | 8.55 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2024-07-29 17:33 | 2024-07-29 18:19 | 0:46 | T | 33 kv green city feeder fault | 30 | 23 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 HT | 2024-07-01 12:32 | 2024-07-01 14:27 | 1:55 | E/O | CT bushing heating problem | 24 | 46 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 HT | 2024-07-09 04:00 | 2024-07-09 05:30 | 1:30 | T | 33kv outgoing feeder fault | 38 | 57 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 HT | 2024-07-11 07:00 | 2024-07-11 22:49 | 15:49 | E/O | T1 transformer 33 kv bussing oil leakage maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-07-30 09:58 | 2024-07-30 10:45 | 0:47 | T | 33 kv out going feeder fault | 31 | 24.2833 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-07-30 11:42 | 2024-07-31 13:51 | 26:09 | E/O | Due to emergency maint.work | 45 | 383.25 | Power interruption 11:42 to 20:13
Kushtia 132/33kV Grid Sub-Station | T-3 LT | 2024-07-30 10:30 | 2024-07-30 13:18 | 2:48 | E/O | Due to 132 kv control & relay panel DC fail | 58 | 162.4 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-07-09 04:00 | 2024-07-09 05:15 | 1:15 | T | 33kv outgoing feeder fault | 40 | 50 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-07-09 06:55 | 2024-07-09 08:54 | 1:59 | E/O | T2A B phase Breaker to CB loop I-clamp bolt Red Hot | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-07-30 09:58 | 2024-07-30 10:46 | 0:48 | T | 33 kv out going feeder fault | 31 | 24.8 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-07-30 19:31 | 2024-07-30 21:42 | 2:11 | E/O | Due to emergency maint.work | 50 | 109.1667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-2 LT | 2024-07-03 03:50 | 2024-07-03 04:05 | 0:15 | T | chatmohar 33 kv(PBS-1) Trip ( E/F+ O/C) | 13 | 3.25 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-2 LT | 2024-07-03 18:50 | 2024-07-03 19:00 | 0:10 | T | Tripped showing E/F, TCSR relays. | 17 | 2.8333 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-2 LT | 2024-07-08 16:09 | 2024-07-08 16:30 | 0:21 | T | Tripped showing O/C trip. relays. | 17 | 5.95 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-2 LT | 2024-07-09 14:53 | 2024-07-09 14:58 | 0:05 | T | Chatmohar 33 kv BKR trip | 15 | 1.25 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-3 HT | 2024-07-08 16:09 | 2024-07-08 21:11 | 5:02 | T | None | 20 | 100.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-3 LT | 2024-07-03 03:50 | 2024-07-03 04:05 | 0:15 | T | chatmohar 33 kv(PBS-1) Trip ( E/F+ O/C) | 26 | 6.5 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-3 LT | 2024-07-03 18:50 | 2024-07-03 19:00 | 0:10 | T |  | 33 | 5.5 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-3 LT | 2024-07-09 14:53 | 2024-07-09 14:58 | 0:05 | T | Chatmohar 33 kv trip | 30 | 2.5 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-07-15 16:01 | 2024-07-15 16:01 | 0:00 | E/O | ds insulator broken | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) HT | 2024-07-09 13:15 | 2024-07-09 14:43 | 1:28 | E/O | Loop changing work for T-3 x-former 33kv ds-c.b | 0 | 0 | No interruption
|  |  | Total : | 65:13 |  | Unserved Energy: |  | 1056.5333
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T HT | 2024-07-10 08:47 | 2024-07-10 08:53 | 0:06 | T | Earth fault | 0 | …... | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T HT | 2024-07-10 13:44 | 2024-07-10 13:44 | 0:00 | T | RET 521 Main-1 Relay Oparated | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T HT | 2024-07-10 14:37 | 2024-07-10 17:41 | 3:04 | E/O | Emergency Maintenance. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T LT | 2024-07-10 13:44 | 2024-07-10 13:44 | 0:00 | T | TEF-3 Trip, 50N- 51N- 400KV HV - Trip etc | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2024-07-07 12:17 | 2024-07-07 13:01 | 0:44 | T | Due to 33kV feeder fault. | 52 | 38.1333 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2024-07-07 12:17 | 2024-07-07 13:01 | 0:44 | T | Due to 33kV feeder fault. | 52 | 38.1333 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-07-03 11:58 | 2024-07-03 13:24 | 1:26 | E/O | Puran Bogura 33kV feeders 33kV bus Isolator Red hot maintenance work under T-1 33kV Busbar. | 35 | 50.1667 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-07-14 19:25 | 2024-07-14 20:15 | 0:50 | T | T-1 33kv incoming CB Trip due to Puran bogura-2 33kv feeder CB Blust. | 28 | 23.3333 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-07-14 21:57 | 2024-07-14 23:45 | 1:48 | E/O | Red hot (132 KV CB upper loop-B phase) | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-07-14 19:25 | 2024-07-14 20:15 | 0:50 | T | T-2 33kv incoming CB Trip due to Puran bogura-2 33kv feeder CB Blust. | 42 | 35 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-07-14 23:58 | 2024-07-15 00:25 | 0:27 | E/O | Red hot 132KV CT (R-Phase) | 35 | 15.75 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-07-16 07:09 | 2024-07-16 10:28 | 3:19 | E/O | Red hot to CT connector. | 5 | 16.5833 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-07-10 10:03 | 2024-07-10 13:06 | 3:03 | E/O | T-3 33kV Isolator Red hot maintenance work. | 6 | 18.3 | Power interruption
Bogura 230/132kV Grid Sub-Station | T-02 HT | 2024-07-11 23:11 | 2024-07-11 23:43 | 0:32 | T | Rain &Thundering. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T-2 LT | 2024-07-10 09:20 | 2024-07-10 11:54 | 2:34 | E/O | Due to maintenance 33kv bus section-2 isolator. | 35 | 89.8333 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2024-07-06 22:59 | 2024-07-07 00:22 | 1:23 | E/O | T-1 33KV Incomer CT Connector Red Hot. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-3(426T) HT | 2024-07-01 11:59 | 2024-07-01 12:56 | 0:57 | E/O | DC earth fault maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-3(426T) LT | 2024-07-01 10:15 | 2024-07-01 10:25 | 0:10 | T | Tripped showing E/F relays at 33 kV feeder | 13 | 2.1667 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) HT | 2024-07-17 14:18 | 2024-07-17 18:18 | 4:00 | T | due to 33 kv haragach cable fault and kaunia feeder fault. | 60 | 240 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) LT | 2024-07-29 06:34 | 2024-07-29 07:56 | 1:22 | E/O | 33kv Bus1Red Hot | 40 | 54.6667 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2024-07-09 02:17 | 2024-07-09 02:40 | 0:23 | T | Kamarkhanda 33 kv Feeder Fault | 51 | 19.55 | Power interruption 02:17 to 02:40
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2024-07-14 07:45 | 2024-07-14 08:46 | 1:01 | E/O | Section BUS DS red hot bolt Re-place work. | 30 | 30.5 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2024-07-26 07:18 | 2024-07-26 09:03 | 1:45 | E/O | Sirajgonj PBS-2 has taken shut down for T1 33kv section DS emergency maintenance | 30 | 52.5 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) HT | 2024-07-09 14:17 | 2024-07-09 14:38 | 0:21 | T | Kamarkhanda 33 kv Feeder Fault (T1 and T2 Paralla Oparation ) | 50 | 17.5 | Power interruption
|  |  | Total : | 30:49 |  | Unserved Energy: |  | 742.1167
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 309:43 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2024-07-29 11:36 | 2024-07-29 13:08 | 1:32 | E/O | Line isolator clamp melted | 0 | 0 | No interruption
Ghatail 132/33kV Grid Sub-Station | RPCL-2 | 2024-07-11 17:52 | 2024-07-11 18:09 | 0:17 | T | Due to Thundering and strom | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-1 | 2024-07-16 05:59 | 2024-07-16 07:55 | 1:56 | E/O | High Temperature Maintenance | 80 | 154.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 2024-07-27 13:56 | 2024-07-27 14:17 | 0:21 | T | Earth fault | 70 | 24.5 | Power interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-07-01 13:32 | 2024-07-01 13:52 | 0:20 | T | None | 13 | 4.3333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-07-15 07:32 | 2024-07-15 10:08 | 2:36 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-07-07 07:28 | 2024-07-07 08:01 | 0:33 | T | Trip Due to Line Differential Relay(ABB RED670) Shown (87L Trip) signal. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-07-29 11:55 | 2024-07-29 13:09 | 1:14 | E/O | ahuganj End | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2024-07-08 13:25 | 2024-07-08 13:56 | 0:31 | E/O | Rectification work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-2 | 2024-07-08 13:57 | 2024-07-08 14:12 | 0:15 | E/O | Rectification work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Tongi 80 MW PS | 2024-07-14 11:44 | 2024-07-14 12:58 | 1:14 | E/O | 132 kV Circuit breaker maintenance work at 80 MW power station site | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2024-07-07 14:46 | 2024-07-07 14:58 | 0:12 | T | TRIP | 0 | 0 | No interruption
|  |  | Total : | 11:01 |  | Unserved Energy: |  | 183.5
Dhaka (South) Grid Circle :
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-07-27 09:29 | 2024-07-27 12:05 | 2:36 | T | Tripped showing 21 Trip Zone-1 Trip relays. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-07-31 01:24 | 2024-07-31 01:24 | 0:00 | T | TRIP | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2024-07-31 01:24 | 2024-07-31 02:03 | 0:39 | T | Unknown | 65 | 42.25 | Power interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-07-15 12:08 | 2024-07-15 12:18 | 0:10 | E/O | Order by NLDC | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-07-27 09:30 | 2024-07-27 12:06 | 2:36 | T | General trip, Zone -1 B-ph Pick-up | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-07-31 01:24 | 2024-07-31 01:24 | 0:00 | T | None | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-1 | 2024-07-30 04:18 | 2024-07-30 14:46 | 10:28 | T | 33KV Kumartuli ckt-1&2 and 132/33KV GT-1 trip at Narinda end. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-1 | 2024-07-31 18:20 | 2024-07-31 20:15 | 1:55 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-2 | 2024-07-30 04:20 | 2024-07-30 18:18 | 13:58 | T | 132/33KV GT-2 trip at Narinda end. | 44 | 614.5333 | Power interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-07-07 11:14 | 2024-07-07 11:25 | 0:11 | T | Unknown | 100 | 18.3333 | Power interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-07-07 11:14 | 2024-07-07 13:24 | 2:10 | T | Jumper out from Basundhara Sub-Station. | 100 | 216.6667 | Power interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-07-07 13:25 | 2024-07-08 06:29 | 17:04 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Digital Powerplant | 2024-07-13 07:25 | 2024-07-13 09:53 | 2:28 | T | TRIP | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 2 | 2024-07-18 18:08 | 2024-07-18 18:10 | 0:02 | E/O | Emergency maintenance work | 0 | 0 | No interruption
|  |  | Total : | 54:17 |  | Unserved Energy: |  | 891.7833
Chattogram Grid Circle :
Baroaulia 132/33kV Grid Sub-Station | AKSPL | 2024-07-16 00:14 | 2024-07-17 11:37 | 35:23 | E/O | Instant order by NLDC | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-2 | 2024-07-15 23:53 | 2024-07-17 11:35 | 35:42 | T | Fault at Hathazari end | 10 | 357 | Power interruption
Baroaulia 132/33kV Grid Sub-Station | Kulshi | 2024-07-16 00:14 | 2024-07-17 11:34 | 35:20 | E/O | Instant order by NLDC | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | HATHAZARI-2 | 2024-07-06 11:51 | 2024-07-06 13:15 | 1:24 | E/O | emergency maintenance needed from hathajari side | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-07-11 04:05 | 2024-07-11 04:05 | 0:00 | T | 132kV Hali-Khulshi Ckt-03 tripped for Line Conductor Has been Broken Tower Span No 45-46. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-07-11 06:28 | 2024-07-12 21:23 | 38:55 | E/O | 132kV Hali-Khulshi Ckt-03 Line Repair & Maintenance of Tower Span No 45-46. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-07-09 11:19 | 2024-07-09 11:42 | 0:23 | T | Instantenious trip. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-07-09 13:14 | 2024-07-09 15:15 | 2:01 | T | Instantenious trip. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | GPH-01 | 2024-07-01 14:02 | 2024-07-01 14:32 | 0:30 | T | showing ABB LZ96A (Main) relays. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-3 | 2024-07-11 04:05 | 2024-07-12 21:25 | 41:20 | T | Tripped showing REL670 relays. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2024-07-07 16:49 | 2024-07-07 21:35 | 4:46 | E/O | Redhot maintenance in TK chemical grid. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2024-07-09 11:20 | 2024-07-09 11:43 | 0:23 | T | Tripped showing REL670 relays. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2024-07-09 13:14 | 2024-07-09 13:14 | 0:00 | T | Tripped showing REL670 relays. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 2024-07-30 12:59 | 2024-07-30 18:32 | 5:33 | T | Due to burstng of L/A | 0 | 0 | No interruption
|  |  | Total : | 201:40 |  | Unserved Energy: |  | 357
Cumilla Grid Circle :
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2024-07-15 06:48 | 2024-07-15 12:27 | 5:39 | E/O | Ordered By NLDC | 0 | 0 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-1 | 2024-07-08 09:32 | 2024-07-08 09:54 | 0:22 | T | Unknown | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-1 | 2024-07-14 19:20 | 2024-07-14 19:47 | 0:27 | T | showing Distance Relay relays. | 28 | 12.6 | Power interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-2 | 2024-07-14 19:20 | 2024-07-14 19:47 | 0:27 | T | showing Distance Relay relays. | 28 | 12.6 | Power interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2024-07-04 13:18 | 2024-07-04 13:28 | 0:10 | T | showing Distance Relay relays. | 0 | 0 | No interruption
|  |  | Total : | 7:05 |  | Unserved Energy: |  | 25.2
Khulna Grid Circle :
Barishal 230/132kV Grid Sub-Station | Gopalgonj CKT-1 | 2024-07-12 09:27 | 2024-07-12 14:09 | 4:42 | E/O | Instructed by ALDC | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Madaripur ckt-02 | 2024-07-12 09:02 | 2024-07-12 14:14 | 5:12 | E/O | instructed by ALDC | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-2 | 2024-07-07 13:38 | 2024-07-07 13:38 | 0:00 | T | Ground Fault C-Phase | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | 100MW ERBL Solar PS | 2024-07-08 16:42 | 2024-07-08 19:27 | 2:45 | E/O | Red hot of main bus DS. | 22 | 60.5 | Power interruption
Mongla 132/33kV Grid Sub-Station | Bagerhat-Mongla Line-1 | 2024-07-08 16:44 | 2024-07-08 19:20 | 2:36 | E/O | Red hot of main bus DS. | 22 | 57.2 | Power interruption
Mongla 132/33kV Grid Sub-Station | Bagerhat-Mongla Line-2 | 2024-07-08 16:44 | 2024-07-08 19:21 | 2:37 | E/O | Red hot of main bus DS. | 22 | 57.5667 | Power interruption
|  |  | Total : | 17:52 |  | Unserved Energy: |  | 175.2667
HVDC Grid Circle :
BIPTC | Baharampur-2 | 2024-07-11 19:42 | 2024-07-11 22:50 | 3:08 | T | Distance Zone-1 trip | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2024-07-01 12:48 | 2024-07-02 10:35 | 21:47 | T | showing Distance Relay relays. | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Kushtia 132kV Circuit-1(L1) | 2024-07-10 06:10 | 2024-07-10 07:07 | 0:57 | T | Fault | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Khulna (South) Ckt-2 | 2024-07-31 07:49 | 2024-07-31 08:09 | 0:20 | T | Distance Zone-1 trip | 0 | 0 | No interruption
|  |  | Total : | 26:12 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2024-07-27 11:33 | 2024-07-27 13:09 | 1:36 | E/O | Conductor string maintenance of bogura circuit-1 R phase. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Confidance UN-2 | 2024-07-01 15:32 | 2024-07-01 16:40 | 1:08 | E/O | maintenance work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Nia Ckt-1 | 2024-07-04 13:14 | 2024-07-04 13:14 | 0:00 | E/O | CT, R-Phase Oil Leakage | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132 kV Rahanpur Ckt-2 | 2024-07-18 13:13 | 2024-07-18 13:39 | 0:26 | E/O | Rahanpur ckt-2,control panel shift work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-1 | 2024-07-18 12:57 | 2024-07-18 13:10 | 0:13 | E/O | Rahanpur ckt-1,control panel shift work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-07-05 09:07 | 2024-07-05 14:46 | 5:39 | E/O | ALDC,Bogura à¦à¦° à¦¨à¦¿à¦°à§à¦¦à§‡à¦¶ à¦ Naogoan ckt-1 à¦à¦° CB Open à¦•à¦°à¦¾ à¦¹à§Ÿà¥¤ | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-2 | 2024-07-04 09:10 | 2024-07-04 11:40 | 2:30 | E/O | Red hot Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Jaldhaka CKT-01 | 2024-07-10 01:27 | 2024-07-10 01:40 | 0:13 | T | Thundering | 14 | 3.0333 | Power interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Jaldhaka CKT-02 | 2024-07-10 01:27 | 2024-07-10 01:41 | 0:14 | T | Thundering | 14 | 3.2667 | Power interruption
|  |  | Total : | 11:59 |  | Unserved Energy: |  | 6.3
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 330:06 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
…...

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: July 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV Grid Sub-Station | Auxiliary- 01 LT | 2024-07-14 09:05 | 2024-07-14 09:57 | 0:52 | S/O | Maintenance work | 30 | 26 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Bus A | 2024-07-17 07:35 | 2024-07-17 09:23 | 1:48 | S/O | High temperature maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-07-14 07:25 | 2024-07-14 08:46 | 1:21 | S/O | Maintenance work | 30 | 40.5 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-07-14 09:05 | 2024-07-14 10:21 | 1:16 | S/O | Maintenance work | 30 | 38 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-07-25 06:45 | 2024-07-25 08:43 | 1:58 | S/O | Red hot maintenance. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-07-28 10:35 | 2024-07-28 11:38 | 1:03 | D/W | Project work | 40 | 42 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-07-04 14:22 | 2024-07-04 16:37 | 2:15 | S/O | Work by pbs. | 30 | 67.5 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2024-07-16 05:55 | 2024-07-16 07:37 | 1:42 | S/O | Maintenance of Auxilary X-former-2 | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-4 HT | 2024-07-05 10:12 | 2024-07-05 18:10 | 7:58 | S/O | 132KV GT-4 Transformer 33KV GIS leakage Maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2024-07-09 05:48 | 2024-07-09 08:54 | 3:06 | S/O | High temperature maintenance work at 33kV bus DS source side R phase. | 50 | 155 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 2 | 2024-07-25 14:43 | 2024-07-25 18:30 | 3:47 | S/O | Emergency Maintenance. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2024-07-07 07:30 | 2024-07-07 09:04 | 1:34 | S/O | Under ground cable remove | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-07-03 10:53 | 2024-07-03 18:25 | 7:32 | S/O | 400kV GNDP project work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2024-07-25 08:54 | 2024-07-25 11:09 | 2:15 | S/O | Red hot removal | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-07-01 09:43 | 2024-07-01 18:54 | 9:11 | D/W | Project work | 6 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2024-07-04 15:20 | 2024-07-04 17:58 | 2:38 | D/W | 400 kV GNDP project. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Main Bus | 2024-07-10 06:24 | 2024-07-10 07:53 | 1:29 | D/W | 132/33 KV T3-Power Transformer Bus bay Upgradation. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2024-07-10 08:24 | 2024-07-10 09:45 | 1:21 | D/W | 132 Kv T3-Xfr bay upgradation work by G2G project. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2024-07-05 07:20 | 2024-07-05 10:07 | 2:47 | S/O | CT clamp hotspot maintenance and relay modification work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T3 HT | 2024-07-08 08:07 | 2024-07-08 08:07 | 0:00 | D/W | Transformer upgradation 50/75 to 80/120MVA. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T3 LT | 2024-07-08 08:07 | 2024-07-08 08:07 | 0:00 | D/W | Transformer upgradation 50/75 to 80/120MVA. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) HT | 2024-07-10 06:58 | 2024-07-10 09:01 | 2:03 | S/O | s/d taken by pbs due to 33kv feeder loop repair. | 32 | 65.6 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2024-07-17 08:16 | 2024-07-17 10:27 | 2:11 | S/O | Red hot on 33kV T -2 bus (T-6 bus clamp) | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2024-07-17 10:59 | 2024-07-17 12:23 | 1:24 | S/O | For T-4 transformer installation work. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Transfer Bus | 2024-07-17 08:07 | 2024-07-17 09:50 | 1:43 | S/O | For T-4 transformer installation work. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132 kV BUS-1 | 2024-07-15 06:59 | 2024-07-15 06:59 | 0:00 | S/O | Maintenance due to high temperature at various point | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2024-07-17 07:45 | 2024-07-17 08:25 | 0:40 | S/O | Red Hot | 30 | 20 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2024-07-30 06:45 | 2024-07-30 08:44 | 1:59 | S/O | Red hot Maintenance of pbs | 40 | 79.3333 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2024-07-17 08:52 | 2024-07-17 10:13 | 1:21 | S/O | Red Hot Maintenance. | 45 | 60.75 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2024-07-30 08:48 | 2024-07-30 09:58 | 1:10 | S/O | PBS Work | 40 | 46.6667 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 HT | 2024-07-15 06:20 | 2024-07-15 08:45 | 2:25 | S/O | Maintenance due to high temperature at various point of switchyard equipment | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 LT | 2024-07-17 06:29 | 2024-07-17 07:27 | 0:58 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Auxiliary Transformer - 1 HT | 2024-07-15 06:20 | 2024-07-15 08:45 | 2:25 | S/O | Maintenance work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Auxiliary Transformer - 2 HT | 2024-07-17 06:29 | 2024-07-17 07:28 | 0:59 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-02 HT | 2024-07-03 10:25 | 2024-07-03 18:00 | 7:35 | S/O | Relay replacement work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 LT | 2024-07-04 15:24 | 2024-07-04 22:22 | 6:58 | S/O | Troubleshooting work by SPMD | 0 | 0 | No interruption
|  |  | Total : | 89:44 |  | Unserved Energy: |  | 641.35
Dhaka (South) Grid Circle : | [9 empty] | 39.3333
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2024-07-09 06:02 | 2024-07-09 08:50 | 2:48 | S/O | Oti meter change | 50 | 140 | Power interruption
Bhulta 132/33kV Grid Sub-Station | GT2 HT | 2024-07-25 06:05 | 2024-07-25 07:27 | 1:22 | S/O | Due to red hot maintenance | 50 | 68.3333 | Power interruption
Haripur 230/132kV Grid Sub-Station | 132kV Bus Coupler | 2024-07-11 12:48 | 2024-07-11 14:52 | 2:04 | S/O | Maintenance work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-2 | 2024-07-11 12:48 | 2024-07-11 14:59 | 2:11 | S/O | Maintenance work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-2 HT | 2024-07-02 06:03 | 2024-07-02 09:10 | 3:07 | S/O | Redhot Maintanance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-2 HT | 2024-07-11 11:12 | 2024-07-11 15:03 | 3:51 | S/O | Maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 HT | 2024-07-08 10:40 | 2024-07-08 16:08 | 5:28 | S/O | 33 kv Kalatiya feeder(H13) under ground cable maintenance by PBS. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-2 HT | 2024-07-10 06:29 | 2024-07-10 08:14 | 1:45 | S/O | Relay change to 33Kv side | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) HT | 2024-07-13 06:52 | 2024-07-13 08:29 | 1:37 | S/O | For work on OLTC ( OSR ). | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 LT | 2024-07-01 19:14 | 2024-07-01 20:29 | 1:15 | S/O | T-3, 132kV CB Loop connection point Nutbolts Hotspot . | 50 | 62.5 | Power interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-1 | 2024-07-13 23:44 | 2024-07-14 02:01 | 2:17 | S/O | DS (631S) Red hot maintenance work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-1 | 2024-07-25 08:38 | 2024-07-25 12:28 | 3:50 | D/W | Jack Bus Dismentaled by CCCE . | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-1 | 2024-07-28 08:30 | 2024-07-28 12:58 | 4:28 | S/O | G2G project work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-2 | 2024-07-26 10:52 | 2024-07-26 21:12 | 10:20 | D/W | G2G project work for Tx-3 upper jack bus connection. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 HT | 2024-07-17 03:30 | 2024-07-17 23:17 | 19:47 | S/O | Explode 132 kV ct(3 phase) replace due to testing result not satiesfied | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 HT | 2024-07-05 05:25 | 2024-07-05 06:25 | 1:00 | S/O | New Auxiliary TX-4 connect to Auto Tx-4 | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV MI Cement HT | 2024-07-10 09:36 | 2024-07-10 21:07 | 11:31 | S/O | Regular maintenance | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2024-07-08 06:02 | 2024-07-08 11:30 | 5:28 | S/O | Temperature raising in HT bushing R phase clamp. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS B | 2024-07-11 14:55 | 2024-07-11 16:36 | 1:41 | S/O | Due to red hot corrective maintenance work at bashundhara line feeder. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS B | 2024-07-15 07:10 | 2024-07-15 10:00 | 2:50 | S/O | OPSL B-Bus DS corrective maintenance work. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | 33 kV bus | 2024-07-08 09:07 | 2024-07-08 11:09 | 2:02 | S/O | 33 kV Bus section 01 (ckt-02) Red-hot maintenance by PBS. | 15 | 30.5 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 HT | 2024-07-08 09:07 | 2024-07-08 18:10 | 9:03 | S/O | TR-01 high side red hot maintenance and all required testing were finished. | 0 | 0 | No interruption
|  |  | Total : | 99:45 |  | Unserved Energy: |  | 301.3333
Chattogram Grid Circle :
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 LT | 2024-07-27 11:58 | 2024-07-27 12:28 | 0:30 | S/O | Abnormal Sound Cheking by Contractor(CCCE) | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | Transformer -2 (D07) HT | 2024-07-17 06:52 | 2024-07-17 18:08 | 11:16 | S/O | CT Core allocation checking at 33kV feeders. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 403T(TR-1) HT | 2024-07-15 12:12 | 2024-07-15 12:12 | 0:00 | D/W | Due to old 48/64 MVA T-01 Transformer changing by new 80/120 MVA Transformer under ESPNER project. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 403T(TR-1) LT | 2024-07-08 11:50 | 2024-07-10 21:41 | 57:51 | S/O | Due to ESPNER Project Work. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) HT | 2024-07-15 06:19 | 2024-07-15 08:35 | 2:16 | S/O | Due to maintenance work | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) HT | 2024-07-12 08:20 | 2024-07-12 14:08 | 5:48 | S/O | Due to Auxiliary Transformer shifting work by BPDB. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) LT | 2024-07-15 07:04 | 2024-07-15 08:10 | 1:06 | S/O | Due to red hot at 33 kv side shutdown taken by PDB. | 5 | 5.5 | Power interruption
Khulshi 132/33kV Grid Sub-Station | 405T (T1) HT | 2024-07-06 06:25 | 2024-07-06 09:36 | 3:11 | S/O | 33kV Out-door Bus conductor(R-phase) change by BPDB. | 0 | 0 | No interruption
|  |  | Total : | 81:58 |  |  |  | 5.5
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | 401T HT | 2024-07-04 13:54 | 2024-07-04 16:30 | 2:36 | S/O | Gas leakage maintenance of Tr-1 A incoming. | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-2 HT | 2024-07-12 10:22 | 2024-07-12 12:43 | 2:21 | S/O | Red hot maintanance of Sunamganj pbs 33kv Feeder at Y-phase. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-1 | 2024-07-13 11:21 | 2024-07-13 12:13 | 0:52 | D/W | project work,Loop measurement work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-2 | 2024-07-09 09:33 | 2024-07-09 18:22 | 8:49 | D/W | G2G project work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-2 | 2024-07-10 10:02 | 2024-07-10 17:14 | 7:12 | D/W | G2G project work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 230 KV Bus-2 | 2024-07-08 08:56 | 2024-07-08 16:58 | 8:02 | D/W | G2G Project work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2024-07-13 10:58 | 2024-07-13 12:17 | 1:19 | D/W | Project work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2024-07-18 10:07 | 2024-07-18 17:41 | 7:34 | S/O | Project works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-07-09 09:04 | 2024-07-09 18:34 | 9:30 | D/W | G2G Project work purpose shutdown.. No loadshed occured. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2024-07-05 07:14 | 2024-07-05 08:41 | 1:27 | S/O | For 33KV Bus-1 Maintenance Work by BPDB | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2024-07-16 06:52 | 2024-07-16 18:03 | 11:11 | S/O | For Transformer and Itâ€™s bay Equipment Hotspot Maintenance Work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-07-13 07:40 | 2024-07-13 10:56 | 3:16 | S/O | 33kV REB Incomer-1 & 2 Load side T-Connector hot Spot Maintenance work | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-06 LT | 2024-07-03 17:48 | 2024-07-03 19:02 | 1:14 | S/O | Shutdown taken by PBS for 33KV Jamuna Feeder Load side D/S Maintenance. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-07-05 08:18 | 2024-07-05 12:30 | 4:12 | S/O | BPDB 33KV Bus side Red Hot Maintenance work | 8 | 33.6 | Power interruption
|  |  | Total : | 69:35 |  | Unserved Energy: |  | 33.6
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) HT | 2024-07-16 06:12 | 2024-07-16 07:28 | 1:16 | S/O | Maintenance work | 8 | 10.1333 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-07-10 07:06 | 2024-07-10 07:36 | 0:30 | S/O | For T-1 suspension disc insulator change work. | 40 | 20 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2024-07-25 07:25 | 2024-07-25 08:42 | 1:17 | S/O | S/d taken byPbs barishal 2 | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Main Bus Bar | 2024-07-01 14:26 | 2024-07-01 15:55 | 1:29 | D/W | DS maintenance | 35 | 51.9167 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-07-19 07:18 | 2024-07-19 09:28 | 2:10 | S/O | Due to red hot maintenance | 20 | 43.3333 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-5 HT | 2024-07-27 09:26 | 2024-07-27 11:25 | 1:59 | S/O | WZPDCL taken SD | 10 | 19.8333 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-07-27 09:29 | 2024-07-27 11:26 | 1:57 | S/O | WZPDCL taken SD | 10 | 19.5 | Power interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2024-07-19 07:12 | 2024-07-19 10:50 | 3:38 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2024-07-27 06:45 | 2024-07-27 19:13 | 12:28 | D/W | Blast wall Foundation piling | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2024-07-27 10:33 | 2024-07-27 13:33 | 3:00 | S/O | Red hot maintenance work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2024-07-29 07:30 | 2024-07-29 11:30 | 4:00 | S/O | Maintenance work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2024-07-08 07:50 | 2024-07-08 09:07 | 1:17 | S/O | 33kv shibchar feeder y-phase Source side DS high temperature maintenance | 10 | 12.8333 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T LT | 2024-07-26 06:17 | 2024-07-26 08:42 | 2:25 | S/O | 33 kv bus-section B-Phase- DS Finger chage. | 20 | 48.3333 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T LT | 2024-07-09 22:55 | 2024-07-10 01:07 | 2:12 | S/O | 33 kv agoiljora feeder fault work. | 25 | 55 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2024-07-26 06:14 | 2024-07-26 08:45 | 2:31 | S/O | 33 kv bus-section-03, B-Phase- DS Finger chage. | 20 | 50.3333 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-1 LT | 2024-07-14 07:55 | 2024-07-14 09:41 | 1:46 | S/O | 33kV BUS (Section-1) S/D due to REB-3, REB-4 High Temperature Point Maintenance. | 23 | 40.6333 | Power interruption
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 HT | 2024-07-10 10:16 | 2024-07-21 18:01 | 271:45 | D/W | Project work | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Generator Transformer-1 (GT-1) LT | 2024-07-03 15:27 | 2024-07-13 20:21 | 244:54 | D/W | Due to Maintenance | 0 | 0 | No interruption
|  |  | Total : | 560:34 |  | Unserved Energy : |  | 371.85
HVDC Grid Circle
Bheramara(GK) 132/33kV Grid Sub-Station | TR-1 LT | 2024-07-13 10:56 | 2024-07-13 12:22 | 1:26 | S/O | 33 kV busbar red hot repairing work | 38 | 54.4667 | Power interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-2 LT | 2024-07-13 10:56 | 2024-07-13 12:24 | 1:28 | S/O | 33 kV busbar red hot repairing work | 38 | 55.7333 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T1(416T) LT | 2024-07-13 11:20 | 2024-07-13 11:49 | 0:29 | D/W | SCADA integration with NLDC | 40.8 | 19.72 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T2(426T) LT | 2024-07-13 12:35 | 2024-07-13 12:50 | 0:15 | D/W | SCADA Integration With NLDC | 35 | 8.75 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2024-07-30 07:23 | 2024-07-30 09:09 | 1:46 | S/O | 33 kKV incomer-1 CT oil leakage maintenance | 30 | 53 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 HT | 2024-07-19 07:13 | 2024-07-19 11:35 | 4:22 | S/O | Maintenance work | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 (425T) LT | 2024-07-31 07:02 | 2024-07-31 10:06 | 3:04 | S/O | RED HOT MAINTENANCE. | 20 | 61.3333 | Power interruption
Ruppur 132/11kV Grid Sub-Station | TR-01 LT | 2024-07-03 09:05 | 2024-07-03 13:32 | 4:27 | S/O | Annual Maintenance work by NESCO | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | Power Transformer -1 LT | 2024-07-03 09:23 | 2024-07-03 11:20 | 1:57 | D/W | 132kV T_1 BKR Gas leakage detect . | 0 | 0 | No interruption
|  |  | Total : | 19:14 |  | Unserved Energy : |  | 253.0033
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | T-3 (426T) LT | 2024-07-01 08:22 | 2024-07-01 11:14 | 2:52 | S/O | Due to Isolator installation of Aux-1. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 1 | 2024-07-05 07:10 | 2024-07-08 16:02 | 80:52 | S/O | BUS Upgradation | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-07-11 07:05 | 2024-07-24 14:40 | 319:35 | S/O | 230kV Main Bus Upgradation work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 HT | 2024-07-14 14:25 | 2024-07-14 16:40 | 2:15 | S/O | 230kV Bus Upgradation work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-03 HT | 2024-07-15 09:10 | 2024-07-15 10:55 | 1:45 | S/O | Oil Leakage Maintenance work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-04 HT | 2024-07-05 07:12 | 2024-07-06 16:36 | 33:24 | S/O | BUS Upgradation | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-04 HT | 2024-07-14 13:05 | 2024-07-14 14:23 | 1:18 | S/O | Bus upgradetion | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T-2 LT | 2024-07-25 06:22 | 2024-07-25 10:26 | 4:04 | S/O | 33 KV Bus Section-02 Shutdown for maintenance work of Debiganj-02 33 KV Feeder Source Isolator. | 30 | 122 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) HT | 2024-07-05 07:14 | 2024-07-05 10:24 | 3:10 | S/O | Red hot maintanance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-4 (435 T) LT | 2024-07-02 09:31 | 2024-07-12 12:08 | 242:37 | D/W | Transformer upgrading work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-3(426T) HT | 2024-07-16 09:53 | 2024-07-16 09:53 | 0:00 | D/W | Upgradation of Tr-03 bay equipment. | 0 | …... | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-3(426T) LT | 2024-07-16 09:53 | 2024-07-16 09:53 | 0:00 | D/W | Upgradation of Tr-3 bay equipment. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-4 Transformer LT | 2024-07-17 08:17 | 2024-07-17 15:23 | 7:06 | S/O | Control status rectification | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) HT | 2024-07-08 07:37 | 2024-07-08 09:06 | 1:29 | S/O | Red hot maintenance at 33 KV BUs of PBS | 25 | 37.0833 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-07-27 07:09 | 2024-07-27 09:04 | 1:55 | S/O | Due to Taherpur Feeder Red Hot (Bus DS) Maintenance work. | 40 | 76.6667 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-02 (416T) HT | 2024-07-10 11:31 | 2024-07-10 17:12 | 5:41 | S/O | 33kV Feeder Basantopur, Kakonhut Dismantling | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | 132KV Bus A | 2024-07-13 09:41 | 2024-07-13 13:44 | 4:03 | S/O | Maintenance work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | 132KV Bus B | 2024-07-13 13:46 | 2024-07-13 15:14 | 1:28 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 713:34 |  | Unserved Energy : |  | 235.75
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1634:24 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:July 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-07-25 10:25 | 2024-07-25 20:29 | 10:04 | D/W | New tower erection work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-07-26 09:19 | 2024-07-26 18:48 | 9:29 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-07-27 10:00 | 2024-07-27 18:15 | 8:15 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-07-29 10:02 | 2024-07-29 21:23 | 11:21 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-07-30 09:35 | 2024-07-30 18:44 | 9:09 | S/O | Tower erection work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-02 | 2024-07-17 06:50 | 2024-07-17 06:50 | 0:00 | D/W | Conductor Reinstringing | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2024-07-10 08:46 | 2024-07-10 19:31 | 10:45 | S/O | Line Ds wiring | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-1 | 2024-07-29 08:11 | 2024-07-29 12:52 | 4:41 | D/W | AIS to GIS project work | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur Ckt- 01 | 2024-07-15 06:33 | 2024-07-15 10:08 | 3:35 | S/O | High Temperature maintenance. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur Ckt- 02 | 2024-07-17 06:44 | 2024-07-17 09:49 | 3:05 | S/O | High temperature maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-01 | 2024-07-31 07:42 | 2024-07-31 20:09 | 12:27 | D/W | Project Work | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-07-26 07:41 | 2024-07-26 17:44 | 10:03 | D/W | Project work | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-07-27 06:28 | 2024-07-27 20:04 | 13:36 | D/W | Project Work | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-07-28 07:08 | 2024-07-28 18:50 | 11:42 | D/W | Project Work | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-07-29 06:31 | 2024-07-29 19:50 | 13:19 | D/W | Project Work | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-07-31 06:32 | 2024-07-31 07:42 | 1:10 | D/W | Project Work | 15 | 17.5 | Power interruption
Ghatail 132/33kV Grid Sub-Station | Tangail -2 | 2024-07-05 08:30 | 2024-07-05 18:16 | 9:46 | D/W | 400KV Boropukuria-bogura-kaliakair line Conductor Stringing. | 0 | 0 | No interruption
Ghatail 132/33kV Grid Sub-Station | Tangail-1 | 2024-07-05 08:30 | 2024-07-05 18:15 | 9:45 | D/W | 400KV Boropukuria-bogura-kaliakair line Conductor Stringing. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2024-07-09 10:15 | 2024-07-09 12:52 | 2:37 | S/O | Line maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2024-07-17 07:50 | 2024-07-26 18:48 | 226:58 | S/O | Works at aminbazar end. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2024-07-28 09:42 | 2024-07-30 18:44 | 57:02 | S/O | NLDC. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2024-07-31 09:31 | 2024-07-31 17:45 | 8:14 | S/O | By NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -2 | 2024-07-09 12:58 | 2024-07-09 15:03 | 2:05 | S/O | Line maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -2 | 2024-07-17 07:06 | 2024-07-17 07:06 | 0:00 | S/O | Works at Aminbazar end. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-1 | 2024-07-12 08:40 | 2024-07-12 15:45 | 7:05 | D/W | Project Work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-2 | 2024-07-12 08:49 | 2024-07-12 15:45 | 6:56 | D/W | Project Work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-07-30 08:32 | 2024-07-30 11:22 | 2:50 | S/O | project works | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-07-01 09:43 | 2024-07-01 18:54 | 9:11 | D/W | Project work. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Kaliakoir ckt-2B(E-09) | 2024-07-12 08:48 | 2024-07-12 15:52 | 7:04 | D/W | S/D taken by 400kv Aminbazar-Kaliakoir Line project | 34 | 240.2667 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-1 | 2024-07-15 06:30 | 2024-07-15 10:07 | 3:37 | S/O | Maintenance due to high temperature at various point of switchyard equipment | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2024-07-17 06:40 | 2024-07-17 09:50 | 3:10 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Kaliakair-1 | 2024-07-12 08:44 | 2024-07-12 15:51 | 7:07 | D/W | project purpose | 100 | 711.6667 | Power interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2024-07-05 08:30 | 2024-07-05 18:20 | 9:50 | D/W | Project work | 55 | 540.8333 | Power interruption
Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2024-07-05 08:30 | 2024-07-05 18:20 | 9:50 | D/W | Project work | 55 | 540.8333 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2024-07-09 13:52 | 2024-07-09 16:04 | 2:12 | S/O | Maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-2 | 2024-07-09 16:11 | 2024-07-09 17:58 | 1:47 | S/O | Maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-07-11 07:02 | 2024-07-11 08:12 | 1:10 | S/O | Maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2024-07-04 10:22 | 2024-07-04 12:52 | 2:30 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 523:27 |  | Unserved Energy: |  | 2051.1
Dhaka (South) Grid Circle :
Bhulta 400/230kV Grid Sub-Station | Ghorashal-02 | 2024-07-13 08:12 | 2024-07-13 13:30 | 5:18 | S/O | Red hot maintenance work at Ghorashal end. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-07-04 13:10 | 2024-07-04 18:23 | 5:13 | S/O | CB Open: 13:10 Line Isolator Open: 13:11 Earth S/W Close: 13:22 for Project Work | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-07-10 07:28 | 2024-07-14 12:07 | 100:39 | S/O | Maintenance work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Madanganj-2 | 2024-07-11 11:21 | 2024-07-11 14:27 | 3:06 | S/O | Maintenance work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddhirganj-1 | 2024-07-09 13:25 | 2024-07-09 16:09 | 2:44 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Shitallakhya | 2024-07-04 13:29 | 2024-07-04 18:39 | 5:10 | S/O | Tower dismantled | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2024-07-16 15:49 | 2024-07-16 18:47 | 2:58 | D/W | Project work,S/D taken by NLDC. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | 132 KV BUS Coupler CB | 2024-07-10 11:35 | 2024-07-10 14:37 | 3:02 | S/O | Maintenance work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2024-07-11 11:19 | 2024-07-11 15:26 | 4:07 | S/O | Maintenance work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-1 | 2024-07-10 11:38 | 2024-07-10 14:35 | 2:57 | S/O | Maintenance work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-07-04 13:09 | 2024-07-04 18:24 | 5:15 | D/W | None | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-07-10 07:26 | 2024-07-14 12:08 | 100:42 | D/W | Project work | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -2 | 2024-07-14 14:26 | 2024-07-14 16:15 | 1:49 | S/O | P T-(R phase) Harming Mentenance work. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Mero Rail - 2 | 2024-07-02 00:57 | 2024-07-17 23:33 | 382:36 | S/O | TT para underground Railway Crossing Pilling work. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-1 | 2024-07-30 14:58 | 2024-07-30 16:25 | 1:27 | S/O | Shut down taken by Mr. Rokonul Islam, SDE, Grid South-2, DPDC. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-2 | 2024-07-31 14:34 | 2024-07-31 17:40 | 3:06 | S/O | Maintenance Works. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-ST (MPL) | 2024-07-11 06:45 | 2024-07-11 09:28 | 2:43 | S/O | Preventive maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Aminbazar 400KV Ckt-2 | 2024-07-09 10:51 | 2024-07-09 21:16 | 10:25 | D/W | Project work | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Reliance PP 400KV Ckt-2 | 2024-07-15 12:10 | 2024-07-15 12:10 | 0:00 | D/W | SAS & DFDR Configuration | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Summit PP 400KV Ckt-1 | 2024-07-07 10:10 | 2024-07-07 18:08 | 7:58 | D/W | SAS & DFDR Extension work. | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Summit PP 400KV Ckt-1 | 2024-07-08 10:14 | 2024-07-08 21:18 | 11:04 | S/O | SAS & DFDR extension work. | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Summit PP 400KV Ckt-1 | 2024-07-09 09:30 | 2024-07-09 21:36 | 12:06 | D/W | Project work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-07-15 05:28 | 2024-07-15 10:18 | 4:50 | S/O | Line Ds 141s Maintenance | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-04 | 2024-07-25 08:44 | 2024-07-25 08:44 | 0:00 | D/W | shutdown for equipement dismentled. | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-07-29 07:17 | 2024-07-29 07:17 | 0:00 | S/O | By NLDC | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2024-07-08 06:02 | 2024-07-08 11:30 | 5:28 | S/O | Corrective maintenance. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2024-07-16 09:17 | 2024-07-16 13:37 | 4:20 | S/O | EGCB end. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 2 | 2024-07-16 13:47 | 2024-07-16 17:12 | 3:25 | S/O | EGCB end. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2024-07-15 06:42 | 2024-07-15 10:55 | 4:13 | S/O | Corrective maintenance work at Bus-B isolator B-phase Finger point. | 0 | 0 | No interruption
|  |  | Total : | 696:41 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | PHP | 2024-07-07 08:23 | 2024-07-07 17:59 | 9:36 | S/O | PHP s/s maintenance work | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-07-10 09:54 | 2024-07-10 18:30 | 8:36 | S/O | Dismantling Building Railing for Proper Ground Clearance of Hali-Rampur Ckt-02 . | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-07-11 07:29 | 2024-07-11 17:48 | 10:19 | S/O | Dismantling Building Railing for Proper Ground Clearance of Hali-Rampur Ckt-02 . | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | GPH-01 | 2024-07-06 11:55 | 2024-07-06 13:15 | 1:20 | D/W | Safety clearance. For GIS cable pot install | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2024-07-10 09:54 | 2024-07-10 18:29 | 8:35 | D/W | project work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2024-07-11 07:28 | 2024-07-11 17:49 | 10:21 | D/W | PROJECT WORK | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2024-07-10 09:55 | 2024-07-11 18:11 | 32:16 | D/W | project work | 0 | 0 | No interruption
|  |  | Total : | 81:03 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-2 | 2024-07-09 10:59 | 2024-07-15 15:35 | 148:36 | D/W | G2G Project purpose. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | PHP (ISML) Ckt | 2024-07-07 08:20 | 2024-07-07 18:02 | 9:42 | S/O | PHP maintenance work | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-2 | 2024-07-15 19:28 | 2024-07-15 22:31 | 3:03 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 161:21 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-07-01 14:27 | 2024-07-01 15:54 | 1:27 | S/O | Approved by ALDC | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 2024-07-29 11:47 | 2024-07-29 15:35 | 3:48 | S/O | Removes Kites | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-2 | 2024-07-29 11:48 | 2024-07-29 15:37 | 3:49 | S/O | Removes Kites | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Bagerhat | 2024-07-14 09:12 | 2024-07-14 12:46 | 3:34 | S/O | To change damage meter | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Gallamari Ckt-2 | 2024-07-28 06:41 | 2024-07-28 09:29 | 2:48 | S/O | Red Hot maintenance Work. | 0 | 0 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | Khulna Central Ckt-2 | 2024-07-28 08:06 | 2024-07-28 10:14 | 2:08 | S/O | Transformers are ok. Communication Systems are ok. IP camera, Solar system are ok. Security duty is properly. Now Shift charge received in normal condition. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-2 | 2024-07-27 07:39 | 2024-07-27 11:21 | 3:42 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | UPPL (150MW) 132kV LINE | 2024-07-09 12:38 | 2024-07-10 17:58 | 29:20 | S/O | scada related work | 0 | 0 | No interruption
|  |  | Total : | 50:36 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
BIPTC | Baharampur-3 | 2024-07-09 09:41 | 2024-07-09 20:19 | 10:38 | S/O | Shutdown is taken from Berhampore end. | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2024-07-10 10:05 | 2024-07-10 20:35 | 10:30 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2024-07-11 10:09 | 2024-07-11 20:06 | 9:57 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2024-07-12 11:07 | 2024-07-12 20:50 | 9:43 | S/O | Shutdown is taken from Baharampur end. | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2024-07-13 10:03 | 2024-07-13 20:00 | 9:57 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2024-07-14 10:12 | 2024-07-14 19:49 | 9:37 | S/O | Maintenance work | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Sirajgonj-1 | 2024-07-15 06:09 | 2024-07-15 09:56 | 3:47 | D/W | IDRNPP project work | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Sirajgonj-2 | 2024-07-15 06:10 | 2024-07-15 09:58 | 3:48 | D/W | IDRNPP project work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV HVDC 3 | 2024-07-18 16:43 | 2024-07-18 17:38 | 0:55 | S/O | CB TC-1 faulty maintenance | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | 132 KV Sirajgonj Ckt-1 | 2024-07-08 06:00 | 2024-07-08 13:10 | 7:10 | D/W | Project Work | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | 132 KV Sirajgonj Ckt-2 | 2024-07-08 06:02 | 2024-07-08 13:11 | 7:09 | D/W | Project Work | 0 | 0 | No interruption
|  |  | Total : | 83:11 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura 132/33kV Grid Sub-Station | Natore-1 | 2024-07-27 07:30 | 2024-07-27 09:06 | 1:36 | S/O | strand cutting | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2024-07-19 05:03 | 2024-07-19 12:55 | 7:52 | S/O | development work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2024-07-22 06:02 | 2024-07-22 14:38 | 8:36 | S/O | 230kV Bus Upgradation work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Confidance UN-1 | 2024-07-24 10:43 | 2024-07-24 16:57 | 6:14 | S/O | 132kV Sherpur Ckt.-1 1st Span Conductor(R-Phase) place change. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Serajganj Line-1 | 2024-07-11 07:15 | 2024-07-12 17:03 | 33:48 | S/O | 230kV Main Bus Upgradation work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Serajganj Line-2 | 2024-07-15 10:04 | 2024-07-15 21:09 | 11:05 | S/O | 230kV Bus Upgradation work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-1 | 2024-07-24 10:37 | 2024-07-24 17:17 | 6:40 | S/O | 1st Span Conductor(R-Phase) place change. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-07-06 10:32 | 2024-07-06 17:06 | 6:34 | S/O | ALDC à¦¨à¦¿à¦°à§à¦¦à§‡à¦¶à§‡à¥¤ | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-07-16 06:24 | 2024-07-16 18:35 | 12:11 | D/W | In order of ALDC Bogura | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Chowdala 132 KV Line Ckt-01 | 2024-07-03 15:38 | 2024-07-03 15:40 | 0:02 | S/O | Checking | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Chowdala 132 KV Line Ckt-02 | 2024-07-03 15:39 | 2024-07-03 15:41 | 0:02 | S/O | Checking | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Barapukuria-1 | 2024-07-13 08:32 | 2024-07-13 16:18 | 7:46 | S/O | Rad hot remove | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Barapukuria-2 | 2024-07-05 08:24 | 2024-07-05 11:30 | 3:06 | S/O | Temperature Rise | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Confidence-2 | 2024-07-10 07:14 | 2024-07-10 12:23 | 5:09 | S/O | Temperature high CT junction point | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Solar Park 2 | 2024-07-30 11:34 | 2024-07-30 11:34 | 0:00 | D/W | For Testing Perposed | 0 | 0 | No interruption
|  |  | Total : | 110:41 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0:00 |  |  |  | 0:00
…...
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1707:00 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:July 2024
| Area | Previous Month (June' 2024) |  |  |  | Current Month (July '2024)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 31 | 22 | 65 | 119 | 29 | 19 | 74 | 122
2 | Dhaka (South) Grid Circle. | 27 | 18 | 42 | 87 | 19 | 7 | 51 | 77
3 | Chattogram Grid Circle. | 12 | 17 | 44 | 73 | 15 | 19 | 15 | 49
4 | Cumilla Grid Circle. | 20 | 13 | 40 | 73 | 7 | 6 | 17 | 30
5 | Khulna Grid Circle. | 20 | 21 | 30 | 71 | 4 | 16 | 26 | 46
6 | HVDC Grid Circle | 1 | 14 | 10 | 25 | 17 | 11 | 20 | 48
7 | Bogura Grid Circle. | 50 | 24 | 62 | 136 | 7 | 19 | 33 | 59
8 | Others
9 | Total | 161 | 129 | 293 | 584 | 98 | 97 | 236 | 431
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
…...

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:July 2024
| Area | Previous Month (June' 2024) |  |  |  | Current Month (July '2024)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 516.77 | 1347.08 | 2822.78 | 4686.63 | 746.75 | 948.01 | 2692.45 | 4387.21
2 | Dhaka (South) Grid Circle. | 172.84 | 224.07 | 0 | 396.91 | 1281.15 | 186.67 | 301.33 | 1769.15
3 | Chattogram Grid Circle. | 52.59 | 157.92 | 277.25 | 487.76 | 410.29 | 118.47 | 5.5 | 534.26
4 | Cumilla Grid Circle. | 64.2 | 1017.76 | 1168.47 | 2250.43 | 708.36 | 220.58 | 33.6 | 962.54
5 | Khulna Grid Circle. | 782.35 | 590.79 | 1314.73 | 2687.87 | 31.55 | 461.17 | 371.85 | 864.57
6 | HVDC Grid Circle | 0 | 229.82 | 227.3 | 457.12 | 307.53 | 749 | 253 | 1309.53
7 | Bogura Grid Circle. | 572.78 | 428.13 | 2200.25 | 3201.16 | 420.12 | 328.3 | 235.75 | 984.17
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 2161.53 | 3995.57 | 8010.78 | 14167.88 | 3905.75 | 3012.2 | 3893.48 | 10811.43
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
…...

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:July 2024
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 20 | 11 | 31 | 8 | 5 | 18 | 2152.6
2 | Dhaka (South) | 5031.6 | 5 | 4 | 9 | 2 | 1 | 6 | 877.36
3 | Chattogram | 2042 | 10 | 1 | 11 | 3 | 2 | 6 | 177.26
4 | Khulna | 2434 | 10 | 11 | 21 | 3 | 1 | 17 | 689.3
5 | HVDC | 5954.3 | 20 | 6 | 26 | 12 | 3 | 11 | 1309.53
6 | Bogura | 3145.6 | 16 | 3 | 19 | 4 | 4 | 11 | 977.87
7 | Cumilla | 2981 | 5 | 1 | 6 | - | - | 6 | 937.35
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 7121.27
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.96%
3 | Chattogram | 99.98%
4 | Khulna | 99.97%
5 | HVDC | 99.96% | [6 empty] | Executive Engineer
6 | Bogura | 99.95% | [6 empty] | Information Management Division
7 | Cumilla | 99.98% | [6 empty] | LDC, PGCB, Dhaka.
…...

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:July 2024
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 | 5 | 8 | 2 | - | 6 | 2234.6
2 | Dhaka (South) | 990.29 | - | 4 | - | 4 | 1 | 1 | 2 | 891.78
3 | Chattogram | 917 | - | 1 | - | 1 | - |  | 1 | 357
4 | Khulna | 1238.4 | - | 3 |  | 3 | - | - | 3 | 175.27
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 2 | - | 2 | 2 | - | - | 6.3
7 | Cumilla | 1648.16 | - | 2 | - | 2 | 2 | - | - | 25.2
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 3690.15
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.99%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
…...

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:July 2024
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2024-07-01 | 9 | - | 21 | 35hr38 min | 3 | 7hr58 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
…...

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:July 2024
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bhaluka 132/33kV Grid Sub-Station | 3 | 2:11 | 110.83
Dhamrai 132/33kV Grid Sub-Station | 3 | 8:36 | 481.83
Kabirpur 132/33kV Grid Sub-Station | 1 | 2:00 | 120
Kishoreganj 132/33kV Grid Sub-Station | 1 | 0:34 | 8.5
Manikganj 132/33kV Grid Sub-Station | 1 | 1:24 | 28
Mymensingh 132/33kV Grid Sub-Station | 2 | 1:10 | 55.25
Mymensingh 132/33kV Grid Sub-Station | 5 | 0:19 | 20.5833
Sreepur 230/132/33kV Grid Sub-Station | 2 | 0:54 | 31.5
Tangail 132/33kV Grid Sub-Station | 2 | 0:19 | 20.5833
Tangail 132/33kV Grid Sub-Station | 1 | 0:10 | 10.8333
Tangail 132/33kV Grid Sub-Station | 1 | 2:12 | 176
Tangail 132/33kV Grid Sub-Station | 2 | 0:20 | 21.6667
Tangail 132/33kV Grid Sub-Station | 2 | 3:21 | 217.75
Tangail 132/33kV Grid Sub-Station | 1 | 2:14 | 178.6667
Tongi 230/132/33kV Grid Sub-Station | 1 | 0:09 | 29.25
Joydebpur 132/33kV Grid Sub-Station | 2 | 1:56 | 154.6667
Kabirpur 132/33kV Grid Sub-Station | 2 | 0:21 | 24.5
Kallyanpur 132/33kV Grid Sub-Station | 1 | 0:20 | 4.3333
Bhaluka 132/33kV Grid Sub-Station | 3 | 3:29 | 104.5
Dhamrai 132/33kV Grid Sub-Station | 2 | 3:18 | 109.5
Kabirpur 132/33kV Grid Sub-Station | 1 | 3:06 | 155
Mirzapur 132/33kV GIS Grid Sub-Station | 1 | 2:03 | 65.6
Sreepur 230/132/33kV Grid Sub-Station | 4 | 5:10 | 206.75
Dhamrai 132/33kV Grid Sub-Station | 1 | 1:10 | 17.5
Mirzapur 132/33kV GIS Grid Sub-Station | 1 | 7:04 | 240.2667
Tangail 132/33kV Grid Sub-Station | 1 | 26:47 | 1793.33
Bhulta 132/33kV Grid Sub-Station | 2 | 2:48 | 280
Keranigonj 230/132/33kV Grid Sub-Station | 1 | 0:19 | 5.0667
Siddhirganj 132/33kV Grid Sub-Station | 2 | 5:01 | 290.97
Hasnabad 132/33kV Grid Substation | 1 | 0:39 | 42.25
Maniknagar 132/33kV Grid Sub-Station | 1 | 13:58 | 614.5333
Rampura 230/132kV Grid Sub-Station | 2 | 2:21 | 235
Bhulta 132/33kV Grid Sub-Station | 2 | 4:10 | 208.33
Narshingdi 132/33kV Grid Sub-Station | 1 | 1:15 | 62.5
Srinagar 132/33kV Grid Sub-Station | 1 | 2:02 | 30.5
Bakulia 132/33kV Grid Sub-Station | 1 | 0:42 | 8.4
Baroirhat 132/33kV Grid Sub-Station | 1 | 2:09 | 21.5
Coxsbazar 132/33kV Grid Sub-Station | 2 | 2:02 | 72.37
Dohazari 132/33kV Grid Sub-Station | 2 | 1:33 | 25.4
Hathazari 230/132/33kV Grid Sub-Station | 2 | 0:16 | 6.4
TK chemical 132kV Grid Sub-Station | 2 | 62:49 | 37.69
Baroaulia 132/33kV Grid Sub-Station | 1 | 35:42 | 357
Halishahar 132/33kV Grid Sub-Station | 1 | 1:06 | 5.5
Beanibazar 132/33kV Grid Sub-Station | 2 | 3:54 | 109.58
Chowmuhani 132/33kV Grid Sub-Station | 3 | 14:19 | 695.83
Sunamganj 132/33kV Grid Sub-Station | 1 | 3:56 | 98.3333
Kulaura 132/33kV Grid Sub-Station | 2 | 0:54 | 25.2
Sunamganj 132/33kV Grid Sub-Station | 1 | 4:12 | 33.6
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:16 | 10.9333
Barishal 132/33kV Grid Sub-Station | 1 | 0:16 | 10.1333
Bhandaria 132/33kV Grid Sub-Station | 1 | 0:17 | 10.4833
Gopalganj 132/33kV Grid Sub-Station | 1 | 1:40 | 20
Madaripur 132/33kV Grid Sub-Station | 1 | 2:22 | 37.8667
Mongla 132/33kV Grid Sub-Station | 4 | 9:53 | 217.43
Satkhira 132/33kV Grid Sub-Station | 1 | 0:53 | 10.6
Mongla 132/33kV Grid Sub-Station | 3 | 7:58 | 175.27
Bagerhat 132/33kV Grid Sub-Station | 1 | 1:16 | 10.1333
Barishal 132/33kV Grid Sub-Station | 1 | 0:30 | 20
Bhandaria 132/33kV Grid Sub-Station | 1 | 1:29 | 51.9167
Faridpur 132/33kV Grid Sub-Station | 1 | 2:10 | 43.3333
Goalpara 132/33kV Grid Sub-Station | 2 | 3:56 | 39.33
Madaripur 132/33kV Grid Sub-Station | 4 | 8:25 | 166.5
Noapara 132/33kV Grid Sub-Station | 1 | 1:46 | 40.6333
Chuadanga 132/33kV Grid Sub-Station | 3 | 1:25 | 48.18
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:46 | 23
Jhenaidah 132/33kV Grid Sub-Station | 1 | 1:55 | 46
Kushtia 132/33kV Grid Sub-Station | 7 | 35:28 | 810.9
Pabna 132/33kV Grid Sub-Station | 8 | 6:23 | 128.45
Bheramara(GK) 132/33kV Grid Sub-Station | 2 | 2:54 | 110.2
Chuadanga 132/33kV Grid Sub-Station | 2 | 0:44 | 28.47
Ishurdi 132/33kV Grid Sub-Station | 1 | 1:46 | 53
Magura 132/33kV Grid Sub-Station | 1 | 3:04 | 61.3333
Bog-Sherpur 132/33kV Grid Sub-Station | 2 | 1:28 | 76.27
Bogura 132/33kV Grid Sub-Station | 6 | 9:55 | 159.13
Jaldhaka 132/33kV Grid Sub-Station | 1 | 2:34 | 89.8333
Niamatpur 132/33kV Grid Sub-Station | 1 | 0:10 | 2.1667
Rangpur 132/33kV Grid Sub-Station | 2 | 5:22 | 294.67
Sirajganj 132/33kV Grid Sub-Station | 4 | 3:30 | 120.05
Saidpur 132/33kV Grid Sub-Station | 2 | 0:27 | 6.3
Jaldhaka 132/33kV Grid Sub-Station | 1 | 4:04 | 122
Rajshahi 132/33kV Grid Sub-Station | 2 | 3:24 | 113.75
Total Unserved energy : | 152 | 375:10 | 10811.41
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
…...

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July 2024
Sl. No | Name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2024-07-17 23:00 | 40
2 | Agargaon 230/132kV Grid Sub-Station | 2024-07-18 15:00 | 130
3 | Banani 132/33kV Grid Sub-Station | 2024-07-03 16:00 | 86.2
4 | Bangabhaban 132/33kV Grid Sub-Station | 2024-07-28 10:00 | 26
5 | Bashundhara 132/33kV Grid Sub-Station | 2024-07-07 14:00 | 191
6 | BashundharaCement 132/33kV Sub-Station | 2024-07-03 11:00 | 12
7 | Bhulta 132/33kV Grid Sub-Station | 2024-07-04 20:00 | 264
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2024-07-07 15:00 | 142
9 | Charsaidpur 132/33kV Sub-Station | 2024-07-10 20:00 | 44
10 | Dhaka University 132/33kV Grid Sub-Station | 2024-07-31 13:00 | 70
11 | Dhamrai 132/33kV Grid Sub-Station | 2024-07-08 18:00 | 140
12 | Dhanmondi 132/33kV Grid Sub-Station | 2024-07-31 13:00 | 174
13 | Fatullah 132/33kV Grid Sub-Station | 2024-07-18 11:00 | 94
14 | Ghorashal 230/132/33kV Sub-Station | 2024-07-30 21:00 | 68
15 | Gulshan 132/33kV Grid Sub-Station | 2024-07-15 13:00 | 142
16 | HaripurSBU 132/33kV Sub-Station | 2024-07-06 06:00 | 246
17 | Hasnabad 132/33kV Grid Substation | 2024-07-24 17:00 | 138
18 | Joydebpur 132/33kV Grid Sub-Station | 2024-07-27 19:30 | 210
19 | Kabirpur 132/33kV Grid Sub-Station | 2024-07-04 10:00 | 304
20 | Kallyanpur 132/33kV Grid Sub-Station | 2024-07-18 19:30 | 126
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2024-07-11 13:00 | 60.8
22 | Kazla 132/33kV Grid Sub-Station | 2024-07-15 16:00 | 121
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2024-07-03 21:00 | 90
24 | Kodda 132/33kV Grid Sub-Station | 2024-07-30 21:00 | 297
25 | Lalbag 132/33kV Grid Sub-Station | 2024-07-30 10:00 | 107
26 | Madanganj 132/33kV Grid Sub-Station | 2024-07-29 | 48
27 | Madartek 132/33kV Grid Sub-Station | 2024-07-19 01:00 | 108.64
28 | Manikganj 132/33kV Grid Sub-Station | 2024-07-26 22:00 | 133
29 | Maniknagar 132/33kV Grid Sub-Station | 2024-07-08 13:00 | 83
30 | Matuail 132/33kV Grid Sub-Station | 2024-07-17 15:00 | 78
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2024-07-18 15:00 | 144
32 | Mirpur 132/33kV Grid Sub-Station | 2024-07-17 19:30 | 161
33 | MI_Cement 132/33kV Grid Sub-Station | 2024-07-31 15:00 | 19
34 | Mogbazar 132/33kV Grid Sub-Station | 2024-07-15 16:00 | 146.1
35 | Motijheel 132/33kV Grid Sub-Station | 2024-07-31 13:00 | 49
36 | Munshiganj 132/33kV Grid Sub-Station | 2024-07-27 23:00 | 120
37 | Narinda 132/33kV Grid Sub-Station | 2024-07-16 13:00 | 82
38 | Narshingdi 132/33kV Grid Sub-Station | 2024-07-02 19:30 | 181
39 | Nawabganj 132/33kV Grid Sub-Station | 2024-07-18 22:00 | 57.4
40 | New Tongi 132/33kV Grid Sub-Station | 2024-07-29 12:00 | 60.4
41 | Postogola 132/33kV Grid Sub-Station | 2024-07-30 13:00 | 65
42 | Purbachal 132/33kV Grid Sub-Station | 2024-07-18 15:00 | 37
43 | Rahim Steel 132/33kV Sub-Station | 2024-07-31 10:00 | 138
44 | Rajendrapur 132/33kV Grid Sub-Station | 2024-07-06 20:00 | 108
45 | Satmasjid 132/33kV Grid Sub-Station | 2024-07-18 19:30 | 125
46 | Savar 132/33kV Grid Sub-Station | 2024-07-14 12:00 | 222
47 | SevenRings 132/11kV Sub-Station | 2024-07-29 16:00 | 20.9
48 | ShahCement 132/33kV Grid Sub-Station | 2024-07-09 16:00 | 30
49 | Shitalakhya 132/33kV Grid Sub-Station | 2024-07-15 13:00 | 96.3
50 | Shyampur 132/33kV Grid Sub-Station | 2024-07-30 12:00 | 172
51 | Siddhirganj 132/33kV Grid Sub-Station | 2024-07-29 12:00 | 135
52 | Sonargaon 132/33kV Grid Sub-Station | 2024-07-04 11:00 | 101
53 | Sreepur 230/132/33kV Grid Sub-Station | 2024-07-08 18:30 | 103
54 | Srinagar 132/33kV Grid Sub-Station | 2024-07-18 21:00 | 52.46
55 | Tongi 230/132/33kV Grid Sub-Station | 2024-07-06 15:00 | 133
56 | Ullon 132/33kV Grid Sub-Station | 2024-07-18 21:00 | 65
57 | Uttara 132/33kV Grid Sub-Station | 2024-07-18 16:00 | 94
58 | UttaraNew 132/33kV Grid Sub-Station | 2024-07-17 23:00 | 69
59 | Zigatola 132/33kV Grid Sub-Station | 2024-07-17 19:30 | 100
60 | Agrabad 132/33kV Grid Sub-Station | 2024-07-16 19:00 | 102
61 | AKS 132/33kV Grid Sub-Station | 2024-07-31 | 8
62 | AKSML 230/33kV Grid Sub-Station | 2024-07-06 12:00 | 124
63 | Bakulia 132/33kV Grid Sub-Station | 2024-07-14 16:00 | 105
64 | Baroaulia 132/33kV Grid Sub-Station | 2024-07-29 21:00 | 76
65 | Baroirhat 132/33kV Grid Sub-Station | 2024-07-18 19:00 | 76
66 | BSRM 230/33kV Grid Sub-Station | 2024-07-03 03:00 | 195
67 | Chandraghona 132/33kV Grid Sub-Station | 2024-07-28 19:00 | 40
68 | Coxsbazar 132/33kV Grid Sub-Station | 2024-07-18 19:00 | 136
69 | Dohazari 132/33kV Grid Sub-Station | 2024-07-14 19:30 | 110
70 | GPH 230/33kV Grid Sub-Station | 2024-07-06 | 97
71 | Halishahar 132/33kV Grid Sub-Station | 2024-07-15 17:00 | 83.5
72 | Hathazari 230/132/33kV Grid Sub-Station | 2024-07-16 19:30 | 89
73 | Juldah 132/33kV Grid Sub-Station | 2024-07-17 13:00 | 26
74 | Kalurghat 132/33kV Grid Sub-Station | 2024-07-16 15:00 | 39
75 | Khagrachori 132/33kV Grid Sub-Station | 2024-07-28 19:30 | 38
76 | Khulshi 132/33kV Grid Sub-Station | 2024-07-18 15:00 | 211
77 | KSRM 132/33kV Grid Sub-Station | 2024-07-11 18:30 | 80
78 | Madunaghat 132/33kV Grid Sub-Station | 2024-07-13 19:00 | 62
79 | Matarbari 132/33kV Sub-Station | 2024-07-07 08:00 | 151
80 | Mirsorai 230/33kV Grid Sub-Station | 2024-07-13 19:30 | 10
81 | Modern Steel 132/11kV Grid Sub-Station | 2024-07-01 | 0
82 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2024-07-15 22:00 | 45
83 | Rangamati 132/33kV Grid Sub-Station | 2024-07-18 19:00 | 20
84 | Shahmirpur 132/33kV Grid Sub-Station | 2024-07-27 15:00 | 64
85 | Shikalbaha 132/33kV Sub-Station | 2024-07-13 19:30 | 33
86 | Sholosohor 132/33kV Grid Sub-Station | 2024-07-14 17:00 | 48
87 | SSM 132/33kV Grid Sub-Station | 2024-07-31 06:00 | 19
88 | TK chemical 132kV Grid Sub-Station | 2024-07-16 20:00 | 36
89 | Ashuganj 230/132/33kV Sub-Station | 2024-07-13 17:00 | 99
90 | Brahmanbaria 132/33kV Grid Sub-Station | 2024-07-13 21:00 | 181
91 | Chandpur 132/33kV Grid Sub-Station | 2024-07-07 22:00 | 78
92 | Chauddagram 132/33kV Grid Sub-Station | 2024-07-15 | 78
93 | Chowmuhani 132/33kV Grid Sub-Station | 2024-07-13 19:30 | 240
94 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2024-07-18 23:00 | 177
95 | Cumilla(S) 132/33kV Grid Sub-Station | 2024-07-15 23:00 | 206
96 | Daudkandi 132/33kV Grid Sub-Station | 2024-07-14 19:30 | 176
97 | Feni 132/33kV Grid Sub-Station | 2024-07-28 21:00 | 127
98 | Kachua 132/33kV Grid Sub-Station | 2024-07-31 19:00 | 92
99 | PHP 132/33kV Sub-Station | 2024-07-10 15:00 | 11
100 | Ramganj 132/33kV Grid Sub-Station | 2024-07-27 21:00 | 122
101 | Bhaluka 132/33kV Grid Sub-Station | 2024-07-27 15:00 | 156
102 | Ghatail 132/33kV Grid Sub-Station | 2024-07-20 21:00 | 74
103 | Jamalpur 132/33kV Grid Sub-Station | 2024-07-21 23:00 | 131
104 | Kishoreganj 132/33kV Grid Sub-Station | 2024-07-23 22:00 | 158
105 | Mirzapur 132/33kV GIS Grid Sub-Station | 2024-07-24 19:00 | 50
106 | Mymensingh 132/33kV Grid Sub-Station | 2024-07-20 20:00 | 264
107 | Netrakona 132/33kV Grid Sub-Station | 2024-07-20 19:30 | 140
108 | Sherpur 132/33kV Grid Sub-Station | 2024-07-22 19:30 | 162
109 | Tangail 132/33kV Grid Sub-Station | 2024-07-24 | 202
110 | Beanibazar 132/33kV Grid Sub-Station | 2024-07-18 19:00 | 90
111 | Chhatak 132/33kV Grid Sub-Station | 2024-07-27 20:00 | 45
112 | Fenchuganj 230/132/33kV Grid Sub-Station | 2024-07-11 19:30 | 48
113 | Kulaura 132/33kV Grid Sub-Station | 2024-07-25 19:00 | 60
114 | Shahjibazar 132/33kV Grid Sub-Station | 2024-07-23 22:00 | 148
115 | Sreemongol 132/33kV Grid Sub-Station | 2024-07-14 22:00 | 85
116 | Sunamganj 132/33kV Grid Sub-Station | 2024-07-08 21:00 | 62
117 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 2024-07-27 19:00 | 56
118 | Sylhet 132/33kV Grid Sub-Station | 2024-07-27 19:00 | 150
119 | Bagerhat 132/33kV Grid Sub-Station | 2024-07-25 19:30 | 108
120 | Benapole 132/33kV Grid Sub-Station | 2024-07-07 22:00 | 77
121 | Bheramara(GK) 132/33kV Grid Sub-Station | 2024-07-30 20:00 | 84
122 | Chuadanga 132/33kV Grid Sub-Station | 2024-07-31 19:30 | 125
123 | Faridpur 132/33kV Grid Sub-Station | 2024-07-18 22:00 | 187
124 | Goalpara 132/33kV Grid Sub-Station | 2024-07-19 | 62
125 | Gollamari 132/33kV Grid Sub-Station | 2024-07-08 13:00 | 96
126 | Gopalganj 132/33kV Grid Sub-Station | 2024-07-17 23:00 | 119
127 | Jashore 132/33kV Grid Sub-Station | 2024-07-18 20:00 | 161
128 | Jhenaidah 132/33kV Grid Sub-Station | 2024-07-17 19:30 | 153
129 | Khulna (C) 132/33kV Grid Sub-Station | 2024-07-06 12:00 | 95
130 | Kushtia 132/33kV Grid Sub-Station | 2024-07-14 23:00 | 163
131 | Madaripur 132/33kV Grid Sub-Station | 2024-07-18 22:00 | 129
132 | Magura 132/33kV Grid Sub-Station | 2024-07-18 19:30 | 74
133 | Mongla 132/33kV Grid Sub-Station | 2024-07-16 09:00 | 43
134 | Narail 132/33kV Grid Sub-Station | 2024-07-14 19:30 | 65
135 | Noapara 132/33kV Grid Sub-Station | 2024-07-30 19:30 | 58
136 | Rajbari 132/33kV Grid Sub-Station | 2024-07-31 19:30 | 86
137 | Satkhira 132/33kV Grid Sub-Station | 2024-07-11 23:00 | 144
138 | Shariatpur 132/33kV Grid Sub-Station | 2024-07-17 22:00 | 98
139 | Barguna 132/33kV Grid Sub-Station | 2024-07-07 23:00 | 24
140 | Barishal 132/33kV Grid Sub-Station | 2024-07-27 19:30 | 130
141 | Barishal 230/132kV Grid Sub-Station | 2024-07-12 18:00 | 126
142 | Bhandaria 132/33kV Grid Sub-Station | 2024-07-30 23:00 | 60.5
143 | Borhanuddin 230/33kV Grid Sub-Station | 2024-07-06 21:00 | 89
144 | Patuakhali 132/33kV Grid Sub-Station | 2024-07-17 23:00 | 95
145 | Payra 400/132/33kV Grid Sub-Station | 2024-07-16 23:00 | 30
146 | Amnura 132/33kV Grid Sub-Station | 2024-07-30 21:00 | 90
147 | Bhangura 132/33kV Grid Sub-Station | 2024-07-29 01:00 | 68
148 | Bog-Sherpur 132/33kV Grid Sub-Station | 2024-07-31 20:00 | 76
149 | Bogura 132/33kV Grid Sub-Station | 2024-07-27 23:00 | 197
150 | Chapai 132/33kV Grid Sub-Station | 2024-07-08 19:30 | 87
151 | Ishurdi 132/33kV Grid Sub-Station | 2024-07-18 20:00 | 91
152 | Joypurhat 132/33kV Grid Sub-Station | 2024-07-31 21:00 | 77
153 | Mahasthangarh 132/33kV Grid Sub-Station | 2024-07-18 22:00 | 98
154 | Naogaon 132/33kV Grid Sub-Station | 2024-07-31 23:00 | 161
155 | Natore 132/33kV Grid Sub-Station | 2024-07-28 23:00 | 173
156 | Niamatpur 132/33kV Grid Sub-Station | 2024-07-28 23:00 | 99
157 | Pabna 132/33kV Grid Sub-Station | 2024-07-18 20:00 | 134
158 | Rajshahi 132/33kV Grid Sub-Station | 2024-07-18 23:00 | 152
159 | Rajshahi 230/132/33kV Grid Sub-Station | 2024-07-27 14:00 | 88
160 | Ruppur 132/11kV Grid Sub-Station | 2024-07-10 16:00 | 7.6
161 | Shahjadpur 132/33kV Grid Sub-Station | 2024-07-30 20:00 | 94
162 | Sirajganj 132/33kV Grid Sub-Station | 2024-07-30 21:00 | 132
163 | Ullahpara 132/33kV Grid Sub-Station | 2024-07-28 13:00 | 81
164 | Barapukuria 230/132/33kV Grid Sub-Station | 2024-07-30 20:00 | 77
165 | Jaldhaka 132/33kV Grid Sub-Station | 2024-07-24 21:00 | 98
166 | Kurigram 132/33kV Grid Sub-Station | 2024-07-17 19:00 | 100
167 | Lalmonirhat 132/33kV Grid Sub-Station | 2024-07-17 21:00 | 66
168 | Mithapukur 132/33kV Grid Sub-Station | 2024-07-14 03:00 | 74
169 | Palashbari 132/33kV Grid Sub-Station | 2024-07-30 19:30 | 138
170 | Panchagarh 132/33kV Grid Sub-Station | 2024-07-17 20:00 | 67
171 | Purbasadipur 132/33kV Grid Sub-Station | 2024-07-28 12:00 | 147
172 | Rangpur 132/33kV Grid Sub-Station | 2024-07-25 19:30 | 161
173 | Saidpur 132/33kV Grid Sub-Station | 2024-07-27 21:00 | 118
174 | Thakurgaon 132/33kV Grid Sub-Station | 2024-07-29 20:00 | 123
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: July 2024
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5373.12 | 2024-07-28 | 12:00
Chattogram | 1531 | 2024-07-11 | 0:00
Cumilla | 1476 | 2024-07-14 | 23:00
Mymensingh | 1187 | 2024-07-20 | 20:00
Sylhet | 655 | 2024-07-15 | 19:00
Khulna | 1938.2 | 2024-07-18 | 22:00
Barishal | 517.9 | 2024-07-17 | 23:00
Rajshahi | 1719.2 | 2024-07-28 | 23:00
Rangpur | 1047 | 2024-07-25 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July 2024
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 438 | 2024-07-18 03:00 | 364 | 2024-07-07 11:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 409 | 2024-07-01 05:00 | 371 | 2024-07-18 16:00
3 | Bibiana 400/230kV Sub-Station | 400 | 405 | 2024-07-05 18:30 | 384 | 2024-07-25 10:00
4 | BIPTC | 400 | 410 | 2024-07-03 07:00 | 387 | 2024-07-01 20:00
5 | Bogura 400/230kV Grid Sub-Station | 400 | 409 | 2024-07-05 18:30 | 363 | 2024-07-29 21:00
6 | Gopalganj 400/132kV Grid Sub-Station | 400 | 403 | 2024-07-19 18:00 | 379 | 2024-07-03
7 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 393 | 2024-07-01 05:00 | 355 | 2024-07-16 12:00
8 | Payra 400kV Sub-Station | 400 | 413 | 2024-07-23 18:30 | 399 | 2024-07-07 11:00
9 | Rahanpur 400/132kV Grid Sub-Station | 400 | 413 | 2024-07-05 18:30 | 374 | 2024-07-01
10 | Rampal 400/230kV Grid Sub-Station | 400 | 406 | 2024-07-19 18:00 | 382 | 2024-07-03
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 255 | 2024-07-02 | 210 | 2024-07-18 16:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 238 | 2024-07-14 18:00 | 221 | 2024-07-03 02:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 255 | 2024-07-08 23:00 | 220 | 2024-07-29 19:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 224 | 2024-07-05 10:00 | 201 | 2024-07-31 23:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 242 | 2024-07-07 18:30 | 222 | 2024-07-18
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 236 | 2024-07-03 07:00 | 220 | 2024-07-22 20:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 230 | 2024-07-01 18:30 | 209 | 2024-07-29 21:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 237 | 2024-07-08 20:00 | 220 | 2024-07-18 11:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 235 | 2024-07-26 18:00 | 216 | 2024-07-30 12:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 237 | 2024-07-01 14:00 | 220 | 2024-07-31 04:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 240 | 2024-07-01 01:00 | 220 | 2024-07-14 15:00
12 | Ghorashal 230kV Switching Sub-Station | 230 | 236 | 2024-07-01 05:00 | 214 | 2024-07-07 11:00
13 | GPH 230/33kV Grid Sub-Station | 230 | 237 | 2024-07-25 20:00 | 223 | 2024-07-02 17:00
14 | Haripur 230/132kV Grid Sub-Station | 230 | 235 | 2024-07-01 05:00 | 213 | 2024-07-18 15:00
15 | Hasnabad 230/132kV Grid Sub-Station | 230 | 250 | 2024-07-15 10:00 | 214 | 2024-07-25 10:00
16 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 240 | 2024-07-25 19:30 | 224 | 2024-07-04 12:00
17 | Ishurdi 230/132kV Grid Sub-Station | 230 | 255 | 2024-07-21 | 223 | 2024-07-29 19:30
18 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 230 | 2024-07-19 18:30 | 211 | 2024-07-24 23:00
19 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 233 | 2024-07-01 05:00 | 211 | 2024-07-18 13:00
20 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 234 | 2024-07-19 18:30 | 216 | 2024-07-25 14:00
21 | Maniknagar 230/132kV Grid Sub-Station | 230 | 236 | 2024-07-01 04:00 | 213 | 2024-07-18 12:00
22 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 242 | 2024-07-05 18:30 | 223 | 2024-07-13 11:00
23 | Mirsorai 230/33kV Grid Sub-Station | 230 | 238 | 2024-07-10 20:00 | 220 | 2024-07-02 17:00
24 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 236 | 2024-07-13 18:00 | 220 | 2024-07-03 21:00
25 | Rampura 230/132kV Grid Sub-Station | 230 | 235 | 2024-07-21 18:00 | 213 | 2024-07-18 15:00
26 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 240 | 2024-07-09 19:30 | 224 | 2024-07-02 16:00
27 | Shyampur 230/132kV Grid Sub-Station | 230 | 235 | 2024-07-26 18:30 | 214 | 2024-07-18 12:00
28 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 236 | 2024-07-26 18:00 | 215 | 2024-07-18 15:00
29 | Sirajgonj 230 kV Switching Station | 230 | 240 | 2024-07-23 18:30 | 227 | 2024-07-29 21:00
30 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 232 | 2024-07-01 05:00 | 214 | 2024-07-07 11:00
31 | Tongi 230/132/33kV Grid Sub-Station | 230 | 236 | 2024-07-01 05:00 | 211 | 2024-07-13 12:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-22 06:00 | 121 | 2024-07-14 15:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-12 18:00 | 126 | 2024-07-02 10:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 134 | 2024-07-25 19:30 | 126 | 2024-07-02 10:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 141 | 2024-07-31 18:00 | 116 | 2024-07-27 22:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 140 | 2024-07-01 06:00 | 130 | 2024-07-13 11:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-09 18:00 | 117 | 2024-07-23 23:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-09 19:30 | 126 | 2024-07-04 10:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-22 06:00 | 120 | 2024-07-07 11:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 134 | 2024-07-22 07:00 | 117 | 2024-07-18 12:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-31 19:30 | 124 | 2024-07-13 23:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 141 | 2024-07-19 18:30 | 125 | 2024-07-02
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-16 21:00 | 127 | 2024-07-02 10:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 133 | 2024-07-05 18:30 | 118 | 2024-07-18 01:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-21 18:30 | 120 | 2024-07-02 16:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 139 | 2024-07-08 21:00 | 120 | 2024-07-02 16:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 130 | 2024-07-31 16:00 | 113 | 2024-07-18 19:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-12 05:00 | 120 | 2024-07-24 23:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 131 | 2024-07-01 05:00 | 117 | 2024-07-07 11:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-01 06:00 | 120 | 2024-07-03 23:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-01 18:30 | 128 | 2024-07-27 21:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-06 18:30 | 128 | 2024-07-29 19:30
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 130 | 2024-07-05 18:30 | 113 | 2024-07-02 15:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-01 18:30 | 119 | 2024-07-29 21:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-01 18:30 | 121 | 2024-07-29 21:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 130 | 2024-07-01 07:00 | 118 | 2024-07-02 23:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 139 | 2024-07-22 06:00 | 122 | 2024-07-07 11:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-05 18:30 | 114 | 2024-07-13 01:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-09 19:30 | 129 | 2024-07-04 09:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-05 08:00 | 118 | 2024-07-29 21:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 136 | 2024-07-26 18:30 | 121 | 2024-07-31 11:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 133 | 2024-07-31 19:30 | 115 | 2024-07-28 13:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 130 | 2024-07-27 16:00 | 113 | 2024-07-30 21:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 129 | 2024-07-01 | 113 | 2024-07-17 15:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-06 18:30 | 115 | 2024-07-24 23:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 134 | 2024-07-31 18:30 | 115 | 2024-07-08 19:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-26 18:00 | 120 | 2024-07-28 13:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 132 | 2024-07-05 18:30 | 113 | 2024-07-25 11:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-22 07:00 | 118 | 2024-07-18 12:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-24 18:30 | 118 | 2024-07-13 12:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-01 05:00 | 119 | 2024-07-18 12:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-25 18:00 | 120 | 2024-07-22 22:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-06 15:00 | 125 | 2024-07-02 21:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-26 18:30 | 122 | 2024-07-18 13:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 132 | 2024-07-05 18:30 | 113 | 2024-07-28 23:00
45 | Ghatail 132/33kV Grid Sub-Station | 132 | 132 | 2024-07-03 18:30 | 115 | 2024-07-06 19:30
46 | Goalpara 132/33kV Grid Sub-Station | 132 | 141 | 2024-07-09 18:00 | 123 | 2024-07-23 23:00
47 | Gollamari 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-19 18:30 | 126 | 2024-07-25 13:00
48 | Gopalganj 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-19 21:00 | 124 | 2024-07-24 23:00
49 | Gulshan 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-20 18:00 | 121 | 2024-07-07 11:00
50 | Halishahar 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-08 20:00 | 126 | 2024-07-04 10:00
51 | HaripurSBU 132/33kV Sub-Station | 132 | 134 | 2024-07-07 10:00 | 117 | 2024-07-25 01:00
52 | Hasnabad 132/33kV Grid Substation | 132 | 137 | 2024-07-19 18:30 | 124 | 2024-07-02 16:00
53 | Ishurdi 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-06 18:30 | 113 | 2024-07-07 01:00
54 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 132 | 2024-07-05 10:00 | 113 | 2024-07-07 19:30
55 | Jamalpur 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-01 20:00 | 117 | 2024-07-21 12:00
56 | Jashore 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-19 18:00 | 122 | 2024-07-01 22:00
57 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 140 | 2024-07-19 18:00 | 126 | 2024-07-24 23:00
58 | Joydebpur 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-01 05:00 | 120 | 2024-07-07 11:00
59 | Joypurhat 132/33kV Grid Sub-Station | 132 | 131 | 2024-07-06 18:30 | 113 | 2024-07-25 22:00
60 | Juldah 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-09 19:30 | 128 | 2024-07-02 10:00
61 | Kabirpur 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-07 13:00 | 117 | 2024-07-13 10:00
62 | Kachua 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-05 18:30 | 116 | 2024-07-13 01:00
63 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-01 02:00 | 121 | 2024-07-18 16:00
64 | Kalurghat 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-25 18:00 | 128 | 2024-07-02 11:00
65 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-21 18:00 | 120 | 2024-07-18 15:00
66 | Kazla 132/33kV Grid Sub-Station | 132 | 134 | 2024-07-22 07:00 | 116 | 2024-07-18 13:00
67 | Khagrachori 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-16 21:00 | 127 | 2024-07-04 10:00
68 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-09 18:00 | 124 | 2024-07-23 22:00
69 | Khulshi 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-25 18:00 | 125 | 2024-07-02 10:00
70 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 132 | 2024-07-01 06:00 | 118 | 2024-07-15 10:00
71 | Kodda 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-01 05:00 | 114 | 2024-07-15 16:00
72 | KSRM 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-16 18:30 | 128 | 2024-07-02 10:00
73 | Kulaura 132/33kV Grid Sub-Station | 132 | 133 | 2024-07-01 07:00 | 121 | 2024-07-29 22:00
74 | Kurigram 132/33kV Grid Sub-Station | 132 | 132 | 2024-07-01 18:30 | 113 | 2024-07-02 19:30
75 | Kushtia 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-28 03:00 | 126 | 2024-07-29 19:30
76 | Lalbag 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-22 06:00 | 121 | 2024-07-18 16:00
77 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 130 | 2024-07-14 16:00 | 113 | 2024-07-26
78 | Madanganj 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-01 05:00 | 120 | 2024-07-02 16:00
79 | Madaripur 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-19 15:00 | 124 | 2024-07-03
80 | Madartek 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-22 06:00 | 121 | 2024-07-07 11:00
81 | Madunaghat 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-19 14:00 | 124 | 2024-07-31 04:00
82 | Magura 132/33kV Grid Sub-Station | 132 | 140 | 2024-07-19 18:00 | 124 | 2024-07-01 22:00
83 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 134 | 2024-07-01 18:30 | 117 | 2024-07-29 21:00
84 | Manikganj 132/33kV Grid Sub-Station | 132 | 133 | 2024-07-14 06:00 | 114 | 2024-07-15 10:00
85 | Maniknagar 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-29 22:00 | 117 | 2024-07-18 12:00
86 | Matarbari 132/33kV Sub-Station | 132 | 134 | 2024-07-21 12:00 | 114 | 2024-07-08 19:00
87 | Matuail 132/33kV Grid Sub-Station | 132 | 134.1 | 2024-07-12 08:00 | 121 | 2024-07-02 16:00
88 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-22 07:00 | 120 | 2024-07-13 10:00
89 | Mirpur 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-20 18:30 | 123 | 2024-07-02 16:00
90 | Mirzapur 132/33kV GIS Grid Sub-Station | 132 | 133 | 2024-07-01 06:00 | 117 | 2024-07-12 13:00
91 | Mithapukur 132/33kV Grid Sub-Station | 132 | 133 | 2024-07-01 18:30 | 115 | 2024-07-27 19:00
92 | MI_Cement 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-23 15:00 | 121 | 2024-07-02 16:00
93 | Modern Steel 132/11kV Grid Sub-Station | 132 | 136 | 2024-07-10 15:00 | 127 | 2024-07-02 10:00
94 | Mogbazar 132/33kV Grid Sub-Station | 132 | 140 | 2024-07-22 05:00 | 121 | 2024-07-07 11:00
95 | Mongla 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-07 16:00 | 117 | 2024-07-23 23:00
96 | Motijheel 132/33kV Grid Sub-Station | 132 | 134 | 2024-07-22 07:00 | 117 | 2024-07-18 12:00
97 | Munshiganj 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-07 20:00 | 121 | 2024-07-02 16:00
98 | Mymensingh 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-09 | 113 | 2024-07-02 21:00
99 | Naogaon 132/33kV Grid Sub-Station | 132 | 131 | 2024-07-01 18:30 | 113 | 2024-07-27 23:00
100 | Narail 132/33kV Grid Sub-Station | 132 | 140 | 2024-07-20 18:00 | 121 | 2024-07-26 23:00
101 | Narshingdi 132/33kV Grid Sub-Station | 132 | 129 | 2024-07-19 07:00 | 113 | 2024-07-07 10:00
102 | Natore 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-06 18:30 | 120 | 2024-07-19 22:00
103 | Nawabganj 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-26 18:30 | 121 | 2024-07-18 15:00
104 | Netrakona 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-08 18:30 | 116 | 2024-07-21 19:30
105 | New Tongi 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-21 18:30 | 121 | 2024-07-13 11:00
106 | Niamatpur 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-05 17:00 | 122 | 2024-07-29 21:00
107 | Noapara 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-19 18:00 | 123 | 2024-07-23 23:00
108 | Pabna 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-05 10:00 | 125 | 2024-07-29 19:30
109 | Palashbari 132/33kV Grid Sub-Station | 132 | 131 | 2024-07-01 18:30 | 113 | 2024-07-27 19:00
110 | Panchagarh 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-01 18:30 | 113 | 2024-07-08
111 | Patuakhali 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-31 19:00 | 125 | 2024-07-20 23:00
112 | PHP 132/33kV Sub-Station | 132 | 132 | 2024-07-10 18:30 | 117 | 2024-07-14 15:00
113 | Postogola 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-26 18:30 | 123 | 2024-07-20 03:00
114 | Purbachal 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-23 18:30 | 119 | 2024-07-13 11:00
115 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 132 | 2024-07-01 18:30 | 113 | 2024-07-07 23:00
116 | Rahim Steel 132/33kV Sub-Station | 132 | 136 | 2024-07-11 | 116 | 2024-07-14 13:00
117 | Rajbari 132/33kV Grid Sub-Station | 132 | 134 | 2024-07-19 18:30 | 123 | 2024-07-23 12:00
118 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 134 | 2024-07-05 19:00 | 114 | 2024-07-15 17:00
119 | Rajshahi 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-05 18:30 | 125 | 2024-07-21 22:00
120 | Ramganj 132/33kV Grid Sub-Station | 132 | 132 | 2024-07-26 18:00 | 113 | 2024-07-04 23:00
121 | Rangamati 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-16 21:00 | 128 | 2024-07-04 10:00
122 | Rangpur 132/33kV Grid Sub-Station | 132 | 132 | 2024-07-01 18:30 | 114 | 2024-07-07 20:00
123 | Ruppur 132/11kV Grid Sub-Station | 132 | 138 | 2024-07-06 17:00 | 128 | 2024-07-29 19:30
124 | Saidpur 132/33kV Grid Sub-Station | 132 | 132 | 2024-07-01 18:30 | 113 | 2024-07-17 03:00
125 | Satkhira 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-19 18:00 | 118 | 2024-07-23 23:00
126 | Satmasjid 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-22 07:00 | 120 | 2024-07-12 13:00
127 | Savar 132/33kV Grid Sub-Station | 132 | 139 | 2024-07-20 18:30 | 123 | 2024-07-02 10:00
128 | SevenRings 132/11kV Sub-Station | 132 | 141 | 2024-07-01 05:00 | 126 | 2024-07-13 10:00
129 | ShahCement 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-26 18:30 | 121 | 2024-07-31 11:00
130 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-07-01 18:30 | 130 | 2024-07-29 21:00
131 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 128 | 2024-07-01 05:00 | 117 | 2024-07-18 19:00
132 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 137 | 2024-07-08 20:00 | 128 | 2024-07-02 15:00
133 | Shariatpur 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-27 | 122 | 2024-07-03 22:00
134 | Sherpur 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-02 05:00 | 113 | 2024-07-21 19:30
135 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-26 18:00 | 121 | 2024-07-02 16:00
136 | Sholosohor 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-25 21:00 | 126 | 2024-07-04 10:00
137 | Shyampur 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-01 04:00 | 122 | 2024-07-18 12:00
138 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-05 18:30 | 121 | 2024-07-02 16:00
139 | Sirajganj 132/33kV Grid Sub-Station | 132 | 135 | 2024-07-05 18:30 | 120 | 2024-07-29 21:00
140 | Sonargaon 132/33kV Grid Sub-Station | 132 | 133 | 2024-07-05 18:30 | 117 | 2024-07-18 13:00
141 | Sreemongol 132/33kV Grid Sub-Station | 132 | 129 | 2024-07-10 15:00 | 118 | 2024-07-11 20:00
142 | Srinagar 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-19 18:00 | 122 | 2024-07-18 12:00
143 | SSM 132/33kV Grid Sub-Station | 132 | 140 | 2024-07-01 | 120 | 2024-07-21 04:00
144 | Sunamganj 132/33kV Grid Sub-Station | 132 | 129 | 2024-07-01 08:00 | 113 | 2024-07-25 19:30
145 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 132 | 130 | 2024-07-01 08:00 | 115 | 2024-07-29 22:00
146 | Sylhet 132/33kV Grid Sub-Station | 132 | 131 | 2024-07-31 16:00 | 116 | 2024-07-29 21:00
147 | Tangail 132/33kV Grid Sub-Station | 132 | 133 | 2024-07-12 09:00 | 114 | 2024-07-12 12:00
148 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-01 18:30 | 113 | 2024-07-07 23:00
149 | TK chemical 132kV Grid Sub-Station | 132 | 137 | 2024-07-25 18:00 | 127 | 2024-07-02 10:00
150 | Ullahpara 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-01 18:30 | 123 | 2024-07-17 13:00
151 | Ullon 132/33kV Grid Sub-Station | 132 | 138 | 2024-07-22 06:00 | 121 | 2024-07-07 11:00
152 | Uttara 132/33kV Grid Sub-Station | 132 | 141 | 2024-07-20 18:30 | 120 | 2024-07-07 09:00
153 | UttaraNew 132/33kV Grid Sub-Station | 132 | 140 | 2024-07-20 18:30 | 123 | 2024-07-02 16:00
154 | Zigatola 132/33kV Grid Sub-Station | 132 | 136 | 2024-07-05 18:30 | 120 | 2024-07-02 16:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: July 2024
substation | transformer | voltage_level | mw | mvar | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 450 | 146 | 473.092 | 2024-07-18 09:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 480 | 146 | 501.7131 | 2024-07-18 09:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -272 | -84 | 284.6753 | 2024-07-10 19:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -272 | -84 | 284.6753 | 2024-07-10 19:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -178 | -36 | 181.604 | 2024-07-27 13:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -175 | -36 | 178.6645 | 2024-07-27 13:00
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 409 | 30 | 410.0988 | 2024-07-02 21:00
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 409 | 30 | 410.0988 | 2024-07-02 21:00
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 409 | 30 | 410.0988 | 2024-07-02 21:00
Gopalganj 400/132kV Grid Sub-Station | ATR-04 | 400/230 | -114 | -1 | 114.0044 | 2024-07-17 20:00
Gopalganj 400/132kV Grid Sub-Station | ATR-05 | 400/230 | -114 | -1 | 114.0044 | 2024-07-17 20:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 247 | 61 | 254.4209 | 2024-07-06 07:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 270 | 28 | 271.448 | 2024-07-17
Meghnaghat 400/230kV Grid Sub-Station | ATR - 2 | 400/230 | -492 | -286 | 569.087 | 2024-07-11 12:00
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | -493 | -287 | 570.4542 | 2024-07-11 12:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -326.42 | -39.8 | 328.8374 | 2024-07-18 21:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -662 | -8.9 | 662.0598 | 2024-07-31 03:00
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 184 | 78 | 199.8499 | 2024-07-18 15:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -165 | -29 | 167.5291 | 2024-07-02
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -165 | -29 | 167.5291 | 2024-07-02
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -165 | -29 | 167.5291 | 2024-07-02
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 310 | 29 | 311.3535 | 2024-07-03 07:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 310 | 29 | 311.3535 | 2024-07-03 07:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -125 | -54 | 136.1653 | 2024-07-20 22:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -134 | -63 | 148.0709 | 2024-07-13 23:00
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 134 | 387 | 409.5424 | 2024-07-10 20:00
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 178 | 79 | 194.7434 | 2024-07-28 22:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | mw | mvar | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 194 | 80 | 209.8476 | 2024-07-18 15:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 194 | 80 | 209.8476 | 2024-07-18 15:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 189 | 15 | 189.5943 | 2024-07-06 01:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 160 | 48 | 167.0449 | 2024-07-17 21:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 154 | 67 | 167.9434 | 2024-07-06 10:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 254 | 135 | 287.6474 | 2024-07-17 19:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 215 | 40 | 218.6893 | 2024-07-12 14:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 150 | 84 | 171.9186 | 2024-07-21 21:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 112 | 63 | 128.5029 | 2024-07-21 21:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 193 | 38 | 196.7054 | 2024-07-03 19:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 191 | 66 | 202.0817 | 2024-07-10 16:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 241 | 62 | 248.8473 | 2024-07-25 21:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 170 | 48 | 176.6465 | 2024-07-03 16:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 170 | 48 | 176.6465 | 2024-07-03 16:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 130 | -73 | 149.0939 | 2024-07-27
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -73 | 69 | 100.449 | 2024-07-27 01:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 120 | 120 | 169.7056 | 2024-07-09 16:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 162 | 14 | 162.6038 | 2024-07-16 14:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 214 | 43 | 218.2773 | 2024-07-29 22:00
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 214 | 43 | 218.2773 | 2024-07-29 22:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 193 | 66 | 203.973 | 2024-07-19 02:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 195 | 71 | 207.5235 | 2024-07-19 03:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 196 | 71 | 208.4634 | 2024-07-28 22:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 171 | 54 | 179.3237 | 2024-07-27
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 276 | 157 | 317.5295 | 2024-07-24 01:00
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 100 | 0 | 100 | 2024-07-01 18:30
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 100 | 0 | 100 | 2024-07-01 18:30
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 134 | 7 | 134.1827 | 2024-07-02 09:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 154 | 24 | 155.8589 | 2024-07-02 16:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 147 | 9 | 147.2753 | 2024-07-02 09:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 224 | 60 | 231.8965 | 2024-07-03 07:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 64 | 75 | 98.5951 | 2024-07-31 15:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 57 | 94 | 109.9318 | 2024-07-15 19:30
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 125 | 39 | 130.9427 | 2024-07-18 10:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 125 | 39 | 130.9427 | 2024-07-18 10:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 125 | 39 | 130.9427 | 2024-07-18 10:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 125 | 39 | 130.9427 | 2024-07-18 10:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 85 | 60 | 104.0433 | 2024-07-28 03:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 85 | 60 | 104.0433 | 2024-07-28 03:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 84 | 60 | 103.2279 | 2024-07-29 21:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -213 | -96 | 233.6343 | 2024-07-17 19:30
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -213 | -96 | 233.6343 | 2024-07-17 19:30
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 168 | 70 | 182 | 2024-07-14 12:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 117 | 36 | 122.4132 | 2024-07-18 19:30
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 104 | 288 | 306.2025 | 2024-07-19
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 117 | 36 | 122.4132 | 2024-07-18 19:30
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -142 | -34 | 146.0137 | 2024-07-17 19:30
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -157 | -44 | 163.0491 | 2024-07-27 13:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -202 | -50 | 208.0961 | 2024-07-27 13:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 194 | 74 | 207.6343 | 2024-07-13
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 219 | 74 | 231.1644 | 2024-07-12 21:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | -81 | -16 | 82.5651 | 2024-07-22 01:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -81 | -16 | 82.5651 | 2024-07-22 01:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 2 | 2 | 2.8284 | 2024-07-06 06:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 0 | 3 | 3 | 2024-07-05 09:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 0 | 0 | 0 | 2024-07-01
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 395 | 20 | 395.506 | 2024-07-31 18:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 | 230/132 | 310 | 334 | 455.6929 | 2024-07-10 19:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 244 | 86 | 258.7122 | 2024-07-18 08:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 244 | 86 | 258.7122 | 2024-07-18 08:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 224 | 26 | 225.5039 | 2024-07-17
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 105 | 207 | 232.1077 | 2024-07-15 03:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 176 | 153 | 233.2059 | 2024-07-31 06:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 176 | 153 | 233.2059 | 2024-07-31 06:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 209 | 59 | 217.1681 | 2024-07-17 07:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 226 | 72 | 237.1919 | 2024-07-15 08:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 218 | 34 | 220.6354 | 2024-07-07 18:30
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 215 | 35 | 217.8302 | 2024-07-07 16:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 215 | 35 | 217.8302 | 2024-07-07 16:00
270
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: July 2024 | [5 empty] | (For Evening Peak) | [8 empty] | Month: July 2024 | [5 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2024-07-01 | 14004 | 14070 | 63 | 20:00 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | - | 2024-07-01 | 12784 | 12880 | 92 | 12:00 | 75 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | -
2024-07-02 | 13729 | 13800 | 68 | 21:00 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | - | 2024-07-02 | 12548 | 12600 | 50 | 12:00 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-07-03 | 14132 | 14350 | 208 | 19:30 | 48 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | - | 2024-07-03 | 12359 | 12470 | 106 | 12:00 | 86 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | -
2024-07-04 | 14123 | 14250 | 121 | 21:00 | 10 | 0 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | - | 2024-07-04 | 12826 | 12850 | 23 | 12:00 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-07-05 | 13229 | 13229 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-07-05 | 11167 | 11167 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-07-06 | 14551 | 14620 | 95 | 22:00 | 70 | 0 | 0 | 0 | 15 | 10 | 0 | 0 | 0 | - | 2024-07-06 | 12608 | 12750 | 136 | 12:00 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-07-07 | 15064 | 15400 | 321 | 21:00 | 100 | 0 | 0 | 0 | 10 | 170 | 0 | 0 | 41 | - | 2024-07-07 | 13535 | 13580 | 43 | 12:00 | 23 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | -
2024-07-08 | 14895 | 15500 | 578 | 21:00 | 110 | 54 | 159 | 0 | 115 | 115 | 0 | 0 | 25 | - | 2024-07-08 | 13459 | 13580 | 43 | 12:00 | 23 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | -
2024-07-09 | 15047 | 15450 | 385 | 21:00 | 190 | 0 | 0 | 62 | 18 | 115 | 0 | 0 | 0 | - | 2024-07-09 | 13415 | 14100 | 554 | 12:00 | 175 | 94 | 0 | 0 | 125 | 145 | 15 | 0 | 0 | -
2024-07-10 | 14096 | 15500 | 1341 | 21:00 | 561 | 0 | 0 | 110 | 250 | 200 | 100 | 0 | 120 | - | 2024-07-10 | 12618 | 13800 | 1595 | 11:00 | 650 | 205 | 0 | 0 | 230 | 355 | 155 | 0 | 0 | -
2024-07-11 | 13911 | 14350 | 419 | 21:00 | 200 | 0 | 0 | 0 | 90 | 110 | 19 | 0 | 0 | - | 2024-07-11 | 12870 | 14750 | 1795 | 12:00 | 1120 | 100 | 0 | 0 | 260 | 220 | 95 | 0 | 0 | -
2024-07-12 | 13801 | 13587 | 0 | 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-07-12 | 11263 | 11400 | 131 | 12:00 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | -
2024-07-13 | 14973 | 15400 | 408 | 21:00 | 138 | 0 | 0 | 0 | 30 | 190 | 0 | 0 | 50 | - | 2024-07-13 | 12802 | 13100 | 285 | 12:00 | 220 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | -
2024-07-14 | 15172 | 15700 | 504 | 21:00 | 185 | 0 | 0 | 0 | 0 | 180 | 0 | 69 | 70 | - | 2024-07-14 | 13745 | 14050 | 291 | 12:00 | 191 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | -
2024-07-15 | 15062 | 15700 | 609 | 21:00 | 259 | 0 | 0 | 0 | 95 | 160 | 0 | 0 | 95 | - | 2024-07-15 | 13510 | 14150 | 611 | 12:00 | 376 | 0 | 0 | 0 | 65 | 170 | 0 | 0 | 0 | -
2024-07-16 | 15110 | 16000 | 884 | 22:00 | 350 | 15 | 4 | 0 | 165 | 180 | 100 | 0 | 70 | - | 2024-07-16 | 13557 | 14150 | 566 | 12:00 | 360 | 16 | 0 | 0 | 0 | 140 | 50 | 0 | 0 | -
2024-07-17 | 15146 | 15800 | 625 | 21:00 | 260 | 0 | 10 | 0 | 130 | 125 | 80 | 0 | 20 | - | 2024-07-17 | 13196 | 13750 | 529 | 12:00 | 250 | 0 | 0 | 0 | 74 | 190 | 15 | 0 | 0 | -
2024-07-18 | 15219 | 15900 | 650 | 21:00 | 240 | 0 | 10 | 0 | 130 | 160 | 90 | 0 | 20 | - | 2024-07-18 | 13404 | 14600 | 1042 | 12:00 | 445 | 0 | 0 | 120 | 180 | 135 | 64 | 0 | 98 | -
2024-07-19 | 14154 | 14450 | 389 | 24:00' | 0 | 0 | 0 | 0 | 75 | 150 | 125 | 0 | 39 | - | 2024-07-19 | 12362 | 14600 | 1042 | 12:00 | 445 | 0 | 0 | 120 | 180 | 135 | 64 | 0 | 98 | -
2024-07-20 | 13839 | 13800 | 144 | 23:00 | 0 | 0 | 0 | 0 | 75 | 34 | 15 | 0 | 20 | - | 2024-07-20 | 12120 | 12170 | 48 | 12:00 | 28 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | -
2024-07-21 | 13608 | 13500 | 94 | 23:00 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | - | 2024-07-21 | 11156 | 11156 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-07-22 | 13218 | 12820 | 59 | 23:00 | 0 | 0 | 0 | 0 | 45 | 0 | 14 | 0 | 0 | - | 2024-07-22 | 10665 | 10665 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-07-23 | 13727 | 13560 | 43 | 23:00 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | - | 2024-07-23 | 11119 | 11119 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-07-24 | 14605 | 14600 | 190 | 22:00 | 8 | 0 | 0 | 0 | 55 | 107 | 20 | 0 | 0 | - | 2024-07-24 | 13319 | 13380 | 58 | 12:00 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-07-25 | 15051 | 15400 | 333 | 21:00 | 133 | 0 | 5 | 0 | 35 | 120 | 15 | 0 | 25 | - | 2024-07-25 | 13459 | 13750 | 278 | 12:00 | 100 | 0 | 0 | 0 | 128 | 50 | 0 | 0 | 0 | -
2024-07-26 | 14626 | 14700 | 412 | 23:00 | 0 | 0 | 6 | 0 | 60 | 190 | 20 | 0 | 136 | - | 2024-07-26 | 12921 | 13020 | 95 | 12:00 | 40 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | -
2024-07-27 | 15193 | 13395 | 370 | 23:00 | 90 | 0 | 0 | 0 | 25 | 175 | 10 | 0 | 70 | - | 2024-07-27 | 13395 | 13680 | 272 | 12:00 | 105 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | -
2024-07-28 | 15223 | 15950 | 694 | 21:00 | 140 | 0 | 10 | 0 | 35 | 290 | 108 | 0 | 111 | - | 2024-07-28 | 13868 | 14500 | 604 | 12:00 | 295 | 0 | 0 | 0 | 65 | 210 | 34 | 0 | 0 | -
2024-07-29 | 14985 | 15750 | 731 | 21:00 | 200 | 0 | 10 | 0 | 100 | 270 | 30 | 0 | 121 |  | 2024-07-29 | 13617 | 14650 | 987 | 12:00 | 415 | 0 | 0 | 0 | 110 | 282 | 45 | 0 | 135
2024-07-30 | 15156 | 15750 | 567 | 21:00 | 132 | 0 | 50 | 0 | 55 | 220 | 15 | 0 | 95 |  | 2024-07-30 | 13575 | 14370 | 759 | 12:00 | 350 | 0 | 0 | 0 | 120 | 170 | 0 | 0 | 119
2024-07-31 | 14757 | 15300 | 590 | 22:00 | 160 | 0 | 0 | 0 | 60 | 175 | 25 | 0 | 170 |  | 2024-07-31 | 13359 | 14400 | 1006 | 11:00 | 441 | 0 | 0 | 140 | 130 | 125 | 100 | 0 | 70

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: July 2024
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | [13 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
9 | Meghnaghat CCPP(Summit) | IPP | 335 | √ | √ | √ | √
10 | Ashuganj 225 MW CCPP | APSCL | 221
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: July 2024
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 15223 | 2024-07-28 | 21:00
2 | Maximum Day Peak Genaration | MW | 13868 | 2024-07-28 | 12:00
3 | Maximum Evening Peak Demand | MW | 16000 | 2024-07-30 | 21:00
4 | Minimum Generation | MW | 10542 | 2024-07-23 | 6:00
5 | Average of the daily evening peak Genaration | MW | 14431 | - | -
6 | Average of the daily day peak Genaration | MW | 12793.5806 | - | -
7 | Maximum load shed (Evening Peak) | MW | 1341 | 2024-07-10 | 21:00
8 | Minimum load shed | MW | 0 | 2024-07-05 | 21:00
9 | Total nos. of load shed days | Day | 29 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 376.8333 | - | -
11 | Total Generation | MkWh | 9831.86 | - | -
12 | Total Generation by BPDB | MkWh | 1553.74 | % of total Gen. | 15.8%
13 | Total Generation by IPP | MkWh | 3471.59 | '' | 35.31%
14 | A) Total Generation by Generation Companies | MkWh | 2904.26 | '' | 29.54%
| B) Total Generation by REB | MkWh | 72.09 | " | 0.7332%
| C) Total Generation by RENTAL | MkWh | 224.06 | " | 2.279%
| D) Total Imported from India (BIPTC) | MkWh | 679.34 | " | 6.91%
| E) Total Imported from Tripura, India (A.C) | MkWh | 60.63 | " | 0.6167%
| F) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 866.15 |  | 8.81%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3966.4454 | % of total Gen. | 40.34%
| B) Oil | MkWh | 1389.14 | '' | 14.13%
| C) Hydro | MkWh | 138.7193 | '' | 1.411%
| D) Solar | MkWh | 93.2904 | '' | 0.9489%
| E) Coal | MkWh | 2621.6684 | '' | 26.67%
| F) BIPTC (Import from India) | MkWh | 679.3407 | '' | 6.91%
| G) A.C (Import from Tripura, India) | MkWh | 60.6259 | '' | 0.6166%
| H) Adani (Import from India) | MkWh | 866.15 |  | 8.81%
| I) Wind | MkWh | 16.4786 | '' | 0.1676%
16 | Maximun of the daily total Generation . | MkWh | 338.663 | 2024-07-28
17 | Monthly Load factor | % | 81.3292 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 6108.6698 | - | -
| A) Gas | M.Taka | 741.2339 | - | -
| B) Liquid fuel | M.Taka | 1168.5603 | - | -
| C) Coal | M.Taka | 902.1451 | - | -
| D) BIPTC (Import from India) | M.Taka | 2771.7101 | - | -
| E) Tripura(Import from India) | M.Taka | 525.0205 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2622.3067 | 2024-07-01
| A) Gas | M.Taka | 741.2339 | 2024-07-01
| B) Liquid fuel | M.Taka | 1168.5603 | 2024-07-03
| C) Coal | M.Taka | 902.1451 | 2024-07-10
| D) BIPTC (Import from India) | M.Taka | 104.1898 | 2024-07-09
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 0.62131
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 0.63742
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.83 | 31/07/2024 | 06:00
b) | Actual | FT (MSL) | 92.89 | 31/07/2024 | 06:00
22 | Peak Genaration of July 2023 | MW | 15164 | 2023-07-26 | 21:00
23 | Peak Demand of July 2023 | MW | 15700 | 2023-07-30 | 21:00
24 | Maximum peak Generation recorded upto 31/07/2024 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 31/07/2024 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/07/2024 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable | 20 | [7 empty] | 20 | 20 | 20 | 20
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | [14 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable | [5 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable | [5 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant