## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-10-10 | Thursday
|  | Date (day): | 2024-10-10 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13442.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14579 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-10-09 | 2024-10-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 406 | 382 | 400 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 26 | 55 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 13 | 13 | 62 |  | Fuel shortage
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 300 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 57 | 8 | 58 | 44 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 48 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 2 | 35 | 55 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 34 | 35 | 36 |  | 44 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 17 | 24 | 25 |  | 8 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 10 | 20 | 20 |  | 13 | Engine problem
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 17 | 25 | 17 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 10 | 297 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 112 | 132 | 132 | 132 | 17 |  | Fuel shortage
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 52 | 100 |  | 5 | Engine problem
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 72 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 28 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 33 | 36 | 36 | 35 |  | 20 | Engine problem.
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 510 | 200 | 200 | 200 | 383 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 2232 | 2586 | 2413 | 2676 | 2332 | 850
35 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
36 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 8 | 25
37 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
38 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 6 | 18 | 32 |  | Fuel shortage
39 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 170 | 167 | 165 | 169 |  | 61 | Unit-1 Under maint.
40 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 95 | 225 | 225
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
42 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
43 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 10 | 71 | 40 | 70 |  | 28 | Engine problem
44 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 68 | 85 |  | 17 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0
45 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
46 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 13 | 5 | 20
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 42 | 44 | 44 | 64 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 105 | 52 | 52 | 52 | 248 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 35 | 35 | 19 |  | Fuel shortage
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 110 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 21 | 12 | 12 | 88 |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 30 | 35 | 35 | 35 | 81 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 160 | 35 | 163
55 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 612 | 590 | 612 | 612 |  | 612 | Unit-2 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 0 | 42 | 60 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 374 | 148 | 350 | 350 | 800 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1643 | 1697 | 1898 | 2114 | 1688 | 1048
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 214 | 219 | 210 | 210 | 11 |  | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 285 | 300 | 310 |  | 50 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 295 | 285 | 330 | 330 |  |  | FGMO
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 43 | 41 | 44
63 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 15 | 15 | 54 | 54
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 87 | 8 | 8 | 88 | 107 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 15 | 85 | 80 | 90 | 60 |  | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 9 | 43 | 35 | 44 |  | 8 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 86 | 144 | 51 | 180 |  | 20 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 68 | 58 | 60 | 70
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 8 | 50
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 0 | 15 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 106 | 34 | 106 |  | 8 | Engine problem
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 76 | 28 | 53 |  | 60 | Engine problem
76 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 68 | 34 | 92 |  | 23 | Engine problem
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 18 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1329 | 1588 | 1459 | 1840 | 291 | 536
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 3 | 0 | 8 | 8 | 194 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 135 | 150 | 133 | 150 | 50 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 92 | 75 | 96 | 19 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 20 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 6 | 18
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 20 | 0 | 35
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 17 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 250 | 280 | 273.6 | 307 | 194 | 0
84 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 20 | 0 | 0 | 0 |  | 70 | Under maint
85 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 28 | 28 | 28 |  | 62 | Machine problem
86 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
87 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
88 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 5 | 5 | 5 | 46 |  | Gas shortage
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 5 | 5 | 5 | 45 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 5 | 8 |  | 3 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 57 | 60 | 60
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 11 | 31 | 86 | 86
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 138 | 135 | 135 | 137 |  | 94 | ST Under maint.
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 300 | 300 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 360 | 377 | 380 | 380 |  |  | FGMO
99 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 381 | 392 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1445 | 1508 | 1579 | 1584 | 111 | 572
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 904 | 476 | 489 | 489
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 0 | 30 |  | 24 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 57 | 30 | 52 |  | 57 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 151 | 107 | 180 | 180 | 230 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 18 | 17 | 18 | 87 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 92 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 512 | 510 | 500 | 510 | 724 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1659 | 1210 | 1316 | 1279 | 1623 | 81
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 16 | 110
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 7 | 10 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 66 | 67 | 67 | 67 |  | 127 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1220 | 1140 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 150 | 17 | 150
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 307 | 307 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1820 | 2004 | 1824 | 2108 | 0 | 127
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 39 | 35 | 38 |  | 14 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 24 | 0 | 24 |  | 47 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
122 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 28 | 46
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 177 | 173 | 170 | 170 | 40 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 370 | 414 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 22 | 28 |  | 22 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 8 |  | 3 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 50 | 96 |  | 8 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 30 | 113 | 113 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1032 | 1126 | 1000 | 1100
135 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 46 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 105 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1810 | 2133 | 2032 | 2150 | 651 | 94
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 63 | 62 | 63 |  | 22 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 225 | 220 | 230 | 230 |  | 44
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 15 | 106 | 113 | 113
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 115 | 35 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 121 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 456 | 504 | 648 | 521 | 40 | 151
| Total |  |  |  |  | 27791 | 27086 | 12644 | 13510 | 13442.6 | 14579 | 6930 | 3459
A. |  | 2024-10-09 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 13510 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 11003 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13510 | MW
3 | Day peak Generation : |  |  | 12644 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13013.12 | MW
4 | Evening peak Generation : |  |  | 13510 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 299.1194 | MKWHr | By Solar | 3.0893 | MKWHr
| By Gas : | 125.8938 | MKWHr |  | By Oil: | 43.1777 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 78.5162 | MKWHr |  | By Hydro: | 4.072 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 25.3909 | MKWHr |  | By Wind: | 0.018729 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6930 | MW | Dhaka | 4966.12 | 4966.12 |  | 0 |  | 18:00 |  | 92.635
|  |  | For Plants S/D or M/C prob = |  |  | 3459 | MW | Chittagong | 1479 | 1479 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10389 | MW | Khulna | 1110.6 | 1110.6 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 896.85 | MMCFD | **Import Adani: | Taka | 167833908.49 | Rajshahi | 1224.4 | 1224.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 359841688.924 | ii) Oil : | Taka | 792160109.2 | Comilla | 1232 | 1232 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 545367010.72 | Total | Taka | 1865202717.334 | Mymensingh | 1084 | 1084 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 10046.85 | MKWHr. | Sylhet | 579 | 579 |  | 0 |  | 23:00 |  | 88
| ii) During Peak Demand : |  |  | 934 | MW (W to E) at | 19:00 | hrs | Barisal | 401 | 401 |  | 0 |  | 24:00 |  | 118
| iii) Maximum : |  |  | 830 | MW at | 20:00 | hrs | Rangpur | 937 | 937 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33°C |  |  | Total | 13013.12 | 13013.12 |  | 0
B. |  | 2024-10-10 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14579 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11500 | MW
4 | Reserve(Generation end) |  |  |  | 1079 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 298.898 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10335 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.4575 | MKWHr. | ii) HVDC Flow at Peak Time |  | 476 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.5034 | MKWHr. | iii) Maximum HVDC Flow : |  | 906 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.86 |  | (b) Today: | 106.81 |  | (c) Rule Curve: |  | 106.81
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-10-09 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 50 | 335 | 0 | 79 | 0 | 8 | 64 | 6 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 15 | 21 | 22 | 16 | 0 | 0 | 90 | 80 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 0 | 64 | 51 | 0 | 24 | 19 | 0 | 36 | 0 | 0 | 0 | 315 | 0 | 194 | 83 | 70 | 42 | 15 | 0 | 51 | 0 | 45 | 16 | 0 | 0 | 0 | 18 | 62 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 140 | 0 | 57 | 11 | 0 | 140 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 255 | 0 | 0 | 97 | 0 | 56 | 0 | 12 | 69 | 85 | 324 | 58 | 17 | 17 | 0 | 51 | 0 | 92 | 34 | 28 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 39 | 17 | 320 | 17 | 0 | 612 | 0 | 403 | 0 | 70 | 0 | 15 | 0 |  | 905 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 21 | 43 | 0 | 67 | 10 | 64 | 0 | 0 | 0 | 38 | 24 | 0 | 0 | 0 | 35 | 0 | 28 | 0 | 0 | 5 | 64 | 0 | 225 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 18 | 0 | 113 | 0 | 113 | 0 | 0 | 35 | 1244 | 180 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 307 | 1033 | 0 | 0 | 0 | 0 | 0 |  | 6869 | 5812 | 12681 | 3506 | 905 | 1661 | 0 | 1551 | 3363 | 170 | 0 | 430 | 62 | 1033 | 0 | 0 | 304.645 | 106.87
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 40 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 22 | 16 | 0 | 0 | 88 | 80 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 0 | 64 | 51 | 0 | 19 | 19 | 0 | 36 | 0 | 0 | 0 | 315 | 0 | 194 | 83 | 51 | 42 | 15 | 0 | 51 | 0 | 45 | 16 | 0 | 0 | 0 | 18 | 64 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 120 | 0 | 57 | 11 | 0 | 140 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 145 | 0 | 0 | 97 | 0 | 34 | 0 | 12 | 54 | 85 | 341 | 58 | 17 | 17 | 0 | 49 | 0 | 92 | 17 | 29 | 12 | 393 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 40 | 17 | 320 | 17 | 0 | 612 | 0 | 404 | 0 | 70 | 0 | 16 | 0 |  | 906 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 28 | 0 | 0 | 5 | 63 | 0 | 225 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 18 | 0 | 35 | 0 | 113 | 0 | 0 | 35 | 1244 | 180 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 307 | 1034 | 0 | 0 | 0 | 0 | 0 |  | 6562 | 5577 | 12139 | 3479 | 906 | 1687 | 0 | 1181 | 3362 | 168 | 0 | 258 | 64 | 1034 | 0 | 0 | 297.005 | 106.87
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 39 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 22 | 16 | 0 | 0 | 87 | 80 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 0 | 64 | 51 | 0 | 19 | 19 | 0 | 37 | 0 | 0 | 0 | 315 | 0 | 194 | 83 | 50 | 42 | 15 | 0 | 51 | 0 | 45 | 16 | 0 | 0 | 0 | 18 | 60 | 18 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 120 | 0 | 56 | 11 | 0 | 139 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 45 | 0 | 0 | 97 | 0 | 34 | 0 | 12 | 51 | 85 | 341 | 58 | 17 | 17 | 0 | 49 | 0 | 92 | 17 | 29 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 19 | 0 | 40 | 17 | 320 | 17 | 0 | 612 | 0 | 405 | 0 | 70 | 0 | 0 | 0 |  | 904 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 225 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 18 | 0 | 0 | 0 | 85 | 0 | 0 | 35 | 1244 | 180 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 307 | 1034 | 0 | 0 | 0 | 0 | 0 |  | 6421 | 5466 | 11887 | 3496 | 904 | 1667 | 0 | 983 | 3367 | 167 | 0 | 209 | 60 | 1034 | 0 | 0 | 298.915 | 106.87
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 38 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 22 | 17 | 0 | 0 | 88 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 64 | 0 | 0 | 15 | 0 | 0 | 37 | 0 | 0 | 0 | 315 | 0 | 194 | 83 | 71 | 42 | 15 | 0 | 51 | 0 | 45 | 16 | 0 | 0 | 0 | 18 | 64 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 120 | 0 | 57 | 11 | 0 | 139 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 97 | 0 | 34 | 0 | 12 | 48 | 6 | 341 | 58 | 17 | 0 | 0 | 52 | 0 | 51 | 17 | 29 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 34 | 17 | 325 | 0 | 0 | 612 | 0 | 404 | 0 | 70 | 0 | 0 | 0 |  | 905 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 225 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 18 | 0 | 0 | 0 | 49 | 0 | 0 | 35 | 1244 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 307 | 1033 | 0 | 0 | 0 | 0 | 0 |  | 6153 | 5396 | 11549 | 3524 | 905 | 1657 | 0 | 693 | 3364 | 168 | 0 | 141 | 64 | 1033 | 0 | 0 | 239.705 | 106.86
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 38 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 22 | 20 | 0 | 0 | 88 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 315 | 0 | 194 | 83 | 71 | 42 | 15 | 0 | 51 | 0 | 45 | 8 | 0 | 0 | 0 | 18 | 62 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 120 | 0 | 56 | 11 | 0 | 139 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 97 | 0 | 34 | 0 | 12 | 51 | 0 | 341 | 58 | 17 | 0 | 0 | 52 | 0 | 0 | 17 | 29 | 12 | 396 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 34 | 17 | 325 | 0 | 0 | 612 | 0 | 408 | 0 | 70 | 0 | 36 | 0 |  | 905 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 225 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 1244 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 307 | 1036 | 0 | 0 | 0 | 0 | 0 |  | 6070 | 5344 | 11414 | 3514 | 905 | 1708 | 0 | 546 | 3366 | 168 | 0 | 109 | 62 | 1036 | 0 | 0 | 273.13 | 106.86
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 38 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 22 | 20 | 0 | 0 | 88 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 315 | 0 | 194 | 83 | 71 | 39 | 15 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 54 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 120 | 0 | 59 | 11 | 0 | 139 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 97 | 0 | 34 | 0 | 12 | 51 | 0 | 341 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 29 | 0 | 400 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 17 | 335 | 0 | 0 | 600 | 0 | 407 | 0 | 90 | 1 | 36 | 0 |  | 906 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 225 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 267 | 1031 | 0 | 0 | 0 | 0 | 0 |  | 5885 | 5118 | 11003 | 3526 | 906 | 1661 | 0 | 391 | 3233 | 168 | 0 | 32 | 54 | 1031 | 1 | 0 | 188.135 | 106.86
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 430 | 0 | 0 | 0 | 0 | 335 | 0 | 39 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 22 | 15 | 2 | 0 | 88 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 345 | 0 | 198 | 83 | 71 | 39 | 15 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 58 | 11 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 163 | 0 | 59 | 11 | 0 | 139 | 0 | 0 | 0 | 315 | 12 | 8 | 0 | 0 | 0 | 0 | 125 | 0 | 34 | 5 | 12 | 51 | 0 | 359 | 68 | 17 | 0 | 1 | 0 | 0 | 0 | 17 | 28 | 0 | 391 | 0 | 6 | 0 | 0 | 0 | 0 | 4 | 34 | 17 | 365 | 0 | 0 | 550 | 0 | 381 | 0 | 120 | 18 | 50 | 0 |  | 905 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 225 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 180 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 510 | 3 | 200 | 1036 | 13 | 0 | 0 | 4 | 14 |  | 6029 | 4997 | 11026 | 3590 | 905 | 1810 | 0 | 413 | 2931 | 168 | 0 | 32 | 58 | 1036 | 83 | 0 | 194.82 | 106.85
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 430 | 0 | 0 | 0 | 0 | 335 | 0 | 39 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 22 | 15 | 8 | 0 | 88 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 320 | 0 | 194 | 83 | 50 | 39 | 15 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 56 | 8 | 0 | 0 | 1 | 28 | 0 | 0 | 0 | 163 | 0 | 59 | 11 | 0 | 139 | 0 | 0 | 0 | 305 | 12 | 8 | 0 | 0 | 0 | 0 | 135 | 0 | 65 | 11 | 12 | 51 | 0 | 359 | 68 | 17 | 0 | 2 | 0 | 9 | 0 | 17 | 29 | 0 | 391 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 34 | 17 | 335 | 0 | 0 | 550 | 0 | 377 | 0 | 120 | 37 | 0 | 0 |  | 905 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1030 | 180 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 508 | 9 | 200 | 1034 | 27 | 0 | 0 | 8 | 41 |  | 5956 | 5099 | 11055 | 3502 | 905 | 1723 | 0 | 470 | 2960 | 168 | 0 | 48 | 56 | 1034 | 189 | 0 | 90.725 | 106.85
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 39 | 0 | 3 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 21 | 25 | 12 | 17 | 0 | 89 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 194 | 83 | 50 | 38 | 15 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 54 | 6 | 0 | 0 | 1 | 28 | 0 | 0 | 0 | 120 | 0 | 59 | 11 | 0 | 139 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 135 | 0 | 78 | 16 | 12 | 52 | 0 | 373 | 67 | 52 | 0 | 2 | 15 | 35 | 0 | 17 | 29 | 0 | 396 | 0 | 9 | 17 | 4 | 0 | 0 | 21 | 34 | 17 | 305 | 0 | 0 | 612 | 0 | 376 | 0 | 150 | 28 | 0 | 0 |  | 905 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 230 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1160 | 180 | 0 | 0 | 3 | 61 | 0 | 0 | 0 | 514 | 13 | 250 | 1034 | 56 | 0 | 0 | 24 | 65 |  | 6023 | 5441 | 11464 | 3431 | 905 | 1722 | 0 | 592 | 3206 | 169 | 0 | 48 | 54 | 1034 | 303 | 0 | 129.88 | 106.85
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 21 | 25 | 11 | 17 | 0 | 90 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 215 | 83 | 50 | 34 | 15 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 52 | 4 | 0 | 0 | 1 | 28 | 0 | 0 | 0 | 120 | 0 | 57 | 11 | 0 | 138 | 0 | 0 | 0 | 310 | 12 | 5 | 0 | 0 | 0 | 0 | 134 | 0 | 80 | 19 | 12 | 57 | 0 | 374 | 67 | 52 | 0 | 4 | 85 | 35 | 0 | 17 | 29 | 0 | 390 | 10 | 34 | 17 | 17 | 0 | 8 | 27 | 34 | 17 | 300 | 0 | 0 | 612 | 2 | 376 | 0 | 290 | 30 | 0 | 0 |  | 905 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 230 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1200 | 180 | 0 | 0 | 2 | 76 | 0 | 0 | 0 | 510 | 17 | 307 | 1034 | 62 | 0 | 0 | 36 | 88 |  | 6283 | 5567 | 11850 | 3365 | 905 | 1854 | 0 | 721 | 3299 | 170 | 0 | 48 | 52 | 1034 | 400 | 2 | 76.4 | 106.85
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 14 | 21 | 25 | 7 | 17 | 0 | 90 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 300 | 0 | 214 | 81 | 50 | 31 | 15 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 68 | 4 | 0 | 0 | 1 | 28 | 0 | 0 | 0 | 163 | 0 | 55 | 11 | 0 | 138 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 0 | 0 | 0 | 134 | 0 | 85 | 19 | 12 | 86 | 0 | 360 | 65 | 52 | 0 | 4 | 100 | 35 | 0 | 17 | 24 | 12 | 390 | 12 | 27 | 72 | 17 | 0 | 17 | 23 | 34 | 12 | 300 | 0 | 0 | 612 | 2 | 374 | 0 | 480 | 66 | 0 | 16 |  | 905 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 230 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1200 | 180 | 0 | 0 | 4 | 90 | 0 | 0 | 0 | 512 | 24 | 307 | 1031 | 72 | 0 | 0 | 60 | 80 |  | 6744 | 5591 | 12335 | 3340 | 905 | 2146 | 0 | 836 | 3299 | 170 | 0 | 64 | 68 | 1031 | 474 | 2 | 62.075 | 106.84
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 26 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 2 | 17 | 0 | 14 | 21 | 25 | 12 | 17 | 0 | 90 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 295 | 0 | 214 | 87 | 50 | 29 | 15 | 0 | 43 | 0 | 9 | 8 | 0 | 0 | 0 | 18 | 68 | 3 | 0 | 0 | 1 | 20 | 0 | 0 | 0 | 163 | 0 | 55 | 11 | 0 | 138 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 10 | 0 | 0 | 135 | 0 | 112 | 19 | 12 | 86 | 15 | 360 | 57 | 52 | 0 | 5 | 105 | 35 | 0 | 17 | 28 | 12 | 381 | 17 | 20 | 72 | 30 | 0 | 17 | 28 | 34 | 33 | 295 | 36 | 0 | 612 | 0 | 374 | 0 | 510 | 18 | 0 | 17 |  | 904 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 225 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 15 | 0 | 4 | 30 | 1220 | 220 | 0 | 0 | 4 | 92 | 0 | 0 | 0 | 512 | 28 | 307 | 1032 | 121 | 0 | 0 | 46 | 105 |  | 6899 | 5745 | 12644 | 3304 | 904 | 2223 | 0 | 1019 | 3313 | 170 | 0 | 120 | 68 | 1032 | 491 | 0 | 34.38 | 106.84
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 14 | 0 | 25 | 4 | 17 | 0 | 90 | 80 | 0 | 0 | 5 | 225 | 0 | 0 | 0 |  | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 310 | 0 | 216 | 68 | 70 | 33 | 15 | 0 | 43 | 0 | 21 | 8 | 0 | 0 | 0 | 18 | 80 | 0 | 0 | 0 | 1 | 20 | 28 | 0 | 0 | 163 | 0 | 51 | 11 | 0 | 136 | 0 | 0 | 0 | 305 | 12 | 5 | 0 | 65 | 0 | 0 | 134 | 0 | 131 | 19 | 12 | 78 | 47 | 306 | 67 | 52 | 5 | 4 | 88 | 35 | 0 | 17 | 28 | 15 | 392 | 17 | 35 | 72 | 35 | 0 | 17 | 7 | 35 | 0 | 295 | 36 | 0 | 612 | 0 | 368 | 0 | 595 | 48 | 0 | 13 |  | 905 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 225 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 15 | 0 | 46 | 0 | 6 | 55 | 1244 | 220 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 512 | 19 | 307 | 1030 | 104 | 0 | 0 | 7 | 99 |  | 7160 | 5746 | 12906 | 3284 | 905 | 2300 | 0 | 1228 | 3330 | 170 | 0 | 142 | 80 | 1030 | 437 | 0 | 42 | 106.84
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 0 | 14 | 21 | 25 | 10 | 17 | 0 | 90 | 80 | 0 | 0 | 25 | 220 | 0 | 0 | 0 |  | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 335 | 0 | 213 | 8 | 50 | 37 | 15 | 0 | 43 | 0 | 40 | 8 | 0 | 0 | 0 | 18 | 88 | 0 | 0 | 0 | 1 | 0 | 28 | 5 | 5 | 120 | 0 | 50 | 30 | 0 | 134 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 145 | 0 | 0 | 134 | 0 | 132 | 17 | 12 | 51 | 57 | 307 | 67 | 52 | 17 | 2 | 88 | 35 | 0 | 17 | 29 | 17 | 380 | 17 | 38 | 72 | 35 | 0 | 17 | 2 | 35 | 22 | 325 | 36 | 0 | 612 | 4 | 376 | 0 | 450 | 44 | 0 | 0 |  | 729 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 225 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 38 | 0 | 48 | 0 | 5 | 55 | 1244 | 220 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 509 | 19 | 307 | 1034 | 100 | 0 | 0 | 8 | 78 |  | 7038 | 5476 | 12514 | 3200 | 729 | 2011 | 0 | 1394 | 3335 | 170 | 0 | 164 | 88 | 1034 | 385 | 4 | 43.93 | 106.84
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 10 | 64 | 7 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 14 | 20 | 25 | 10 | 17 | 0 | 90 | 80 | 0 | 0 | 25 | 148 | 0 | 0 | 0 |  | 0 | 25 | 0 | 0 | 8 | 1 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 214 | 8 | 50 | 37 | 15 | 0 | 43 | 0 | 43 | 8 | 0 | 0 | 0 | 18 | 72 | 0 | 0 | 0 | 1 | 0 | 28 | 5 | 5 | 163 | 0 | 56 | 31 | 0 | 132 | 0 | 0 | 0 | 315 | 12 | 5 | 0 | 190 | 0 | 0 | 123 | 0 | 131 | 14 | 12 | 51 | 60 | 308 | 67 | 52 | 17 | 3 | 52 | 35 | 17 | 34 | 36 | 17 | 392 | 17 | 4 | 72 | 35 | 0 | 17 | 8 | 50 | 35 | 320 | 17 | 0 | 612 | 3 | 373 | 0 | 340 | 15 | 0 | 0 |  | 476 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 7 | 16 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 108 | 0 | 48 | 0 | 3 | 55 | 1244 | 220 | 0 | 23 | 0 | 28 | 30 | 0 | 0 | 513 | 13 | 307 | 1031 | 82 | 0 | 0 | 1 | 0 |  | 6994 | 5265 | 12259 | 3195 | 476 | 2018 | 0 | 1638 | 3331 | 170 | 0 | 153 | 72 | 1031 | 172 | 3 | 86.905 | 106.84
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 14 | 20 | 0 | 10 | 17 | 0 | 90 | 80 | 0 | 0 | 25 | 149 | 0 | 0 | 0 |  | 0 | 35 | 36 | 0 | 31 | 17 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 217 | 8 | 50 | 39 | 15 | 0 | 43 | 0 | 43 | 8 | 0 | 0 | 0 | 18 | 60 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 130 | 0 | 56 | 31 | 0 | 132 | 0 | 0 | 0 | 275 | 12 | 5 | 0 | 252 | 0 | 0 | 0 | 0 | 132 | 8 | 12 | 51 | 60 | 305 | 0 | 52 | 17 | 1 | 52 | 35 | 72 | 34 | 36 | 18 | 380 | 17 | 4 | 72 | 35 | 0 | 17 | 1 | 51 | 35 | 320 | 17 | 0 | 560 | 5 | 372 | 0 | 210 | 4 | 0 | 0 |  | 476 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 6 | 48 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 70 | 0 | 56 | 0 | 1 | 55 | 1120 | 220 | 0 | 137 | 0 | 29 | 35 | 0 | 0 | 514 | 8 | 280 | 1035 | 46 | 0 | 0 | 0 | 0 |  | 6608 | 5149 | 11757 | 3078 | 476 | 1760 | 0 | 1745 | 3128 | 170 | 0 | 198 | 60 | 1035 | 102 | 5 | 41.065 | 106.84
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 |  | 0 | 400 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 14 | 20 | 0 | 10 | 17 | 0 | 89 | 80 | 0 | 0 | 25 | 70 | 0 | 0 | 0 |  | 7 | 39 | 85 | 0 | 38 | 19 | 0 | 6 | 0 | 0 | 0 | 300 | 0 | 213 | 8 | 70 | 42 | 15 | 0 | 43 | 0 | 43 | 8 | 0 | 0 | 0 | 18 | 60 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 56 | 31 | 0 | 132 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 275 | 0 | 0 | 85 | 0 | 132 | 1 | 12 | 54 | 65 | 309 | 54 | 52 | 17 | 0 | 51 | 35 | 89 | 34 | 37 | 19 | 380 | 17 | 0 | 72 | 35 | 0 | 17 | 0 | 51 | 35 | 330 | 17 | 0 | 550 | 1 | 310 | 0 | 200 | 2 | 0 | 4 |  | 476 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 67 | 6 | 64 | 0 | 0 | 0 | 39 | 5 | 0 | 0 | 0 | 12 | 0 | 22 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 50 | 0 | 55 | 0 | 0 | 55 | 1000 | 180 | 0 | 137 | 0 | 7 | 35 | 0 | 0 | 512 | 2 | 250 | 1029 | 10 | 0 | 0 | 0 | 0 |  | 6721 | 4905 | 11626 | 3002 | 476 | 1677 | 0 | 1963 | 2904 | 169 | 0 | 323 | 60 | 1029 | 22 | 1 | 70.67 | 106.84
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 38 | 335 | 0 | 0 | 0 | 22 | 100 | 13 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 14 | 20 | 17 | 10 | 25 | 0 | 88 | 80 | 0 | 0 | 25 | 75 | 0 | 0 | 0 |  | 18 | 49 | 85 | 0 | 44 | 19 | 0 | 13 | 0 | 0 | 0 | 315 | 0 | 213 | 8 | 50 | 42 | 15 | 0 | 43 | 0 | 43 | 16 | 0 | 0 | 0 | 6 | 62 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 55 | 31 | 0 | 134 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 285 | 0 | 0 | 140 | 0 | 132 | 0 | 12 | 79 | 75 | 308 | 74 | 70 | 17 | 0 | 52 | 35 | 102 | 40 | 73 | 21 | 385 | 17 | 0 | 162 | 35 | 0 | 17 | 0 | 51 | 30 | 320 | 54 | 0 | 600 | 0 | 168 | 0 | 200 | 0 | 0 | 7 |  | 476 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 32 | 63 | 0 | 67 | 10 | 80 | 0 | 0 | 0 | 39 | 12 | 93 | 0 | 0 | 28 | 0 | 28 | 0 | 0 | 2 | 63 | 0 | 220 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 18 | 0 | 64 | 0 | 104 | 0 | 0 | 113 | 1020 | 220 | 0 | 150 | 0 | 0 | 35 | 0 | 0 | 510 | 0 | 307 | 1033 | 0 | 0 | 0 | 0 | 0 |  | 7203 | 5480 | 12683 | 3104 | 476 | 1872 | 0 | 2447 | 2888 | 168 | 0 | 633 | 62 | 1033 | 0 | 0 | 92.635 | 106.84
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 57 | 150 | 13 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 14 | 20 | 17 | 10 | 25 | 0 | 87 | 80 | 0 | 0 | 25 | 95 | 0 | 0 | 0 |  | 18 | 71 | 85 | 0 | 42 | 19 | 0 | 13 | 0 | 0 | 0 | 285 | 0 | 219 | 8 | 50 | 43 | 15 | 0 | 51 | 0 | 43 | 52 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 57 | 31 | 0 | 135 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 297 | 0 | 0 | 150 | 0 | 132 | 0 | 12 | 144 | 85 | 377 | 92 | 105 | 17 | 0 | 52 | 35 | 110 | 106 | 76 | 21 | 392 | 17 | 0 | 162 | 35 | 0 | 20 | 0 | 68 | 36 | 285 | 160 | 0 | 590 | 0 | 148 | 0 | 200 | 0 | 0 | 0 |  | 476 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 42 | 57 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 39 | 24 | 95 | 0 | 0 | 47 | 0 | 28 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 18 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1140 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 510 | 0 | 307 | 1126 | 0 | 0 | 0 | 0 | 0 |  | 7659 | 5851 | 13510 | 3081 | 476 | 1836 | 0 | 2947 | 2978 | 167 | 0 | 841 | 58 | 1126 | 0 | 0 | 0 | 106.84
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 49 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 14 | 20 | 17 | 10 | 25 | 0 | 87 | 80 | 0 | 0 | 25 | 105 | 0 | 0 | 0 |  | 18 | 71 | 83 | 0 | 44 | 19 | 0 | 19 | 0 | 0 | 0 | 285 | 0 | 217 | 8 | 50 | 43 | 15 | 0 | 51 | 0 | 43 | 52 | 0 | 0 | 0 | 16 | 62 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 56 | 31 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 245 | 0 | 0 | 160 | 0 | 132 | 0 | 12 | 145 | 98 | 385 | 93 | 105 | 17 | 0 | 52 | 35 | 72 | 106 | 76 | 22 | 387 | 17 | 0 | 162 | 35 | 0 | 35 | 0 | 92 | 35 | 285 | 160 | 0 | 550 | 0 | 158 | 0 | 200 | 0 | 0 | 0 |  | 476 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 38 | 57 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 39 | 24 | 95 | 0 | 0 | 44 | 0 | 28 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 18 | 0 | 50 | 0 | 106 | 0 | 0 | 113 | 1100 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 512 | 0 | 250 | 1133 | 0 | 0 | 0 | 0 | 0 |  | 7557 | 5692 | 13249 | 3075 | 476 | 1857 | 0 | 2794 | 2853 | 167 | 0 | 832 | 62 | 1133 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 49 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 13 | 20 | 0 | 10 | 25 | 0 | 88 | 80 | 0 | 0 | 25 | 106 | 0 | 0 | 0 |  | 18 | 71 | 83 | 0 | 38 | 19 | 0 | 24 | 0 | 0 | 0 | 285 | 0 | 215 | 8 | 50 | 43 | 15 | 0 | 51 | 0 | 43 | 52 | 0 | 0 | 0 | 18 | 60 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 56 | 31 | 0 | 135 | 0 | 0 | 0 | 285 | 12 | 8 | 0 | 245 | 0 | 0 | 162 | 0 | 132 | 0 | 12 | 145 | 98 | 385 | 93 | 105 | 17 | 0 | 52 | 35 | 68 | 106 | 74 | 10 | 390 | 17 | 0 | 162 | 35 | 0 | 35 | 0 | 91 | 35 | 285 | 108 | 0 | 550 | 0 | 216 | 0 | 200 | 0 | 0 | 0 |  | 475 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 38 | 58 | 0 | 67 | 9 | 110 | 0 | 0 | 0 | 39 | 24 | 95 | 0 | 0 | 47 | 0 | 28 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 18 | 0 | 50 | 0 | 106 | 0 | 0 | 113 | 1110 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 525 | 0 | 250 | 1126 | 0 | 0 | 0 | 0 | 0 |  | 7487 | 5709 | 13196 | 3061 | 475 | 1836 | 0 | 2752 | 2934 | 168 | 0 | 784 | 60 | 1126 | 0 | 0 | 0 | 106.84
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 49 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 13 | 20 | 25 | 11 | 25 | 0 | 89 | 80 | 0 | 0 | 25 | 105 | 0 | 0 | 0 |  | 18 | 71 | 83 | 0 | 41 | 19 | 0 | 29 | 0 | 0 | 0 | 300 | 0 | 216 | 8 | 70 | 43 | 15 | 0 | 51 | 0 | 44 | 52 | 0 | 0 | 0 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 56 | 31 | 0 | 135 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 245 | 0 | 0 | 153 | 0 | 132 | 0 | 12 | 145 | 100 | 354 | 93 | 105 | 17 | 0 | 52 | 35 | 68 | 106 | 73 | 10 | 386 | 17 | 0 | 108 | 35 | 0 | 35 | 0 | 92 | 35 | 290 | 90 | 0 | 550 | 0 | 214 | 0 | 200 | 0 | 1 | 0 |  | 476 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 38 | 58 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 39 | 24 | 96 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 18 | 0 | 50 | 0 | 113 | 0 | 0 | 113 | 1090 | 180 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 610 | 0 | 250 | 1133 | 0 | 0 | 0 | 0 | 0 |  | 7461 | 5716 | 13177 | 3097 | 476 | 1813 | 0 | 2661 | 2997 | 169 | 0 | 767 | 64 | 1133 | 0 | 0 | 0 | 106.84
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 49 | 150 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 0 | 20 | 25 | 11 | 25 | 0 | 90 | 80 | 0 | 0 | 25 | 105 | 0 | 0 | 0 |  | 18 | 71 | 83 | 0 | 44 | 19 | 0 | 33 | 0 | 0 | 0 | 285 | 0 | 219 | 8 | 70 | 43 | 15 | 0 | 51 | 0 | 45 | 52 | 0 | 0 | 0 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 57 | 31 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 245 | 0 | 0 | 153 | 0 | 132 | 0 | 12 | 145 | 98 | 354 | 95 | 105 | 17 | 0 | 52 | 35 | 68 | 106 | 78 | 10 | 392 | 17 | 0 | 108 | 35 | 0 | 35 | 0 | 67 | 35 | 285 | 90 | 0 | 550 | 0 | 211 | 0 | 200 | 0 | 0 | 0 |  | 473 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 38 | 56 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 39 | 24 | 97 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 18 | 0 | 50 | 0 | 113 | 0 | 0 | 113 | 1110 | 180 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 610 | 0 | 250 | 1132 | 0 | 0 | 0 | 0 | 0 |  | 7375 | 5738 | 13113 | 3081 | 473 | 1821 | 0 | 2591 | 3014 | 170 | 0 | 767 | 64 | 1132 | 0 | 0 | 0 | 106.83
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 20 | 25 | 12 | 16 | 0 | 90 | 80 | 0 | 0 | 25 | 226 | 0 | 0 | 0 |  | 14 | 71 | 83 | 0 | 44 | 19 | 0 | 35 | 0 | 0 | 0 | 310 | 0 | 219 | 8 | 50 | 44 | 15 | 0 | 51 | 0 | 45 | 26 | 0 | 0 | 0 | 18 | 66 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 57 | 31 | 0 | 136 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 245 | 0 | 0 | 153 | 0 | 120 | 0 | 12 | 145 | 100 | 353 | 95 | 88 | 17 | 0 | 52 | 35 | 68 | 106 | 78 | 0 | 396 | 17 | 0 | 35 | 35 | 0 | 35 | 0 | 51 | 35 | 325 | 17 | 0 | 550 | 0 | 211 | 0 | 200 | 0 | 0 | 0 |  | 473 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 31 | 55 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 39 | 24 | 97 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 63 | 0 | 225 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 18 | 0 | 50 | 0 | 113 | 0 | 0 | 35 | 1100 | 180 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 609 | 0 | 250 | 1139 | 0 | 0 | 0 | 0 | 0 |  | 7245 | 5663 | 12908 | 3276 | 473 | 1818 | 0 | 2272 | 3008 | 170 | 0 | 686 | 66 | 1139 | 0 | 0 | 88 | 106.83
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 20 | 25 | 12 | 8 | 0 | 90 | 80 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 18 | 71 | 84 | 0 | 44 | 19 | 0 | 36 | 0 | 0 | 0 | 315 | 0 | 217 | 8 | 50 | 44 | 15 | 0 | 51 | 0 | 45 | 8 | 0 | 0 | 0 | 18 | 74 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 57 | 31 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 245 | 0 | 0 | 153 | 0 | 41 | 0 | 12 | 89 | 93 | 352 | 96 | 35 | 17 | 0 | 52 | 17 | 68 | 106 | 39 | 10 | 396 | 17 | 0 | 35 | 17 | 0 | 35 | 0 | 40 | 17 | 320 | 17 | 0 | 600 | 0 | 216 | 0 | 200 | 0 | 0 | 0 |  | 473 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 31 | 55 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 39 | 24 | 97 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 63 | 0 | 225 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 35 | 1170 | 180 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 506 | 0 | 307 | 1128 | 0 | 0 | 0 | 0 | 0 |  | 6933 | 5643 | 12576 | 3272 | 473 | 1824 | 0 | 1929 | 3087 | 170 | 0 | 619 | 74 | 1128 | 0 | 0 | 118 | 106.83
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9568800 | 0 |  | 0 | 10442000 | 0 | 0 | 0 | 588915 | 7669040 | 0 | 492000 | 0 | 349776 | 1706400 | 56000 | 0 | 0 | 0 | 414720 | 447698 | 445144 | 0 | 328200 | 461160 | 529600 | 301100 | 307680 | 0 | 2144029 | 1928000 | 0 | 0 | 306943 | 4357116 | 0 | 0 | 0 |  | 133680 | 911136 | 850854 | 0 | 455040 | 243360 | 0 | 489120 | 0 | 0 | 0 | 7772000 | 0 | 5049000 | 1187636 | 1418860 | 949968 | 364800 | 0 | 1091148 | 0 | 717760 | 400171 | 0 | 0 | 0 | 404610 | 1503360 | 100800 | 0 | 0 | 6850 | 365000 | 312808 | 54000 | 84888 | 3639436 | 0 | 1296864 | 459840 | 0 | 3272550 | 0 | 0 | 0 | 7294500 | 282624 | 171552 | 0 | 3379745 | 0 | 0 | 2940000 | 0 | 2153376 | 136755 | 300480 | 1907040 | 1257890 | 8580000 | 1624800 | 1200960 | 267636 | 27840 | 1234473 | 576589 | 1176758 | 1020300 | 1007160 | 263040 | 9389000 | 321600 | 204160 | 1357920 | 590891 | 0 | 459000 | 122228 | 1118400 | 614160 | 7716400 | 751055 | 0 | 14154544 | 18729 | 8094545 | 0 | 5514091 | 352109 | 197100 | 43200 |  | 17457454 | 0 | 3900960 | 0 | 0 | 0 | 0 | 0 | 240960 | 398336 | 0 | 1593000 | 198859 | 993504 | 0 | 0 | 0 | 351914 | 189327 | 679088 | 0 | 0 | 335960 | 0 | 265000 | 0 | 0 | 98892 | 1495418 | 0 | 5397000 | 0 | 0 | 4428545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9039418 | 182400 | 0 | 977760 | 0 | 1443110 | 0 | 29117 | 1104672 | 29934100 | 5026500 | 0 | 1453200 | 17460 | 586080 | 660672 | 0 | 0 | 12654550 | 158587 | 6786000 | 25390909 | 683280 | 0 | 2901 | 195000 | 566920 |  | 164202510 | 134916853 | 299119363 | 80810449 | 17457454 | 45083336 | 0 | 35736663 | 78516157 | 4072029 | 0 | 7440990 | 1503360 | 25390909 | 3089287 | 18729 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27558144 | 0 |  | 0 | 33205560 | 0 | 0 | 0 | 10376682.3 | 23390572 | 0 | 2632200 | 0 | 6278479.2 | 33138288 | 1044400 | 0 | 0 | 0 | 7572787.2 | 7055720.48 | 8141683.76 | 0 | 246150 | 0 | 0 | 0 | 5510548.8 | 0 | 0 | 0 | 0 | 0 | 5813500.42 | 13899200.04 | 0 | 0 | 0 |  | 2351431.2 | 16045104.96 | 15238795.14 | 0 | 8905132.8 | 4005705.6 | 0 | 0 | 0 | 0 | 0 | 21683880 | 0 | 16762680 | 3978580.6 | 4582917.8 | 3201392.16 | 1597824 | 0 | 4375503.48 | 0 | 12855081.6 | 7227088.26 | 0 | 0 | 0 | 303457.5 | 9862041.6 | 313488 | 0 | 0 | 0 | 1423500 | 1166773.84 | 245700 | 386240.4 | 12446871.12 | 0 | 7197595.2 | 2400364.8 | 0 | 9130414.5 | 0 | 0 | 0 | 22540005 | 211968 | 130379.52 | 0 | 68946798 | 0 | 0 | 56477400 | 0 | 37920951.36 | 0 | 5351548.8 | 33087144 | 20855816.2 | 22737000 | 30968688 | 22530009.6 | 4801389.84 | 0 | 20183633.55 | 11208890.16 | 21111038.52 | 19497933 | 19548975.6 | 4684742.4 | 24974740 | 5489712 | 0 | 24836356.8 | 9915150.98 | 0 | 8202330 | 0 | 20153568 | 10403870.4 | 22917708 | 10574854.4 | 0 | 98657171.68 | 0 | 47757815.5 | 0 | 0 | 0 | 0 | 0 |  | 49055445.74 | 0 | 11507832 | 0 | 0 | 0 | 0 | 0 | 4532457.6 | 7492700.16 | 0 | 5033880 | 942591.66 | 17128008.96 | 0 | 0 | 0 | 6302779.74 | 3474150.45 | 11415469.28 | 0 | 0 | 6017043.6 | 0 | 4746150 | 0 | 0 | 74861.244 | 16494460.54 | 0 | 45550680 | 0 | 0 | 14614198.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26395100.56 | 3115392 | 0 | 19379203.2 | 0 | 28746751.2 | 0 | 0 | 21916692.48 | 193972968 | 15632415 | 0 | 28119420 | 0 | 0 | 11462659.2 | 0 | 0 | 92378215 | 0 | 50555700 | 167833908.49 | 0 | 0 | 0 | 0 | 0 |  | 1060229070.07 | 863891134.604 | 1924120204.674 | 235694932.304 | 49055445.74 | 124146756.62 | 0 | 660327234.27 | 545367010.72 | 0 | 0 | 131832874.93 | 9862041.6 | 167833908.49 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 26 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 2 | 17 | 0 | 14 | 21 | 25 | 12 | 17 | 0 | 90 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 295 | 0 | 214 | 87 | 50 | 29 | 15 | 0 | 43 | 0 | 9 | 8 | 0 | 0 | 0 | 18 | 68 | 3 | 0 | 0 | 1 | 20 | 0 | 0 | 0 | 163 | 0 | 55 | 11 | 0 | 138 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 10 | 0 | 0 | 135 | 0 | 112 | 19 | 12 | 86 | 15 | 360 | 57 | 52 | 0 | 5 | 105 | 35 | 0 | 17 | 28 | 12 | 381 | 17 | 20 | 72 | 30 | 0 | 17 | 28 | 34 | 33 | 295 | 36 | 0 | 612 | 0 | 374 | 0 | 510 | 18 | 0 | 17 |  | 904 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 225 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 15 | 0 | 4 | 30 | 1220 | 220 | 0 | 0 | 4 | 92 | 0 | 0 | 0 | 512 | 28 | 307 | 1032 | 121 | 0 | 0 | 46 | 105 |  | 12644 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 57 | 150 | 13 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 14 | 20 | 17 | 10 | 25 | 0 | 87 | 80 | 0 | 0 | 25 | 95 | 0 | 0 | 0 | 0 | 18 | 71 | 85 | 0 | 42 | 19 | 0 | 13 | 0 | 0 | 0 | 285 | 0 | 219 | 8 | 50 | 43 | 15 | 0 | 51 | 0 | 43 | 52 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 57 | 31 | 0 | 135 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 297 | 0 | 0 | 150 | 0 | 132 | 0 | 12 | 144 | 85 | 377 | 92 | 105 | 17 | 0 | 52 | 35 | 110 | 106 | 76 | 21 | 392 | 17 | 0 | 162 | 35 | 0 | 20 | 0 | 68 | 36 | 285 | 160 | 0 | 590 | 0 | 148 | 0 | 200 | 0 | 0 | 0 |  | 476 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 42 | 57 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 39 | 24 | 95 | 0 | 0 | 47 | 0 | 28 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 18 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1140 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 510 | 0 | 307 | 1126 | 0 | 0 | 0 | 0 | 0 |  | 13510 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 58 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 21 | 25 | 20 | 25 | 0 | 89 | 80 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 18 | 70 | 85 | 0 | 44 | 18 | 0 | 20 | 0 | 0 |  | 310 | 0 | 210 | 88 | 50 | 44 | 54 | 0 | 51 | 0 | 44 | 50 | 0 | 0 |  | 18 | 70 | 8 | 0 | 0 | 0 | 0 | 28 | 5 | 5 | 163 | 0 | 60 | 86 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 300 | 0 | 0 | 150 | 0 | 132 | 0 | 12 | 180 | 90 | 380 | 96 | 100 | 17 | 0 | 52 | 35 | 110 | 106 | 53 | 12 | 400 | 17 | 0 | 162 | 35 | 0 | 35 | 0 | 92 | 35 | 330 | 163 | 0 | 612 | 60 | 350 | 0 | 200 |  |  |  |  | 489 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 30 | 52 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 38 | 24 | 96 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 18 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 510 | 0 | 307 | 1100 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 14 | 21 | 24 | 20 | 17 | 0 | 85 | 80 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 40 | 68 | 0 | 44 | 6 | 0 | 5 | 0 | 0 | 0 | 300 | 0 | 210 | 8 | 50 | 41 | 54 | 0 | 51 | 0 | 35 | 8 | 0 | 0 |  | 15 | 60 | 8 | 0 | 0 | 1.6 | 0 | 28 | 5 | 5 | 163 | 0 | 60 | 86 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 300 | 0 | 0 | 133 | 0 | 132 | 20 | 12 | 51 | 80 | 380 | 75 | 52 | 17 | 5 | 52 | 35 | 110 | 34 | 28 | 12 | 400 | 17 | 50 | 72 | 35 | 0 | 0 | 35 | 34 | 36 | 330 | 35 | 0 | 612 | 42 | 350 | 0 | 200 | 70 |  |  |  | 489 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 67 | 10 | 16 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 28 | 0 | 22 | 0 | 0 | 5 | 62 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 500 | 30 | 250 | 1000 | 170 | 0 |  | 29 | 47 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 21 | 24 | 12 | 8 | 0 | 87 | 80 | 0 | 0 | 5 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 350 | 0 | 215 | 8 | 50 | 38 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 52 | 0 | 0 | 0 | 1 | 0 | 28 | 5 | 5 | 163 | 0 | 59 | 30 | 0 | 138 | 0 | 0 | 0 | 320 | 12 | 8 | 0 | 0 | 0 | 0 | 135 | 0 | 35 | 11 | 0 | 52 | 0 | 383 | 68 | 17 | 0 | 1 | 0 | 0 | 0 | 34 | 28 | 0 | 392 | 0 | 5 | 0 | 0 | 0 | 0 | 11 | 34 | 17 | 330 | 0 | 0 | 550 | 0 | 352 | 0 | 200 | 14 | 0 | 0 | 0 | 479 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1100 | 180 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 508 | 4 | 260 | 1033 | 51 | 0 | 0 | 24 | 26 | 0 |  |  |  | 125893785 | 17457454 | 0 | 78516157 | 43177653 | 1503360 | 3089287 | 18729 | 4072029 |  |  |  | 273728454
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 125.8938 | 17.4575 | 0 | 78.5162 | 43.1777 | 1.5034 | 3.0893 | 0.018729 | 4.072
| Minimum Generation |  | 11003 | 6:00
| Highest Generation |  | 13510 | 19:00 | [129 empty] | 0 | [76 empty] | 273.7285
| Day Peak Generation |  | 12644 | 12:00
| Evening Peak Generation |  | 13510 | 19:00 | [206 empty] | 202699852
| HVDC Max Flow |  | 906 | 2:00 | [206 empty] | 202.6999
| HVDC EvPeak Flow |  | 476 | 19:00
| Load factor L.F |  | 92.25% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-10-10
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-10-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12644 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10335
Evening Peak Generation : |  |  | 13510 | MW Hour : | 19:00 | Available Max Generation : |  | 14579
E.P. Demand (at gen end) : |  |  | 13510 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13500
Maximum Generation : |  |  | 13510 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1079
Total Gen. (MKWH) : |  |  | 299.1194 | System Load Factor : | 92.25% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 830 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-10-10
Actual : |  | 106.81 | Ft.(MSL) , | Rule curve : | 106.81 | Ft.( MSL )
Gas Consumed : |  | Total = | 896.85 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 359841688.924 | Adani : | 167833908.49
|  |  | Coal : | 545367010.72 | Oil: | 792160109.2 | Total: | 1865202717.334
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4533.8427 |  |  | 0 | -9.558%
Chittagong Area |  | 0 | 0:00 | 1245.692 |  |  | 0 | -7.543%
Khulna Area |  | 0 | 0:00 | 1744.9061 |  |  | 0 | -7.112%
Rajshahi Area |  | 0 | 0:00 | 1516.5797 |  |  | 0 | -6.654%
Cumilla Area |  | 0 | 0:00 | 1247.9061 |  |  | 0 | -6.938%
Mymensingh Area |  | 0 | 0:00 | 928.0993 |  |  | 0 | -6.541%
Sylhet Area |  | 0 | 0:00 | 520.2585 |  |  | 0 | -7.299%
Barisal Area |  | 0 | 0:00 | 433.5457 |  |  | 0 | -6.468%
Rangpur Area |  | 0 | 0:00 | 847.94 |  |  | 0 | -6.478%
Total |  | 0 |  | 13018.7703 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
- | 8:16 | Saidpur 132/33kV S/S TR-3 (424T) HT is restored.
- | 8:17 | Saidpur 132/33kV S/S TR-3 (424T) LT is restored.
8:20 | 15:58 | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D
8:23 | 16:11 | Khagrachari-Rangamati 132kV Ckt-1 Scheduled S/D from Khagrachori 132/33kV end Due to Rangamati-Khagrachari Ckt-01 Dead line
Checking and from Rangamati 132/33kV end Due to Annual deadline checking and maintenance
8:24 | 15:55 | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D
8:25 | 15:33 | Shariatpur 132/33kV S/S Auxiliary-02 (PGCB) LT Scheduled S/D Due to Annual Maintenance
8:27 | 15:20 | Shariatpur 132/33kV S/S Auxiliary-02 (PGCB) HT Scheduled S/D Due to Annual Maintenance
8:36 | 17:07 | Chandraghona-Madunaghat 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end Due to Annual maintenance and from
Madunaghat 132/33kV end Due to Annual Dead line checking and maintenance.
- | 8:40 | Bhaluka 132/33kV S/S Transformer- 02 HT is restored.
- | 8:41 | Bhaluka 132/33kV S/S Transformer- 02 LT is restored.
8:44 | 10:05 | Satkhira 132/33kV S/S Transformer-1 (T-1) LT Forced S/D |  |  |  |  | 40.0MW load interrup.
8:45 | 10:04 | Satkhira 132/33kV S/S Transformer-1 (T-1) HT Forced S/D Due to Source side isolator red-hot(maintenance) at 33 kv kalaroa feeder.
9:10 | - | Patuakhali 132/33kV S/S 415T (T-2) HT Scheduled S/D Due to Maintenance work
9:10 | - | Patuakhali 132/33kV S/S 415T (T-2) LT Scheduled S/D Due to Maintenance work
9:20 | - | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D Due to Annual Maintenance
- | 9:32 | Cumilla(S) 132/33kV S/S TR-2 HT is restored.
- | 9:34 | Cumilla(S) 132/33kV S/S TR-2 LT is restored.
9:48 | 12:56 | Aminbazar 400/230/132kV S/S 230 kv Bus 01 Scheduled S/D Due to Annual maintenance
9:50 | 16:54 | Haripur-Sonargaon 132kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to Shutdown taken due to relay change. and from
Haripur 230/132kV end Due to works at sonargoan S/S
10:41 | 12:07 | Cumilla(S) 132/33kV S/S TR-1 LT Scheduled S/D Due to Red hot maintenance. |  |  |  |  | 40.0MW load interrup.
10:41 | 12:07 | Cumilla(S) 132/33kV S/S TR-1 HT Scheduled S/D Due to Red hot maintenance. |  |  |  |  | 40.0MW load interrup.
11:21 | 16:36 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to Oil Leakage Chaek
12:00 | - | Day peak generation: 12644 MW
13:30 | - | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 Tripped from Sirajganj 132/33kV end showing 21-Distance Relay (Quadramho SHPM 101)
relays Due to None
13:48 | 14:08 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance relay relays Due to Unknown.
14:29 | 14:38 | Khulshi 132/33kV S/S 405T (T1) LT Tripped showing Micom relays Due to monsurabad 33kv feeder trip and that time feeder breaker dont trip |  |  |  |  | 54.0MW load interrup.
- | 15:33 | Shariatpur 132/33kV S/S Auxiliary-02 (PGCB) LT is restored.
15:41 | 15:53 | Mymensingh RPCL-Tangail 132kV Ckt-1 Tripped from Ghatail 132/33kV end showing REL 650, REL 670 relays.
15:43 | - | Power Fail of 132kV -A -Bus (Jamalpur,Sherpur & Netrakona) Due to 132kB GH- RPCL Ckt-1(Z1,Dist.-RB )&Ckt 2(Z1,DIST.RYB) |  |  |  |  | 173MW generation interrup. and 228MW load interrup.
Triped From RPCL . In GH side Ckt1 GCB Triped Due to Z1,Dist. L1,L3. Power Restor at 15:53
- | 15:48 | Aminbazar-Kaliakoir 230kV Ckt-1 is restored.
15:53 | 16:05 | Bagerhat-Goalpara 132 kV Ckt-1 Tripped from Goalpara 132/33kV end showing Distance Relay. relays Due to Temporary Fault, Zone-1
- | 15:58 | Thakurgaon 132/33kV S/S T-3(432T) LT is restored.
- | 16:18 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 is restored.
17:44 | 17:53 | Benapole 132/33kV S/S Transformer-2(416T) LT Tripped showing REF630 relays Due to Navaron, chutipur feeder fault |  |  |  |  | 15.0MW load interrup.
18:08 | - | Matarbari U-1 FSD due to coal shortage
18:56 | 19:01 | Noapara 132/33kV S/S T-2 LT Tripped showing SIEMENS 7SJ81 relays Due to R-4 33kV Feeder Fault |  |  |  |  | 11.5MW load interrup.
18:56 | 19:01 | Noapara 132/33kV S/S T-1 LT Tripped showing SIEMENS 7SJ81 relays Due to R-4 33kV Feeder Fault |  |  |  |  | 11.5MW load interrup.
19:00 | - | Evening peak Generation is 13510 MW
19:15 | 19:32 | Jashore 132/33kV S/S JH-2(L1) Tripped showing Trip ABC , Phase -C ,Zone-1, D-6.7Km relays Due to Thandaring
6:15 | - | Ashuganj-Brahmanbaria 132kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end. and from Ashuganj 230/132/33kV end Due to CB maintenance work
6:17 | 7:27 | Jashore 132/33kV S/S T-2 LT Forced S/D |  |  |  |  | 20.0MW load interrup.
6:18 | 7:25 | Jashore 132/33kV S/S T-2 HT Forced S/D Due to B phase red-hot |  |  |  |  | 20.0MW load interrup.
6:43 | 7:35 | Chattak-Sylhet 132 kV Ckt-2 Scheduled S/D from Sylhet 132/33kV end Due to Maintenance work due to Chatak Grid SS.
6:48 | - | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to According to NLDC suggestions and directions.
7:00 | - | Minimum Generation: 10335 MW.
7:06 | - | Hathazari-Madunaghat 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to According to NLDC suggestions and
directions. and from Hathazari 230/132/33kV end Due to red hot maintenance work
7:50 | - | Khagrachari-Rangamati 132kV Ckt-1 Scheduled S/D from Khagrachori 132/33kV end Due to Annual maintenance of Transmission
Line(Deadline Checking) and from Rangamati 132/33kV end Due to Annual Deadline checking

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-10-09
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 382 | 9568800 | Frequency control
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10442000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 588915
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 56000 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 492000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 7669040 | Frequency control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 57 | 349776 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 414720
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1706400
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 447698 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 445144
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 789360 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 529600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 10 | 301100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 307680 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 297 | 3379745
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2153376 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1200960
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 321600 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1357920
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 122228
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 614160 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 200 | 5514091 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 197100 | On test.
| Dhaka area Total |  |  |  | 5915 | 2586 | 48969413
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 306943
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 136755
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 243360 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 4072029 | Unit-1 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 95 | 4357116 | ST preparation
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 267636 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 71 | 911136 | Engine problem
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 850854 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 300480 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 489120
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 42 | 455040 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27840
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1234473 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 576589 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1176758
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 21 | 263040 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 590891 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 160 | 751055
60 | SS Power I |  | SS Power | 2*612 | 1224 | 590 | 14154544 | Unit-2 S/D due to coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 18729
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 148 | 8094545 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1697 | 39278933
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 219 | 5049000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7772000
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 285 | 7716400 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 43 | 949968
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 15 | 364800 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1187636 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1091148
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 85 | 1257890 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 717760 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1418860 | Gas shortage
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 144 | 1907040 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 58 | 1503360
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 400171
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 0 | 404610 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1020300 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 76 | 1007160 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 1118400 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 352109
| Cumilla Area Total |  |  |  | 2917 | 1588 | 35238612
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 0 | 100800 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6850
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 150 | 2940000 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 92 | 1624800 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 204160
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 133680 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 20 | 459000 | Fuel shortage
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 43200
| Mymensingh Area Total |  |  |  | 646 | 280 | 5512490
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 365000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 312808 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3639436
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 54000 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 84888 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 171552 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 57 | 1296864
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 31 | 459840 | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 135 | 3272550 | ST under maint.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 282624 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7294500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 377 | 8580000 | Machine problem.
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 392 | 9389000
| Sylhet Area Total |  |  |  | 2417 | 1508 | 35203062
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 476 | 17457454
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 240960 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 57 | 398336 | Fuel shortage
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 107 | 3900960 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 18 | 182400 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 586080
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 510 | 12654550 | Machine problem.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1210 | 35420740
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 993504
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 198859 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1593000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1140 | 29934100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5026500
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1453200
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 6786000
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 2901
| Barisal Area Total |  |  |  | 2236 | 2004 | 45988064
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 39 | 351914 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 24 | 189327 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 47 | 335960 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 173 | 4428545 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 9039418 | Frequency control
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 265000 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 98892 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 679088 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 977760
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1104672
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17460
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1126 | 25390909
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 195000
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 566920
| Rajshahi Area Total |  |  |  | 3449 | 2133 | 43640865
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 63 | 1495418
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 5397000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1443110 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29117
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 660672
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 158587
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 683280
| Rangpur Area Total |  |  |  | 950 | 504 | 9867184
| Total |  |  |  | 27086 | 13510 | 299119363
| Eastern Grid Total |  |  |  | 16752 | 7659 | 164202510
| Western Grid Total |  |  |  | 10334 | 5851 | 134916853
| National Grid Total |  |  |  | 27086 | 13510 | 299119363
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-10-08
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9390.56 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4496.2 | MW
i) Dhaka area |  |  | 5088.66 |  | MW | i) Khulna area |  |  |  | 1720 | MW
ii) Chattogram area |  |  | 1411.9 |  | MW | ii) Barishal area |  |  |  | 451.2 | MW
iii) Cumilla area |  |  | 1324 |  | MW | iii) Rajshahi area |  |  |  | 1394 | MW
iv) Mymensingh area |  |  | 1020 |  | MW | iv) Rangpur area |  |  |  | 931 | MW
v) Sylhet area |  |  | 546 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13886.76 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 10:00 | 67 | Jashore | 124 | 13:00 | 133 | Rajbari | 58 | 00:00
2 | AKSML | 6 | 23:00 | 68 | Jhenaidah | 105 | 00:00 | 134 | Rajendrapur | 108 | 20:00
3 | Aftabnagar | 56 | 12:00 | 69 | Joydebpur | 198 | 18:30 | 135 | Rajshahi | 136 | 00:00
4 | Agargaon | 118 | 13:00 | 70 | Joypurhat | 55 | 18:30 | 136 | Rajshahi-230 | 64 | 13:00
5 | Agrabad | 102 | 15:00 | 71 | Juldah | 16 | 00:00 | 137 | Ramganj | 114 | 21:00
6 | Amnura | 56 | 20:00 | 72 | KSRM | 24 | 16:00 | 138 | Rampur | 42 | 22:00
7 | Ashuganj | 81 | 03:00 | 73 | Kabirpur | 282 | 18:00 | 139 | Rangamati | 15 | 19:00
8 | BSRM | 148 | 19:30 | 74 | Kachua | 80 | 19:30 | 140 | Rangpur | 146 | 18:30
9 | Bagerhat | 86 | 19:00 | 75 | Kallyanpur | 108 | 13:00 | 141 | Ruppur | 7 | 11:00
10 | Bakulia | 100 | 15:00 | 76 | Kalurghat | 38 | 16:00 | 142 | SSM | 10 | 00:00
11 | Banani | 67.2 | 12:00 | 77 | Kamrangirchar | 58 | 13:00 | 143 | Saidpur | 107 | 18:30
12 | Bangabhaban | 20 | 10:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 121 | 18:30
13 | Barapukuria | 62 | 20:00 | 79 | Kazla | 121 | 13:00 | 145 | Satmasjid | 107 | 13:00
14 | Barguna | 22 | 21:00 | 80 | Keranigonj | 77 | 13:00 | 146 | Savar | 215 | 14:00
15 | Barishal | 105 | 13:00 | 81 | Khagrachori | 30 | 18:00 | 147 | SevenRings | 14.13 | 12:00
16 | Barishal-230 | 82 | 21:00 | 82 | Khulna | 92 | 13:00 | 148 | ShahCement | 24 | 00:00
17 | Baroaulia | 75 | 08:00 | 83 | Khulshi | 181 | 16:00 | 149 | Shahjadpur | 66 | 12:00
18 | Baroirhat | 75 | 18:30 | 84 | Kishoreganj | 150 | 21:00 | 150 | Shahjibazar | 140 | 18:30
19 | Bashundhara | 169 | 12:00 | 85 | Kodda | 296 | 18:00 | 151 | Shahmirpur | 55 | 03:00
20 | BashundharaCement | 6 | 00:00 | 86 | Kulaura | 44 | 18:00 | 152 | Shariatpur | 73 | 00:00
21 | Beanibazar | 68 | 18:00 | 87 | Kurigram | 62 | 18:00 | 153 | Sherpur | 130 | 19:00
22 | Benapole | 57 | 00:00 | 88 | Kushtia | 120 | 00:00 | 154 | Shikalbaha | 29 | 16:00
23 | Bhaluka | 150 | 15:00 | 89 | Lalbag | 84 | 13:00 | 155 | Shitalakhya | 88.8 | 12:00
24 | Bhandaria | 57 | 00:00 | 90 | Lalmonirhat | 60 | 18:00 | 156 | Sholosohor | 47 | 15:00
25 | Bhangura | 27 | 00:00 | 91 | MI_Cement | 8.8 | 01:00 | 157 | Shyampur | 154 | 06:00
26 | Bheramara(GK) | 47 | 00:00 | 92 | Madanganj | 33 | 15:00 | 158 | Siddhirganj | 108 | 11:00
27 | Bhulta | 252 | 18:00 | 93 | Madaripur | 97 | 00:00 | 159 | Sirajganj | 98 | 19:00
28 | Bog-Sherpur | 54 | 00:00 | 94 | Madartek | 67.76 | 00:00 | 160 | Sonargaon | 85 | 10:00
29 | Bogura | 151 | 19:00 | 95 | Madunaghat | 56 | 19:00 | 161 | Sreemongol | 71 | 19:30
30 | Borhanuddin | 81 | 00:00 | 96 | Magura | 54 | 00:00 | 162 | Sreepur | 73 | 12:00
31 | Brahmanbaria | 168 | 19:00 | 97 | Mahasthangarh | 66 | 18:30 | 163 | Srinagar | 42.27 | 00:00
32 | Cantonment | 114 | 13:00 | 98 | Manikganj | 115 | 13:00 | 164 | Sunamganj | 54 | 22:00
33 | Chandpur | 58 | 18:30 | 99 | Maniknagar | 72 | 13:00 | 165 | Sylhet | 40 | 18:00
34 | Chandraghona | 34 | 19:00 | 100 | Matarbari | 48 | 19:30 | 166 | Sylhet-132 | 110 | 18:00
35 | Chapai | 59 | 01:00 | 101 | Matuail | 54 | 09:00 | 167 | TK | 32 | 00:00
36 | Charsaidpur | 42 | 12:00 | 102 | Millgate | 124 | 12:00 | 168 | Tangail | 166 | 00:00
37 | Chauddagram | 68 | 18:30 | 103 | Mirpur | 137 | 12:00 | 169 | Thakurgaon | 100 | 19:00
38 | Chhatak | 32 | 19:00 | 104 | Mirsorai | 5 | 00:00 | 170 | Tongi | 125 | 11:00
39 | Chowmuhani | 232 | 19:30 | 105 | Mirzapur | 51 | 21:00 | 171 | Ullahpara | 24 | 18:00
40 | Chuadanga | 94 | 00:00 | 106 | Mithapukur | 54 | 18:00 | 172 | Ullon | 53 | 13:00
41 | Coxsbazar | 114 | 13:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 80 | 13:00
42 | Cumilla(N) | 150 | 21:00 | 108 | Mogbazar | 114.4 | 13:00 | 174 | UttaraNew | 50 | 13:00
43 | Cumilla(S) | 163 | 14:00 | 109 | Mongla | 42 | 23:00 | 175 | Zigatola | 99 | 13:00
44 | Daudkandi | 156 | 21:00 | 110 | Motijheel | 49 | 13:00
45 | Dhaka | 39 | 12:00 | 111 | Munshiganj | 100 | 00:00
46 | Dhamrai | 128 | 18:00 | 112 | Mymensingh | 206 | 18:30
47 | Dhanmondi | 144 | 13:00 | 113 | Naogaon | 118 | 00:00
48 | Dohazari | 99 | 19:30 | 114 | Narail | 50 | 00:00
49 | Faridpur | 140 | 00:00 | 115 | Narinda | 72 | 13:00
50 | Fatullah | 103 | 15:00 | 116 | Narshingdi | 164 | 22:00
51 | Fenchuganj | 41 | 18:00 | 117 | Natore | 120 | 00:00
52 | Feni | 92 | 19:00 | 118 | Nawabganj | 41.2 | 21:00
53 | GPH | 89 | 01:00 | 119 | Netrakona | 118 | 19:00
54 | Ghatail | 62 | 18:00 | 120 | New | 56.1 | 12:00
55 | Ghorashal | 58 | 21:00 | 121 | Niamatpur | 60 | 22:00
56 | Goalpara | 32 | 12:00 | 122 | Noapara | 37 | 00:00
57 | Gollamari | 62 | 00:00 | 123 | PHP | 9 | 10:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-10-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 386 | 22:00 | 367 | 11:00 | Kaliakoir | 375 | 19:00 | 353 | 11:00
| Ashuganj | 406 | 22:00 | 384 | 10:00 | Madunaghat | 396 | 20:00 | 384 | 11:00
| Bhulta | 398 | 21:00 | 376 | 12:00 | Meghnaghat | 383 | 22:00 | 364 | 12:00
| Bibiana | 397 | 19:00 | 384 | 10:00 | Payra | 410 | 18:00 | 401 | 12:00
| BIPTC | 407 | 16:00 | 395 | 00:00 | Rahanpur | 394 | 17:00 | 387 | 12:00
| Bogura | 381 | 17:00 | 372 | 12:00 | Rampal | 401 | 19:30 | 388 | 12:00
| Gopalganj | 397 | 17:00 | 381 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 22:00 | 216 | 10:00 | Haripur | 229 | 19:30 | 217 | 12:00
| AKSML | 236 | 18:30 | 230 | 04:00 | Hasnabad | 231 | 19:00 | 217 | 10:00
| Aminbazar | 232 | 22:00 | 211 | 11:00 | Hathazari | 239 | 18:30 | 230 | 10:00
| Ashuganj | 233 | 19:30 | 222 | 12:00 | Ishurdi | 237 | 17:00 | 228 | 12:00
| Ashuganj-400 | 234 | 22:00 | 224 | 12:00 | Jhenaidah | 231 | 18:00 | 218 | 13:00
| Baghabari | 230 | 15:00 | 223 | 10:00 | Kaliakoir | 233 | 19:00 | 217 | 11:00
| Barapukuria | 222 | 00:00 | 216 | 12:00 | Keranigonj | 231 | 22:00 | 215 | 11:00
| Barapukuria-230 | 222 | 00:00 | 216 | 12:00 | Khulna(S) | 231 | 19:30 | 218 | 12:00
| Barishal | 237 | 22:00 | 226 | 13:00 | Madunaghat | 239 | 18:00 | 230 | 12:00
| Bheramara | 236 | 17:00 | 225 | 12:00 | Maniknagar | 229 | 21:00 | 216 | 11:00
| Bhulta | 233 | 22:00 | 218 | 11:00 | Meghnaghat | 239 | 22:00 | 224 | 10:00
| Bibiana | 226 | 19:00 | 218 | 10:00 | Meghnaghat-400 | 234 | 22:00 | 219 | 01:00
| BIPTC | 236 | 16:00 | 225 | 12:00 | Mirsorai | 239 | 20:00 | 225 | 11:00
| Bogura | 231 | 16:00 | 224 | 10:00 | Rajshahi | 236 | 17:00 | 226 | 12:00
| Bogura-400 | 233 | 16:00 | 227 | 12:00 | Rampal | 230 | 19:30 | 219 | 12:00
| Borhanuddin | 239 | 17:00 | 231 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 238 | 19:00 | 225 | 10:00 | Rampura | 231 | 22:00 | 216 | 11:00
| Cumilla(N) | 230 | 20:00 | 217 | 11:00 | Shikalbaha | 238 | 21:00 | 228 | 12:00
| Faridpur | 234 | 20:00 | 225 | 10:00 | Shyampur | 232 | 22:00 | 217 | 11:00
| Fenchuganj | 226 | 08:00 | 221 | 10:00 | Siddhirganj | 229 | 03:00 | 219 | 11:00
| Ghorashal | 231 | 13:00 | 230 | 00:00 | Sirajgonj | 238 | 17:00 | 232 | 11:00
| Ghorashal-230 | 231 | 22:00 | 216 | 11:00 | Sreepur | 230 | 19:30 | 222 | 11:00
| Gopalganj | 235 | 22:00 | 225 | 11:00 | Tongi | 234 | 22:00 | 212 | 11:00
| GPH | 238 | 19:00 | 227 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 134 | 03:00 | 123 | 12:00 | Kushtia | 138 | 17:00 | 130 | 00:00
| Agargaon | 136 | 22:00 | 126 | 10:00 | Lalbag | 134 | 22:00 | 124 | 11:00
| Agrabad | 136 | 22:00 | 128 | 11:00 | Lalmonirhat | 130 | 00:00 | 122 | 18:00
| AKS | 134 | 18:30 | 126 | 11:00 | Madanganj | 128 | 18:30 | 119 | 10:00
| Aminbazar | 140 | 22:00 | 124 | 13:00 | Madaripur | 131 | 17:00 | 125 | 12:00
| Amnura | 140 | 18:00 | 125 | 21:00 | Madartek | 134 | 06:00 | 123 | 12:00
| Ashuganj | 138 | 20:00 | 134 | 11:00 | Madunaghat | 137 | 22:00 | 130 | 11:00
| Bagerhat | 132 | 18:00 | 124 | 00:00 | Magura | 138 | 17:00 | 127 | 13:00
| Bakulia | 137 | 22:00 | 128 | 11:00 | Mahasthangarh | 137 | 16:00 | 131 | 11:00
| Banani | 134 | 21:00 | 122 | 12:00 | Manikganj | 128 | 18:30 | 117 | 11:00
| Bangabhaban | 130 | 22:00 | 119 | 11:00 | Maniknagar | 130 | 22:00 | 119 | 12:00
| Barapukuria | 138 | 23:00 | 132 | 12:00 | Matarbari | 125 | 17:00 | 116 | 06:00
| Barguna | 141 | 17:00 | 131 | 04:00 | Matuail | 129 | 01:00 | 121.5 | 11:00
| Barishal | 133 | 19:00 | 124 | 11:00 | Millgate | 134 | 21:00 | 121 | 11:00
| Barishal-230 | 133 | 22:00 | 124 | 13:00 | Mirpur | 138 | 21:00 | 126 | 10:00
| Baroaulia | 137 | 22:00 | 128 | 12:00 | Mirzapur | 128 | 19:00 | 118 | 12:00
| Baroirhat | 128 | 20:00 | 114 | 13:00 | Mithapukur | 135 | 23:00 | 126 | 12:00
| Bashundhara | 135 | 22:00 | 120 | 09:00 | MI_Cement | 137 | 22:00 | 124 | 11:00
| BashundharaCement | 128 | 18:30 | 119 | 10:00 | Modern | 135 | 19:00 | 128 | 10:00
| Beanibazar | 125 | 08:00 | 120 | 18:00 | Mogbazar | 135 | 03:00 | 124 | 11:00
| Benapole | 138 | 19:00 | 123 | 13:00 | Mongla | 132 | 19:30 | 122 | 00:00
| Bhaluka | 127 | 06:00 | 120 | 12:00 | Motijheel | 130 | 22:00 | 119 | 11:00
| Bhandaria | 129 | 17:00 | 117 | 12:00 | Munshiganj | 129 | 19:00 | 120 | 10:00
| Bhangura | 138 | 17:00 | 133 | 11:00 | Mymensingh | 134 | 18:00 | 118 | 12:00
| Bheramara | 137 | 16:00 | 132 | 12:00 | Naogaon | 136 | 16:00 | 123 | 00:00
| Bheramara(GK) | 137 | 16:00 | 132 | 12:00 | Narail | 138 | 19:00 | 125 | 00:00
| Bhulta | 121 | 02:00 | 111 | 10:00 | Narinda | 130 | 22:00 | 119 | 12:00
| Bog-Sherpur | 137 | 17:00 | 129 | 11:00 | Narshingdi | 123 | 18:00 | 112 | 11:00
| Bogura | 140 | 15:00 | 129 | 18:00 | Natore | 137 | 17:00 | 131 | 11:00
| Bogura-230 | 140 | 18:00 | 134 | 10:00 | Nawabganj | 134 | 19:00 | 124 | 12:00
| Brahmanbaria | 127 | 05:00 | 120 | 12:00 | Netrakona | 135 | 18:00 | 114 | 18:30
| Cantonment | 136 | 22:00 | 125 | 11:00 | New | 134 | 20:00 | 122 | 11:00
| Chandpur | 133 | 20:00 | 117 | 14:00 | Niamatpur | 132 | 17:00 | 128 | 00:00
| Chandraghona | 137 | 20:00 | 131 | 11:00 | Noapara | 137 | 19:00 | 126 | 13:00
| Chapai | 130 | 06:00 | 126 | 21:00 | Pabna | 140 | 16:00 | 131 | 12:00
| Charsaidpur | 128 | 18:00 | 120 | 10:00 | Palashbari | 133 | 16:00 | 127 | 11:00
| Chauddagram | 130 | 19:30 | 117 | 13:00 | Panchagarh | 137 | 00:00 | 120 | 12:00
| Chhatak | 126 | 09:00 | 120 | 18:00 | Patuakhali | 140 | 17:00 | 130 | 14:00
| Chowmuhani | 125 | 21:00 | 112 | 13:00 | Payra | 138 | 17:00 | 133 | 12:00
| Chuadanga | 136 | 17:00 | 121 | 00:00 | PHP | 128 | 20:00 | 115 | 14:00
| Coxsbazar | 125 | 17:00 | 116 | 11:00 | Postogola | 137 | 21:00 | 126 | 12:00
| Cumilla(N) | 133 | 20:00 | 123 | 14:00 | Purbachal | 135 | 22:00 | 120 | 12:00
| Cumilla(S) | 132 | 20:00 | 121 | 14:00 | Purbasadipur | 134 | 23:00 | 120 | 12:00
| Daudkandi | 127 | 19:00 | 118 | 10:00 | Rahanpur | 133 | 05:00 | 131 | 10:00
| Dhaka | 135 | 22:00 | 124 | 11:00 | Rahim | 129 | 19:00 | 122 | 11:00
| Dhamrai | 132 | 22:00 | 121 | 11:00 | Rajbari | 130 | 17:00 | 123 | 12:00
| Dhanmondi | 135.8 | 22:00 | 123 | 12:00 | Rajendrapur | 130 | 19:30 | 115 | 11:00
| Dohazari | 132 | 18:00 | 124 | 13:00 | Rajshahi | 136 | 17:00 | 130 | 12:00
| Faridpur | 131 | 17:00 | 126 | 11:00 | Rajshahi-230 | 137 | 19:00 | 122 | 12:00
| Fatullah | 135 | 20:00 | 125 | 11:00 | Ramganj | 126 | 20:00 | 113 | 13:00
| Fenchuganj | 132 | 08:00 | 129 | 12:00 | Rampur | 136 | 04:00 | 128 | 11:00
| Feni | 130 | 19:30 | 117 | 13:00 | Rampura | 135 | 22:00 | 123 | 12:00
| Ghatail | 128 | 08:00 | 122 | 01:00 | Rangamati | 136 | 20:00 | 130 | 10:00
| Ghorashal | 139 | 20:00 | 129 | 10:00 | Rangpur | 133 | 23:00 | 125 | 08:00
| Goalpara | 138 | 19:00 | 128 | 12:00 | Ruppur | 138 | 15:00 | 133 | 00:00
| Gollamari | 137 | 19:00 | 128 | 12:00 | Saidpur | 133 | 00:00 | 122 | 12:00
| Gopalganj | 134 | 19:00 | 125 | 12:00 | Satkhira | 137 | 20:00 | 124 | 12:00
| Gopalganj-400 | 132 | 17:00 | 126 | 11:00 | Satmasjid | 136 | 22:00 | 125 | 11:00
| Gulshan | 134 | 21:00 | 123 | 11:00 | Savar | 138 | 20:00 | 125 | 09:00
| Halishahar | 136 | 19:00 | 128 | 11:00 | SevenRings | 138 | 20:00 | 129 | 12:00
| Haripur | 129 | 19:00 | 119 | 07:00 | ShahCement | 128 | 18:00 | 120 | 10:00
| HaripurSBU | 129 | 19:00 | 122 | 11:00 | Shahjadpur | 141 | 15:00 | 136 | 12:00
| Hasnabad | 137 | 21:00 | 126 | 12:00 | Shahjibazar | 127 | 07:00 | 123 | 13:00
| Hathazari | 139 | 18:30 | 132 | 10:00 | Shahmirpur | 136 | 17:00 | 128 | 11:00
| Ishurdi | 139 | 16:00 | 135 | 00:00 | Shariatpur | 133 | 17:00 | 124 | 11:00
| Jaldhaka | 132 | 23:00 | 121 | 12:00 | Sherpur | 138 | 18:00 | 125 | 16:00
| Jamalpur | 140 | 18:00 | 120 | 16:00 | Shikalbaha | 125 | 17:00 | 117 | 11:00
| Jashore | 138 | 19:00 | 125 | 12:00 | Shikalbaha-230 | 138 | 22:00 | 129 | 12:00
| Jhenaidah | 138 | 17:00 | 129 | 00:00 | Shitalakhya | 137 | 22:00 | 124 | 11:00
| Jhenaidah-230 | 138 | 17:00 | 129 | 00:00 | Sholosohor | 136 | 19:30 | 128 | 10:00
| Joydebpur | 136 | 20:00 | 122 | 12:00 | Shyampur | 134 | 20:00 | 125 | 02:00
| Joypurhat | 126 | 06:00 | 121 | 21:00 | Shyampur-230 | 135 | 21:00 | 125 | 10:00
| Juldah | 136 | 19:00 | 129 | 10:00 | Siddhirganj | 129 | 19:00 | 121 | 11:00
| Kabirpur | 131 | 20:00 | 119 | 11:00 | Sirajganj | 135 | 01:00 | 128 | 12:00
| Kachua | 132 | 19:00 | 119 | 00:00 | Sonargaon | 128 | 03:00 | 117 | 11:00
| Kaliakoir | 134 | 17:00 | 123 | 09:00 | Sreemongol | 128 | 08:00 | 123 | 12:00
| Kallyanpur | 130 | 19:30 | 123 | 12:00 | Sreepur | 130 | 07:00 | 125 | 12:00
| Kalurghat | 138 | 22:00 | 129 | 11:00 | Srinagar | 133 | 19:00 | 125 | 10:00
| Kamrangirchar | 134 | 20:00 | 122 | 12:00 | SSM | 140 | 17:00 | 129 | 12:00
| Kaptai | 132 | 6:00 | 126 | 19:00 | Sunamganj | 124 | 07:00 | 118 | 18:00
| Kazla | 129 | 22:00 | 119 | 11:00 | Sylhet | 127 | 07:00 | 123 | 00:00
| Keranigonj | 134 | 20:00 | 125 | 10:00 | Sylhet-132 | 127 | 07:00 | 124 | 12:00
| Khagrachori | 135 | 20:00 | 128 | 11:00 | Tangail | 126 | 19:30 | 119 | 16:00
| Khulna | 137 | 19:00 | 128 | 12:00 | Thakurgaon | 137 | 00:00 | 118 | 12:00
| Khulna(S) | 138 | 19:30 | 129 | 12:00 | TK | 137 | 21:00 | 130 | 12:00
| Khulshi | 135 | 19:30 | 126 | 12:00 | Tongi | 135 | 21:00 | 125 | 11:00
| Kishoreganj | 130 | 06:00 | 124 | 12:00 | Ullahpara | 136 | 16:00 | 124 | 03:00
| Kodda | 135 | 20:00 | 118 | 09:00 | Ullon | 135 | 22:00 | 123 | 11:00
| KSRM | 138 | 18:30 | 129 | 12:00 | Uttara | 139 | 22:00 | 127 | 10:00
| Kulaura | 131 | 05:00 | 128 | 00:00 | UttaraNew | 138 | 20:00 | 126 | 10:00
| Kurigram | 130 | 23:00 | 121 | 18:00 | Zigatola | 134 | 22:00 | 124 | 12:00

## L-Curve
Date | 2024-10-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1206 | 6933 | 5643 | 12576 |  |  |  | QF-LDC-11
0:30 | 1114 | 6901 | 5727.5 | 12628.5 | Date: | 2024-10-09
1:00 | 1022 | 6869 | 5812 | 12681
1:30 | 1001 | 6715.5 | 5694.5 | 12410
2:00 | 980 | 6562 | 5577 | 12139
2:30 | 976 | 6491.5 | 5521.5 | 12013 | [5 empty] | Gen. at Eve. Peak | 13510 | 13510 MW (19:00 )
3:00 | 972 | 6421 | 5466 | 11887 | [6 empty] | 19:00
3:30 | 1001 | 6287 | 5431 | 11718 | [5 empty] | Gen. at Day Peak | 12644 | 12644 MW (12:00 )
4:00 | 1030 | 6153 | 5396 | 11549 | [6 empty] | 12:00
4:30 | 1067 | 6111.5 | 5370 | 11481.5 | [5 empty] | Highest Generation | 13510
5:00 | 1104 | 6070 | 5344 | 11414 | [6 empty] | 19:00
5:30 | 1148 | 5977.5 | 5231 | 11208.5
6:00 | 1192 | 5885 | 5118 | 11003
6:30 | 1191 | 5957 | 5057.5 | 11014.5
7:00 | 1190 | 6029 | 4997 | 11026
7:30 | 1257 | 5992.5 | 5048 | 11040.5
8:00 | 1324 | 5956 | 5099 | 11055
8:30 | 1432 | 5989.5 | 5270 | 11259.5
9:00 | 1540 | 6023 | 5441 | 11464
9:30 | 1522 | 6153 | 5504 | 11657
10:00 | 1504 | 6283 | 5567 | 11850
10:30 | 1465 | 6513.5 | 5579 | 12092.5
11:00 | 1426 | 6744 | 5591 | 12335
11:30 | 1385 | 6821.5 | 5668 | 12489.5
12:00 | 1344 | 6899 | 5745 | 12644
12:30 | 1274 | 7029.5 | 5745.5 | 12775
13:00 | 1204 | 7160 | 5746 | 12906
13:30 | 1289 | 7099 | 5611 | 12710
14:00 | 1374 | 7038 | 5476 | 12514
14:30 | 1384 | 7016 | 5370.5 | 12386.5
15:00 | 1394 | 6994 | 5265 | 12259
15:30 | 1378 | 6801 | 5207 | 12008
16:00 | 1362 | 6608 | 5149 | 11757
16:30 | 1366 | 6664.5 | 5027 | 11691.5
17:00 | 1370 | 6721 | 4905 | 11626
17:30 | 1292 | 6962 | 5192.5 | 12154.5
18:00 | 1214 | 7203 | 5480 | 12683
18:30 | 1074 | 7431 | 5665.5 | 13096.5
19:00 | 934 | 7659 | 5851 | 13510
19:30 | 942 | 7557 | 5692 | 13249
20:00 | 830 | 7487 | 5709 | 13196 |  |  |  | Executive Engineer
20:30 | 910 | 7474 | 5712.5 | 13186.5 |  |  |  | Network Operation Division
21:00 | 990 | 7461 | 5716 | 13177
21:30 | 1025 | 7418 | 5727 | 13145
22:00 | 1060 | 7375 | 5738 | 13113 |  |  |  |  | Page 6 of 7
22:30 | 1105 | 7310 | 5700.5 | 13010.5
23:00 | 1150 | 7245 | 5663 | 12908
23:30 | 1178 | 7089 | 5653 | 12742
24:00 | 1206 | 6933 | 5643 | 12576
13510 MW (19:00 )
12644 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-10-09 |  | Energy |  | 299119363
[15 empty] | Date: | 2024-10-09 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3272 | 473 | 1824 | 0 | 1929 | 3087 | 170 | 0 | 619 | 74 | 1128 | 0 | 0 | 118
0:30 | 3389 | 689 | 1742.5 | 0 | 1740 | 3225 | 170 | 0 | 524.5 | 68 | 1080.5 | 0 | 0 | 211.3225 |  |  | Date: | 44112
1:00 | 3506 | 905 | 1661 | 0 | 1551 | 3363 | 170 | 0 | 430 | 62 | 1033 | 0 | 0 | 304.645
1:30 | 3492.5 | 905.5 | 1674 | 0 | 1366 | 3362.5 | 169 | 0 | 344 | 63 | 1033.5 | 0 | 0 | 300.825 | [8 empty] | Total Energy | 299.1194 | 299.1194 | Total Energy Gen 299.119 MKWHr Energy Not Served 2.721 MKWHr Energy Requirement 301.840 MKWHr
2:00 | 3479 | 906 | 1687 | 0 | 1181 | 3362 | 168 | 0 | 258 | 64 | 1034 | 0 | 0 | 297.005 | [8 empty] | Energy not Served | 2.7206 | 2.7206
2:30 | 3487.5 | 905 | 1677 | 0 | 1082 | 3364.5 | 167.5 | 0 | 233.5 | 62 | 1034 | 0 | 0 | 297.96 | [8 empty] | Energy Requirement | 301.84 | 301.84
3:00 | 3496 | 904 | 1667 | 0 | 983 | 3367 | 167 | 0 | 209 | 60 | 1034 | 0 | 0 | 298.915
3:30 | 3510 | 904.5 | 1662 | 0 | 838 | 3365.5 | 167.5 | 0 | 175 | 62 | 1033.5 | 0 | 0 | 269.31 | [7 empty] | Shortage
4:00 | 3524 | 905 | 1657 | 0 | 693 | 3364 | 168 | 0 | 141 | 64 | 1033 | 0 | 0 | 239.705
4:30 | 3519 | 905 | 1682.5 | 0 | 619.5 | 3365 | 168 | 0 | 125 | 63 | 1034.5 | 0 | 0 | 256.4175
5:00 | 3514 | 905 | 1708 | 0 | 546 | 3366 | 168 | 0 | 109 | 62 | 1036 | 0 | 0 | 273.13
5:30 | 3520 | 905.5 | 1684.5 | 0 | 468.5 | 3299.5 | 168 | 0 | 70.5 | 58 | 1033.5 | 0.5 | 0 | 230.6325
6:00 | 3526 | 906 | 1661 | 0 | 391 | 3233 | 168 | 0 | 32 | 54 | 1031 | 1 | 0 | 188.135
6:30 | 3558 | 905.5 | 1735.5 | 0 | 402 | 3082 | 168 | 0 | 32 | 56 | 1033.5 | 42 | 0 | 191.4775 | [6 empty] | Coal
7:00 | 3590 | 905 | 1810 | 0 | 413 | 2931 | 168 | 0 | 32 | 58 | 1036 | 83 | 0 | 194.82
7:30 | 3546 | 905 | 1766.5 | 0 | 441.5 | 2945.5 | 168 | 0 | 40 | 57 | 1035 | 136 | 0 | 142.7725 | [5 empty] | Oil
8:00 | 3502 | 905 | 1723 | 0 | 470 | 2960 | 168 | 0 | 48 | 56 | 1034 | 189 | 0 | 90.725
8:30 | 3466.5 | 905 | 1722.5 | 0 | 531 | 3083 | 168.5 | 0 | 48 | 55 | 1034 | 246 | 0 | 110.3025
9:00 | 3431 | 905 | 1722 | 0 | 592 | 3206 | 169 | 0 | 48 | 54 | 1034 | 303 | 0 | 129.88
9:30 | 3398 | 905 | 1788 | 0 | 656.5 | 3252.5 | 169.5 | 0 | 48 | 53 | 1034 | 351.5 | 1 | 103.14
10:00 | 3365 | 905 | 1854 | 0 | 721 | 3299 | 170 | 0 | 48 | 52 | 1034 | 400 | 2 | 76.4
10:30 | 3352.5 | 905 | 2000 | 0 | 778.5 | 3299 | 170 | 0 | 56 | 60 | 1032.5 | 437 | 2 | 69.2375
11:00 | 3340 | 905 | 2146 | 0 | 836 | 3299 | 170 | 0 | 64 | 68 | 1031 | 474 | 2 | 62.075
11:30 | 3322 | 904.5 | 2184.5 | 0 | 927.5 | 3306 | 170 | 0 | 92 | 68 | 1031.5 | 482.5 | 1 | 48.2275
12:00 | 3304 | 904 | 2223 | 0 | 1019 | 3313 | 170 | 0 | 120 | 68 | 1032 | 491 | 0 | 34.38
12:30 | 3294 | 904.5 | 2261.5 | 0 | 1123.5 | 3321.5 | 170 | 0 | 131 | 74 | 1031 | 464 | 0 | 39.155
13:00 | 3284 | 905 | 2300 | 0 | 1228 | 3330 | 170 | 0 | 142 | 80 | 1030 | 437 | 0 | 43.93
13:30 | 3284 | 905 | 2300 | 0 | 1228 | 3330 | 170 | 0 | 142 | 80 | 1030 | 437 | 0 | 43.93
14:00 | 3284 | 905 | 2300 | 0 | 1228 | 3330 | 170 | 0 | 142 | 80 | 1030 | 437 | 0 | 43.93
14:30 | 3239.5 | 690.5 | 2159 | 0 | 1433 | 3330.5 | 170 | 0 | 147.5 | 76 | 1030.5 | 304.5 | 1.5 | 65.4175
15:00 | 3195 | 476 | 2018 | 0 | 1638 | 3331 | 170 | 0 | 153 | 72 | 1031 | 172 | 3 | 86.905
15:30 | 3136.5 | 476 | 1889 | 0 | 1691.5 | 3229.5 | 170 | 0 | 175.5 | 66 | 1033 | 137 | 4 | 63.985
16:00 | 3078 | 476 | 1760 | 0 | 1745 | 3128 | 170 | 0 | 198 | 60 | 1035 | 102 | 5 | 41.065
16:30 | 3040 | 476 | 1718.5 | 0 | 1854 | 3016 | 169.5 | 0 | 260.5 | 60 | 1032 | 62 | 3 | 55.8675
17:00 | 3002 | 476 | 1677 | 0 | 1963 | 2904 | 169 | 0 | 323 | 60 | 1029 | 22 | 1 | 70.67
17:30 | 3053 | 476 | 1774.5 | 0 | 2205 | 2896 | 168.5 | 0 | 478 | 61 | 1031 | 11 | 0.5 | 81.6525
18:00 | 3104 | 476 | 1872 | 0 | 2447 | 2888 | 168 | 0 | 633 | 62 | 1033 | 0 | 0 | 92.635
18:30 | 3092.5 | 476 | 1854 | 0 | 2697 | 2933 | 167.5 | 0 | 737 | 60 | 1079.5 | 0 | 0 | 46.3175
19:00 | 3081 | 476 | 1836 | 0 | 2947 | 2978 | 167 | 0 | 841 | 58 | 1126 | 0 | 0 | 0
19:30 | 3075 | 476 | 1857 | 0 | 2794 | 2853 | 167 | 0 | 832 | 62 | 1133 | 0 | 0 | 0
20:00 | 3061 | 475 | 1836 | 0 | 2752 | 2934 | 168 | 0 | 784 | 60 | 1126 | 0 | 0 | 0
20:30 | 3079 | 475.5 | 1824.5 | 0 | 2706.5 | 2965.5 | 168.5 | 0 | 775.5 | 62 | 1129.5 | 0 | 0 | 0
21:00 | 3097 | 476 | 1813 | 0 | 2661 | 2997 | 169 | 0 | 767 | 64 | 1133 | 0 | 0 | 0
21:30 | 3089 | 474.5 | 1817 | 0 | 2626 | 3005.5 | 169.5 | 0 | 767 | 64 | 1132.5 | 0 | 0 | 0
22:00 | 3081 | 473 | 1821 | 0 | 2591 | 3014 | 170 | 0 | 767 | 64 | 1132 | 0 | 0 | 0
22:30 | 3178.5 | 473 | 1819.5 | 0 | 2431.5 | 3011 | 170 | 0 | 726.5 | 65 | 1135.5 | 0 | 0 | 44
23:00 | 3276 | 473 | 1818 | 0 | 2272 | 3008 | 170 | 0 | 686 | 66 | 1139 | 0 | 0 | 88
23:30 | 3274 | 473 | 1821 | 0 | 2100.5 | 3047.5 | 170 | 0 | 652.5 | 70 | 1133.5 | 0 | 0 | 103 |  |  | Max Temp. in Dhaka |  | 33°C
24:00 | 3272 | 473 | 1824 | 0 | 1929 | 3087 | 170 | 0 | 619 | 74 | 1128 | 0 | 0 | 118
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 299.119 MKWHr Energy Not Served 2.721 MKWHr Energy Requirement 301.840 MKWHr
Note on X13: Author:

## Generation
2024-10-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 88 | 87 | 88 | 88 | 88 | 88 | 88 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 88 |  | 87 | 87 | 88 | 89 | 90 | 90 | 90 | 2144029
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1928000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 0 | [8 empty] | 5 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 306943
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 11 | 16 | 19 | 19 | 19 | 19 | 17 | 14 | 8 | 1 | [9 empty] | 136755
6 | Sikalbaha 225MW CCPP (Gas) | 225 | 225 | 226 | 226 | 225 | 225 | 225 | 224 | 222 | 221 | 219 | 220 | 225 | 220 | 148 | 149 | 70 | 75 |  | 95 | 105 | 106 | 105 | 105 | 226 | 225 | 4357116
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 0 | [11 empty] | 36 | 85 | 85 |  | 85 | 83 | 83 | 83 | 83 | 83 | 84 | 850854
12 | Hathazari 100 MW peaking PP | 64 | 64 | 64 | 64 | 32 | 0 | [5 empty] | 10 | 24 | 24 | 25 | 35 | 39 | 49 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 911136
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 0 | [8 empty] | 5 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 267636
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 45 | 45 | 45 | 45 | 45 | 0 | [5 empty] | 9 | 21 | 40 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 44 | 45 | 45 | 45 | 717760
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 79 | 40 | 39 | 38 | 38 | 38 | 39 | 39 | 39 | [17 empty] | 492000
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 334 | 335 | 335 | 280 | 335 | 280 | 280 | 335 |  | 300 | 280 | 280 | 280 | 280 | 280 | 280 | 7669040
18 | Kodda 300 MW PP Unit-2 (Summit) | 255 | 145 | 45 | 0 | [7 empty] | 10 | 65 | 145 | 190 | 252 | 275 | 285 |  | 297 | 245 | 245 | 245 | 245 | 245 | 245 | 3379745
19 | Ashuganj 195 MW PP (APSCL-United) | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 81 | 87 | 68 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 1187636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 612 | 612 | 612 | 612 | 600 | 550 | 550 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 560 | 550 | 600 |  | 590 | 550 | 550 | 550 | 550 | 550 | 600 | 14154544
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 42 | 42 | 42 | 39 | 39 | 39 | 38 | 34 | 31 | 29 | 33 | 37 | 37 | 39 | 42 | 42 |  | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 949968
33 | Ashuganj 225 MW CCPP | 194 | 194 | 194 | 194 | 194 | 194 | 198 | 194 | 194 | 215 | 214 | 214 | 216 | 213 | 214 | 217 | 213 | 213 |  | 219 | 217 | 215 | 216 | 219 | 219 | 217 | 5049000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 315 | 315 | 315 | 315 | 315 | 315 | 345 | 320 | 280 | 285 | 300 | 295 | 310 | 335 | 310 | 280 | 300 | 315 |  | 285 | 285 | 285 | 300 | 285 | 310 | 315 | 7772000
| Ashuganj 420 MW CCPP(East) | 320 | 320 | 320 | 325 | 325 | 335 | 365 | 335 | 305 | 300 | 300 | 295 | 295 | 325 | 320 | 320 | 330 | 320 |  | 285 | 285 | 285 | 290 | 285 | 325 | 320 | 7716400
35 | Ashuganj 55 MW PP (Precision) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 364800
36 | Chandpur 150 MW CCPP | 70 | 51 | 50 | 71 | 71 | 71 | 71 | 50 | 50 | 50 | 50 | 50 | 70 | 50 | 50 | 50 | 70 | 50 |  | 50 | 50 | 50 | 70 | 70 | 50 | 50 | 1418860
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 380 | 400 | 414 | 416 | 414 | 412 | 405 | 406 | 399 | 397 | 407 | 406 | 408 | 370 | 401 | 411 | 362 | 409 |  | 382 | 371 | 372 | 371 | 371 | 371 | 371 | 9568800
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 70 | 70 | 70 | 70 | 70 | 90 | 120 | 120 | 150 | 290 | 480 | 510 | 595 | 450 | 340 | 210 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 5514091
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 430 | 430 | 380 | 380 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10442000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 18 | 18 | 18 | 16 | 11 | 11 | 11 | 8 | 6 | 4 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100800
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 6 | 9 | 34 | 27 | 20 | 35 | 38 | 4 | 4 | 0 | [9 empty] | 204160
44 | Fenchugonj CCPP Phase-1 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 20 | 20 | 0 | 0 | [11 empty] | 365000
45 | Fenchugonj CCPP Phase-2 | [11 empty] | 0 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 312808
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 57 | 56 | 57 | 56 | 59 | 59 | 59 | 59 | 57 | 55 | 55 | 51 | 50 | 56 | 56 | 56 | 55 |  | 57 | 56 | 56 | 56 | 57 | 57 | 57 | 1296864
48 | Shahjibazar 86 MW PP (Shahjibazar) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 30 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 459840
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 138 | 138 | 138 | 136 | 134 | 132 | 132 | 132 | 134 |  | 135 | 135 | 135 | 135 | 135 | 136 | 136 | 3272550
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 171552
55 | Fenchugonj 51 MW PP (Barakatullah) | [13 empty] | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 54000
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 282624
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 295 | 290 | 280 | 295 | 280 | 315 | 305 | 310 | 310 | 300 | 300 | 305 | 300 | 315 | 275 | 295 | 295 |  | 295 | 310 | 285 | 295 | 300 | 295 | 300 | 7294500
| Bibiyana South 400 MW | 400 | 393 | 400 | 400 | 396 | 400 | 391 | 391 | 396 | 390 | 390 | 381 | 392 | 380 | 392 | 380 | 380 | 385 |  | 392 | 387 | 390 | 386 | 392 | 396 | 396 | 9389000
58 | Nababganj 55 MW PP (Southern power ) | 35 | 0 | [9 empty] | 17 | 17 | 17 | 35 | 55 | 55 | 55 |  | 55 | 35 | 35 | 35 |  |  |  | 445144
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 7 | 18 |  | 18 | 18 | 18 | 18 | 18 | 14 | 18 | 133680
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 62 | 64 | 60 | 64 | 62 | 54 | 58 | 56 | 54 | 52 | 68 | 68 | 80 | 88 | 72 | 60 | 60 | 62 |  | 58 | 62 | 60 | 64 | 64 | 66 | 74 | 1503360
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 37 | 37 | 37 | 38 | 35 | 9 | 2 | 2 | 3 | 3 | 9 | 7 | 2 | 2 | 6 | 13 |  | 13 | 19 | 24 | 29 | 33 | 35 | 36 | 489120
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 6 |  | 0 | 16 | 18 | 18 | 18 | 18 | 18 | 404610
69 | Summit Ashulia | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 13 | 13 | 0 | 13 | 13 | 328200
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 461160
71 | Maona 33 MW PP(Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  |  | 17 |  | 17 | 17 | 0 | 25 | 25 | 25 | 25 | 529600
72 | Rupganj 33 MW PP(Summit) | 16 | 16 | 16 | 17 | 20 | 20 | 15 | 15 | 12 | 11 | 7 | 12 | 4 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 11 | 11 | 12 | 12 | 301100
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 40 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 1020300
| Chowmuhani 113 MW | 28 | 29 | 29 | 29 | 29 | 29 | 28 | 29 | 29 | 29 | 24 | 28 | 28 | 29 | 36 | 36 | 37 | 73 |  | 76 | 76 | 74 | 73 | 78 | 78 | 39 | 1007160
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 0 |  |  | 17 | 17 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 162 |  | 162 | 162 | 162 | 108 | 108 | 35 | 35 | 1357920
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 |  | 25 | 25 | 25 | 25 | 25 | 16 | 8 | 307680
79 | Kodda 150 MW PP | 64 | 48 | 32 | 32 | 32 | 32 | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 64 | 64 | 48 | 48 | 100 |  | 150 | 150 | 150 | 150 | 150 | 150 | 82 | 1706400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 52 | 52 | 52 | 52 | 52 | 26 | 8 | 400171
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 70 |  | 105 | 105 | 105 | 105 | 105 | 88 | 35 | 1200960
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 4 | 4 | 5 | 4 | 2 | 3 | 1 | 0 | [9 empty] | 27840
| Jodiac Power | [7 empty] | 9 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 576589
| Karnaphuli Power Ltd. | 92 | 92 | 92 | 51 | 0 | [9 empty] | 17 | 72 | 89 | 102 |  | 110 | 72 | 68 | 68 | 68 | 68 | 68 | 1176758
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 6 | 0 | [12 empty] | 7 | 13 | 13 | 13 |  | 13 | [6 empty] | 56000
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 10 | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 321600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | [13 empty] | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 84888
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1091148
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 0 |  |  | 3 | 8 | 8 | 8 | 8 | 8 | 10 | 8 | 8 | 22 |  | 57 | 49 | 49 | 49 | 49 | 8 | 8 | 349776
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 0 | [10 empty] | 1 | 17 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 243360
96 | Chattogram 108 MW PP (ECPV) | 24 | 19 | 19 | 15 | 0 | [9 empty] | 8 | 31 | 38 | 44 |  | 42 | 44 | 38 | 41 | 44 | 44 | 44 | 455040
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 50 | 0 | [9 empty] | 26 | 55 | 55 | 55 | 30 | 30 | 38 |  | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 588915
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 2 | 35 | 55 | 55 | 55 | 55 | 35 |  | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 447698
101 | Kushiara 163 MW CCPP (KP) | 140 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 120 | 120 | 163 | 163 | 163 | 120 | 163 | 130 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3639436
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 6850
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 54 | 54 |  | 54 | 54 | 35 | 35 | 35 |  |  | 414720
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 97 | 97 | 97 | 97 | 97 | 125 | 135 | 135 | 134 | 134 | 135 | 134 | 134 | 123 |  | 85 | 140 |  | 150 | 160 | 162 | 153 | 153 | 153 | 153 | 2940000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 56 | 34 | 34 | 34 | 34 | 34 | 34 | 65 | 78 | 80 | 85 | 112 | 131 | 132 | 131 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 120 | 41 | 2153376
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 300480
116 | Chandpur 200 MW (Desh energy) | 69 | 54 | 51 | 48 | 51 | 51 | 51 | 51 | 52 | 57 | 86 | 86 | 78 | 51 | 51 | 51 | 54 | 79 |  | 144 | 145 | 145 | 145 | 145 | 145 | 89 | 1907040
117 | Ashuganj 150 MW PP (Midland) | 85 | 85 | 85 | 6 | 0 | [6 empty] | 15 | 47 | 57 | 60 | 60 | 65 | 75 |  | 85 | 98 | 98 | 100 | 98 | 100 | 93 | 1257890
118 | Bibiyana-III 400 MW CCPP | 324 | 341 | 341 | 341 | 341 | 341 | 359 | 359 | 373 | 374 | 360 | 360 | 306 | 307 | 308 | 305 | 309 | 308 |  | 377 | 385 | 385 | 354 | 354 | 353 | 352 | 8580000
| Jamalpur 115 MW PP (United) | 58 | 58 | 58 | 58 | 58 | 58 | 68 | 68 | 67 | 67 | 65 | 57 | 67 | 67 | 67 |  | 54 | 74 |  | 92 | 93 | 93 | 93 | 95 | 95 | 96 | 1624800
| Anwara 300 MW PP (United) | 51 | 49 | 49 | 52 | 52 | 0 |  |  | 15 | 85 | 100 | 105 | 88 | 88 | 52 | 52 | 51 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1234473
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 0 |  |  |  |  | 12 | 12 | 15 | 17 | 17 | 18 | 19 | 21 |  | 21 | 22 | 10 | 10 | 10 |  | 10 | 263040
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 0 |  |  | 4 | 17 | 17 | 30 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 590891
| Bhairob 54.5 MW | 35 | 35 | 19 | 17 | 0 |  |  |  |  | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 459000
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 6 | 21 | 27 | 23 | 28 | 7 | 2 | 8 | 1 | [10 empty] | 122228
| Chandpur 115(Doreen) | 39 | 40 | 40 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 35 | 50 | 51 | 51 | 51 |  | 68 | 92 | 91 | 92 | 67 | 51 | 40 | 1118400
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 12 | 33 |  | 22 | 35 | 35 | 35 | 30 |  | 36 | 35 | 35 | 35 | 35 | 35 | 17 | 614160
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 0 | [7 empty] | 36 | 36 | 36 | 17 | 17 | 17 | 54 |  | 160 | 160 | 108 | 90 | 90 | 17 | 17 | 751055
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 4 | 3 | 5 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18729
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 18 | 37 | 28 | 30 | 66 | 18 | 48 | 44 | 15 | 4 | 2 | [9 empty] | 352109
| Matarbari 2*600 MW (CPGCL) | 403 | 404 | 405 | 404 | 408 | 407 | 381 | 377 | 376 | 376 | 374 | 374 | 368 | 376 | 373 | 372 | 310 | 168 |  | 148 | 158 | 216 | 214 | 211 | 211 | 216 | 8094545
| Meghnaghat (Reliance) 718MW CCPP | 15 | 16 | 0 | 0 | 36 | 36 | 50 | [15 empty] | 1 |  |  | 0 | 197100
| Sreepur 150 MW | [10 empty] | 16 | 17 | 13 |  |  |  | 4 | 7 | [8 empty] | 43200
120
121 | Eastern Zone Total | 6869 | 6562 | 6421 | 6153 | 6070 | 5885 | 6029 | 5956 | 6023 | 6283 | 6744 | 6899 | 7160 | 7038 | 6994 | 6608 | 6721 | 7203 |  | 7659 | 7557 | 7487 | 7461 | 7375 | 7245 | 6933 | 164202510
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | 21 | 0 | [14 empty] | 6 | 32 |  | 42 | 38 | 38 | 38 | 38 | 31 | 31 | 240960
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | 18 | 18 | 18 | 18 | 0 | [12 empty] | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 |  | 182400
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 15 | 40 | 61 | 76 | 90 | 92 | 88 | 71 | 28 | 29 | 7 | [9 empty] | 586080
132 | Rampal 1320 MW (BIFPCL) | 508 | 507 | 510 | 508 | 507 | 510 | 510 | 508 | 514 | 510 | 512 | 512 | 512 | 509 | 513 | 514 | 512 | 510 |  | 510 | 512 | 525 | 610 | 610 | 609 | 506 | 12654550
133 | United Payra Power Ltd. | 17 | 17 | 17 | 0 | [10 empty] | 23 | 137 | 137 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1453200
| Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 180 | 220 |  | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 5026500
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 32 | 16 | 0 | [10 empty] | 16 | 48 | 64 | 80 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 993504
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 307 | 307 | 267 | 200 | 200 | 250 | 307 | 307 | 307 | 307 | 307 | 307 | 280 | 250 | 307 |  | 307 | 250 | 250 | 250 | 250 | 250 | 307 | 6786000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2901
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 66 | 64 | 64 | 64 | 67 | 67 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1593000
141 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 6 | 6 | 6 | 6 | 7 | 7 | 8 | 7 | 6 | 6 | 10 |  | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 198859
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP | 43 | 0 | [14 empty] | 3 | 63 |  | 57 | 57 | 58 | 58 | 56 | 55 | 55 | 398336
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
147 | Bheramara HVDC | 905 | 906 | 904 | 905 | 905 | 906 | 905 | 905 | 905 | 905 | 905 | 904 | 905 | 729 | 476 | 476 | 476 | 476 |  | 476 | 476 | 475 | 476 | 473 | 473 | 473 | 17457454
148 | Bheramara 410 MW CCPP | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 197 | 193 | 178 | 163 | 151 | 137 | 122 | 120 | 111 | 107 | 107 |  | 107 | 107 | 106 | 112 | 116 | 124 | 124 | 3900960
149 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1160 | 1000 | 1030 | 1160 | 1200 | 1200 | 1220 | 1244 | 1244 | 1244 | 1120 | 1000 | 1020 |  | 1140 | 1100 | 1110 | 1090 | 1110 | 1100 | 1170 | 29934100
150
151 | Barapukuria TPP Unit-1 | 64 | 63 | 64 | 64 | 63 | 64 | 65 | 65 | 64 | 64 | 64 | 63 | 62 | 62 | 62 | 62 | 62 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 1495418
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 230 | 230 | 230 | 230 | 225 | 225 | 225 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 225 | 225 | 5397000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 38 | 0 | [14 empty] | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 351914
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 3 | 2 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 17460
157 | Sirajganj 68 MW Solar Park | [6 empty] | 4 | 8 | 24 | 36 | 60 | 46 | 7 | 8 | 1 | 0 | [10 empty] | 195000
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 194 | 195 | 194 | 195 | 195 | 195 | 197 | 196 | 196 | 185 | 177 | 177 | 178 | 178 | 174 | 172 | 172 | 172 |  | 173 | 172 | 172 | 172 | 175 | 177 | 177 | 4428545
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 320 | 350 | 350 | 350 | 350 | 300 | 350 | 350 | 414 | 414 | 414 | 414 | 414 | 350 | 414 | 360 | 320 | 414 |  | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 9039418
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | 24 | 0 | [12 empty] | 4 | 4 | 5 | 12 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 189327
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 98892
166 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | 35 | 5 | 0 | [13 empty] | 12 | 28 |  | 47 | 44 | 47 | 46 | 46 | 46 | 46 | 335960
169 | Santahar 50 MW Peaking PP | 28 | 28 | 0 | [12 empty] | 15 | 22 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 265000
170 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
171 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 93 |  | 95 | 95 | 95 | 96 | 97 | 97 | 97 | 679088
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | 113 | 35 | 0 | [9 empty] | 15 | 38 | 108 | 70 | 50 | 64 |  | 113 | 50 | 50 | 50 | 50 | 50 | 35 | 977760
173 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 0 | [6 empty] | 30 | 55 | 55 | 55 | 55 | 55 | 113 |  | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 1104672
175 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 85 | 49 | 49 | 0 | [5 empty] | 15 | 46 | 48 | 48 | 56 | 55 | 104 |  | 106 | 106 | 106 | 113 | 113 | 113 | 113 | 1443110
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 4 | 4 | 4 | 4 | 6 | 5 | 3 | 1 | 0 | [9 empty] | 29117
| Energypac Power Venture Thakurgaon Ltd. | [14 empty] | 30 | 35 | 35 | 35 |  | 115 | 115 | 115 | 75 | 75 | 75 | 75 | 660672
| Intraco Solar 30 MW | [6 empty] | 3 | 9 | 13 | 17 | 24 | 28 | 19 | 19 | 13 | 8 | 2 | [9 empty] | 158587
178 | Adani Power Jharkhanda Ltd | 1033 | 1034 | 1034 | 1033 | 1036 | 1031 | 1036 | 1034 | 1034 | 1034 | 1031 | 1032 | 1030 | 1034 | 1031 | 1035 | 1029 | 1033 |  | 1126 | 1133 | 1126 | 1133 | 1132 | 1139 | 1128 | 25390909
| Teesta Solar Limited | [6 empty] | 13 | 27 | 56 | 62 | 72 | 121 | 104 | 100 | 82 | 46 | 10 | [9 empty] | 683280