## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-10-12 | Saturday
|  | Date (day): | 2024-10-12 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13629.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15227 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-10-11 | 2024-10-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 401 | 411 | 400 | 412
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 13 | 13 | 62 |  | Fuel shortage
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 50 | 8 | 50 | 52 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 21 | 54 | 54 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 64 | 48 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 55 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 55 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 36 | 36 | 36 |  | 44 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 24 | 24 | 24 |  | 9 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 19 | 21 | 21 |  | 12 | Engine problem
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 17 | 17 | 17 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 17 | 45 | 145 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 66 | 114 | 132 | 132 | 17 |  | Fuel shortage
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 34 | 52 | 100 |  | 5 | Engine problem
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 16 | 16 | 17 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 54 | 72 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 11 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 36 | 35 |  | 20 | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 200 | 200 | 200 | 200 | 383 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1767 | 1973 | 2260 | 2680 | 2340 | 850
35 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
36 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25
37 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 9 | 0 | 20 | 0
38 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 19 | 31 |  | Fuel shortage
39 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 214 | 214 | 213 | 213 |  | 17
40 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 225 | 225 | 225
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
42 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 8 | 0 | 17 | 17 | 88 |  | Fuel shortage
43 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 80 | 56 | 82 |  | 16 | Engine problem
44 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 35 | 51 | 85 | 85 |  | 17 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0
45 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 12 | 12 | 88 |  | Fuel shortage
46 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 30 | 15 | 30
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 44 | 44 | 64 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 52 | 52 | 52 | 248 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 35 | 35 | 19 |  | Fuel shortage
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 15 | 0 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 10 | 12 | 12 | 88 |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 35 | 35 | 35 | 81 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 35 | 35 | 163
55 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 300 | 608 | 300 | 612 |  | 612 | Unit-2 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 0 | 42 | 60 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 256 | 232 | 350 | 350 | 800 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1217 | 1631 | 1677 | 2181 | 1687 | 992
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 211 | 218 | 215 | 215 | 6 |  | Gas shortage
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 285 | 320 | 320 |  | 40 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 290 | 285 | 330 | 330 |  |  | FGMO
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 44 | 41 | 44
63 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 30 | 13 | 10 | 30
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 26 | 45 | 45 | 150 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 3 | 48 | 80 | 100 | 50 |  | Fuel shortage
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 35 | 44 |  | 8 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 50 | 80 | 80 | 83 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 155 | 55 | 155 |  | 45 | Engine problem
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 58 | 68 | 66 | 70
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 50
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 15 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 34 | 34 | 106 |  | 8 | Engine problem
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 32 | 76 | 28 | 74 |  | 39 | Fuel shortage
76 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 92 | 34 | 92 |  | 23 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 72 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1349 | 1508 | 1517 | 1824 | 289 | 530
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 0 | 0 | 8 | 8 | 194 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 132 | 152 | 133 | 150 | 50 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 97 | 75 | 96 | 19 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 19 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 6 | 18
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 0 | 35 |  |  | Fuel shortage
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 0 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 221 | 284 | 273.6 | 307 | 194 | 0
84 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 26 | 30 | 30 | 30 |  | 40
85 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint
86 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 150 | 120 | 163 | 163
87 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
88 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 50 | 25 | 50 | 1 |  | Gas shortage
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 33 | 36 | 25 | 36 | 14 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 5 | 8 |  | 3 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 62 | 62
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 83 | 83 | 83
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 135 | 137 |  | 94 | ST Under maint.
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 300 | 300 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 325 | 370 | 380 | 380 |  |  | FGMO
99 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 389 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1439 | 1466 | 1620 | 1661 | 35 | 570
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 477 | 544 | 844 | 844
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 41 |  | 13 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 52 |  | 57 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 147 | 185 | 220 | 220 | 190 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 18 | 87 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 83 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 509 | 507 | 500 | 510 | 724 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1216 | 1253 | 1711 | 1685 | 1583 | 70
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 16 | 110
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 7 | 10 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 66 | 67 | 67 | 67 |  | 127 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1120 | 1244 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 11 | 126 | 17 | 150
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 307 | 307 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1747 | 2084 | 1881 | 2108 | 0 | 127
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 35 | 38 |  | 14 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 24 |  | 47 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
122 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 28 | 46
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 181 | 184 | 180 | 180 | 30 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 414 | 414 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 22 | 28 |  | 22 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 8 | 5 | 8 |  | 3 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 48 | 50 | 96 |  | 8 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 45 | 70 | 113 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1036 | 1232 | 1000 | 1200
135 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 35 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 93 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1744 | 1956 | 2042 | 2260 | 641 | 94
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 63 | 62 | 63 |  | 22
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230 |  | 44
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 74 | 35 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 193 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 553 | 480 | 648 | 521 | 40 | 151
| Total |  |  |  |  | 27791 | 27086 | 11253 | 12635 | 13629.6 | 15227 | 6809 | 3384
A. |  | 2024-10-11 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 12798 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10527 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12635 | MW
3 | Day peak Generation : |  |  | 11253 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12095.93 | MW
4 | Evening peak Generation : |  |  | 12635 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | + | MW
5 | Total Energy Generation : |  | 283.4364 | MKWHr | By Solar | 3.58 | MKWHr
| By Gas : | 126.6992 | MKWHr |  | By Oil: | 36.9171 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 71.1516 | MKWHr |  | By Hydro: | 5.166 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 26.2909 | MKWHr |  | By Wind: | 0.01584 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6809 | MW | Dhaka | 3885.43 | 3885.43 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3384 | MW | Chittagong | 1228.8 | 1228.8 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10193 | MW | Khulna | 1602.4 | 1602.4 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 908.35 | MMCFD | **Import Adani: | Taka | 173782908.49 | Rajshahi | 1307.8 | 1307.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 366918915.982 | ii) Oil : | Taka | 680827866.3 | Comilla | 1308 | 1308 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 496106911.72 | Total | Taka | 1717636602.492 | Mymensingh | 1067 | 1067 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 4672.8 | MKWHr. | Sylhet | 465 | 465 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 514 | MW (W to E) at | 21:00 | hrs | Barisal | 451.5 | 451.5 |  | 0 |  | 24:00 |  | 103
| iii) Maximum : |  |  | 362 | MW at | 19:30 | hrs | Rangpur | 780 | 780 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.0°C |  |  | Total | 12095.93 | 12095.93 |  | 0
B. |  | 2024-10-12 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 34.0°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15227 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
4 | Reserve(Generation end) |  |  |  | 1227 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 310.057 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10039 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.0989 | MKWHr. | ii) HVDC Flow at Peak Time |  | 544 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.5168 | MKWHr. | iii) Maximum HVDC Flow : |  | 886 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 0 |  | (b) Today: | 106.58 |  | (c) Rule Curve: |  | 106.81
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-10-11 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 64 | 13 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 13 | 20 | 25 | 12 | 0 | 0 | 135 | 80 | 0 | 0 | 8 | 227 | 0 | 0 | 0 |  | 0 | 72 | 68 | 0 | 31 | 19 | 0 | 36 | 0 | 0 | 0 | 310 | 0 | 217 | 8 | 70 | 43 | 30 | 0 | 51 | 0 | 30 | 25 | 0 | 0 | 0 | 18 | 76 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 5 | 163 | 0 | 56 | 31 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 290 | 0 | 0 | 95 | 0 | 46 | 0 | 12 | 70 | 85 | 372 | 59 | 17 | 17 | 0 | 52 | 0 | 110 | 106 | 28 | 10 | 394 | 16 | 0 | 72 | 17 | 0 | 35 | 0 | 34 | 17 | 295 | 17 | 0 | 310 | 0 | 352 | 0 | 215 | 0 | 0 | 0 |  | 478 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 25 | 46 | 0 | 67 | 10 | 64 | 0 | 0 | 0 | 38 | 19 | 0 | 0 | 0 | 30 | 0 | 28 | 0 | 0 | 5 | 64 | 0 | 225 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 307 | 1032 | 0 | 0 | 0 | 0 | 0 |  | 6890 | 5495 | 12385 | 3377 | 478 | 1884 | 0 | 1874 | 3012 | 215 | 0 | 437 | 76 | 1032 | 0 | 0 | 377.225 | 0
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 64 | 12 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 13 | 21 | 25 | 12 | 0 | 0 | 135 | 80 | 0 | 0 | 8 | 228 | 0 | 0 | 0 |  | 0 | 72 | 68 | 0 | 26 | 0 | 0 | 36 | 0 | 0 | 0 | 315 | 0 | 216 | 8 | 50 | 43 | 30 | 0 | 51 | 0 | 30 | 8 | 0 | 0 | 0 | 18 | 74 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 5 | 163 | 0 | 56 | 31 | 0 | 137 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 294 | 0 | 0 | 95 | 0 | 34 | 0 | 12 | 51 | 85 | 365 | 59 | 17 | 17 | 0 | 50 | 0 | 110 | 106 | 28 | 10 | 397 | 16 | 0 | 54 | 17 | 0 | 17 | 0 | 34 | 17 | 295 | 17 | 0 | 300 | 0 | 353 | 0 | 215 | 0 | 0 | 0 |  | 478 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 0 | 67 | 10 | 64 | 0 | 0 | 0 | 35 | 19 | 0 | 0 | 0 | 30 | 0 | 28 | 0 | 0 | 5 | 64 | 0 | 225 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 307 | 1037 | 0 | 0 | 0 | 0 | 0 |  | 6694 | 5539 | 12233 | 3364 | 478 | 1918 | 0 | 1727 | 3007 | 215 | 0 | 413 | 74 | 1037 | 0 | 0 | 207.235 | 0
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 21 | 25 | 12 | 0 | 0 | 135 | 80 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 72 | 68 | 0 | 25 | 0 | 0 | 26 | 0 | 0 | 0 | 315 | 0 | 215 | 8 | 70 | 43 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 74 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 5 | 163 | 0 | 56 | 31 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 195 | 0 | 0 | 95 | 0 | 36 | 0 | 12 | 51 | 83 | 365 | 59 | 17 | 17 | 0 | 52 | 0 | 110 | 106 | 29 | 10 | 394 | 16 | 0 | 54 | 17 | 0 | 17 | 0 | 34 | 17 | 295 | 17 | 0 | 300 | 0 | 312 | 0 | 215 | 0 | 0 | 0 |  | 478 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 225 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 509 | 0 | 307 | 1046 | 0 | 0 | 0 | 0 | 0 |  | 6443 | 5313 | 11756 | 3389 | 478 | 1918 | 0 | 1486 | 2961 | 215 | 0 | 189 | 74 | 1046 | 0 | 0 | 213.92 | 0
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 21 | 25 | 14 | 0 | 0 | 135 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 72 | 17 | 0 | 25 | 0 | 0 | 37 | 0 | 0 | 0 | 315 | 0 | 216 | 8 | 70 | 43 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 70 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 5 | 163 | 0 | 56 | 31 | 0 | 137 | 0 | 0 | 0 | 300 | 4 | 8 | 0 | 95 | 0 | 0 | 95 | 0 | 35 | 0 | 12 | 51 | 60 | 366 | 59 | 17 | 17 | 0 | 52 | 0 | 110 | 106 | 28 | 10 | 394 | 16 | 0 | 17 | 17 | 0 | 17 | 0 | 37 | 17 | 295 | 17 | 0 | 300 | 0 | 282 | 0 | 215 | 0 | 0 | 0 |  | 476 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 9 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 225 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 307 | 1031 | 0 | 0 | 0 | 0 | 0 |  | 6199 | 5262 | 11461 | 3389 | 476 | 1938 | 0 | 1274 | 2930 | 215 | 0 | 138 | 70 | 1031 | 0 | 0 | 180.495 | 0
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 21 | 25 | 14 | 0 | 0 | 135 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 38 | 0 | 0 | 0 | 320 | 0 | 215 | 8 | 80 | 43 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 64 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 5 | 163 | 0 | 59 | 31 | 0 | 138 | 0 | 0 | 0 | 305 | 12 | 8 | 0 | 0 | 0 | 0 | 97 | 0 | 35 | 0 | 12 | 51 | 51 | 324 | 59 | 17 | 17 | 0 | 52 | 0 | 110 | 106 | 28 | 10 | 394 | 16 | 0 | 17 | 17 | 0 | 0 | 0 | 35 | 17 | 295 | 17 | 0 | 300 | 0 | 254 | 0 | 215 | 0 | 14 | 0 |  | 476 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 9 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 225 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 509 | 0 | 307 | 1030 | 0 | 0 | 0 | 0 | 0 |  | 5959 | 5265 | 11224 | 3376 | 476 | 1958 | 0 | 1153 | 2903 | 215 | 0 | 49 | 64 | 1030 | 0 | 0 | 168.08 | 0
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 21 | 25 | 14 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 38 | 0 | 0 | 0 | 315 | 0 | 217 | 8 | 80 | 43 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 50 | 0 | 0 | 0 | 0 | 28 | 0 | 25 | 15 | 120 | 0 | 60 | 31 | 0 | 64 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 97 | 0 | 35 | 0 | 12 | 51 | 40 | 306 | 59 | 17 | 17 | 0 | 52 | 0 | 17 | 88 | 28 | 0 | 400 | 16 | 0 | 17 | 17 | 0 | 0 | 0 | 34 | 17 | 295 | 17 | 0 | 300 | 0 | 244 | 0 | 215 | 1 | 45 | 0 |  | 476 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 225 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 35 | 1244 | 220 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 307 | 1034 | 0 | 0 | 0 | 0 | 0 |  | 5711 | 5088 | 10799 | 3287 | 476 | 1961 | 0 | 833 | 2894 | 214 | 0 | 49 | 50 | 1034 | 1 | 0 | 163.305 | 0
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 21 | 25 | 13 | 2 | 0 | 133 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 360 | 0 | 214 | 8 | 80 | 43 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 56 | 0 | 0 | 0 | 0 | 28 | 0 | 25 | 21 | 120 | 0 | 58 | 51 | 0 | 64 | 0 | 0 | 0 | 305 | 12 | 8 | 0 | 0 | 0 | 0 | 134 | 0 | 34 | 5 | 0 | 51 | 0 | 312 | 69 | 17 | 0 | 1 | 52 | 0 | 0 | 70 | 28 | 0 | 386 | 16 | 4 | 0 | 0 | 0 | 0 | 4 | 34 | 17 | 375 | 0 | 0 | 300 | 0 | 225 | 0 | 200 | 7 | 15 | 0 |  | 476 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 225 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1120 | 220 | 0 | 54 | 0 | 14 | 0 | 0 | 0 | 510 | 3 | 307 | 1031 | 17 | 0 | 0 | 6 | 12 |  | 5675 | 4852 | 10527 | 3374 | 476 | 1893 | 0 | 628 | 2751 | 213 | 0 | 32 | 56 | 1031 | 73 | 0 | 136.565 | 0
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 25 | 13 | 8 | 0 | 133 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 285 | 0 | 220 | 8 | 80 | 40 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 56 | 0 | 0 | 0 | 1 | 28 | 0 | 25 | 25 | 163 | 0 | 61 | 61 | 0 | 64 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 134 | 0 | 34 | 11 | 0 | 51 | 0 | 309 | 69 | 17 | 0 | 2 | 52 | 9 | 0 | 70 | 29 | 0 | 400 | 16 | 15 | 0 | 0 | 0 | 0 | 12 | 34 | 17 | 290 | 0 | 0 | 300 | 0 | 215 | 0 | 200 | 36 | 0 | 0 |  | 476 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 225 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 1100 | 180 | 0 | 54 | 1 | 37 | 0 | 0 | 0 | 510 | 14 | 307 | 1031 | 60 | 0 | 0 | 21 | 29 |  | 5575 | 4966 | 10541 | 3181 | 476 | 1947 | 0 | 644 | 2721 | 213 | 0 | 32 | 56 | 1031 | 240 | 0 | 123.195 | 106.72
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 21 | 25 | 13 | 16 | 0 | 133 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 285 | 0 | 215 | 8 | 50 | 40 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 56 | 0 | 0 | 0 | 1 | 28 | 0 | 25 | 25 | 163 | 0 | 61 | 61 | 0 | 0 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 134 | 0 | 35 | 15 | 0 | 51 | 0 | 312 | 69 | 52 | 0 | 3 | 52 | 29 | 0 | 70 | 28 | 0 | 400 | 16 | 23 | 0 | 0 | 0 | 0 | 18 | 34 | 17 | 290 | 0 | 0 | 300 | 0 | 215 | 0 | 200 | 56 | 0 | 0 |  | 476 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 225 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 1080 | 180 | 0 | 17 | 2 | 60 | 0 | 0 | 0 | 512 | 12 | 307 | 1027 | 106 | 0 | 0 | 32 | 57 |  | 5604 | 4979 | 10583 | 3108 | 476 | 1895 | 0 | 670 | 2703 | 213 | 0 | 48 | 56 | 1027 | 387 | 0 | 0 | 106.71
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 21 | 25 | 13 | 17 | 0 | 133 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 285 | 0 | 212 | 45 | 50 | 39 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 56 | 0 | 0 | 0 | 2 | 28 | 0 | 25 | 25 | 150 | 0 | 60 | 61 | 0 | 0 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 115 | 0 | 54 | 17 | 0 | 51 | 0 | 316 | 69 | 17 | 0 | 2 | 51 | 35 | 0 | 70 | 28 | 0 | 388 | 16 | 19 | 0 | 0 | 0 | 0 | 25 | 34 | 17 | 290 | 0 | 0 | 300 | 0 | 216 | 0 | 200 | 68 | 0 | 0 |  | 476 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 228 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 1050 | 180 | 0 | 0 | 4 | 83 | 0 | 0 | 0 | 510 | 25 | 307 | 1034 | 134 | 0 | 0 | 47 | 79 |  | 5564 | 5040 | 10604 | 3061 | 476 | 1908 | 0 | 624 | 2674 | 213 | 0 | 48 | 56 | 1034 | 510 | 0 | 0 | 106.71
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 13 | 21 | 25 | 16 | 17 | 0 | 133 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 216 | 45 | 51 | 36 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 56 | 0 | 0 | 0 | 2 | 28 | 0 | 25 | 25 | 150 | 0 | 60 | 85 | 0 | 0 | 0 | 0 | 0 | 315 | 12 | 8 | 0 | 0 | 0 | 0 | 115 | 0 | 69 | 5 | 0 | 51 | 0 | 316 | 69 | 17 | 0 | 5 | 51 | 35 | 0 | 70 | 30 | 0 | 386 | 16 | 44 | 0 | 0 | 0 | 0 | 18 | 33 | 35 | 315 | 0 | 0 | 300 | 0 | 234 | 0 | 200 | 72 | 0 | 0 |  | 477 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 180 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 1040 | 220 | 0 | 0 | 2 | 97 | 0 | 0 | 0 | 507 | 33 | 307 | 1028 | 182 | 0 | 0 | 45 | 90 |  | 5739 | 5124 | 10863 | 3112 | 477 | 2027 | 0 | 673 | 2631 | 213 | 0 | 48 | 56 | 1028 | 598 | 0 | 0 | 106.7
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 21 | 17 | 17 | 0 | 14 | 21 | 25 | 16 | 17 | 0 | 134 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 285 | 0 | 211 | 45 | 51 | 40 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 58 | 0 | 0 | 0 | 2 | 26 | 0 | 51 | 33 | 150 | 0 | 60 | 85 | 0 | 0 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 17 | 0 | 0 | 132 | 0 | 66 | 9 | 0 | 51 | 3 | 325 | 68 | 52 | 8 | 1 | 52 | 35 | 15 | 70 | 32 | 10 | 389 | 16 | 19 | 35 | 17 | 0 | 0 | 11 | 34 | 35 | 290 | 36 | 0 | 300 | 0 | 256 | 0 | 200 | 72 | 0 | 0 |  | 477 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 230 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 45 | 1120 | 220 | 0 | 11 | 2 | 83 | 0 | 0 | 0 | 509 | 32 | 307 | 1036 | 193 | 0 | 0 | 35 | 93 |  | 5993 | 5260 | 11253 | 3087 | 477 | 1982 | 0 | 942 | 2785 | 214 | 0 | 119 | 58 | 1036 | 553 | 0 | 0 | 106.7
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 14 | 21 | 25 | 18 | 17 | 0 | 134 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 48 | 68 | 0 | 16 | 0 | 0 | 20 | 0 | 0 | 0 | 310 | 0 | 216 | 83 | 51 | 36 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 64 | 0 | 0 | 0 | 2 | 26 | 0 | 52 | 32 | 163 | 0 | 60 | 85 | 0 | 0 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 95 | 0 | 0 | 132 | 0 | 77 | 19 | 0 | 51 | 25 | 347 | 67 | 52 | 17 | 1 | 51 | 35 | 63 | 102 | 29 | 10 | 392 | 16 | 19 | 90 | 35 | 0 | 0 | 14 | 38 | 35 | 320 | 36 | 0 | 300 | 0 | 251 | 0 | 200 | 66 | 0 | 0 |  | 477 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 230 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 15 | 0 | 34 | 0 | 5 | 55 | 1244 | 180 | 0 | 103 | 2 | 85 | 0 | 0 | 0 | 510 | 23 | 307 | 1034 | 168 | 0 | 0 | 41 | 85 |  | 6609 | 5427 | 12036 | 3204 | 477 | 2013 | 0 | 1379 | 2905 | 214 | 0 | 216 | 64 | 1034 | 530 | 0 | 0 | 106.69
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 21 | 25 | 19 | 17 | 0 | 134 | 80 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 48 | 68 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 345 | 0 | 209 | 83 | 51 | 34 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 64 | 0 | 0 | 0 | 1 | 26 | 0 | 52 | 32 | 130 | 0 | 60 | 85 | 0 | 0 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 95 | 0 | 0 | 123 | 0 | 100 | 17 | 0 | 51 | 6 | 348 | 66 | 52 | 0 | 2 | 52 | 17 | 0 | 106 | 28 | 10 | 375 | 16 | 33 | 35 | 17 | 0 | 14 | 15 | 34 | 35 | 370 | 0 | 0 | 300 | 3 | 251 | 0 | 200 | 57 | 0 | 0 |  | 479 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 230 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 55 | 1244 | 180 | 0 | 35 | 0 | 74 | 0 | 0 | 0 | 510 | 7 | 307 | 1039 | 107 | 0 | 0 | 8 | 57 |  | 6206 | 5264 | 11470 | 3180 | 479 | 1943 | 0 | 1082 | 2905 | 214 | 0 | 180 | 64 | 1039 | 381 | 3 | 0 | 106.7
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 20 | 24 | 19 | 17 | 0 | 135 | 80 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 48 | 68 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 315 | 0 | 211 | 83 | 51 | 39 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 64 | 0 | 0 | 0 | 1 | 26 | 0 | 52 | 32 | 163 | 0 | 61 | 85 | 0 | 0 | 0 | 0 | 0 | 320 | 12 | 0 | 0 | 95 | 0 | 0 | 123 | 0 | 103 | 12 | 0 | 51 | 5 | 371 | 76 | 34 | 0 | 2 | 52 | 22 | 0 | 106 | 28 | 10 | 394 | 16 | 25 | 72 | 18 | 0 | 17 | 9 | 34 | 35 | 320 | 0 | 0 | 300 | 6 | 235 | 0 | 200 | 41 | 0 | 0 |  | 480 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 77 | 1244 | 220 | 0 | 72 | 0 | 15 | 0 | 0 | 0 | 510 | 20 | 307 | 1035 | 106 | 0 | 0 | 24 | 28 |  | 6324 | 5351 | 11675 | 3213 | 480 | 2127 | 0 | 1197 | 2888 | 215 | 0 | 164 | 64 | 1035 | 286 | 6 | 0 | 106.68
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 14 | 24 | 18 | 17 | 0 | 135 | 80 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 6 | 46 | 63 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 310 | 0 | 214 | 26 | 70 | 39 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 58 | 0 | 0 | 0 | 1 | 26 | 0 | 52 | 35 | 163 | 0 | 62 | 83 | 0 | 0 | 0 | 0 | 0 | 280 | 12 | 0 | 0 | 95 | 0 | 0 | 123 | 0 | 103 | 3 | 12 | 51 | 5 | 370 | 76 | 34 | 0 | 1 | 52 | 35 | 0 | 106 | 23 | 10 | 400 | 16 | 5 | 72 | 35 | 0 | 17 | 2 | 34 | 19 | 285 | 0 | 0 | 300 | 3 | 223 | 0 | 200 | 21 | 0 | 0 |  | 480 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 7 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 35 | 1120 | 220 | 0 | 72 | 0 | 33 | 0 | 0 | 0 | 510 | 10 | 250 | 1035 | 55 | 0 | 0 | 3 | 26 |  | 6164 | 4944 | 11108 | 3175 | 480 | 1966 | 0 | 1163 | 2695 | 215 | 0 | 157 | 58 | 1035 | 161 | 3 | 0 | 106.68
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 5 | 0 | 13 | 14 | 24 | 18 | 17 | 0 | 135 | 80 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 18 | 46 | 70 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 300 | 0 | 217 | 26 | 70 | 38 | 30 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 56 | 0 | 0 | 0 | 0 | 26 | 0 | 50 | 35 | 120 | 0 | 40 | 83 | 0 | 0 | 0 | 0 | 0 | 285 | 12 | 0 | 0 | 95 | 0 | 0 | 123 | 0 | 103 | 1 | 12 | 51 | 5 | 325 | 76 | 34 | 0 | 0 | 52 | 35 | 0 | 106 | 39 | 10 | 388 | 16 | 0 | 72 | 35 | 0 | 17 | 1 | 46 | 28 | 285 | 0 | 0 | 300 | 0 | 215 | 0 | 200 | 4 | 0 | 0 |  | 480 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 7 | 48 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 960 | 180 | 0 | 72 | 0 | 4 | 15 | 0 | 0 | 509 | 2 | 200 | 1131 | 11 | 0 | 0 | 2 | 1 |  | 5875 | 4657 | 10532 | 3013 | 480 | 1701 | 0 | 1266 | 2476 | 215 | 0 | 168 | 56 | 1131 | 26 | 0 | 0 | 106.67
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 19 | 17 | 17 | 0 | 14 | 20 | 24 | 18 | 17 | 0 | 136 | 80 | 0 | 0 | 0 | 200 | 0 | 0 | 0 |  | 18 | 53 | 85 | 0 | 3 | 0 | 0 | 28 | 0 | 0 | 0 | 357 | 0 | 213 | 26 | 50 | 43 | 30 | 0 | 18 | 0 | 31 | 7 | 0 | 0 | 0 | 18 | 66 | 0 | 0 | 0 | 0 | 26 | 0 | 31 | 33 | 163 | 0 | 58 | 83 | 0 | 0 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 142 | 0 | 0 | 130 | 0 | 105 | 0 | 12 | 70 | 33 | 356 | 76 | 34 | 0 | 0 | 52 | 35 | 0 | 70 | 75 | 10 | 387 | 16 | 0 | 96 | 35 | 0 | 17 | 0 | 51 | 35 | 380 | 35 | 0 | 440 | 0 | 218 | 0 | 200 | 0 | 0 | 0 |  | 480 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 48 | 0 | 0 | 0 | 0 | 4 | 49 | 0 | 0 | 27 | 0 | 13 | 0 | 0 | 5 | 62 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 1 | 0 | 80 | 0 | 0 | 100 | 960 | 220 | 0 | 108 | 0 | 0 | 55 | 0 | 0 | 509 | 0 | 295 | 1237 | 0 | 0 | 0 | 0 | 0 |  | 6684 | 5305 | 11989 | 3294 | 480 | 1996 | 0 | 1609 | 2714 | 216 | 0 | 377 | 66 | 1237 | 0 | 0 | 0 | 106.67
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 5 | 333 | 0 | 0 | 0 | 33 | 64 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 14 | 20 | 24 | 18 | 17 | 0 | 136 | 80 | 0 | 0 | 0 | 197 | 0 | 0 | 0 |  | 18 | 80 | 57 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 0 | 310 | 0 | 219 | 26 | 50 | 43 | 30 | 0 | 37 | 0 | 36 | 7 | 0 | 0 | 0 | 18 | 66 | 0 | 0 | 0 | 0 | 26 | 0 | 50 | 33 | 163 | 0 | 60 | 83 | 0 | 0 | 0 | 0 | 0 | 275 | 12 | 5 | 0 | 45 | 0 | 0 | 152 | 0 | 115 | 0 | 12 | 136 | 68 | 359 | 95 | 52 | 0 | 0 | 52 | 35 | 0 | 52 | 75 | 10 | 392 | 16 | 0 | 108 | 35 | 0 | 17 | 0 | 61 | 35 | 330 | 70 | 0 | 600 | 0 | 206 | 0 | 200 | 0 | 0 | 0 |  | 480 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 48 | 0 | 0 | 0 | 39 | 12 | 49 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 8 | 62 | 0 | 230 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 0 | 0 | 113 | 0 | 0 | 70 | 1190 | 180 | 0 | 126 | 0 | 0 | 74 | 0 | 0 | 508 | 0 | 307 | 1243 | 0 | 0 | 0 | 0 | 0 |  | 6916 | 5602 | 12518 | 3261 | 480 | 1917 | 0 | 1751 | 3103 | 216 | 0 | 481 | 66 | 1243 | 0 | 0 | 0 | 106.65
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 332 | 0 | 0 | 0 | 50 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 11 | 20 | 24 | 18 | 17 | 0 | 135 | 80 | 0 | 0 | 0 | 197 | 0 | 0 | 0 |  | 18 | 73 | 53 | 0 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 325 | 0 | 215 | 26 | 50 | 43 | 30 | 0 | 51 | 0 | 36 | 7 | 0 | 0 | 0 | 18 | 68 | 0 | 0 | 0 | 0 | 26 | 0 | 50 | 33 | 163 | 0 | 59 | 83 | 0 | 0 | 0 | 0 | 0 | 310 | 12 | 5 | 0 | 45 | 0 | 0 | 152 | 0 | 115 | 0 | 12 | 155 | 68 | 363 | 95 | 34 | 0 | 0 | 52 | 35 | 0 | 34 | 75 | 10 | 392 | 17 | 0 | 54 | 35 | 0 | 17 | 0 | 90 | 35 | 335 | 35 | 0 | 612 | 0 | 204 | 0 | 200 | 0 | 0 | 0 |  | 480 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 9 | 48 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 0 | 0 | 113 | 0 | 0 | 70 | 1220 | 180 | 0 | 126 | 0 | 0 | 74 | 0 | 0 | 509 | 0 | 307 | 1250 | 0 | 0 | 0 | 0 | 0 |  | 6946 | 5527 | 12473 | 3290 | 480 | 1965 | 0 | 1751 | 3144 | 215 | 0 | 310 | 68 | 1250 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 328 | 0 | 0 | 0 | 50 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 11 | 20 | 24 | 18 | 17 | 0 | 135 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 18 | 80 | 51 | 0 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 345 | 0 | 214 | 26 | 50 | 43 | 30 | 0 | 51 | 0 | 36 | 8 | 0 | 0 | 0 | 18 | 68 | 0 | 0 | 0 | 0 | 26 | 0 | 50 | 35 | 163 | 0 | 59 | 83 | 0 | 0 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 45 | 0 | 0 | 141 | 0 | 115 | 0 | 12 | 155 | 60 | 365 | 96 | 34 | 0 | 0 | 52 | 35 | 0 | 34 | 77 | 10 | 388 | 16 | 0 | 54 | 35 | 0 | 17 | 0 | 82 | 35 | 340 | 35 | 0 | 612 | 0 | 212 | 0 | 200 | 0 | 0 | 0 |  | 490 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 9 | 64 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 0 | 0 | 105 | 0 | 0 | 70 | 1230 | 180 | 0 | 126 | 0 | 0 | 74 | 0 | 0 | 509 | 0 | 307 | 1258 | 0 | 0 | 0 | 0 | 0 |  | 6969 | 5568 | 12537 | 3336 | 490 | 1957 | 0 | 1735 | 3163 | 215 | 0 | 315 | 68 | 1258 | 0 | 0 | 0 | 106.66
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 50 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 15 | 21 | 24 | 19 | 17 | 0 | 134 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 18 | 80 | 51 | 0 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 285 | 0 | 218 | 26 | 50 | 44 | 13 | 0 | 51 | 0 | 37 | 8 | 0 | 0 | 0 | 18 | 68 | 0 | 0 | 0 | 0 | 30 | 0 | 50 | 36 | 120 | 0 | 60 | 83 | 0 | 0 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 45 | 0 | 0 | 152 | 0 | 114 | 0 | 12 | 155 | 48 | 370 | 97 | 34 | 0 | 0 | 52 | 35 | 0 | 34 | 76 | 10 | 400 | 16 | 0 | 54 | 35 | 0 | 17 | 0 | 92 | 35 | 285 | 35 | 0 | 608 | 0 | 232 | 0 | 200 | 0 | 0 | 0 |  | 544 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 0 | 0 | 113 | 0 | 0 | 70 | 1244 | 220 | 0 | 126 | 0 | 0 | 74 | 0 | 0 | 507 | 0 | 307 | 1232 | 0 | 0 | 0 | 0 | 0 |  | 6862 | 5773 | 12635 | 3271 | 544 | 2003 | 0 | 1797 | 3191 | 214 | 0 | 315 | 68 | 1232 | 0 | 0 | 0 | 106.65
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 50 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 21 | 24 | 20 | 17 | 0 | 134 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 18 | 64 | 51 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 320 | 0 | 215 | 26 | 50 | 44 | 10 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 70 | 0 | 0 | 0 | 0 | 30 | 0 | 50 | 36 | 120 | 0 | 59 | 83 | 0 | 0 | 0 | 0 | 0 | 310 | 12 | 5 | 0 | 45 | 0 | 0 | 152 | 0 | 114 | 0 | 12 | 155 | 43 | 374 | 96 | 34 | 0 | 0 | 52 | 35 | 0 | 70 | 75 | 12 | 390 | 16 | 0 | 54 | 35 | 0 | 0 | 0 | 92 | 35 | 360 | 35 | 0 | 424 | 0 | 246 | 0 | 200 | 0 | 12 | 0 |  | 588 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 1220 | 220 | 0 | 126 | 0 | 0 | 108 | 0 | 0 | 507 | 0 | 307 | 1225 | 0 | 0 | 0 | 0 | 0 |  | 6771 | 5864 | 12635 | 3357 | 588 | 2034 | 0 | 1888 | 2997 | 214 | 0 | 262 | 70 | 1225 | 0 | 0 | 0 | 106.65
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 14 | 13 | 0 | 17 | 21 | 24 | 22 | 17 | 0 | 135 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 64 | 51 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 315 | 0 | 216 | 26 | 50 | 44 | 10 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 76 | 0 | 0 | 0 | 0 | 30 | 0 | 50 | 36 | 163 | 0 | 59 | 81 | 0 | 0 | 0 | 0 | 0 | 335 | 12 | 5 | 0 | 50 | 0 | 0 | 153 | 0 | 114 | 0 | 12 | 156 | 41 | 377 | 97 | 34 | 0 | 0 | 52 | 35 | 0 | 70 | 78 | 12 | 390 | 16 | 0 | 100 | 35 | 0 | 11 | 0 | 83 | 35 | 350 | 35 | 0 | 300 | 0 | 225 | 0 | 200 | 0 | 36 | 0 |  | 715 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 4 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 514 | 0 | 307 | 1240 | 0 | 0 | 0 | 0 | 0 |  | 6730 | 6068 | 12798 | 3354 | 715 | 2124 | 0 | 1928 | 2884 | 215 | 0 | 262 | 76 | 1240 | 0 | 0 | 0 | 106.64
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 0 |  | 0 | 380 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 21 | 24 | 23 | 17 | 0 | 135 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 64 | 51 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 0 | 217 | 26 | 50 | 44 | 10 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 82 | 0 | 0 | 0 | 0 | 30 | 0 | 50 | 36 | 163 | 0 | 60 | 81 | 0 | 20 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 125 | 0 | 0 | 153 | 0 | 114 | 0 | 12 | 157 | 38 | 376 | 97 | 34 | 17 | 0 | 52 | 35 | 21 | 70 | 45 | 12 | 394 | 16 | 0 | 108 | 17 | 0 | 11 | 0 | 44 | 17 | 330 | 17 | 0 | 300 | 0 | 230 | 0 | 200 | 0 | 46 | 0 |  | 886 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 65 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 511 | 0 | 307 | 1219 | 0 | 0 | 0 | 0 | 0 |  | 6592 | 6110 | 12702 | 3322 | 886 | 1970 | 0 | 1879 | 2885 | 215 | 0 | 244 | 82 | 1219 | 0 | 0 | 103 | 106.64
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9684000 | 0 |  | 0 | 10332500 | 0 | 0 | 0 | 215669 | 7708976 | 0 | 0 | 0 | 336960 | 1283040 | 23000 | 0 | 0 | 0 | 415800 | 142836 | 187585 | 0 | 324600 | 471960 | 619800 | 387800 | 276000 | 0 | 3238042 | 1928000 | 0 | 0 | 21430 | 5157454 | 0 | 0 | 0 |  | 154080 | 998592 | 998079 | 0 | 264000 | 38880 | 0 | 690720 | 0 | 0 | 0 | 7800200 | 0 | 5226000 | 702545 | 1393840 | 977616 | 647040 | 0 | 1069120 | 0 | 228592 | 207067 | 0 | 0 | 0 | 410830 | 1516800 | 0 | 0 | 0 | 11200 | 652000 | 0 | 789600 | 609912 | 3801273 | 0 | 1380193 | 1513920 | 0 | 964110 | 0 | 0 | 0 | 7323500 | 272256 | 147504 | 0 | 2157818 | 0 | 0 | 2961600 | 0 | 1809792 | 124875 | 173760 | 1910400 | 806254 | 8681000 | 1764000 | 716160 | 149709 | 20637 | 1257055 | 583463 | 777810 | 1980180 | 1003800 | 203520 | 9329800 | 388800 | 218000 | 1131840 | 514364 | 0 | 269280 | 0 | 1111680 | 644400 | 7639800 | 423200 | 0 | 8416362 | 15840 | 6014545 | 0 | 5031818 | 504327 | 168000 | 0 |  | 12098909 | 0 | 3814848 | 0 | 0 | 0 | 0 | 0 | 53280 | 92544 | 0 | 1581000 | 208617 | 1181088 | 0 | 0 | 0 | 116327 | 55968 | 364656 | 0 | 0 | 123005 | 0 | 89255 | 0 | 0 | 110286 | 1445236 | 0 | 5472000 | 0 | 0 | 4288455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9526181 | 115680 | 0 | 548832 | 0 | 1642876 | 0 | 29338 | 1162368 | 30261500 | 5260170 | 0 | 2252400 | 23460 | 586080 | 588288 | 0 | 0 | 12320000 | 193839 | 7222000 | 26290909 | 1043280 | 0 | 3934 | 279750 | 541260 |  | 152448810 | 130987619 | 283436429 | 79024328 | 12098909 | 47674916 | 0 | 32090524 | 71151643 | 5166042 | 0 | 4826538 | 1516800 | 26290909 | 3579980 | 15840 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27889920 | 0 |  | 0 | 32857350 | 0 | 0 | 0 | 3800087.78 | 23512376.8 | 0 | 0 | 0 | 6048432 | 24916636.8 | 428950 | 0 | 0 | 0 | 7592508 | 2251095.36 | 3430929.65 | 0 | 243450 | 0 | 0 | 0 | 4943160 | 0 | 0 | 0 | 0 | 0 | 405884.2 | 16452278.26 | 0 | 0 | 0 |  | 2710267.2 | 17585205.12 | 17875594.89 | 0 | 5166480 | 639964.8 | 0 | 0 | 0 | 0 | 0 | 21762558 | 0 | 17350320 | 2353525.75 | 4502103.2 | 3294565.92 | 2834035.2 | 0 | 4287171.2 | 0 | 4094082.72 | 3739630.02 | 0 | 0 | 0 | 308122.5 | 9950208 | 0 | 0 | 0 | 0 | 2542800 | 0 | 3592680 | 2775099.6 | 13000353.66 | 0 | 7660071.15 | 7902662.4 | 0 | 2689866.9 | 0 | 0 | 0 | 22629615 | 204192 | 112103.04 | 0 | 44019487.2 | 0 | 0 | 56892336 | 0 | 31870437.12 | 0 | 3094665.6 | 33145440 | 13367691.32 | 23004650 | 33621840 | 13435161.6 | 2685779.46 | 0 | 20552849.25 | 11342520.72 | 13953911.4 | 37841239.8 | 19483758 | 3624691.2 | 24817268 | 6636816 | 0 | 20701353.6 | 8631027.92 | 0 | 4812033.6 | 0 | 20032473.6 | 10916136 | 22690206 | 5958656 | 0 | 58662043.14 | 0 | 35485815.5 | 0 | 0 | 0 | 0 | 0 |  | 33997934.29 | 0 | 11253801.6 | 0 | 0 | 0 | 0 | 0 | 1002196.8 | 1740752.64 | 0 | 4995960 | 988844.58 | 20361957.12 | 0 | 0 | 0 | 2083416.57 | 1027012.8 | 6129867.36 | 0 | 0 | 2203019.55 | 0 | 1598557.05 | 0 | 0 | 83486.502 | 15940953.08 | 0 | 46183680 | 0 | 0 | 14151901.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27816448.52 | 1975814.4 | 0 | 10877850.24 | 0 | 32726089.92 | 0 | 0 | 23061381.12 | 196094520 | 16359128.7 | 0 | 43583940 | 0 | 0 | 10206796.8 | 0 | 0 | 89936000 | 0 | 53803900 | 173782908.49 | 0 | 0 | 0 | 0 | 0 |  | 917616625.15 | 843968119.632 | 1761584744.782 | 229522001.372 | 33997934.29 | 137396914.61 | 0 | 594612868 | 496106911.72 | 0 | 0 | 86214998.3 | 9950208 | 173782908.49 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 21 | 17 | 17 | 0 | 14 | 21 | 25 | 16 | 17 | 0 | 134 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 285 | 0 | 211 | 45 | 51 | 40 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 58 | 0 | 0 | 0 | 2 | 26 | 0 | 51 | 33 | 150 | 0 | 60 | 85 | 0 | 0 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 17 | 0 | 0 | 132 | 0 | 66 | 9 | 0 | 51 | 3 | 325 | 68 | 52 | 8 | 1 | 52 | 35 | 15 | 70 | 32 | 10 | 389 | 16 | 19 | 35 | 17 | 0 | 0 | 11 | 34 | 35 | 290 | 36 | 0 | 300 | 0 | 256 | 0 | 200 | 72 | 0 | 0 |  | 477 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 230 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 45 | 1120 | 220 | 0 | 11 | 2 | 83 | 0 | 0 | 0 | 509 | 32 | 307 | 1036 | 193 | 0 | 0 | 35 | 93 |  | 11253 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 50 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 15 | 21 | 24 | 19 | 17 | 0 | 134 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 18 | 80 | 51 | 0 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 285 | 0 | 218 | 26 | 50 | 44 | 13 | 0 | 51 | 0 | 37 | 8 | 0 | 0 | 0 | 18 | 68 | 0 | 0 | 0 | 0 | 30 | 0 | 50 | 36 | 120 | 0 | 60 | 83 | 0 | 0 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 45 | 0 | 0 | 152 | 0 | 114 | 0 | 12 | 155 | 48 | 370 | 97 | 34 | 0 | 0 | 52 | 35 | 0 | 34 | 76 | 10 | 400 | 16 | 0 | 54 | 35 | 0 | 17 | 0 | 92 | 35 | 285 | 35 | 0 | 608 | 0 | 232 | 0 | 200 | 0 | 0 | 0 |  | 544 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 0 | 0 | 113 | 0 | 0 | 70 | 1244 | 220 | 0 | 126 | 0 | 0 | 74 | 0 | 0 | 507 | 0 | 307 | 1232 | 0 | 0 | 0 | 0 | 0 |  | 12635 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 50 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 21 | 24 | 21 | 25 | 0 | 133 | 80 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 18 | 82 | 85 | 0 | 44 | 19 | 0 | 30 | 0 | 0 |  | 320 | 0 | 215 | 45 | 80 | 44 | 30 | 0 | 51 | 0 | 44 | 50 | 0 | 0 |  | 18 | 70 | 8 | 0 | 0 | 0 | 30 | 0 | 50 | 36 | 163 | 0 | 62 | 83 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 300 | 0 | 0 | 150 | 0 | 132 | 0 | 12 | 155 | 100 | 380 | 96 | 100 | 17 | 0 | 52 | 35 | 110 | 106 | 74 | 12 | 400 | 17 | 0 | 162 | 35 | 0 | 35 | 0 | 92 | 35 | 330 | 163 | 0 | 612 | 60 | 350 | 0 | 200 |  |  |  |  | 844 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 41 | 52 | 0 | 67 | 10 | 110 | 0 | 0 | 0 | 38 | 24 | 96 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 8 | 63 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 18 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 510 | 0 | 307 | 1200 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 21 | 24 | 21 | 17 | 0 | 133 | 80 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 56 | 85 | 0 | 44 | 6 | 0 | 15 | 0 | 0 | 0 | 320 | 0 | 215 | 45 | 80 | 41 | 10 | 0 | 51 | 0 | 35 | 8 | 0 | 0 |  | 15 | 66 | 8 | 0 | 0 | 1.6 | 30 | 0 | 25 | 25 | 163 | 0 | 62 | 83 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 145 | 0 | 0 | 133 | 0 | 132 | 20 | 12 | 55 | 80 | 380 | 75 | 52 | 17 | 5 | 52 | 35 | 110 | 34 | 28 | 12 | 400 | 17 | 50 | 72 | 35 | 0 | 0 | 35 | 34 | 36 | 330 | 35 | 0 | 300 | 42 | 350 | 0 | 200 | 70 |  |  |  | 844 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 67 | 10 | 16 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 28 | 0 | 22 | 0 | 0 | 5 | 62 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 500 | 30 | 307 | 1000 | 170 | 0 |  | 29 | 47 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 24 | 21 | 8 | 0 | 135 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 325 | 0 | 216 | 45 | 50 | 41 | 10 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 66 | 5 | 0 | 0 | 1 | 30 | 0 | 5 | 5 | 120 | 0 | 62 | 31 | 0 | 91 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 0 | 0 | 0 | 135 | 0 | 35 | 10 | 0 | 55 | 0 | 347 | 69 | 17 | 0 | 2 | 52 | 0 | 0 | 17 | 27 | 0 | 390 | 16 | 20 | 0 | 0 | 0 | 0 | 0 | 33 | 17 | 325 | 0 | 0 | 300 | 0 | 246 | 0 | 200 | 27 | 0 | 0 | 0 | 908 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 870 | 180 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 409 | 8 | 200 | 1027 | 37 | 0 | 0 | 12 | 40 | 0 |  |  |  | 126699244 | 12098909 | 0 | 71151643 | 36917062 | 1516800 | 3579980 | 15840 | 5166042 |  |  |  | 257145520
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 126.6992 | 12.0989 | 0 | 71.1516 | 36.9171 | 1.5168 | 3.58 | 0.01584 | 5.166
| Minimum Generation |  | 10527 | 7:00
| Highest Generation |  | 12798 | 23:00 | [129 empty] | 0 | [76 empty] | 257.1455
| Day Peak Generation |  | 11253 | 12:00
| Evening Peak Generation |  | 12635 | 21:00 | [206 empty] | 202699852
| HVDC Max Flow |  | 886 | 24:00 | [206 empty] | 202.6999
| HVDC EvPeak Flow |  | 544 | 21:00
| Load factor L.F |  | 92.28% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-10-12
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-10-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11253 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10039
Evening Peak Generation : |  |  | 12635 | MW Hour : | 21:00 | Available Max Generation : |  | 15227
E.P. Demand (at gen end) : |  |  | 12635 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 12798 | MW Hour : | 23:00 | Reserve(Generation end) |  | 1227
Total Gen. (MKWH) : |  |  | 283.4364 | System Load Factor : | 92.28% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 362 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-10-12
Actual : |  | 106.58 | Ft.(MSL) , | Rule curve : | 106.81 | Ft.( MSL )
Gas Consumed : |  | Total = | 908.35 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 366918915.982 | Adani : | 173782908.49
|  |  | Coal : | 496106911.72 | Oil: | 680827866.3 | Total: | 1717636602.492
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4533.8427 |  |  | 0 | -9.558%
Chittagong Area |  | 0 | 0:00 | 1245.692 |  |  | 0 | -7.543%
Khulna Area |  | 0 | 0:00 | 1744.9061 |  |  | 0 | -7.112%
Rajshahi Area |  | 0 | 0:00 | 1516.5797 |  |  | 0 | -6.654%
Cumilla Area |  | 0 | 0:00 | 1247.9061 |  |  | 0 | -6.938%
Mymensingh Area |  | 0 | 0:00 | 928.0993 |  |  | 0 | -6.541%
Sylhet Area |  | 0 | 0:00 | 520.2585 |  |  | 0 | -7.299%
Barisal Area |  | 0 | 0:00 | 433.5457 |  |  | 0 | -6.468%
Rangpur Area |  | 0 | 0:00 | 847.94 |  |  | 0 | -6.478%
Total |  | 0 |  | 13018.7703 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
09:07 | 11:03 | Chowmuhani-Ramganj 132 kV Ckt-1 Forced S/D from Chowmuhani 132/33kV end.
09:07 | 11:03 | Chowmuhani-Ramganj 132 kV Ckt-2 Forced S/D from Chowmuhani 132/33kV end.
09:09 | 11:02 | Ramganj 132/33kV S/S Ramgonj-Desh Energy Ckt-02 Scheduled S/D Due to remove foreign
particle of thin wire conveyed by bird near 132kV gantry disc insulator.
10:33 | 12:19 | Coxsbazar 132/33kV S/S 415T-T2 HT Tripped showing Siemens relays Due to T-2 primay |  |  |  |  | 50.0MW load interrup.
breaker open due to T- 2 secondary breaker open.
10:33 |  | Cox's Bazar T-2 Transformer 80/120 MVA tripped due to damage to the 33kV BREAKER of the
CHOKORIA FEEDER. A 52 MW Load shed occurred.
12:00 |  | Day Peak Gen. 11258 MW
12:15 |  | Cox's Bazar T-2 Transformer 80/120 MVA was switched on. No interruption is occurring.
16:33 | 16:40 | Brahmanbaria 132/33kV S/S 403T LT Forced S/D |  |  |  |  | 16.0MW load interrup.
| 16:51 | Rajbari 132/33kV S/S Transformer-2 HT is restored.
| 16:55 | Rajbari 132/33kV S/S Transformer-2 LT is restored.
18:34 | 18:42 | Rampura 230/132kV S/S NLDC Trafo HT Forced S/D Due to Tap change
21:00 |  | Evening Peak Generation = 12,635MW
06:00 | 07:06 | Coxsbazar 132/33kV S/S 415T-T2 HT Forced S/D Due to 33 KV PDB Chakaria post insulator |  |  |  |  | 50.0MW load interrup.
damaged.
06:02 |  | Rajbari 132/33kV S/S Transformer-2 LT Project Work S/D Due to Construction of Fire wall
between T-3 and T-2.
06:04 |  | Rajbari 132/33kV S/S Transformer-2 HT Project Work S/D Due to Construction of Fire wall
between T-3 and T-2.
06:50 |  | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Forced S/D Due to Red hot maintenance |  |  |  |  | 28.0MW load interrup.
06:51 |  | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Forced S/D Due to Red hot maintenance |  |  |  |  | 28.0MW load interrup.
06:53 |  | Cumilla(N)-Shahjibazar 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing
Distance Relay(21 Trip) Zone-1 trip R phase General Trip relays.
07:00 |  | Minimum Generation is 10039 MW
07:20 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Forced S/D |  |  |  |  | 40.0MW load interrup.
07:20 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Forced S/D |  |  |  |  | 40.0MW load interrup.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-10-11
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 411 | 9684000
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10332500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 215669 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 23000 | NENP Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7708976
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 336960 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 415800
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 1283040 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 142836 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 187585 | Reserve
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 36 | 796560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 619800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 19 | 387800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 276000 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 45 | 2157818 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 114 | 1809792 | Low demand
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 716160 | Low demand
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 16 | 388800 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 1131840 | Low demand
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 644400 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 200 | 5031818 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 168000 | On test.
| Dhaka area Total |  |  |  | 5915 | 1973 | 44459154
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 21430 | Reserve
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 124875
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 38880 | Reserve
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 214 | 5166042
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5157454
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 0 | 149709 | Reserve
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 80 | 998592 | Engine problem
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 998079 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 173760 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 690720
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 264000 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20637
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1257055 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 583463 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 777810 | Reserve
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 203520 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 514364 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 35 | 423200 | Low demand
60 | SS Power I |  | SS Power | 2*612 | 1224 | 608 | 8416362 | Unit-2 S/D due to coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 15840
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 232 | 6014545 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1631 | 32010337
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 218 | 5226000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7800200
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 285 | 7639800 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 44 | 977616
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 13 | 647040 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 702545 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1069120
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 48 | 806254 | Low demand
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 228592 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1393840 | Gas shortage
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 1910400 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 68 | 1516800
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 207067 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 410830 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 1980180 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 76 | 1003800 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 1111680 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 504327
| Cumilla Area Total |  |  |  | 2917 | 1508 | 35136091
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 0 | 0 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11200
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 152 | 2961600 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 1764000 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 218000
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 154080 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 269280 | Fuel shortage
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 646 | 284 | 5378160
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 652000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3801273 | Frequency control
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 789600
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 36 | 609912 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 147504 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1380193
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1513920
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 964110 | Under maint.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 272256 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7323500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 370 | 8681000 | Machine problem.
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9329800
| Sylhet Area Total |  |  |  | 2417 | 1466 | 35465068
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 544 | 12098909
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 53280 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 92544 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 185 | 3814848 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 115680 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 586080
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 507 | 12320000 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1253 | 29081341
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1181088 | Low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 208617 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1581000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 30261500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5260170
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 126 | 2252400 | Low demand
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 7222000
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 3934
| Barisal Area Total |  |  |  | 2236 | 2084 | 47970709
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 116327 | Reserve
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 55968 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 123005 | Reserve
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 184 | 4288455 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9526181
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 89255 | Reserve
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 110286 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 48 | 364656 | Low demand
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 548832 | Reserve
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 1162368 | Low demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 23460
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1232 | 26290909
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 279750
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 541260
| Rajshahi Area Total |  |  |  | 3449 | 1956 | 43520712
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 63 | 1445236
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5472000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1642876
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29338
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 74 | 588288 | Low demand
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 193839
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1043280
| Rangpur Area Total |  |  |  | 950 | 480 | 10414857
| Total |  |  |  | 27086 | 12635 | 283436429
| Eastern Grid Total |  |  |  | 16752 | 6862 | 152448810
| Western Grid Total |  |  |  | 10334 | 5773 | 130987619
| National Grid Total |  |  |  | 27086 | 12635 | 283436429
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-10-11
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7947.23 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4141.7 | MW
i) Dhaka area |  |  | 3878.43 |  | MW | i) Khulna area |  |  |  | 1602.4 | MW
ii) Chattogram area |  |  | 1228.8 |  | MW | ii) Barishal area |  |  |  | 451.5 | MW
iii) Cumilla area |  |  | 1308 |  | MW | iii) Rajshahi area |  |  |  | 1307.8 | MW
iv) Mymensingh area |  |  | 1067 |  | MW | iv) Rangpur area |  |  |  | 780 | MW
v) Sylhet area |  |  | 465 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12088.93 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 00:00 | 67 | Jashore | 124 | 18:30 | 133 | Rajbari | 62 | 22:00
2 | AKSML | 6.7 | 16:00 | 68 | Jhenaidah | 119 | 18:00 | 134 | Rajendrapur | 84 | 00:00
3 | Aftabnagar | 42 | 12:00 | 69 | Joydebpur | 165 | 00:00 | 135 | Rajshahi | 122 | 00:00
4 | Agargaon | 91 | 13:00 | 70 | Joypurhat | 55 | 21:00 | 136 | Rajshahi-230 | 60 | 00:00
5 | Agrabad | 80 | 00:00 | 71 | Juldah | 15 | 00:00 | 137 | Ramganj | 120 | 22:00
6 | Amnura | 59 | 21:00 | 72 | KSRM | 30 | 06:00 | 138 | Rampur | 40 | 00:00
7 | Ashuganj | 91 | 01:00 | 73 | Kabirpur | 219 | 00:00 | 139 | Rangamati | 16 | 18:00
8 | BSRM | 142 | 15:00 | 74 | Kachua | 86 | 21:00 | 140 | Rangpur | 125 | 18:30
9 | Bagerhat | 80 | 22:00 | 75 | Kallyanpur | 102 | 13:00 | 141 | Ruppur | 6.8 | 12:00
10 | Bakulia | 85 | 00:00 | 76 | Kalurghat | 28 | 00:00 | 142 | SSM | 4 | 01:00
11 | Banani | 46.8 | 18:00 | 77 | Kamrangirchar | 47.4 | 00:00 | 143 | Saidpur | 89 | 18:30
12 | Bangabhaban | 5 | 11:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 122 | 23:00
13 | Barapukuria | 52 | 18:30 | 79 | Kazla | 101 | 00:00 | 145 | Satmasjid | 95 | 13:00
14 | Barguna | 22 | 00:00 | 80 | Keranigonj | 66 | 00:00 | 146 | Savar | 174 | 00:00
15 | Barishal | 99 | 00:00 | 81 | Khagrachori | 30 | 18:00 | 147 | SevenRings | 11.58 | 02:00
16 | Barishal-230 | 94 | 22:00 | 82 | Khulna | 83 | 00:00 | 148 | ShahCement | 32 | 19:00
17 | Baroaulia | 67 | 14:00 | 83 | Khulshi | 166 | 19:30 | 149 | Shahjadpur | 72 | 19:00
18 | Baroirhat | 63 | 00:00 | 84 | Kishoreganj | 150 | 00:00 | 150 | Shahjibazar | 127 | 00:00
19 | Bashundhara | 156 | 13:00 | 85 | Kodda | 242 | 11:00 | 151 | Shahmirpur | 41 | 00:00
20 | BashundharaCement | 12 | 00:00 | 86 | Kulaura | 42 | 00:00 | 152 | Shariatpur | 86 | 22:00
21 | Beanibazar | 58 | 18:00 | 87 | Kurigram | 60 | 18:30 | 153 | Sherpur | 144 | 18:30
22 | Benapole | 58 | 21:00 | 88 | Kushtia | 138 | 18:30 | 154 | Shikalbaha | 21 | 18:00
23 | Bhaluka | 126 | 01:00 | 89 | Lalbag | 82 | 00:00 | 155 | Shitalakhya | 63.8 | 13:00
24 | Bhandaria | 54 | 23:00 | 90 | Lalmonirhat | 54 | 18:30 | 156 | Sholosohor | 38 | 00:00
25 | Bhangura | 35 | 18:30 | 91 | MI_Cement | 4.4 | 23:00 | 157 | Shyampur | 138 | 00:00
26 | Bheramara(GK) | 57 | 18:30 | 92 | Madanganj | 29 | 00:00 | 158 | Siddhirganj | 94 | 00:00
27 | Bhulta | 242 | 23:00 | 93 | Madaripur | 105 | 21:00 | 159 | Sirajganj | 92 | 19:30
28 | Bog-Sherpur | 58 | 18:30 | 94 | Madartek | 71.48 | 13:00 | 160 | Sonargaon | 70 | 01:00
29 | Bogura | 143 | 00:00 | 95 | Madunaghat | 50 | 18:00 | 161 | Sreemongol | 62 | 01:00
30 | Borhanuddin | 82 | 00:00 | 96 | Magura | 61 | 18:30 | 162 | Sreepur | 65 | 00:00
31 | Brahmanbaria | 171 | 23:00 | 97 | Mahasthangarh | 80 | 23:00 | 163 | Srinagar | 46.8 | 22:00
32 | Cantonment | 98 | 12:00 | 98 | Manikganj | 122 | 21:00 | 164 | Sunamganj | 52 | 21:00
33 | Chandpur | 67 | 23:00 | 99 | Maniknagar | 54 | 13:00 | 165 | Sylhet | 40 | 00:00
34 | Chandraghona | 34 | 18:00 | 100 | Matarbari | 46 | 19:00 | 166 | Sylhet-132 | 100 | 23:00
35 | Chapai | 60 | 23:00 | 101 | Matuail | 44 | 01:00 | 167 | TK | 31.4 | 18:00
36 | Charsaidpur | 28 | 16:00 | 102 | Millgate | 95 | 00:00 | 168 | Tangail | 188 | 18:30
37 | Chauddagram | 67 | 23:00 | 103 | Mirpur | 124 | 13:00 | 169 | Thakurgaon | 89 | 18:30
38 | Chhatak | 28 | 00:00 | 104 | Mirsorai | 5 | 00:00 | 170 | Tongi | 104 | 11:00
39 | Chowmuhani | 221 | 22:00 | 105 | Mirzapur | 36 | 00:00 | 171 | Ullahpara | 23 | 18:00
40 | Chuadanga | 105 | 19:00 | 106 | Mithapukur | 54 | 18:30 | 172 | Ullon | 51 | 14:00
41 | Coxsbazar | 117 | 00:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 73 | 18:00
42 | Cumilla(N) | 172 | 21:00 | 108 | Mogbazar | 81.1 | 18:00 | 174 | UttaraNew | 46 | 13:00
43 | Cumilla(S) | 151 | 23:00 | 109 | Mongla | 44 | 00:00 | 175 | Zigatola | 87 | 13:00
44 | Daudkandi | 133 | 19:30 | 110 | Motijheel | 34 | 12:00
45 | Dhaka | 24 | 09:00 | 111 | Munshiganj | 160 | 23:00
46 | Dhamrai | 114 | 00:00 | 112 | Mymensingh | 204 | 00:00
47 | Dhanmondi | 96 | 18:00 | 113 | Naogaon | 121 | 23:00
48 | Dohazari | 98 | 21:00 | 114 | Narail | 56 | 18:30
49 | Faridpur | 153 | 17:00 | 115 | Narinda | 47.5 | 13:00
50 | Fatullah | 91 | 00:00 | 116 | Narshingdi | 162 | 20:00
51 | Fenchuganj | 37 | 01:00 | 117 | Natore | 133 | 19:30
52 | Feni | 98 | 22:00 | 118 | Nawabganj | 46.6 | 22:00
53 | GPH | 3 | 00:00 | 119 | Netrakona | 98 | 17:00
54 | Ghatail | 68 | 18:30 | 120 | New | 39 | 00:00
55 | Ghorashal | 57 | 00:00 | 121 | Niamatpur | 63 | 22:00
56 | Goalpara | 30 | 00:00 | 122 | Noapara | 37 | 00:00
57 | Gollamari | 62 | 00:00 | 123 | PHP | 6 | 17:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-10-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 391 | 17:00 | 378 | 00:00 | Kaliakoir | 381 | 17:00 | 367 | 04:00
| Ashuganj | 412 | 17:00 | 399 | 4:00 | Madunaghat | 397 | 18:00 | 390 | 07:00
| Bhulta | 405 | 17:00 | 393 | 00:00 | Meghnaghat | 389 | 17:00 | 376 | 00:00
| Bibiana | 401 | 17:00 | 389 | 01:00 | Payra | 414 | 17:00 | 405 | 00:00
| BIPTC | 409 | 08:00 | 400 | 23:00 | Rahanpur | 393 | 09:00 | 381 | 20:00
| Bogura | 380 | 17:00 | 372 | 19:00 | Rampal | 407 | 17:00 | 390 | 00:00
| Gopalganj | 401 | 17:00 | 388 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 17:00 | 228 | 00:00 | Haripur | 234 | 17:00 | 226 | 00:00
| AKSML | 238 | 03:00 | 231 | 06:00 | Hasnabad | 237 | 17:00 | 226 | 00:00
| Aminbazar | 236 | 17:00 | 228 | 00:00 | Hathazari | 240 | 16:00 | 234 | 10:00
| Ashuganj | 236 | 18:30 | 229 | 00:00 | Ishurdi | 236 | 17:00 | 225 | 22:00
| Ashuganj-400 | 234 | 21:00 | 230 | 4:00 | Jhenaidah | 230 | 17:00 | 216 | 00:00
| Baghabari | 229 | 16:00 | 222 | 21:00 | Kaliakoir | 238 | 17:00 | 228 | 04:00
| Barapukuria | 221 | 00:00 | 217 | 01:00 | Keranigonj | 235 | 17:00 | 227 | 00:00
| Barapukuria-230 | 221 | 16:00 | 217 | 20:00 | Khulna(S) | 232 | 17:00 | 218 | 22:00
| Barishal | 238 | 17:00 | 230 | 00:00 | Madunaghat | 239 | 18:00 | 234 | 07:00
| Bheramara | 235 | 17:00 | 224 | 21:00 | Maniknagar | 234 | 17:00 | 227 | 00:00
| Bhulta | 238 | 17:00 | 228 | 00:00 | Meghnaghat | 240 | 18:30 | 235 | 00:00
| Bibiana | 229 | 17:00 | 222 | 00:00 | Meghnaghat-400 | 238 | 17:00 | 223 | 23:00
| BIPTC | 235 | 17:00 | 222 | 20:00 | Mirsorai | 236 | 17:00 | 231 | 06:00
| Bogura | 230 | 17:00 | 223 | 20:00 | Rajshahi | 234 | 17:00 | 222 | 21:00
| Bogura-400 | 232 | 12:00 | 227 | 19:00 | Rampal | 233 | 17:00 | 218 | 00:00
| Borhanuddin | 239 | 08:00 | 235 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 237 | 17:00 | 231 | 07:00 | Rampura | 236 | 17:00 | 228 | 00:00
| Cumilla(N) | 234 | 17:00 | 225 | 00:00 | Shikalbaha | 237 | 17:00 | 231 | 06:00
| Faridpur | 233 | 09:00 | 227 | 00:00 | Shyampur | 236 | 17:00 | 228 | 00:00
| Fenchuganj | 232 | 16:00 | 29 | 18:00 | Siddhirganj | 237 | 17:00 | 229 | 00:00
| Ghorashal | 232 | 04:00 | 230 | 00:00 | Sirajgonj | 239 | 17:00 | 233 | 20:00
| Ghorashal-230 | 236 | 17:00 | 227 | 00:00 | Sreepur | 233 | 17:00 | 225 | 00:00
| Gopalganj | 237 | 17:00 | 229 | 00:00 | Tongi | 237 | 17:00 | 227 | 11:00
| GPH | 238 | 17:00 | 232 | 07:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 164 | 06:00 | 132 | 18:00 | Kushtia | 136 | 17:00 | 127 | 22:00
| Agargaon | 139 | 17:00 | 134 | 00:00 | Lalbag | 137 | 17:00 | 130 | 00:00
| Agrabad | 136 | 17:00 | 132 | 10:00 | Lalmonirhat | 130 | 00:00 | 125 | 18:00
| AKS | 134 | 13:00 | 130 | 04:00 | Madanganj | 131 | 17:00 | 125 | 01:00
| Aminbazar | 142 | 17:00 | 130 | 02:00 | Madaripur | 134 | 17:00 | 128 | 00:00
| Amnura | 137 | 17:00 | 121 | 22:00 | Madartek | 136 | 17:00 | 131 | 18:00
| Ashuganj | 140 | 17:00 | 136 | 00:00 | Madunaghat | 138 | 13:00 | 133 | 07:00
| Bagerhat | 136 | 17:00 | 122 | 00:00 | Magura | 137 | 17:00 | 125 | 22:00
| Bakulia | 136 | 17:00 | 133 | 10:00 | Mahasthangarh | 136 | 13:00 | 131 | 19:30
| Banani | 137 | 17:00 | 130 | 18:00 | Manikganj | 130 | 17:00 | 122 | 01:00
| Bangabhaban | 132 | 18:00 | 128 | 00:00 | Maniknagar | 133 | 17:00 | 128 | 00:00
| Barapukuria | 137 | 00:00 | 134 | 12:00 | Matarbari | 126 | 17:00 | 118 | 20:00
| Barguna | 140 | 17:00 | 133 | 11:00 | Matuail | 133 | 17:00 | 127 | 00:00
| Barishal | 134 | 17:00 | 127 | 00:00 | Millgate | 137 | 17:00 | 131 | 11:00
| Barishal-230 | 135 | 17:00 | 128 | 00:00 | Mirpur | 141 | 17:00 | 135 | 00:00
| Baroaulia | 137 | 17:00 | 132 | 07:00 | Mirzapur | 131 | 17:00 | 122 | 01:00
| Baroirhat | 132 | 17:00 | 121 | 03:00 | Mithapukur | 133 | 00:00 | 130 | 11:00
| Bashundhara | 138 | 17:00 | 131 | 12:00 | MI_Cement | 139 | 17:00 | 133 | 00:00
| BashundharaCement | 131 | 17:00 | 125 | 01:00 | Modern | 136 | 17:00 | 132 | 10:00
| Beanibazar | 131 | 17:00 | 123 | 01:00 | Mogbazar | 138 | 17:00 | 133 | 13:00
| Benapole | 136 | 17:00 | 123 | 22:00 | Mongla | 135 | 17:00 | 120 | 00:00
| Bhaluka | 129 | 09:00 | 123 | 00:00 | Motijheel | 132 | 18:00 | 128 | 00:00
| Bhandaria | 129 | 17:00 | 121 | 00:00 | Munshiganj | 130 | 18:30 | 125 | 00:00
| Bhangura | 138 | 17:00 | 132 | 22:00 | Mymensingh | 134 | 17:00 | 119 | 00:00
| Bheramara | 136 | 17:00 | 130 | 22:00 | Naogaon | 135 | 17:00 | 120 | 19:30
| Bheramara(GK) | 137 | 17:00 | 130 | 00:00 | Narail | 137 | 17:00 | 125 | 23:00
| Bhulta | 127 | 21:00 | 118 | 00:00 | Narinda | 133 | 17:00 | 128 | 00:00
| Bog-Sherpur | 137 | 16:00 | 132 | 19:30 | Narshingdi | 126 | 17:00 | 116 | 02:00
| Bogura | 139 | 13:00 | 133 | 20:00 | Natore | 136 | 17:00 | 129 | 20:00
| Bogura-230 | 139 | 17:00 | 133 | 20:00 | Nawabganj | 137 | 17:00 | 131 | 00:00
| Brahmanbaria | 136 | 17:00 | 125 | 00:00 | Netrakona | 136 | 18:30 | 123 | 07:00
| Cantonment | 139 | 17:00 | 133 | 12:00 | New | 137 | 18:00 | 132 | 11:00
| Chandpur | 131 | 17:00 | 123 | 15:00 | Niamatpur | 131 | 08:00 | 125 | 19:30
| Chandraghona | 137 | 17:00 | 134 | 10:00 | Noapara | 137 | 17:00 | 125 | 23:00
| Chapai | 130 | 17:00 | 123 | 20:00 | Pabna | 136 | 17:00 | 129 | 22:00
| Charsaidpur | 131 | 17:00 | 126 | 00:00 | Palashbari | 132 | 03:00 | 127 | 20:00
| Chauddagram | 130 | 17:00 | 121 | 23:00 | Panchagarh | 136 | 23:00 | 123 | 12:00
| Chhatak | 131 | 17:00 | 122 | 00:00 | Patuakhali | 140 | 17:00 | 134 | 07:00
| Chowmuhani | 131 | 17:00 | 117 | 23:00 | Payra | 139 | 17:00 | 135 | 11:00
| Chuadanga | 132 | 16:00 | 115 | 23:00 | PHP | 132 | 17:00 | 121 | 22:00
| Coxsbazar | 127 | 11:00 | 120 | 00:00 | Postogola | 140 | 17:00 | 134 | 00:00
| Cumilla(N) | 135 | 17:00 | 127 | 01:00 | Purbachal | 137 | 17:00 | 131 | 11:00
| Cumilla(S) | 133 | 17:00 | 16 | 10:00 | Purbasadipur | 131 | 22:00 | 123 | 12:00
| Daudkandi | 131 | 17:00 | 123 | 23:00 | Rahanpur | 133 | 08:00 | 128 | 20:00
| Dhaka | 138 | 17:00 | 133 | 00:00 | Rahim | 132 | 17:00 | 127 | 00:00
| Dhamrai | 135 | 17:00 | 129 | 05:00 | Rajbari | 132 | 17:00 | 125 | 00:00
| Dhanmondi | 138 | 17:00 | 132 | 18:00 | Rajendrapur | 130 | 18:00 | 120 | 05:00
| Dohazari | 134 | 17:00 | 128 | 00:00 | Rajshahi | 135 | 17:00 | 128 | 22:00
| Faridpur | 132 | 16:00 | 127 | 19:30 | Rajshahi-230 | 137 | 17:00 | 118 | 20:00
| Fatullah | 138 | 17:00 | 132 | 00:00 | Ramganj | 129 | 17:00 | 118 | 02:00
| Fenchuganj | 140 | 17:00 | 131 | 02:00 | Rampur | 135 | 17:00 | 132 | 07:00
| Feni | 132 | 17:00 | 121 | 23:00 | Rampura | 137 | 17:00 | 131 | 18:00
| Ghatail | 131 | 17:00 | 122 | 01:00 | Rangamati | 137 | 17:00 | 133 | 10:00
| Ghorashal | 138 | 20:00 | 135 | 00:00 | Rangpur | 132 | 00:00 | 127 | 19:00
| Goalpara | 139 | 17:00 | 127 | 00:00 | Ruppur | 137 | 15:00 | 130 | 00:00
| Gollamari | 138 | 17:00 | 129 | 00:00 | Saidpur | 133 | 00:00 | 126 | 19:30
| Gopalganj | 134 | 17:00 | 126 | 22:00 | Satkhira | 135 | 17:00 | 122 | 22:00
| Gopalganj-400 | 133 | 17:00 | 128 | 00:00 | Satmasjid | 138 | 17:00 | 133 | 00:00
| Gulshan | 137 | 17:00 | 131 | 18:00 | Savar | 141 | 17:00 | 133 | 11:00
| Halishahar | 136 | 17:00 | 132 | 02:00 | SevenRings | 141 | 17:00 | 135 | 00:00
| Haripur | 132 | 17:00 | 127 | 00:00 | ShahCement | 131 | 17:00 | 126 | 00:00
| HaripurSBU | 132 | 17:00 | 127 | 00:00 | Shahjadpur | 142 | 17:00 | 136 | 20:00
| Hasnabad | 140 | 17:00 | 134 | 00:00 | Shahjibazar | 137 | 17:00 | 125 | 00:00
| Hathazari | 139 | 18:30 | 135 | 15:00 | Shahmirpur | 137 | 17:00 | 134 | 03:00
| Ishurdi | 136 | 08:00 | 132 | 00:00 | Shariatpur | 133 | 17:00 | 125 | 23:00
| Jaldhaka | 130 | 00:00 | 125 | 07:00 | Sherpur | 137 | 09:00 | 121 | 18:00
| Jamalpur | 138 | 08:00 | 126 | 18:00 | Shikalbaha | 126 | 17:00 | 120 | 08:00
| Jashore | 136 | 17:00 | 124 | 22:00 | Shikalbaha-230 | 137 | 17:00 | 133 | 10:00
| Jhenaidah | 137 | 17:00 | 126 | 22:00 | Shitalakhya | 139 | 17:00 | 133 | 00:00
| Jhenaidah-230 | 137 | 17:00 | 128 | 00:00 | Sholosohor | 136 | 17:00 | 132 | 07:00
| Joydebpur | 140 | 17:00 | 130 | 02:00 | Shyampur | 134 | 08:00 | 130 | 11:00
| Joypurhat | 127 | 08:00 | 118 | 19:30 | Shyampur-230 | 138 | 17:00 | 132 | 00:00
| Juldah | 135 | 00:00 | 133 | 07:00 | Siddhirganj | 133 | 17:00 | 127 | 00:00
| Kabirpur | 136 | 17:00 | 125 | 03:00 | Sirajganj | 137 | 17:00 | 129 | 20:00
| Kachua | 132 | 17:00 | 122 | 02:00 | Sonargaon | 132 | 17:00 | 125 | 00:00
| Kaliakoir | 135 | 19:00 | 128 | 11:00 | Sreemongol | 136 | 17:00 | 126 | 01:00
| Kallyanpur | 134 | 17:00 | 128 | 00:00 | Sreepur | 132 | 17:00 | 126 | 00:00
| Kalurghat | 135 | 00:00 | 133 | 07:00 | Srinagar | 136 | 18:30 | 131 | 00:00
| Kamrangirchar | 137 | 17:00 | 127 | 00:00 | SSM | 140 | 00:00 | 136 | 05:00
| Kaptai | 138 | 17:00 | 135 | 15:00 | Sunamganj | 130 | 17:00 | 121 | 21:00
| Kazla | 132 | 18:00 | 128 | 00:00 | Sylhet | 133 | 17:00 | 126 | 00:00
| Keranigonj | 138 | 17:00 | 132 | 00:00 | Sylhet-132 | 133 | 17:00 | 126 | 00:00
| Khagrachori | 135 | 17:00 | 132 | 10:00 | Tangail | 129 | 17:00 | 118 | 18:00
| Khulna | 138 | 17:00 | 127 | 23:00 | Thakurgaon | 136 | 00:00 | 121 | 12:00
| Khulna(S) | 139 | 17:00 | 128 | 22:00 | TK | 137 | 17:00 | 133 | 06:00
| Khulshi | 135 | 17:00 | 131 | 04:00 | Tongi | 140 | 17:00 | 133 | 11:00
| Kishoreganj | 133 | 19:00 | 125 | 00:00 | Ullahpara | 138 | 17:00 | 131 | 19:30
| Kodda | 139 | 17:00 | 122 | 00:00 | Ullon | 138 | 17:00 | 133 | 00:00
| KSRM | 138 | 17:00 | 132 | 05:00 | Uttara | 140 | 17:00 | 134 | 11:00
| Kulaura | 138 | 17:00 | 129 | 00:00 | UttaraNew | 141 | 18:30 | 135 | 11:00
| Kurigram | 131 | 01:00 | 126 | 07:00 | Zigatola | 136 | 17:00 | 131 | 00:00

## L-Curve
Date | 2024-10-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 982 | 6592 | 6110 | 12702 |  |  |  | QF-LDC-11
0:30 | 778 | 6741 | 5802.5 | 12543.5 | Date: | 2024-10-11
1:00 | 574 | 6890 | 5495 | 12385
1:30 | 571 | 6792 | 5517 | 12309
2:00 | 568 | 6694 | 5539 | 12233
2:30 | 555 | 6568.5 | 5426 | 11994.5 | [5 empty] | Gen. at Eve. Peak | 12635 | 12635 MW (21:00 )
3:00 | 542 | 6443 | 5313 | 11756 | [6 empty] | 21:00
3:30 | 544 | 6321 | 5287.5 | 11608.5 | [5 empty] | Gen. at Day Peak | 11253 | 11253 MW (12:00 )
4:00 | 546 | 6199 | 5262 | 11461 | [6 empty] | 12:00
4:30 | 584 | 6079 | 5263.5 | 11342.5 | [5 empty] | Highest Generation | 12798
5:00 | 622 | 5959 | 5265 | 11224 | [6 empty] | 23:00
5:30 | 703 | 5835 | 5176.5 | 11011.5
6:00 | 784 | 5711 | 5088 | 10799
6:30 | 726 | 5693 | 4970 | 10663
7:00 | 668 | 5675 | 4852 | 10527
7:30 | 711 | 5625 | 4909 | 10534
8:00 | 754 | 5575 | 4966 | 10541
8:30 | 832 | 5589.5 | 4972.5 | 10562
9:00 | 910 | 5604 | 4979 | 10583
9:30 | 965 | 5584 | 5009.5 | 10593.5
10:00 | 1020 | 5564 | 5040 | 10604
10:30 | 987 | 5651.5 | 5082 | 10733.5
11:00 | 954 | 5739 | 5124 | 10863
11:30 | 915 | 5866 | 5192 | 11058
12:00 | 876 | 5993 | 5260 | 11253
12:30 | 775 | 6301 | 5343.5 | 11644.5
13:00 | 674 | 6609 | 5427 | 12036
13:30 | 695 | 6407.5 | 5345.5 | 11753
14:00 | 716 | 6206 | 5264 | 11470
14:30 | 750 | 6265 | 5307.5 | 11572.5
15:00 | 784 | 6324 | 5351 | 11675
15:30 | 754 | 6244 | 5147.5 | 11391.5
16:00 | 724 | 6164 | 4944 | 11108
16:30 | 707 | 6019.5 | 4800.5 | 10820
17:00 | 690 | 5875 | 4657 | 10532
17:30 | 617 | 6279.5 | 4981 | 11260.5
18:00 | 544 | 6684 | 5305 | 11989
18:30 | 504 | 6800 | 5453.5 | 12253.5
19:00 | 464 | 6916 | 5602 | 12518
19:30 | 362 | 6946 | 5527 | 12473
20:00 | 380 | 6969 | 5568 | 12537 |  |  |  | Executive Engineer
20:30 | 447 | 6915.5 | 5670.5 | 12586 |  |  |  | Network Operation Division
21:00 | 514 | 6862 | 5773 | 12635
21:30 | 573 | 6816.5 | 5818.5 | 12635
22:00 | 632 | 6771 | 5864 | 12635 |  |  |  |  | Page 6 of 7
22:30 | 738 | 6750.5 | 5966 | 12716.5
23:00 | 844 | 6730 | 6068 | 12798
23:30 | 913 | 6661 | 6089 | 12750
24:00 | 982 | 6592 | 6110 | 12702
12635 MW (21:00 )
11253 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-10-11 |  | Energy |  | 283436429
[16 empty] | 2024-10-11 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3322 | 886 | 1970 | 0 | 1879 | 2885 | 215 | 0 | 244 | 82 | 1219 | 0 | 0 | 103
0:30 | 3349.5 | 682 | 1927 | 0 | 1876.5 | 2948.5 | 215 | 0 | 340.5 | 79 | 1125.5 | 0 | 0 | 240.1125 |  |  | Date: | 44114
1:00 | 3377 | 478 | 1884 | 0 | 1874 | 3012 | 215 | 0 | 437 | 76 | 1032 | 0 | 0 | 377.225
1:30 | 3370.5 | 478 | 1901 | 0 | 1800.5 | 3009.5 | 215 | 0 | 425 | 75 | 1034.5 | 0 | 0 | 292.23 | [8 empty] | Total Energy | 283.4364 | 283.4364 | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 3364 | 478 | 1918 | 0 | 1727 | 3007 | 215 | 0 | 413 | 74 | 1037 | 0 | 0 | 207.235 | [8 empty] | Energy not Served | 1.6555 | 1.6555
2:30 | 3376.5 | 478 | 1918 | 0 | 1606.5 | 2984 | 215 | 0 | 301 | 74 | 1041.5 | 0 | 0 | 210.5775 | [8 empty] | Energy Requirement | 285.092 | 285.092
3:00 | 3389 | 478 | 1918 | 0 | 1486 | 2961 | 215 | 0 | 189 | 74 | 1046 | 0 | 0 | 213.92
3:30 | 3389 | 477 | 1928 | 0 | 1380 | 2945.5 | 215 | 0 | 163.5 | 72 | 1038.5 | 0 | 0 | 197.2075 | [7 empty] | Shortage
4:00 | 3389 | 476 | 1938 | 0 | 1274 | 2930 | 215 | 0 | 138 | 70 | 1031 | 0 | 0 | 180.495
4:30 | 3382.5 | 476 | 1948 | 0 | 1213.5 | 2916.5 | 215 | 0 | 93.5 | 67 | 1030.5 | 0 | 0 | 174.2875
5:00 | 3376 | 476 | 1958 | 0 | 1153 | 2903 | 215 | 0 | 49 | 64 | 1030 | 0 | 0 | 168.08
5:30 | 3331.5 | 476 | 1959.5 | 0 | 993 | 2898.5 | 214.5 | 0 | 49 | 57 | 1032 | 0.5 | 0 | 165.6925
6:00 | 3287 | 476 | 1961 | 0 | 833 | 2894 | 214 | 0 | 49 | 50 | 1034 | 1 | 0 | 163.305
6:30 | 3330.5 | 476 | 1927 | 0 | 730.5 | 2822.5 | 213.5 | 0 | 40.5 | 53 | 1032.5 | 37 | 0 | 149.935 | [6 empty] | Coal
7:00 | 3374 | 476 | 1893 | 0 | 628 | 2751 | 213 | 0 | 32 | 56 | 1031 | 73 | 0 | 136.565
7:30 | 3277.5 | 476 | 1920 | 0 | 636 | 2736 | 213 | 0 | 32 | 56 | 1031 | 156.5 | 0 | 129.88 | [5 empty] | Oil
8:00 | 3181 | 476 | 1947 | 0 | 644 | 2721 | 213 | 0 | 32 | 56 | 1031 | 240 | 0 | 123.195
8:30 | 3144.5 | 476 | 1921 | 0 | 657 | 2712 | 213 | 0 | 40 | 56 | 1029 | 313.5 | 0 | 61.5975
9:00 | 3108 | 476 | 1895 | 0 | 670 | 2703 | 213 | 0 | 48 | 56 | 1027 | 387 | 0 | 0
9:30 | 3084.5 | 476 | 1901.5 | 0 | 647 | 2688.5 | 213 | 0 | 48 | 56 | 1030.5 | 448.5 | 0 | 0
10:00 | 3061 | 476 | 1908 | 0 | 624 | 2674 | 213 | 0 | 48 | 56 | 1034 | 510 | 0 | 0
10:30 | 3086.5 | 476.5 | 1967.5 | 0 | 648.5 | 2652.5 | 213 | 0 | 48 | 56 | 1031 | 554 | 0 | 0
11:00 | 3112 | 477 | 2027 | 0 | 673 | 2631 | 213 | 0 | 48 | 56 | 1028 | 598 | 0 | 0
11:30 | 3099.5 | 477 | 2004.5 | 0 | 807.5 | 2708 | 213.5 | 0 | 83.5 | 57 | 1032 | 575.5 | 0 | 0
12:00 | 3087 | 477 | 1982 | 0 | 942 | 2785 | 214 | 0 | 119 | 58 | 1036 | 553 | 0 | 0
12:30 | 3145.5 | 477 | 1997.5 | 0 | 1160.5 | 2845 | 214 | 0 | 167.5 | 61 | 1035 | 541.5 | 0 | 0
13:00 | 3204 | 477 | 2013 | 0 | 1379 | 2905 | 214 | 0 | 216 | 64 | 1034 | 530 | 0 | 0
13:30 | 3204 | 477 | 2013 | 0 | 1379 | 2905 | 214 | 0 | 216 | 64 | 1034 | 530 | 0 | 0
14:00 | 3204 | 477 | 2013 | 0 | 1379 | 2905 | 214 | 0 | 216 | 64 | 1034 | 530 | 0 | 0
14:30 | 3208.5 | 478.5 | 2070 | 0 | 1288 | 2896.5 | 214.5 | 0 | 190 | 64 | 1034.5 | 408 | 3 | 0
15:00 | 3213 | 480 | 2127 | 0 | 1197 | 2888 | 215 | 0 | 164 | 64 | 1035 | 286 | 6 | 0
15:30 | 3194 | 480 | 2046.5 | 0 | 1180 | 2791.5 | 215 | 0 | 160.5 | 61 | 1035 | 223.5 | 4.5 | 0
16:00 | 3175 | 480 | 1966 | 0 | 1163 | 2695 | 215 | 0 | 157 | 58 | 1035 | 161 | 3 | 0
16:30 | 3094 | 480 | 1833.5 | 0 | 1214.5 | 2585.5 | 215 | 0 | 162.5 | 57 | 1083 | 93.5 | 1.5 | 0
17:00 | 3013 | 480 | 1701 | 0 | 1266 | 2476 | 215 | 0 | 168 | 56 | 1131 | 26 | 0 | 0
17:30 | 3153.5 | 480 | 1848.5 | 0 | 1437.5 | 2595 | 215.5 | 0 | 272.5 | 61 | 1184 | 13 | 0 | 0
18:00 | 3294 | 480 | 1996 | 0 | 1609 | 2714 | 216 | 0 | 377 | 66 | 1237 | 0 | 0 | 0
18:30 | 3277.5 | 480 | 1956.5 | 0 | 1680 | 2908.5 | 216 | 0 | 429 | 66 | 1240 | 0 | 0 | 0
19:00 | 3261 | 480 | 1917 | 0 | 1751 | 3103 | 216 | 0 | 481 | 66 | 1243 | 0 | 0 | 0
19:30 | 3290 | 480 | 1965 | 0 | 1751 | 3144 | 215 | 0 | 310 | 68 | 1250 | 0 | 0 | 0
20:00 | 3336 | 490 | 1957 | 0 | 1735 | 3163 | 215 | 0 | 315 | 68 | 1258 | 0 | 0 | 0
20:30 | 3303.5 | 517 | 1980 | 0 | 1766 | 3177 | 214.5 | 0 | 315 | 68 | 1245 | 0 | 0 | 0
21:00 | 3271 | 544 | 2003 | 0 | 1797 | 3191 | 214 | 0 | 315 | 68 | 1232 | 0 | 0 | 0
21:30 | 3314 | 566 | 2018.5 | 0 | 1842.5 | 3094 | 214 | 0 | 288.5 | 69 | 1228.5 | 0 | 0 | 0
22:00 | 3357 | 588 | 2034 | 0 | 1888 | 2997 | 214 | 0 | 262 | 70 | 1225 | 0 | 0 | 0
22:30 | 3355.5 | 651.5 | 2079 | 0 | 1908 | 2940.5 | 214.5 | 0 | 262 | 73 | 1232.5 | 0 | 0 | 0
23:00 | 3354 | 715 | 2124 | 0 | 1928 | 2884 | 215 | 0 | 262 | 76 | 1240 | 0 | 0 | 0
23:30 | 3338 | 800.5 | 2047 | 0 | 1903.5 | 2884.5 | 215 | 0 | 253 | 79 | 1229.5 | 0 | 0 | 51.5 |  |  | Max Temp. in Dhaka |  | 34.0°C
24:00 | 3322 | 886 | 1970 | 0 | 1879 | 2885 | 215 | 0 | 244 | 82 | 1219 | 0 | 0 | 103
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on X13: Author:

## Generation
2024-10-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 135 | 135 | 135 | 135 | 135 | 134 | 133 | 133 | 133 | 133 | 133 | 134 | 134 | 134 | 135 | 135 | 135 | 136 |  | 136 | 135 | 135 | 134 | 134 | 135 | 135 | 3238042
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1928000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | [23 empty] | 0 | 21430
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 11 | 15 | 17 | 5 | 9 | 19 | 17 | 12 | 3 | 1 | [9 empty] | 124875
6 | Sikalbaha 225MW CCPP (Gas) | 227 | 228 | 228 | 227 | 227 | 227 | 227 | 227 | 226 | 223 | 219 | 219 | 218 | 215 | 215 | 206 | 205 | 200 |  | 197 | 197 | 224 | 225 | 225 | 222 | 222 | 5157454
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 68 | 17 | [7 empty] | 35 | 68 | 68 | 68 | 63 | 70 | 85 |  | 57 | 53 | 51 | 51 | 51 | 51 | 51 | 998079
12 | Hathazari 100 MW peaking PP | 72 | 72 | 72 | 72 | [8 empty] | 48 | 48 | 48 | 46 | 46 | 53 |  | 80 | 73 | 80 | 80 | 64 | 64 | 64 | 998592
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 8 | 17 | [12 empty] | 17 | 149709
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 30 | 30 | [15 empty] | 31 |  | 36 | 36 | 36 | 37 |  |  | 0 | 228592
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 280 | 280 | 280 | 280 | 280 | 325 | 280 | 327 | 324 | 270 | 327 |  | 333 | 332 | 328 | 335 | 335 | 335 | 335 | 7708976
18 | Kodda 300 MW PP Unit-2 (Summit) | 290 | 294 | 195 | 95 | [7 empty] | 17 | 95 | 95 | 95 | 95 | 95 | 142 |  | 45 | 45 | 45 | 45 | 45 | 50 | 125 | 2157818
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 45 | 45 | 83 | 83 | 83 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 702545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 310 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 440 |  | 600 | 612 | 612 | 608 | 424 | 300 | 300 | 8416362
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 40 | 39 | 36 | 40 | 36 | 34 | 39 | 39 | 38 | 43 |  | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 977616
33 | Ashuganj 225 MW CCPP | 217 | 216 | 215 | 216 | 215 | 217 | 214 | 220 | 215 | 212 | 216 | 211 | 216 | 209 | 211 | 214 | 217 | 213 |  | 219 | 215 | 214 | 218 | 215 | 216 | 217 | 5226000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 315 | 315 | 315 | 320 | 315 | 360 | 285 | 285 | 285 | 310 | 285 | 310 | 345 | 315 | 310 | 300 | 357 |  | 310 | 325 | 345 | 285 | 320 | 315 | 285 | 7800200
| Ashuganj 420 MW CCPP(East) | 295 | 295 | 295 | 295 | 295 | 295 | 375 | 290 | 290 | 290 | 315 | 290 | 320 | 370 | 320 | 285 | 285 | 380 |  | 330 | 335 | 340 | 285 | 360 | 350 | 330 | 7639800
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 13 | 10 | 10 | 10 | 647040
36 | Chandpur 150 MW CCPP | 70 | 50 | 70 | 70 | 80 | 80 | 80 | 80 | 50 | 50 | 51 | 51 | 51 | 51 | 51 | 70 | 70 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1393840
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 401 | 401 | 405 | 406 | 406 | 406 | 380 | 398 | 411 | 385 | 387 | 401 | 394 | 354 | 380 | 405 | 397 | 400 |  | 411 | 412 | 409 | 411 | 410 | 407 | 399 | 9684000
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 215 | 215 | 215 | 215 | 215 | 215 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 5031818
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 450 | 450 | 350 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 380 | 10332500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 4 | 15 | 23 | 19 | 44 | 19 | 19 | 33 | 25 | 5 | 0 | [9 empty] | 218000
44 | Fenchugonj CCPP Phase-1 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 652000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 59 | 60 | 58 | 61 | 61 | 60 | 60 | 60 | 60 | 60 | 61 | 62 | 40 | 58 |  | 60 | 59 | 59 | 60 | 59 | 59 | 60 | 1380193
48 | Shahjibazar 86 MW PP (Shahjibazar) | 31 | 31 | 31 | 31 | 31 | 31 | 51 | 61 | 61 | 61 | 85 | 85 | 85 | 85 | 85 | 83 | 83 | 83 |  | 83 | 83 | 83 | 83 | 83 | 81 | 81 | 1513920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 137 | 137 | 138 | 64 | 64 | 64 | [17 empty] | 20 | 964110
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 147504
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 5 | 5 | 25 | 25 | 25 | 25 | 25 | 25 | 51 | 52 | 52 | 52 | 52 | 50 | 31 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 789600
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 4 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 272256
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 280 | 290 | 300 | 305 | 290 | 305 | 300 | 290 | 295 | 315 | 300 | 310 | 290 | 320 | 280 | 285 | 290 |  | 275 | 310 | 300 | 300 | 310 | 335 | 295 | 7323500
| Bibiyana South 400 MW | 394 | 397 | 394 | 394 | 394 | 400 | 386 | 400 | 400 | 388 | 386 | 389 | 392 | 375 | 394 | 400 | 388 | 387 |  | 392 | 392 | 388 | 400 | 390 | 390 | 394 | 9329800
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | [9 empty] | 17 | 17 |  |  |  | 5 | 17 | [6 empty] | 13 | 17 | 187585
59 | Tangail Palli Power Gen 22 MW | [15 empty] | 6 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 154080
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 76 | 74 | 74 | 70 | 64 | 50 | 56 | 56 | 56 | 56 | 56 | 58 | 64 | 64 | 64 | 58 | 56 | 66 |  | 66 | 68 | 68 | 68 | 70 | 76 | 82 | 1516800
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 26 | 37 | 38 | 38 | 40 | 34 | 26 | 10 | 10 | 10 | 20 | 23 | 19 | 19 | 25 | 28 |  | 30 | 30 | 30 | 30 | 42 | 42 | 42 | 690720
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 410830
69 | Summit Ashulia | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 14 | 14 | 16 | 15 | 15 | 13 | 14 |  | 14 | 11 | 11 | 15 |  | 17 | 17 | 324600
70 | Summit Madhabdi | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 14 | 14 | 20 |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 471960
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 619800
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 16 | 16 | 18 | 19 | 19 | 18 | 18 | 18 |  | 18 | 18 | 18 | 19 | 20 | 22 | 23 | 387800
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 106 | 106 | 106 | 106 | 106 | 88 | 70 | 70 | 70 | 70 | 70 | 70 | 102 | 106 | 106 | 106 | 106 | 70 |  | 52 | 34 | 34 | 34 | 70 | 70 | 70 | 1980180
| Chowmuhani 113 MW | 28 | 28 | 29 | 28 | 28 | 28 | 28 | 29 | 28 | 28 | 30 | 32 | 29 | 28 | 28 | 23 | 39 | 75 |  | 75 | 75 | 77 | 76 | 75 | 78 | 45 | 1003800
| Manikgonj 162MW PP(MPGL) | 72 | 54 | 54 | 17 | 17 | 17 | [5 empty] | 35 | 90 | 35 | 72 | 72 | 72 | 96 |  | 108 | 54 | 54 | 54 | 54 | 100 | 108 | 1131840
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 276000
79 | Kodda 150 MW PP | 64 | 64 | 32 | 32 | 32 | 32 | 32 | 32 | 48 | 48 | 48 | 48 | 64 | 64 | 48 | 48 | 48 | 80 |  | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 1283040
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 |  | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 207067
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 17 | 17 | 52 | 52 | 52 | 34 | 34 | 34 | 34 |  | 52 | 34 | 34 | 34 | 34 | 34 | 34 | 716160
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 2 | 5 | 1 | 1 | 2 | 2 | 1 | [10 empty] | 20637
| Jodiac Power | [7 empty] | 9 | 29 | 35 | 35 | 35 | 35 | 17 | 22 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 583463
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 17 | [5 empty] | 15 | 63 | [12 empty] | 21 | 777810
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 13 | 12 | [23 empty] | 0 | 23000
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 17 | 16 | 16 | 16 | 16 | 16 | 388800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 15 | 21 | 25 | 25 | 25 | 25 | 33 | 32 | 32 | 32 | 35 | 35 | 33 |  | 33 | 33 | 35 | 36 | 36 | 36 | 36 | 609912
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 | 18 |  | 37 | 51 | 51 | 51 | 51 | 51 | 51 | 1069120
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 33 | 50 | 50 | 50 | 50 | 8 | 8 | 336960
95 | Patenga 50MW PP (Baraka) | 19 | [18 empty] | 0 | [5 empty] | 0 | 38880
96 | Chattogram 108 MW PP (ECPV) | 31 | 26 | 25 | 25 | 25 | 19 |  |  |  |  | 0 |  | 16 |  |  |  |  | 3 |  | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 264000
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 15 | [17 empty] | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 215669
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | [8 empty] | 17 | 35 |  |  |  | 17 | 17 | [6 empty] | 14 | 17 | 142836
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 163 | 163 | 150 | 150 | 150 | 163 | 130 | 163 | 163 | 120 | 163 |  | 163 | 163 | 163 | 120 | 120 | 163 | 163 | 3801273
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [9 empty] | 11200
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 15 | 21 | 35 | 17 | 17 | 17 | 17 | 19 |  | 42 | 54 | 54 | 54 | 54 | 17 | 0 | 415800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 95 | 95 | 95 | 95 | 97 | 97 | 134 | 134 | 134 | 115 | 115 | 132 | 132 | 123 | 123 | 123 | 123 | 130 |  | 152 | 152 | 141 | 152 | 152 | 153 | 153 | 2961600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 46 | 34 | 36 | 35 | 35 | 35 | 34 | 34 | 35 | 54 | 69 | 66 | 77 | 100 | 103 | 103 | 103 | 105 |  | 115 | 115 | 115 | 114 | 114 | 114 | 114 | 1809792
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | [9 empty] | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 173760
116 | Chandpur 200 MW (Desh energy) | 70 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 70 |  | 136 | 155 | 155 | 155 | 155 | 156 | 157 | 1910400
117 | Ashuganj 150 MW PP (Midland) | 85 | 85 | 83 | 60 | 51 | 40 | [5 empty] | 3 | 25 | 6 | 5 | 5 | 5 | 33 |  | 68 | 68 | 60 | 48 | 43 | 41 | 38 | 806254
118 | Bibiyana-III 400 MW CCPP | 372 | 365 | 365 | 366 | 324 | 306 | 312 | 309 | 312 | 316 | 316 | 325 | 347 | 348 | 371 | 370 | 325 | 356 |  | 359 | 363 | 365 | 370 | 374 | 377 | 376 | 8681000
| Jamalpur 115 MW PP (United) | 59 | 59 | 59 | 59 | 59 | 59 | 69 | 69 | 69 | 69 | 69 | 68 | 67 | 66 | 76 | 76 | 76 | 76 |  | 95 | 95 | 96 | 97 | 96 | 97 | 97 | 1764000
| Anwara 300 MW PP (United) | 52 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 52 | 51 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1257055
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | [6 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 203520
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 17 | 35 | 17 | 18 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 514364
| Bhairob 54.5 MW | 35 | 17 | 17 | 17 | [9 empty] | 14 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  | 11 | 11 | 269280
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 12 | 18 | 25 | 18 | 11 | 14 | 15 | 9 | 2 | 1
| Chandpur 115(Doreen) | 34 | 34 | 34 | 37 | 35 | 34 | 34 | 34 | 34 | 34 | 33 | 34 | 38 | 34 | 34 | 34 | 46 | 51 |  | 61 | 90 | 82 | 92 | 92 | 83 | 44 | 1111680
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 19 | 28 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 644400
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 36 | 36 |  |  |  |  | 35 |  | 70 | 35 | 35 | 35 | 35 | 35 | 17 | 423200
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 3 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15840
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 7 | 36 | 56 | 68 | 72 | 72 | 66 | 57 | 41 | 21 | 4 | [9 empty] | 504327
| Matarbari 2*600 MW (CPGCL) | 352 | 353 | 312 | 282 | 254 | 244 | 225 | 215 | 215 | 216 | 234 | 256 | 251 | 251 | 235 | 223 | 215 | 218 |  | 206 | 204 | 212 | 232 | 246 | 225 | 230 | 6014545
| Meghnaghat (Reliance) 718MW CCPP |  |  |  |  | 14 | 45 | 15 | [16 empty] | 12 | 36 | 46 | 168000
Sreepur 150 MW
120
121 | Eastern Zone Total | 6890 | 6694 | 6443 | 6199 | 5959 | 5711 | 5675 | 5575 | 5604 | 5564 | 5739 | 5993 | 6609 | 6206 | 6324 | 6164 | 5875 | 6684 |  | 6916 | 6946 | 6969 | 6862 | 6771 | 6730 | 6592 | 152448810
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | 25 | 20 | [24 empty] | 53280
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 115680
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 14 | 37 | 60 | 83 | 97 | 83 | 85 | 74 | 15 | 33 | 4 | [9 empty] | 586080
132 | Rampal 1320 MW (BIFPCL) | 510 | 514 | 509 | 508 | 509 | 510 | 510 | 510 | 512 | 510 | 507 | 509 | 510 | 510 | 510 | 510 | 509 | 509 |  | 508 | 509 | 509 | 507 | 507 | 514 | 511 | 12320000
133 | United Payra Power Ltd. | 150 | 150 | 150 | 150 | 150 | 100 | 54 | 54 | 17 |  |  | 11 | 103 | 35 | 72 | 72 | 72 | 108 |  | 126 | 126 | 126 | 126 | 126 | 150 | 150 | 2252400
| Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 220 | 220 | 180 | 220 |  | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 5260170
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 64 | 103 | 110 | 110 | [6 empty] | 16 | 16 | 16 | 32 | 48 | 48 | 48 |  | 48 | 48 | 64 | 110 | 110 | 110 | 16 | 1181088
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 250 | 200 | 295 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 7222000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3934
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1581000
141 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 9 | 9 | 9 | 7 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 8 | 7 | 7 | 10 |  | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 208617
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP | 46 | 30 | [24 empty] | 92544
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
147 | Bheramara HVDC | 478 | 478 | 478 | 476 | 476 | 476 | 476 | 476 | 476 | 476 | 477 | 477 | 477 | 479 | 480 | 480 | 480 | 480 |  | 480 | 480 | 490 | 544 | 588 | 715 | 886 | 12098909
148 | Bheramara 410 MW CCPP | 142 | 147 | 145 | 149 | 149 | 152 | 152 | 152 | 150 | 146 | 146 | 147 | 143 | 145 | 145 | 145 | 145 | 164 |  | 172 | 178 | 181 | 185 | 185 | 180 | 180 | 3814848
149 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1120 | 1100 | 1080 | 1050 | 1040 | 1120 | 1244 | 1244 | 1244 | 1120 | 960 | 960 |  | 1190 | 1220 | 1230 | 1244 | 1220 | 1244 | 1244 | 30261500
150
151 | Barapukuria TPP Unit-1 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 63 | 63 | 62 | 62 | 62 | 62 |  | 62 | 62 | 63 | 63 | 63 | 64 | 63 | 1445236
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 228 | 180 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5472000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 38 | 35 | [17 empty] | 39 | [5 empty] | 0 | 116327
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 4 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | [9 empty] | 23460
157 | Sirajganj 68 MW Solar Park | [6 empty] | 6 | 21 | 32 | 47 | 45 | 35 | 41 | 8 | 24 | 3 | 2 | [9 empty] | 279750
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 170 | 170 | 178 | 178 | 181 | 180 | 181 | 181 | 181 | 181 | 181 | 181 | 182 | 181 | 182 | 150 | 140 | 150 |  | 173 | 180 | 181 | 184 | 185 | 185 | 185 | 4288455
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 360 | 414 | 414 | 414 | 414 | 414 | 350 | 414 | 380 | 380 | 414 | 350 | 350 | 380 | 414 | 350 | 300 | 414 |  | 350 | 350 | 350 | 414 | 414 | 414 | 360 | 9526181
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | 19 | 19 | [14 empty] | 4 | 4 |  | 12 | [5 empty] | 0 | 55968
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 110286
166 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | 30 | 30 | [15 empty] | 27 |  | 46 | [6 empty] | 123005
169 | Santahar 50 MW Peaking PP | 28 | 28 | [15 empty] | 13 |  | 28 | [6 empty] | 89255
170 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
171 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 49 |  | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 364656
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | 113 | 113 | [10 empty] | 15 | 35 | 35 |  |  | 1 | [6 empty] | 4 | 65 | 548832
173 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | [5 empty] | 45 | 55 | 55 | 77 | 35 | 35 | 100 |  | 70 | 70 | 70 | 70 | 113 | 113 | 113 | 1162368
175 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 70 | 70 | 49 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 80 |  | 113 | 113 | 105 | 113 | 113 | 113 | 113 | 1642876
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 2 | 5 | 3 | 1 | 5 | 3 | 3 | 1 | 0 | [9 empty] | 29338
| Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 15 | 55 |  | 74 | 74 | 74 | 74 | 108 | 115 | 115 | 588288
| Intraco Solar 30 MW | [5 empty] | 0 | 3 | 14 | 12 | 25 | 33 | 32 | 23 | 7 | 20 | 10 | 2 | [9 empty] | 193839
178 | Adani Power Jharkhanda Ltd | 1032 | 1037 | 1046 | 1031 | 1030 | 1034 | 1031 | 1031 | 1027 | 1034 | 1028 | 1036 | 1034 | 1039 | 1035 | 1035 | 1131 | 1237 |  | 1243 | 1250 | 1258 | 1232 | 1225 | 1240 | 1219 | 26290909
| Teesta Solar Limited | [6 empty] | 17 | 60 | 106 | 134 | 182 | 193 | 168 | 107 | 106 | 55 | 11 | [9 empty] | 1043280