## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-10-21 | Monday
|  | Date (day): | 2024-10-21 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13583.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14740 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-10-20 | 2024-10-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 406 | 370 | 400 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 15 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 13 | 13 | 62 |  | Fuel shortage
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 8 | 8 |  |  | Fuel shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 290 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 145 | 48 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 38 | 42 | 42 |  | 38 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 28 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 34 | 17 | 34 | 18 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 192 | 95 | 280 | 20 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 33 | 113 | 34 | 132 | 17 |  | Fuel shortage
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 52 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 16 | 4 | 17 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 22 |  | 33 | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 200 | 200 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1851 | 2336 | 1911 | 2434 | 2601 | 831
35 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
36 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
37 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
38 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 18 | 19 | 19 | 31 |  | Fuel shortage
39 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 216 | 213 | 215 | 215 |  | 15
40 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 149 | 148 | 150 | 150 |  | 75 | ST Under maint
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
42 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
43 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 39 | 39 | 56 | 85 |  | 13 | Under maint
44 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 84 | 51 | 85 |  | 17 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0
45 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 72 | 88 | 50 | 100 | 0 |  | Fuel shortage
46 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 15 | 5 | 15
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 19 | 19 | 20 | 20 | 88 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 45 | 52 | 50 | 100 | 200 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 20 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 35 | 35 | 35 | 81 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 160 | 36 | 163
55 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 536 | 610 | 612 | 612 |  | 612 | Unit-2 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 9 | 42 | 60 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 215 | 212 | 210 | 210 | 940 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1371 | 1811 | 1757 | 2068 | 1715 | 1062
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 216 | 218 | 215 | 217 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 300 | 310 | 310 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 335 | 295 | 330 | 330 |  |  | FGMO
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 41 | 42 | 44 | 44
63 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 5 | 5 | 5 | 5 | 35 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 55 | 8 | 55 | 140 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 32 | 74 | 140 | 140 | 10 |  | Fuel shortage
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 29 | 29 | 29 |  | 23 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 181 | 200 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 86 | 88 | 68 | 86
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 50 |  |  | Fuel shortage
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
74 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 106 | 106 | 106 |  | 8 | Engine problem
75 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 39 | 77 | 27 | 65 | 48 |  | Fuel shortage
76 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 91 | 17 | 92 | 23 |  | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 68 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1496 | 1674 | 1688 | 1840 | 369 | 398
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 11 | 12 | 26 | 26 | 176 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 125 | 154 | 125 | 144 | 56 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 96 | 68 | 96 | 19 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 6 | 18
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 0 | 35 | 19 |  | Fuel shortage
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 15 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 279 | 280 | 276.6 | 319 | 176 | 0
84 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 28 | 28 | 28 | 28 |  | 42 | Gas shortage
85 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Gas shortage
86 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 120 | 163 | 163
87 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
88 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 49 | 52 | 52 | 52
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 36 | 33 | 36 | 36 | 14 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 2 | 5 | 5 |  | 6 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 58 | 59 | 62
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 205 | 207 | 212 | 212 |  | 19 | Machine problem
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 15 | 15 | 5 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 280 | 320 | 320 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 388 | 339 | 375 | 375 |  |  | FGMO
99 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1338 | 1262 | 1393 | 1396 | 19 | 853
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 920 | 920 | 936 | 937
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 57 | 30 | 60 |  | 49 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 342 | 285 | 300 | 300 | 110 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 86 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 507 | 619 | 517 | 600 | 634 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1855 | 1898 | 1900 | 1944 | 1414 | 73
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 16 | 94 |  | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 8 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 127 | 100 | 132 | 132 |  | 62 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1200 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 125 | 180 | 180 | 180 |  | 110
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 150 | 150
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 286 | 307 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1805 | 1945 | 2023 | 2039 | 94 | 172
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 37 | 35 | 38 |  | 14 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 24 |  | 47 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
122 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 28 | 46
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 140 | 180 | 200 | 200 | 10
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 321 | 318 | 414 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 22 | 28 |  | 22 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 87 | 50 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 108 | 113 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1033 | 1035 | 1000 | 1100
135 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 64 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 103 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1671 | 1956 | 2062 | 2176 | 621 | 98
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 64 | 66 | 66 |  | 19
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230 |  | 44
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 108 | 34 | 113
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 90 | 35 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 185 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 508 | 492 | 573 | 524 | 40 | 148
| Total |  |  |  |  | 27791 | 27086 | 12174 | 13654 | 13583.6 | 14740 | 7049 | 3635
A. |  | 2024-10-20 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 13654 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 10147 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13730 | MW
3 | Day peak Generation : |  |  | 12174 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13305.4 | MW
4 | Evening peak Generation : |  |  | 13654 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 73 | MW
5 | Total Energy Generation : |  | 289.3262 | MKWHr | By Solar | 4.0961 | MKWHr
| By Gas : | 123.947 | MKWHr |  | By Oil: | 32.2463 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 74.1768 | MKWHr |  | By Hydro: | 5.1508 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 25.4345 | MKWHr |  | By Wind: | 0.11856 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7049 | MW | Dhaka | 5016 | 4981 |  | 35 |  | 18:00 |  | 86.905
|  |  | For Plants S/D or M/C prob = |  |  | 3635 | MW | Chittagong | 1368.9 | 1368.9 |  | 0 |  | 19:00 |  | 73
|  |  | Total = |  |  | 10684 | MW | Khulna | 1508.6 | 1508.6 |  | 0 |  | 19:30 |  | 53
7 | Total Gas Supplied : |  | 906.44 | MMCFD | **Import Adani: | Taka | 168122263.13 | Rajshahi | 1275.6 | 1275.6 |  | 0 |  | 20:00 |  | 54
8 | Fuel Cost : | i) Gas : | Taka | 365313429.474 | ii) Oil : | Taka | 589928392.88 | Comilla | 1294 | 1294 |  | 0 |  | 21:00 |  | 48
|  | iii) Coal : | Taka | 518571672.88 | Total | Taka | 1641935758.364 | Mymensingh | 1075 | 1037 |  | 38 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 12921.15 | MKWHr. | Sylhet | 570 | 570 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1288 | MW (W to E) at | 19:00 | hrs | Barisal | 396.3 | 396.3 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 1250 | MW at | 18:30 | hrs | Rangpur | 801 | 801 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.1°C |  |  | Total | 13305.4 | 13232.4 |  | 73
B. |  | 2024-10-21 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.1°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14740 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12400 | MW
4 | Reserve(Generation end) |  |  |  | 940 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 292.4199 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10246 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1804 | MKWHr. | ii) HVDC Flow at Peak Time |  | 920 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9757 | MKWHr. | iii) Maximum HVDC Flow : |  | 921 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.71 |  | (b) Today: | 104.47 |  | (c) Rule Curve: |  | 107.8
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-10-20 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 21 | 21 | 25 | 33 | 0 | 0 | 136 | 80 | 0 | 0 | 0 | 155 | 0 | 0 | 0 |  | 0 | 64 | 0 | 0 | 19 | 5 | 0 | 37 | 0 | 0 | 0 | 310 | 0 | 217 | 8 | 70 | 43 | 5 | 0 | 43 | 0 | 29 | 8 | 0 | 0 | 0 | 12 | 82 | 22 | 0 | 0 | 0 | 28 | 30 | 49 | 36 | 163 | 0 | 40 | 86 | 0 | 209 | 15 | 0 | 0 | 280 | 12 | 5 | 0 | 0 | 0 | 0 | 97 | 0 | 30 | 0 | 50 | 120 | 0 | 371 | 57 | 17 | 0 | 0 | 51 | 0 | 0 | 17 | 42 | 12 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 61 | 17 | 335 | 11 | 0 | 570 | 0 | 211 | 0 | 200 | 0 | 6 | 0 |  | 909 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 9 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 70 | 1244 | 112 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 307 | 1036 | 0 | 0 | 0 | 0 | 0 |  | 5941 | 5784 | 11725 | 3373 | 909 | 1868 | 0 | 934 | 3133 | 216 | 0 | 174 | 82 | 1036 | 0 | 0 | 38.2 | 104.81
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 25 | 33 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 155 | 0 | 0 | 0 |  | 0 | 40 | 0 | 0 | 19 | 0 | 0 | 37 | 0 | 0 | 0 | 280 | 0 | 217 | 8 | 70 | 43 | 5 | 0 | 43 | 0 | 29 | 8 | 0 | 0 | 0 | 12 | 80 | 22 | 0 | 0 | 0 | 28 | 30 | 49 | 36 | 163 | 0 | 59 | 86 | 0 | 209 | 15 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 97 | 0 | 17 | 0 | 25 | 120 | 0 | 335 | 57 | 17 | 0 | 0 | 52 | 0 | 0 | 17 | 34 | 12 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 40 | 17 | 295 | 0 | 0 | 570 | 1 | 216 | 0 | 200 | 0 | 24 | 0 |  | 914 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244 | 112 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 307 | 1033 | 0 | 0 | 0 | 0 | 0 |  | 5720 | 5554 | 11274 | 3247 | 914 | 1853 | 0 | 692 | 3139 | 214 | 0 | 101 | 80 | 1033 | 0 | 1 | 34.38 | 104.79
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 25 | 33 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 155 | 0 | 0 | 0 |  | 0 | 24 | 0 | 0 | 19 | 0 | 0 | 37 | 0 | 0 | 0 | 280 | 0 | 217 | 8 | 70 | 43 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 88 | 22 | 0 | 0 | 0 | 28 | 30 | 49 | 36 | 163 | 0 | 59 | 86 | 0 | 209 | 15 | 0 | 0 | 280 | 12 | 5 | 0 | 0 | 0 | 0 | 97 | 0 | 17 | 0 | 12 | 120 | 0 | 335 | 58 | 17 | 0 | 0 | 52 | 0 | 0 | 17 | 27 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 295 | 0 | 0 | 570 | 8 | 216 | 0 | 200 | 0 | 24 | 0 |  | 921 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 112 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 509 | 0 | 307 | 1036 | 0 | 0 | 0 | 0 | 0 |  | 5620 | 5331 | 10951 | 3276 | 921 | 1836 | 0 | 538 | 2996 | 212 | 0 | 40 | 88 | 1036 | 0 | 8 | 27.695 | 104.77
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | 25 | 33 | 0 | 0 | 131 | 80 | 0 | 0 | 0 | 155 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 19 | 0 | 0 | 37 | 0 | 0 | 0 | 280 | 0 | 217 | 8 | 70 | 43 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 86 | 22 | 0 | 0 | 0 | 28 | 30 | 49 | 36 | 130 | 0 | 60 | 86 | 0 | 208 | 15 | 0 | 0 | 280 | 12 | 5 | 0 | 0 | 0 | 0 | 97 | 0 | 17 | 0 | 12 | 85 | 0 | 310 | 58 | 17 | 0 | 0 | 52 | 0 | 0 | 17 | 31 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 295 | 0 | 0 | 520 | 17 | 216 | 0 | 200 | 0 | 70 | 0 |  | 920 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 250 | 1032 | 0 | 0 | 0 | 0 | 0 |  | 5515 | 5142 | 10657 | 3205 | 920 | 1844 | 0 | 490 | 2828 | 211 | 0 | 24 | 86 | 1032 | 0 | 17 | 26.74 | 104.75
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | 25 | 33 | 0 | 0 | 131 | 80 | 0 | 0 | 0 | 155 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 280 | 0 | 217 | 8 | 70 | 43 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 82 | 23 | 0 | 0 | 0 | 28 | 30 | 49 | 36 | 130 | 0 | 62 | 86 | 0 | 212 | 15 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 97 | 0 | 16 | 0 | 12 | 85 | 0 | 331 | 58 | 17 | 0 | 0 | 15 | 0 | 0 | 17 | 26 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 17 | 295 | 0 | 0 | 440 | 10 | 217 | 0 | 200 | 0 | 93 | 0 |  | 920 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 200 | 1034 | 0 | 0 | 0 | 0 | 0 |  | 5411 | 4965 | 10376 | 3233 | 920 | 1887 | 0 | 422 | 2561 | 211 | 0 | 16 | 82 | 1034 | 0 | 10 | 0 | 104.73
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | 25 | 33 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 155 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 280 | 0 | 217 | 8 | 70 | 44 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 74 | 23 | 0 | 0 | 0 | 28 | 30 | 49 | 36 | 130 | 0 | 62 | 86 | 0 | 212 | 15 | 0 | 0 | 300 | 12 | 5 | 0 | 0 | 0 | 0 | 97 | 0 | 16 | 0 | 12 | 68 | 0 | 335 | 58 | 17 | 0 | 0 | 15 | 0 | 0 | 17 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 17 | 300 | 0 | 0 | 400 | 16 | 214 | 0 | 200 | 1 | 96 | 0 |  | 919 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 200 | 1034 | 0 | 0 | 0 | 0 | 0 |  | 5228 | 4919 | 10147 | 3165 | 919 | 1797 | 0 | 395 | 2518 | 212 | 0 | 16 | 74 | 1034 | 1 | 16 | 0 | 104.71
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | 25 | 33 | 8 | 0 | 133 | 80 | 0 | 0 | 0 | 155 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 365 | 0 | 218 | 8 | 70 | 44 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 76 | 23 | 0 | 0 | 0 | 28 | 30 | 49 | 36 | 130 | 0 | 62 | 86 | 0 | 213 | 15 | 0 | 0 | 300 | 12 | 5 | 0 | 0 | 0 | 0 | 125 | 0 | 16 | 4 | 12 | 68 | 0 | 335 | 67 | 17 | 0 | 1 | 15 | 0 | 0 | 17 | 28 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 3 | 33 | 17 | 330 | 0 | 0 | 402 | 15 | 217 | 0 | 200 | 13 | 340 | 0 |  | 921 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 112 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 516 | 3 | 200 | 1033 | 26 | 0 | 0 | 3 | 11 |  | 5625 | 4957 | 10582 | 3249 | 921 | 2019 | 0 | 431 | 2529 | 213 | 0 | 16 | 76 | 1033 | 80 | 15 | 0 | 104.7
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | 25 | 32 | 8 | 0 | 134 | 80 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 335 | 0 | 214 | 8 | 70 | 43 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 72 | 16 | 0 | 0 | 0 | 28 | 30 | 50 | 36 | 163 | 0 | 60 | 86 | 0 | 213 | 15 | 0 | 0 | 295 | 12 | 5 | 0 | 0 | 0 | 0 | 125 | 0 | 17 | 0 | 12 | 68 | 0 | 377 | 67 | 17 | 0 | 2 | 15 | 0 | 0 | 17 | 28 | 1 | 0 | 16 | 21 | 0 | 0 | 0 | 0 | 10 | 34 | 17 | 320 | 0 | 0 | 404 | 1 | 217 | 0 | 200 | 13 | 0 | 0 |  | 921 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 111 | 0 | 0 | 1 | 27 | 0 | 0 | 0 | 511 | 10 | 200 | 1034 | 66 | 0 | 0 | 18 | 34 |  | 5314 | 5127 | 10441 | 3237 | 921 | 1712 | 0 | 450 | 2566 | 214 | 0 | 32 | 72 | 1034 | 202 | 1 | 0 | 104.69
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | 25 | 30 | 17 | 0 | 135 | 80 | 0 | 0 | 4 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 2 | 7 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 217 | 8 | 70 | 40 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 70 | 16 | 0 | 0 | 1 | 28 | 30 | 50 | 36 | 163 | 0 | 59 | 86 | 0 | 209 | 15 | 0 | 0 | 305 | 12 | 5 | 0 | 0 | 0 | 0 | 125 | 0 | 33 | 15 | 50 | 68 | 0 | 386 | 77 | 52 | 0 | 3 | 15 | 14 | 0 | 17 | 28 | 12 | 0 | 16 | 34 | 0 | 0 | 0 | 0 | 17 | 34 | 17 | 300 | 0 | 0 | 402 | 0 | 217 | 0 | 200 | 22 | 0 | 0 |  | 920 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1000 | 111 | 0 | 0 | 3 | 56 | 0 | 0 | 0 | 509 | 18 | 200 | 1035 | 119 | 0 | 0 | 40 | 63 |  | 5531 | 5377 | 10908 | 3295 | 920 | 1714 | 0 | 596 | 2622 | 215 | 0 | 48 | 70 | 1035 | 393 | 0 | 0 | 104.68
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 20 | 21 | 25 | 24 | 25 | 0 | 135 | 80 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 19 | 19 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 214 | 36 | 70 | 42 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 76 | 11 | 0 | 0 | 1 | 28 | 30 | 50 | 36 | 163 | 0 | 59 | 83 | 0 | 207 | 15 | 0 | 0 | 310 | 12 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 33 | 16 | 50 | 69 | 0 | 386 | 77 | 52 | 0 | 4 | 15 | 17 | 0 | 17 | 29 | 12 | 0 | 16 | 42 | 0 | 0 | 0 | 0 | 22 | 34 | 17 | 340 | 0 | 0 | 470 | 1 | 214 | 0 | 200 | 54 | 0 | 0 |  | 920 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1070 | 112 | 0 | 0 | 4 | 74 | 0 | 0 | 0 | 509 | 25 | 250 | 1034 | 153 | 0 | 0 | 51 | 88 |  | 5809 | 5568 | 11377 | 3336 | 920 | 1742 | 0 | 659 | 2807 | 215 | 0 | 48 | 76 | 1034 | 539 | 1 | 0 | 104.67
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 18 | 21 | 25 | 24 | 25 | 0 | 136 | 80 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 19 | 19 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 216 | 45 | 50 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 78 | 11 | 0 | 0 | 2 | 28 | 30 | 50 | 36 | 120 | 0 | 60 | 86 | 0 | 206 | 15 | 0 | 0 | 275 | 12 | 5 | 0 | 18 | 0 | 0 | 125 | 0 | 33 | 16 | 63 | 99 | 10 | 386 | 77 | 52 | 0 | 3 | 45 | 17 | 0 | 17 | 29 | 12 | 0 | 16 | 48 | 35 | 13 | 0 | 0 | 27 | 34 | 17 | 330 | 0 | 0 | 500 | 0 | 215 | 0 | 200 | 69 | 0 | 0 |  | 920 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1200 | 110 | 0 | 9 | 5 | 84 | 0 | 0 | 0 | 508 | 28 | 250 | 1037 | 180 | 0 | 0 | 60 | 99 |  | 5966 | 5703 | 11669 | 3289 | 920 | 1643 | 0 | 843 | 2968 | 216 | 0 | 48 | 78 | 1037 | 627 | 0 | 30 | 104.66
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 18 | 21 | 25 | 24 | 25 | 0 | 136 | 80 | 0 | 0 | 8 | 149 | 0 | 0 | 0 |  | 0 | 39 | 0 | 0 | 19 | 19 | 0 | 3 | 0 | 0 | 0 | 310 | 0 | 216 | 73 | 50 | 41 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 86 | 11 | 0 | 0 | 2 | 28 | 30 | 49 | 36 | 120 | 0 | 59 | 86 | 0 | 205 | 15 | 0 | 0 | 305 | 12 | 5 | 0 | 45 | 0 | 0 | 125 | 0 | 33 | 0 | 72 | 100 | 32 | 388 | 77 | 52 | 0 | 4 | 45 | 17 | 0 | 52 | 39 | 12 | 0 | 16 | 49 | 72 | 17 | 0 | 0 | 27 | 34 | 17 | 335 | 0 | 0 | 536 | 0 | 215 | 0 | 200 | 68 | 0 | 15 |  | 920 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1244 | 125 | 0 | 17 | 5 | 86 | 0 | 0 | 0 | 507 | 25 | 286 | 1033 | 185 | 0 | 0 | 64 | 103 |  | 6335 | 5839 | 12174 | 3309 | 920 | 1772 | 0 | 1032 | 3081 | 216 | 0 | 102 | 86 | 1033 | 623 | 0 | 92 | 104.65
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 18 | 21 | 25 | 30 | 25 | 0 | 136 | 80 | 0 | 0 | 13 | 149 | 0 | 0 | 0 |  | 0 | 39 | 0 | 0 | 19 | 0 | 0 | 2 | 0 | 0 | 0 | 325 | 0 | 212 | 73 | 50 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 90 | 11 | 0 | 0 | 2 | 28 | 30 | 49 | 36 | 120 | 0 | 57 | 86 | 0 | 205 | 15 | 0 | 0 | 310 | 12 | 5 | 0 | 82 | 0 | 0 | 125 | 0 | 33 | 0 | 72 | 100 | 45 | 389 | 76 | 52 | 0 | 4 | 45 | 17 | 0 | 52 | 30 | 12 | 0 | 0 | 47 | 72 | 17 | 0 | 0 | 24 | 34 | 17 | 330 | 0 | 0 | 580 | 9 | 216 | 0 | 200 | 56 | 0 | 18 |  | 920 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 230 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1244 | 130 | 0 | 17 | 5 | 83 | 0 | 0 | 0 | 506 | 27 | 307 | 1037 | 174 | 0 | 0 | 59 | 97 |  | 6392 | 5939 | 12331 | 3315 | 920 | 1874 | 0 | 1042 | 3146 | 216 | 0 | 99 | 90 | 1037 | 583 | 9 | 75 | 104.64
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 18 | 21 | 25 | 18 | 25 | 0 | 135 | 80 | 0 | 0 | 17 | 148 | 0 | 0 | 0 |  | 0 | 39 | 0 | 0 | 19 | 2 | 0 | 3 | 0 | 0 | 0 | 285 | 0 | 213 | 55 | 50 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 86 | 8 | 0 | 0 | 2 | 28 | 30 | 51 | 35 | 163 | 0 | 57 | 86 | 0 | 203 | 15 | 0 | 0 | 300 | 12 | 5 | 0 | 97 | 0 | 0 | 134 | 0 | 33 | 10 | 63 | 100 | 50 | 390 | 67 | 52 | 0 | 2 | 102 | 21 | 0 | 70 | 27 | 12 | 0 | 0 | 39 | 72 | 17 | 0 | 0 | 21 | 34 | 17 | 295 | 0 | 0 | 612 | 7 | 215 | 0 | 200 | 53 | 0 | 2 |  | 921 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 230 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1244 | 164 | 0 | 54 | 4 | 51 | 0 | 0 | 0 | 510 | 23 | 307 | 1037 | 141 | 0 | 0 | 50 | 71 |  | 6482 | 5852 | 12334 | 3229 | 921 | 1914 | 0 | 1172 | 3178 | 215 | 0 | 104 | 86 | 1037 | 471 | 7 | 82.13 | 104.66
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 |  | 0 | 450 | 0 | 0 | 0 | 4 | 332 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 17 | 21 | 25 | 24 | 17 | 0 | 134 | 80 | 0 | 0 | 16 | 148 | 0 | 0 | 0 |  | 0 | 39 | 0 | 0 | 20 | 19 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 214 | 55 | 50 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 84 | 8 | 0 | 0 | 1 | 28 | 30 | 51 | 35 | 163 | 0 | 57 | 86 | 0 | 203 | 15 | 0 | 0 | 310 | 12 | 5 | 0 | 117 | 0 | 0 | 134 | 0 | 35 | 8 | 63 | 100 | 50 | 390 | 76 | 35 | 0 | 2 | 102 | 35 | 0 | 70 | 29 | 12 | 0 | 0 | 21 | 72 | 17 | 0 | 0 | 15 | 34 | 17 | 295 | 0 | 0 | 608 | 2 | 214 | 0 | 200 | 38 | 0 | 4 |  | 920 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 230 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 1244 | 220 | 0 | 54 | 2 | 38 | 0 | 0 | 0 | 509 | 16 | 307 | 1040 | 101 | 0 | 0 | 40 | 55 |  | 6476 | 5917 | 12393 | 3248 | 920 | 2040 | 0 | 1225 | 3175 | 214 | 0 | 105 | 84 | 1040 | 340 | 2 | 83.085 | 104.62
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 331 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 17 | 21 | 25 | 30 | 17 | 0 | 134 | 80 | 0 | 0 | 17 | 149 | 0 | 0 | 0 |  | 6 | 39 | 0 | 0 | 19 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 214 | 55 | 50 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 82 | 8 | 0 | 0 | 1 | 28 | 30 | 52 | 36 | 163 | 0 | 57 | 86 | 0 | 205 | 15 | 0 | 0 | 295 | 12 | 5 | 0 | 125 | 0 | 0 | 127 | 0 | 44 | 0 | 50 | 100 | 50 | 374 | 76 | 35 | 0 | 1 | 105 | 35 | 0 | 70 | 33 | 12 | 0 | 0 | 14 | 72 | 17 | 0 | 0 | 6 | 34 | 17 | 295 | 0 | 0 | 608 | 0 | 214 | 0 | 200 | 20 | 0 | 8 |  | 920 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 230 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 35 | 1240 | 220 | 0 | 54 | 1 | 24 | 0 | 0 | 0 | 507 | 7 | 307 | 1037 | 48 | 0 | 0 | 15 | 28 |  | 6409 | 5791 | 12200 | 3241 | 920 | 2026 | 0 | 1252 | 3168 | 214 | 0 | 94 | 82 | 1037 | 166 | 0 | 76.4 | 104.61
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 332 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 17 | 21 | 25 | 24 | 17 | 0 | 134 | 80 | 0 | 0 | 17 | 148 | 0 | 0 | 0 |  | 18 | 39 | 0 | 0 | 19 | 0 | 0 | 5 | 0 | 0 | 0 | 280 | 0 | 213 | 55 | 50 | 42 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 76 | 12 | 0 | 0 | 0 | 28 | 30 | 52 | 36 | 163 | 0 | 58 | 86 | 0 | 205 | 15 | 0 | 0 | 300 | 12 | 2 | 0 | 120 | 0 | 0 | 135 | 0 | 57 | 1 | 50 | 100 | 50 | 373 | 78 | 35 | 0 | 0 | 105 | 35 | 0 | 70 | 57 | 12 | 0 | 0 | 1 | 72 | 17 | 0 | 0 | 1 | 34 | 17 | 295 | 0 | 0 | 612 | 6 | 213 | 0 | 200 | 4 | 0 | 11 |  | 920 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 230 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 1120 | 220 | 0 | 54 | 0 | 5 | 0 | 0 | 0 | 506 | 1 | 250 | 1032 | 8 | 0 | 0 | 2 | 4 |  | 6438 | 5521 | 11959 | 3224 | 920 | 2035 | 0 | 1316 | 2991 | 214 | 0 | 118 | 76 | 1032 | 27 | 6 | 58.255 | 104.6
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 17 | 21 | 25 | 28 | 34 | 0 | 133 | 80 | 0 | 0 | 23 | 148 | 0 | 0 | 0 |  | 18 | 39 | 85 | 0 | 19 | 0 | 0 | 8 | 0 | 0 | 0 | 325 | 0 | 213 | 55 | 50 | 42 | 5 | 0 | 43 | 0 | 0 | 6 | 0 | 0 | 0 | 12 | 86 | 11 | 0 | 0 | 0 | 28 | 30 | 52 | 33 | 163 | 0 | 60 | 86 | 0 | 205 | 15 | 0 | 0 | 320 | 12 | 2 | 0 | 128 | 0 | 0 | 144 | 0 | 95 | 0 | 75 | 125 | 58 | 372 | 96 | 88 | 4 | 0 | 52 | 35 | 7 | 98 | 67 | 12 | 0 | 0 | 0 | 162 | 20 | 0 | 0 | 0 | 52 | 17 | 335 | 36 | 0 | 608 | 7 | 217 | 0 | 200 | 0 | 0 | 0 |  | 920 | 0 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 127 | 8 | 0 | 0 | 0 | 0 | 5 | 0 | 95 | 0 | 0 | 27 | 0 | 15 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 106 | 0 | 0 | 100 | 1140 | 220 | 0 | 137 | 0 | 0 | 36 | 0 | 0 | 504 | 0 | 307 | 1035 | 0 | 0 | 0 | 0 | 0 |  | 7069 | 6070 | 13139 | 3293 | 920 | 2057 | 0 | 2006 | 3070 | 213 | 0 | 452 | 86 | 1035 | 0 | 7 | 86.905 | 104.59
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 17 | 21 | 25 | 28 | 34 | 0 | 133 | 80 | 0 | 0 | 25 | 148 | 0 | 0 | 0 |  | 18 | 39 | 84 | 0 | 19 | 18 | 0 | 15 | 0 | 0 | 0 | 300 | 0 | 218 | 55 | 50 | 42 | 5 | 0 | 43 | 0 | 29 | 8 | 0 | 0 | 0 | 12 | 88 | 12 | 0 | 0 | 0 | 28 | 30 | 52 | 33 | 120 | 0 | 58 | 86 | 0 | 207 | 15 | 0 | 0 | 280 | 12 | 2 | 0 | 192 | 0 | 0 | 154 | 0 | 113 | 0 | 88 | 181 | 74 | 339 | 96 | 88 | 17 | 0 | 52 | 35 | 20 | 106 | 77 | 12 | 0 | 4 | 0 | 162 | 35 | 0 | 0 | 0 | 91 | 17 | 295 | 160 | 0 | 610 | 9 | 212 | 0 | 200 | 0 | 0 | 0 |  | 920 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 100 | 8 | 0 | 0 | 0 | 0 | 37 | 0 | 87 | 0 | 0 | 45 | 0 | 28 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 17 | 0 | 108 | 0 | 108 | 0 | 0 | 113 | 1200 | 180 | 0 | 150 | 0 | 0 | 90 | 0 | 0 | 619 | 0 | 307 | 1035 | 0 | 0 | 0 | 0 | 0 |  | 7363 | 6291 | 13654 | 3089 | 920 | 1845 | 0 | 2502 | 3242 | 213 | 0 | 711 | 88 | 1035 | 0 | 9 | 73 | 104.56
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 380 | 0 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 8 | 145 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 17 | 21 | 25 | 28 | 34 | 0 | 133 | 80 | 0 | 0 | 25 | 148 | 0 | 0 | 0 |  | 18 | 39 | 84 | 0 | 19 | 19 | 0 | 20 | 0 | 0 | 0 | 290 | 0 | 213 | 55 | 50 | 43 | 5 | 0 | 43 | 0 | 29 | 8 | 0 | 0 | 0 | 14 | 88 | 13 | 0 | 0 | 0 | 28 | 30 | 52 | 33 | 120 | 0 | 60 | 86 | 0 | 209 | 15 | 0 | 0 | 305 | 12 | 2 | 0 | 80 | 0 | 0 | 154 | 0 | 113 | 0 | 75 | 140 | 80 | 342 | 96 | 88 | 17 | 0 | 52 | 35 | 34 | 74 | 78 | 12 | 0 | 10 | 0 | 162 | 35 | 0 | 0 | 0 | 92 | 17 | 285 | 160 | 0 | 611 | 2 | 216 | 0 | 180 | 0 | 0 | 0 |  | 920 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 37 | 0 | 95 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 17 | 0 | 50 | 0 | 111 | 0 | 0 | 113 | 1200 | 220 | 0 | 137 | 0 | 0 | 94 | 0 | 0 | 614 | 0 | 307 | 1145 | 0 | 0 | 0 | 0 | 0 |  | 7063 | 6411 | 13474 | 3061 | 920 | 1861 | 0 | 2224 | 3242 | 213 | 0 | 718 | 88 | 1145 | 0 | 2 | 53 | 104.58
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 380 | 0 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 8 | 130 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 18 | 21 | 25 | 28 | 34 | 0 | 134 | 80 | 0 | 0 | 25 | 148 | 0 | 0 | 0 |  | 18 | 39 | 84 | 0 | 18 | 19 | 0 | 20 | 0 | 0 | 0 | 280 | 0 | 215 | 55 | 70 | 43 | 5 | 0 | 43 | 0 | 29 | 8 | 0 | 0 | 0 | 15 | 88 | 14 | 0 | 0 | 0 | 28 | 30 | 52 | 33 | 120 | 0 | 60 | 86 | 0 | 208 | 15 | 0 | 0 | 285 | 12 | 2 | 0 | 30 | 0 | 0 | 154 | 0 | 111 | 0 | 86 | 136 | 80 | 341 | 96 | 88 | 17 | 0 | 52 | 35 | 34 | 52 | 78 | 12 | 0 | 16 | 0 | 162 | 35 | 0 | 6 | 0 | 91 | 17 | 285 | 160 | 0 | 610 | 0 | 214 | 0 | 180 | 0 | 0 | 0 |  | 920 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 100 | 9 | 16 | 0 | 0 | 0 | 37 | 0 | 95 | 0 | 0 | 46 | 0 | 30 | 0 | 0 | 5 | 63 | 0 | 230 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 17 | 0 | 50 | 0 | 111 | 0 | 0 | 113 | 1210 | 220 | 0 | 150 | 0 | 0 | 95 | 0 | 0 | 619 | 0 | 307 | 1132 | 0 | 0 | 0 | 0 | 0 |  | 6962 | 6411 | 13373 | 3076 | 920 | 1807 | 0 | 2179 | 3253 | 214 | 0 | 704 | 88 | 1132 | 0 | 0 | 54 | 104.57
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 |  | 0 | 380 | 0 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 8 | 112 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 18 | 21 | 25 | 28 | 25 | 0 | 135 | 80 | 0 | 0 | 25 | 148 | 0 | 0 | 0 |  | 18 | 39 | 84 | 0 | 19 | 19 | 0 | 27 | 0 | 0 | 0 | 280 | 0 | 216 | 55 | 70 | 40 | 5 | 0 | 43 | 0 | 29 | 8 | 0 | 0 | 0 | 16 | 86 | 16 | 0 | 0 | 0 | 28 | 30 | 52 | 33 | 120 | 0 | 61 | 86 | 0 | 209 | 15 | 0 | 0 | 285 | 12 | 2 | 0 | 30 | 0 | 0 | 154 | 0 | 96 | 0 | 36 | 100 | 85 | 341 | 96 | 70 | 17 | 0 | 52 | 35 | 34 | 52 | 78 | 12 | 0 | 16 | 0 | 108 | 35 | 0 | 17 | 0 | 92 | 17 | 285 | 54 | 0 | 610 | 0 | 214 | 0 | 180 | 0 | 0 | 0 |  | 920 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 100 | 10 | 16 | 0 | 0 | 0 | 38 | 0 | 95 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 5 | 63 | 0 | 230 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 17 | 0 | 35 | 0 | 112 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 95 | 0 | 0 | 624 | 0 | 307 | 1139 | 0 | 0 | 0 | 0 | 0 |  | 6638 | 6462 | 13100 | 3078 | 920 | 1832 | 0 | 1958 | 3292 | 215 | 0 | 580 | 86 | 1139 | 0 | 0 | 48 | 104.56
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 380 | 0 | 0 | 0 | 15 | 300 | 0 | 0 | 0 | 8 | 112 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 18 | 21 | 25 | 30 | 25 | 0 | 135 | 80 | 0 | 0 | 8 | 148 | 0 | 0 | 0 |  | 18 | 39 | 84 | 0 | 19 | 12 | 0 | 35 | 0 | 0 | 0 | 330 | 0 | 214 | 55 | 50 | 43 | 5 | 0 | 43 | 0 | 29 | 8 | 0 | 0 | 0 | 17 | 88 | 18 | 0 | 0 | 0 | 28 | 30 | 52 | 33 | 163 | 0 | 58 | 86 | 0 | 209 | 15 | 0 | 0 | 295 | 12 | 2 | 0 | 30 | 0 | 0 | 154 | 0 | 78 | 0 | 36 | 100 | 10 | 341 | 96 | 70 | 17 | 0 | 52 | 35 | 17 | 52 | 79 | 12 | 0 | 16 | 0 | 54 | 35 | 0 | 17 | 0 | 92 | 17 | 340 | 54 | 0 | 610 | 0 | 215 | 0 | 0 | 0 | 0 | 0 |  | 921 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 10 | 16 | 0 | 0 | 0 | 38 | 0 | 95 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 35 | 0 | 49 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 54 | 0 | 0 | 622 | 0 | 307 | 1139 | 0 | 0 | 0 | 0 | 0 |  | 6445 | 6344 | 12789 | 3214 | 921 | 1727 | 0 | 1667 | 3292 | 215 | 0 | 526 | 88 | 1139 | 0 | 0 | 0 | 104.55
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 8 | 112 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 18 | 21 | 23 | 31 | 17 | 0 | 136 | 80 | 0 | 0 | 8 | 147 | 0 | 0 | 0 |  | 15 | 39 | 84 | 0 | 19 | 0 | 0 | 36 | 0 | 0 | 0 | 330 | 0 | 215 | 55 | 50 | 43 | 5 | 0 | 43 | 0 | 30 | 8 | 0 | 0 | 0 | 17 | 88 | 18 | 0 | 0 | 0 | 28 | 30 | 52 | 33 | 163 | 0 | 59 | 86 | 0 | 209 | 15 | 0 | 0 | 290 | 12 | 2 | 0 | 30 | 0 | 0 | 154 | 0 | 78 | 0 | 36 | 100 | 10 | 342 | 96 | 52 | 17 | 0 | 52 | 35 | 17 | 52 | 77 | 12 | 0 | 16 | 0 | 54 | 35 | 0 | 17 | 0 | 61 | 17 | 340 | 17 | 0 | 612 | 0 | 216 | 0 | 0 | 0 | 0 | 0 |  | 920 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 10 | 16 | 0 | 0 | 0 | 37 | 0 | 96 | 0 | 0 | 44 | 0 | 30 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 17 | 0 | 0 | 0 | 49 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 54 | 0 | 0 | 618 | 0 | 307 | 1140 | 0 | 0 | 0 | 0 | 0 |  | 6311 | 6305 | 12616 | 3211 | 920 | 1718 | 0 | 1543 | 3291 | 216 | 0 | 489 | 88 | 1140 | 0 | 0 | 0 | 104.54
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 0 | 19 | 21 | 23 | 33 | 8 | 0 | 136 | 80 | 0 | 0 | 8 | 148 | 0 | 0 | 0 |  | 18 | 40 | 84 | 0 | 18 | 0 | 0 | 30 | 0 | 0 | 0 | 315 | 0 | 216 | 45 | 50 | 43 | 5 | 0 | 43 | 0 | 30 | 8 | 0 | 0 | 0 | 17 | 92 | 18 | 0 | 0 | 0 | 28 | 30 | 52 | 26 | 163 | 0 | 57 | 86 | 0 | 208 | 15 | 0 | 0 | 315 | 12 | 2 | 0 | 32 | 0 | 0 | 126 | 0 | 78 | 0 | 50 | 103 | 15 | 370 | 77 | 17 | 17 | 0 | 52 | 35 | 35 | 52 | 78 | 12 | 0 | 0 | 0 | 72 | 35 | 0 | 17 | 0 | 17 | 17 | 330 | 17 | 0 | 610 | 6 | 215 | 0 | 0 | 0 | 0 | 0 |  | 920 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 10 | 0 | 0 | 0 | 0 | 37 | 0 | 96 | 0 | 0 | 44 | 0 | 15 | 0 | 0 | 8 | 64 | 0 | 230 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 54 | 0 | 0 | 511 | 0 | 307 | 1109 | 0 | 0 | 0 | 0 | 0 |  | 6248 | 6214 | 12462 | 3221 | 920 | 1809 | 0 | 1481 | 3181 | 216 | 0 | 427 | 92 | 1109 | 0 | 6 | 0 | 104.53
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9428400 | 0 |  | 0 | 9736500 | 0 | 0 | 0 | 199282 | 7429631 | 0 | 0 | 0 | 86832 | 1466880 | 0 | 0 | 0 | 0 | 400932 | 316799 | 427056 | 0 | 464400 | 502560 | 601920 | 711300 | 376800 | 0 | 3214805 | 1936000 | 0 | 0 | 247780 | 3584603 | 0 | 0 | 0 |  | 150960 | 645936 | 544301 | 0 | 364800 | 197310 | 0 | 478080 | 0 | 0 | 0 | 7654800 | 0 | 5241000 | 869818 | 1472460 | 1023120 | 126240 | 0 | 944432 | 0 | 236944 | 137520 | 0 | 0 | 0 | 305290 | 1975680 | 355200 | 0 | 0 | 11950 | 669000 | 704400 | 1204800 | 832896 | 3663900 | 0 | 1388928 | 2049600 | 0 | 5188480 | 363000 | 0 | 0 | 7257000 | 280656 | 89712 | 0 | 1181782 | 0 | 0 | 3004800 | 0 | 1145232 | 102330 | 1072320 | 2553600 | 682472 | 9011000 | 1804800 | 1024320 | 123781 | 25320 | 1216909 | 489076 | 205745 | 1015740 | 1090320 | 247680 | 0 | 135360 | 316160 | 1205280 | 440345 | 0 | 115560 | 160114 | 1128960 | 432360 | 7660300 | 511855 | 0 | 13025453 | 118560 | 5221818 | 0 | 4494541 | 410864 | 0 | 58800 |  | 22180363 | 0 | 7811712 | 0 | 0 | 0 | 0 | 0 | 0 | 215040 | 0 | 3066000 | 178859 | 52128 | 0 | 0 | 0 | 233956 | 0 | 617616 | 0 | 0 | 265300 | 0 | 174592 | 0 | 0 | 164862 | 1465309 | 0 | 5594000 | 0 | 0 | 4384636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8698181 | 109440 | 0 | 340704 | 0 | 605232 | 0 | 35754 | 945216 | 29444700 | 3854740 | 0 | 1536000 | 34320 | 544320 | 463872 | 0 | 0 | 12814550 | 187867 | 6611000 | 25434533 | 1197360 | 0 | 3740 | 404250 | 661800 |  | 148994250 | 140331952 | 289326202 | 79557370 | 22180363 | 44389587 | 0 | 27275105 | 74176830 | 5150805 | 0 | 4971220 | 1975680 | 25434533 | 4096149 | 118560 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27153792 | 0 |  | 0 | 30962070 | 0 | 0 | 0 | 3511348.84 | 22660374.55 | 0 | 0 | 0 | 1558634.4 | 28486809.6 | 0 | 0 | 0 | 0 | 7321018.32 | 4992752.24 | 7810854.24 | 0 | 348300 | 0 | 0 | 0 | 6748488 | 0 | 0 | 0 | 0 | 0 | 4692953.2 | 11434883.57 | 0 | 0 | 0 |  | 2655386.4 | 11374932.96 | 9748430.91 | 0 | 7139136 | 3247722.6 | 0 | 0 | 0 | 0 | 0 | 21356892 | 0 | 17400120 | 2913890.3 | 4756045.8 | 3447914.4 | 552931.2 | 0 | 3787172.32 | 0 | 4243667.04 | 2483611.2 | 0 | 0 | 0 | 228967.5 | 12960460.8 | 1104672 | 0 | 0 | 0 | 2609100 | 2627412 | 5481840 | 3789676.8 | 12530538 | 0 | 7708550.4 | 10698912 | 0 | 14475859.2 | 2388540 | 0 | 0 | 22424130 | 210492 | 68181.12 | 0 | 24108352.8 | 0 | 0 | 57722208 | 0 | 20167535.52 | 0 | 19098019.2 | 44304960 | 11315385.76 | 23879150 | 34399488 | 19216243.2 | 2220631.14 | 0 | 19896462.15 | 9507637.44 | 3691065.3 | 19410791.4 | 21163111.2 | 4411180.8 | 0 | 2310595.2 | 0 | 22044571.2 | 7388989.1 | 0 | 2065057.2 | 0 | 20343859.2 | 7324178.4 | 22751091 | 7206918.4 | 0 | 90787407.41 | 0 | 30808726.2 | 0 | 0 | 0 | 0 | 0 |  | 62326820.03 | 0 | 23044550.4 | 0 | 0 | 0 | 0 | 0 | 0 | 4044902.4 | 0 | 9688560 | 847791.66 | 898686.72 | 0 | 0 | 0 | 4190151.96 | 0 | 10382124.96 | 0 | 0 | 4751523 | 0 | 3126942.72 | 0 | 0 | 124800.534 | 16162358.27 | 0 | 47213360 | 0 | 0 | 14469298.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25398688.52 | 1869235.2 | 0 | 6752753.28 | 0 | 12056221.44 | 0 | 0 | 18753085.44 | 190801656 | 11988241.4 | 0 | 29721600 | 0 | 0 | 8048179.2 | 0 | 0 | 93546215 | 0 | 49251950 | 168122263.13 | 0 | 0 | 0 | 0 | 0 |  | 899641079.13 | 817581960.064 | 1717223039.194 | 233937547.274 | 62326820.03 | 131375882.2 | 0 | 502371988.93 | 518571672.88 | 0 | 0 | 87556403.95 | 12960460.8 | 168122263.13 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 18 | 21 | 25 | 24 | 25 | 0 | 136 | 80 | 0 | 0 | 8 | 149 | 0 | 0 | 0 |  | 0 | 39 | 0 | 0 | 19 | 19 | 0 | 3 | 0 | 0 | 0 | 310 | 0 | 216 | 73 | 50 | 41 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 86 | 11 | 0 | 0 | 2 | 28 | 30 | 49 | 36 | 120 | 0 | 59 | 86 | 0 | 205 | 15 | 0 | 0 | 305 | 12 | 5 | 0 | 45 | 0 | 0 | 125 | 0 | 33 | 0 | 72 | 100 | 32 | 388 | 77 | 52 | 0 | 4 | 45 | 17 | 0 | 52 | 39 | 12 | 0 | 16 | 49 | 72 | 17 | 0 | 0 | 27 | 34 | 17 | 335 | 0 | 0 | 536 | 0 | 215 | 0 | 200 | 68 | 0 | 15 |  | 920 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1244 | 125 | 0 | 17 | 5 | 86 | 0 | 0 | 0 | 507 | 25 | 286 | 1033 | 185 | 0 | 0 | 64 | 103 |  | 12174 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 17 | 21 | 25 | 28 | 34 | 0 | 133 | 80 | 0 | 0 | 25 | 148 | 0 | 0 | 0 | 0 | 18 | 39 | 84 | 0 | 19 | 18 | 0 | 15 | 0 | 0 | 0 | 300 | 0 | 218 | 55 | 50 | 42 | 5 | 0 | 43 | 0 | 29 | 8 | 0 | 0 | 0 | 12 | 88 | 12 | 0 | 0 | 0 | 28 | 30 | 52 | 33 | 120 | 0 | 58 | 86 | 0 | 207 | 15 | 0 | 0 | 280 | 12 | 2 | 0 | 192 | 0 | 0 | 154 | 0 | 113 | 0 | 88 | 181 | 74 | 339 | 96 | 88 | 17 | 0 | 52 | 35 | 20 | 106 | 77 | 12 | 0 | 4 | 0 | 162 | 35 | 0 | 0 | 0 | 91 | 17 | 295 | 160 | 0 | 610 | 9 | 212 | 0 | 200 | 0 | 0 | 0 |  | 920 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 100 | 8 | 0 | 0 | 0 | 0 | 37 | 0 | 87 | 0 | 0 | 45 | 0 | 28 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 17 | 0 | 108 | 0 | 108 | 0 | 0 | 113 | 1200 | 180 | 0 | 150 | 0 | 0 | 90 | 0 | 0 | 619 | 0 | 307 | 1035 | 0 | 0 | 0 | 0 | 0 |  | 13654 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 8 | 0 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 22 | 33 | 33 | 34 | 0 | 135 | 80 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 18 | 85 | 85 | 0 | 20 | 19 | 0 | 15 | 0 | 0 |  | 310 | 0 | 217 | 55 | 50 | 44 | 5 | 0 | 43 | 0 | 29 | 50 | 0 | 0 |  | 18 | 86 | 26 | 0 | 0 | 0 | 28 | 30 | 52 | 36 | 163 | 0 | 62 | 86 | 0 | 212 | 15 | 0 | 0 | 320 | 12 | 5 | 0 | 280 | 0 | 0 | 144 | 0 | 132 | 0 | 100 | 200 | 140 | 375 | 96 | 105 | 17 | 0 | 100 | 35 | 110 | 106 | 65 | 12 | 0 | 17 | 0 | 162 | 35 | 0 | 35 | 0 | 92 | 22 | 330 | 163 | 0 | 612 | 60 | 210 | 0 | 0 |  |  |  |  | 937 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 30 | 60 | 0 | 132 | 10 | 16 | 0 | 0 | 0 | 38 | 24 | 95 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 66 | 0 | 230 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1244 | 180 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 600 | 0 | 307 | 1100 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 8 | 0 | 48 | 13 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 20 | 22 | 33 | 33 | 17 | 0 | 135 | 80 | 0 | 0 | 25 | 150 |  | 0 | 0 | 0 | 6 | 56 | 51 | 0 | 20 | 19 | 0 | 5 | 0 | 0 | 0 | 310 | 0 | 215 | 8 | 50 | 44 | 5 | 0 | 43 | 0 | 29 | 8 | 0 | 0 |  | 18 | 68 | 26 | 0 | 0 | 1.6 | 28 | 30 | 52 | 36 | 163 | 0 | 59 | 86 | 0 | 212 | 15 | 0 | 0 | 320 | 12 | 5 | 0 | 95 | 0 | 0 | 125 | 0 | 34 | 20 | 50 | 200 | 140 | 375 | 68 | 52 | 17 | 5 | 50 | 17 | 110 | 106 | 27 | 12 | 0 | 17 | 50 | 162 | 35 | 0 | 0 | 35 | 17 | 17 | 330 | 36 | 0 | 612 | 42 | 210 | 0 | 0 | 70 |  |  |  | 936 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 132 | 10 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 28 | 0 | 22 | 0 | 0 | 5 | 66 | 0 | 230 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 34 | 0 | 8 | 113 | 1244 | 180 |  | 150 | 6 | 100 | 35 | 0 | 0 | 517 | 30 | 307 | 1000 | 170 | 0 |  | 29 | 47 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 23 | 25 | 8 | 0 | 133 | 80 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 285 | 0 | 216 | 8 | 50 | 43 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 64 | 26 | 0 | 0 | 1 | 28 | 30 | 50 | 35 | 163 | 0 | 60 | 86 | 0 | 209 | 15 | 0 | 0 | 290 | 12 | 2 | 0 | 0 | 0 | 0 | 137 | 0 | 34 | 11 | 0 | 34 | 0 | 341 | 68 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 10 | 34 | 0 | 330 | 0 | 0 | 582 | 0 | 215 | 0 | 0 | 35 | 0 | 0 | 0 | 921 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 0 | 172 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1220 | 180 | 0 | 0 | 1 | 14 | 0 | 0 | 0 | 517 | 14 | 270 | 1032 | 37 | 0 | 0 | 21 | 45 | 0 |  |  |  | 123946957 | 22180363 | 0 | 74176830 | 32246325 | 1975680 | 4096149 | 118560 | 5150805 |  |  |  | 263891669
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 123.947 | 22.1804 | 0 | 74.1768 | 32.2463 | 1.9757 | 4.0961 | 0.11856 | 5.1508
| Minimum Generation |  | 10147 | 6:00
| Highest Generation |  | 13654 | 19:00 | [129 empty] | 0 | [76 empty] | 263.8917
| Day Peak Generation |  | 12174 | 12:00
| Evening Peak Generation |  | 13654 | 19:00 | [206 empty] | 202699852
| HVDC Max Flow |  | 921 | 3:00 | [206 empty] | 202.6999
| HVDC EvPeak Flow |  | 920 | 19:00
| Load factor L.F |  | 88.29% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-10-21
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-10-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12174 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 10246
Evening Peak Generation : |  |  | 13654 | MW Hour : | 19:00 | Available Max Generation : |  | 14740
E.P. Demand (at gen end) : |  |  | 13730 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13800
Maximum Generation : |  |  | 13654 | MW Hour : | 19:00 | Reserve(Generation end) |  | 940
Total Gen. (MKWH) : |  |  | 289.3262 | System Load Factor : | 88.29% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1250 | MW at | 18:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-10-21
Actual : |  | 104.47 | Ft.(MSL) , | Rule curve : | 107.8 | Ft.( MSL )
Gas Consumed : |  | Total = | 906.44 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 365313429.474 | Adani : | 168122263.13
|  |  | Coal : | 518571672.88 | Oil: | 589928392.88 | Total: | 1641935758.364
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 35 | 840:00 | 4630.817 |  |  | 0 | -8.715%
Chittagong Area |  | 0 | 0:00 | 1272.9296 |  |  | 0 | -6.726%
Khulna Area |  | 0 | 0:00 | 1783.2374 |  |  | 0 | -6.299%
Rajshahi Area |  | 0 | 0:00 | 1550.0593 |  |  | 0 | -5.848%
Cumilla Area |  | 0 | 0:00 | 1275.3707 |  |  | 0 | -6.128%
Mymensingh Area |  | 38 | 912:00 | 948.6126 |  |  | 0 | -5.736%
Sylhet Area |  | 0 | 0:00 | 531.6643 |  |  | 0 | -6.484%
Barisal Area |  | 0 | 0:00 | 443.1356 |  |  | 0 | -5.664%
Rangpur Area |  | 0 | 0:00 | 866.6942 |  |  | 0 | -5.674%
Total |  | 73 |  | 13302.5207 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:02 | 15:58 | Khulna (C) S/S Tr-2 415 T LT Scheduled S/D Due to For Annual Maintenance.
08:03 | 15:57 | Khulna (C) S/S Tr-2 415 T HT Scheduled S/D Due to For Annual maintenance.
08:11 | 16:26 | Bogura-Sirajganj 230 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to Annual
Maintenance. and from Sirajgonj 230 end Due to Annual Maintenance
08:18 | 17:20 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 LT Scheduled S/D Due to Annual
Maintenance
08:19 | 17:18 | Payra 400/132/33kV S/S 132/33 kV Transformer-04 HT Scheduled S/D Due to Annual
Maintenance
08:24 | 14:20 | Palashbari 132/33kV S/S TR2-404T LT Scheduled S/D Due to Annual maintenance
08:25 | 14:18 | Palashbari 132/33kV S/S TR2-404T HT Scheduled S/D Due to Annual maintenance
08:25 | 16:10 | Chandraghona-Rangamati 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end. and
from Rangamati 132/33kV end Due to Annual deadline checking
08:26 | 17:58 | Chauddagram-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to Annual
Maintenance. and from Chauddagram 132/33kV end Due to Annual Maintenance.
08:30 | 17:37 | Chandraghona-Madunaghat 132 kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to
Annual Maintenance and from Chandraghona 132/33kVend.
08:32 | 10:30 | Chowmuhani 132/33kV S/S TR2-425T LT Forced S/D Due to For 132KV Tr-02 shutdown 33kv |  |  |  |  | 25.0MW load interrup.
Incoming Y-Phase DS Red-HOT maintenance. Load shade will occur 25MW . Informed to all
utilities and XEN sir, GMD, PGCB, Cumilla.And All Consumer (PBS & PDB) Work will be done
by Power Grid, Chowmuhani
09:04 | 16:16 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Scheduled S/D Due to Annual Maintenance Work
09:05 | 16:15 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Scheduled S/D Due to Annual Maintenance work
| 09:20 | Shahjibazar 132/33kV S/S TR-02 HT is restored.
09:21 | 18:09 | Mymensingh-Netrokona 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to Annual
Maintenance Work
| 09:26 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 is restored.
| 09:34 | Shahjibazar 132/33kV S/S TR-02 LT is restored.
10:24 | 17:41 | Rajbari 132/33kV S/S 132 kV Bus-I Scheduled S/D Due to Annual maintenance
10:28 | 11:44 | BIPTC S/S 20DF13 Scheduled S/D Due to CB general fault
11:11 | 13:40 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Dhamrai 132/33kV end Due to Relay
testing by SPMD and from Kaliakoir 400/230/132kV end Due to Relay Test
11:42 | 12:56 | BIPTC S/S 10CF15 Tripped showing 87.1 relays Due to C1 unbalance 60/61 instant L2 trip
12:00 |  | Day Peak Generation = 12,178MW
12:12 | 12:56 | BIPTC S/S 10CF15 Scheduled S/D
12:45 | 13:50 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Tripped from Faridpur 132/33kV end showing Distance,
C-Phase, Reverse relays Due to LA Blast of 132KV Rajbari CKT-2
12:45 | 17:25 | Faridpur 132/33kV S/S 132 KV Rajbari ckt-2 Tripped showing Distance Zone-1, U Black, B
Phase relays Due to LA Blast B Phase
13:05 | 17:25 | Faridpur 132/33kV S/S 132 KV Rajbari ckt-2 Forced S/D Due to LA Blast B Phase
| 13:19 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT is restored.
| 13:29 | Ishurdi 132/33kV S/S 132/33 kV T-2 LT is restored.
13:31 | 15:17 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Forced S/D Due to due to pbs red hot |  |  |  |  | 20.0MW load interrup.
maintanance work
13:32 | 15:16 | Mirzapur 132/33kV S/S Transformer-01(E05) HT Forced S/D Due to due to pbs red hot
maintanance work
13:42 | 14:28 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Relay
testing by SPMD and from Kaliakoir 400/230/132kV end Due to Relay Test
13:43 | 14:43 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Forced S/D Due to 33KV Bajitpur Feeder incoming |  |  |  |  | 48.0MW load interrup.
loop burn
| 14:07 | Chandpur 132/33kV S/S 50MW(ST) Power Plant Incomer(T3) is restored.
| 14:12 | Bhulta-Rampura 230 kV Ckt-4 is restored.
| 15:30 | Barapukuria-Bogura 230 kV Ckt-1 is restored.
| 16:32 | Hathazari 230/132/33kV S/S MT-02 LT is restored.
| 16:32 | Hathazari 230/132/33kV S/S MT-02 HT is restored.
| 16:55 | Baroirhat-Feni 132 kV Ckt-2 is restored.
| 17:07 | Barishal 230/132kV S/S T-5 HT is restored.
| 17:11 | Barishal 230/132kV S/S T-5 LT is restored.
19:00 |  | Evening peak Generation is 13654 MW
22:18 | 23:04 | Joydebpur 132/33kV S/S GT-3 HT Scheduled S/D Due to Auxiliary transformer(AT-2) Y-Phase |  |  |  |  | 35.0MW load interrup.
cable maintenance
06:00 |  | Minimum Generation is 10246 MW
06:38 |  | Barapukuria-Bogura 230 kV Ckt-2 Project Work S/D from Barapukuria 230/132/33kV end Due to
Project work and from Bogura 400/230kV end Due to project work on barapukuria site
07:07 | 07:23 | Munshiganj 132/33kV S/S Transformer-1 LT Tripped showing no relays Due to 33kV Feeder |  |  |  |  | 37.0MW load interrup.
Munshiganj Zonal (PBS) : Trip Circuit Unhealthy
07:07 | 07:24 | Munshiganj 132/33kV S/S Transformer-2 LT Tripped showing No relays Due to 33kV Feeder
Munshiganj Zonal (PBS) : Trip Circuit Unhealthy
07:13 |  | Sherpur 132/33kV S/S Transformer- 03 LT Project Work S/D
07:14 |  | Sherpur 132/33kV S/S Transformer- 03 HT Project Work S/D
07:30 |  | Sherpur 132/33kV S/S Transformer- 02 HT Project Work S/D
07:30 |  | Sherpur 132/33kV S/S Transformer- 02 LT Project Work S/D
07:50 |  | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to 132 kv T2 CT connector temperature
maintenance work
07:50 |  | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to 132 kv T2 CT connector temperature
maintenance work

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-10-20
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 370 | 9428400 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9736500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 199282
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 290 | 7429631 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 86832 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 400932 | Engine problem
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 145 | 1466880
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 316799
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 427056 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 966960 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 601920 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 711300 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 34 | 376800 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 192 | 1181782 | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 113 | 1145232 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1024320 | Engine problem
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 4 | 135360 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1205280
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 160114
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432360 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 200 | 4494541 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 2336 | 41928281
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 247780
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 102330
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 197310 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 213 | 5150805
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 148 | 3584603 | ST under maint
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 123781 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 39 | 645936 | Engine problem
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 544301 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 1072320 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 478080
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 19 | 364800 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25320
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1216909 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 489076 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 20 | 205745 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 247680 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 440345 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 160 | 511855
60 | SS Power I |  | SS Power | 2*612 | 1224 | 610 | 13025453 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 60 | 9 | 118560
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 212 | 5221818 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1811 | 34014807
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 218 | 5241000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7654800
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 295 | 7660300 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 1023120
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 5 | 126240 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 869818 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 944432 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 74 | 682472 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 29 | 236944 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1472460 | Gas shortage
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 181 | 2553600 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 88 | 1975680
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 137520 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 305290 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1015740 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 77 | 1090320 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 91 | 1128960 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 410864
| Cumilla Area Total |  |  |  | 2917 | 1674 | 34529560
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 12 | 355200 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11950
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 154 | 3004800 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 1804800 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 316160
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 150960 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 115560 | Fuel shortage
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 58800
| Mymensingh Area Total |  |  |  | 646 | 280 | 5818230
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 28 | 669000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 704400 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3663900 | Frequency control
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 52 | 1204800
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 33 | 832896 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 89712 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 58 | 1388928
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2049600
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 207 | 5188480 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 363000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 280656 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7257000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 339 | 9011000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2417 | 1262 | 32703372
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 920 | 22180363
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Auxiliary problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 57 | 215040 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 285 | 7811712 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 109440 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 544320
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 619 | 12814550 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1898 | 43675425
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 52128 | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 8 | 178859 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 100 | 3066000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 29444700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 180 | 3854740 | Frequency control
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1536000
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 6611000
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 3740
| Barisal Area Total |  |  |  | 2236 | 1945 | 44747167
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 37 | 233956 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 265300
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4384636 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 318 | 8698181 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 174592 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 164862 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 617616 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 108 | 340704
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 945216
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34320
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1035 | 25434533
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 404250
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 661800
| Rajshahi Area Total |  |  |  | 3449 | 1956 | 42359966
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 64 | 1465309
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5594000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 605232
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35754
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 463872 | Fuel shortage
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 187867
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1197360
| Rangpur Area Total |  |  |  | 950 | 492 | 9549394
| Total |  |  |  | 27086 | 13654 | 289326202
| Eastern Grid Total |  |  |  | 16752 | 7363 | 148994250
| Western Grid Total |  |  |  | 10334 | 6291 | 140331952
| National Grid Total |  |  |  | 27086 | 13654 | 289326202
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-10-20
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9275.68 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4274.2 | MW
i) Dhaka area |  |  | 4986.08 |  | MW | i) Khulna area |  |  |  | 1644.9 | MW
ii) Chattogram area |  |  | 1281.6 |  | MW | ii) Barishal area |  |  |  | 461.5 | MW
iii) Cumilla area |  |  | 1346 |  | MW | iii) Rajshahi area |  |  |  | 1364.8 | MW
iv) Mymensingh area |  |  | 1097 |  | MW | iv) Rangpur area |  |  |  | 803 | MW
v) Sylhet area |  |  | 565 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13549.88 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jashore | 120 | 18:30 | 133 | Rajbari | 70 | 18:00
2 | AKSML | 88.5 | 00:00 | 68 | Jhenaidah | 113 | 18:30 | 134 | Rajendrapur | 100 | 18:30
3 | Aftabnagar | 54 | 13:00 | 69 | Joydebpur | 182 | 18:30 | 135 | Rajshahi | 106 | 21:00
4 | Agargaon | 113 | 12:00 | 70 | Joypurhat | 50 | 18:30 | 136 | Rajshahi-230 | 71 | 13:00
5 | Agrabad | 96 | 18:30 | 71 | Juldah | 15 | 00:00 | 137 | Ramganj | 106 | 00:00
6 | Amnura | 53 | 18:30 | 72 | KSRM | 20 | 22:00 | 138 | Rampur | 39 | 18:00
7 | Ashuganj | 80 | 02:00 | 73 | Kabirpur | 276 | 19:00 | 139 | Rangamati | 17 | 18:00
8 | BSRM | 132 | 10:00 | 74 | Kachua | 78 | 18:00 | 140 | Rangpur | 133 | 18:30
9 | Bagerhat | 80 | 21:00 | 75 | Kallyanpur | 102 | 18:00 | 141 | Ruppur | 6.8 | 10:00
10 | Bakulia | 99 | 18:00 | 76 | Kalurghat | 38 | 15:00 | 142 | SSM | 15 | 01:00
11 | Banani | 67 | 13:00 | 77 | Kamrangirchar | 60 | 13:00 | 143 | Saidpur | 99 | 18:30
12 | Bangabhaban | 23 | 10:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 111 | 18:30
13 | Barapukuria | 56 | 18:00 | 79 | Kazla | 84 | 01:00 | 145 | Satmasjid | 100 | 13:00
14 | Barguna | 20 | 00:00 | 80 | Keranigonj | 74 | 18:30 | 146 | Savar | 218 | 14:00
15 | Barishal | 101 | 18:30 | 81 | Khagrachori | 32 | 18:00 | 147 | SevenRings | 15.03 | 00:00
16 | Barishal-230 | 80 | 18:00 | 82 | Khulna | 78 | 13:00 | 148 | ShahCement | 14 | 13:00
17 | Baroaulia | 64 | 15:00 | 83 | Khulshi | 167 | 12:00 | 149 | Shahjadpur | 80 | 18:30
18 | Baroirhat | 66 | 18:00 | 84 | Kishoreganj | 136 | 00:00 | 150 | Shahjibazar | 131 | 21:00
19 | Bashundhara | 169 | 13:00 | 85 | Kodda | 313 | 18:30 | 151 | Shahmirpur | 53 | 00:00
20 | BashundharaCement | 7 | 02:00 | 86 | Kulaura | 44 | 18:00 | 152 | Shariatpur | 73 | 21:00
21 | Beanibazar | 68 | 18:00 | 87 | Kurigram | 52 | 18:30 | 153 | Sherpur | 126 | 18:30
22 | Benapole | 52 | 18:30 | 88 | Kushtia | 128 | 18:30 | 154 | Shikalbaha | 24 | 00:00
23 | Bhaluka | 136 | 18:00 | 89 | Lalbag | 82 | 13:00 | 155 | Shitalakhya | 84.4 | 12:00
24 | Bhandaria | 47 | 22:00 | 90 | Lalmonirhat | 49 | 18:30 | 156 | Sholosohor | 45 | 18:00
25 | Bhangura | 32 | 18:30 | 91 | MI_Cement | 14.6 | 07:00 | 157 | Shyampur | 162 | 14:00
26 | Bheramara(GK) | 56 | 18:30 | 92 | Madanganj | 35 | 00:00 | 158 | Siddhirganj | 114 | 09:00
27 | Bhulta | 240 | 09:00 | 93 | Madaripur | 92 | 22:00 | 159 | Sirajganj | 88 | 19:00
28 | Bog-Sherpur | 58 | 18:00 | 94 | Madartek | 79.76 | 19:00 | 160 | Sonargaon | 75 | 09:00
29 | Bogura | 145 | 18:30 | 95 | Madunaghat | 49 | 18:00 | 161 | Sreemongol | 68 | 00:00
30 | Borhanuddin | 68 | 21:00 | 96 | Magura | 56 | 18:00 | 162 | Sreepur | 73 | 18:30
31 | Brahmanbaria | 170 | 18:30 | 97 | Mahasthangarh | 62 | 18:00 | 163 | Srinagar | 41.7 | 21:00
32 | Cantonment | 108 | 13:00 | 98 | Manikganj | 124 | 18:00 | 164 | Sunamganj | 50 | 18:00
33 | Chandpur | 58 | 18:00 | 99 | Maniknagar | 64 | 11:00 | 165 | Sylhet | 44 | 18:30
34 | Chandraghona | 35 | 18:00 | 100 | Matarbari | 49 | 18:00 | 166 | Sylhet-132 | 113 | 18:00
35 | Chapai | 58 | 21:00 | 101 | Matuail | 60 | 09:00 | 167 | TK | 33 | 18:30
36 | Charsaidpur | 40 | 15:00 | 102 | Millgate | 119 | 12:00 | 168 | Tangail | 180 | 18:30
37 | Chauddagram | 65 | 18:00 | 103 | Mirpur | 131 | 13:00 | 169 | Thakurgaon | 83 | 18:30
38 | Chhatak | 30 | 18:00 | 104 | Mirsorai | 6 | 18:00 | 170 | Tongi | 130 | 09:00
39 | Chowmuhani | 211 | 19:00 | 105 | Mirzapur | 36 | 18:00 | 171 | Ullahpara | 42 | 18:00
40 | Chuadanga | 100 | 18:30 | 106 | Mithapukur | 50 | 18:00 | 172 | Ullon | 54 | 19:30
41 | Coxsbazar | 115 | 19:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 82 | 13:00
42 | Cumilla(N) | 143 | 18:00 | 108 | Mogbazar | 120.8 | 15:00 | 174 | UttaraNew | 50 | 18:00
43 | Cumilla(S) | 179 | 18:00 | 109 | Mongla | 44 | 10:00 | 175 | Zigatola | 87 | 00:00
44 | Daudkandi | 152 | 18:30 | 110 | Motijheel | 43 | 13:00
45 | Dhaka | 39 | 13:00 | 111 | Munshiganj | 94 | 00:00
46 | Dhamrai | 122 | 18:00 | 112 | Mymensingh | 212 | 19:30
47 | Dhanmondi | 136 | 13:00 | 113 | Naogaon | 112 | 18:30
48 | Dohazari | 109 | 18:00 | 114 | Narail | 50 | 18:00
49 | Faridpur | 141 | 18:00 | 115 | Narinda | 72 | 13:00
50 | Fatullah | 93 | 10:00 | 116 | Narshingdi | 171 | 21:00
51 | Fenchuganj | 38 | 19:30 | 117 | Natore | 133 | 18:30
52 | Feni | 94 | 18:30 | 118 | Nawabganj | 49.4 | 20:00
53 | GPH | 96 | 04:00 | 119 | Netrakona | 119 | 18:00
54 | Ghatail | 54 | 19:00 | 120 | New | 54 | 11:00
55 | Ghorashal | 62 | 19:00 | 121 | Niamatpur | 52 | 21:00
56 | Goalpara | 30 | 12:00 | 122 | Noapara | 39 | 18:00
57 | Gollamari | 66 | 18:30 | 123 | PHP | 2 | 06:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-10-20 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 386 | 07:00 | 369 | 13:00 | Kaliakoir | 369 | 19:00 | 354 | 12:00
| Ashuganj | 404 | 5:00 | 385 | 13:00 | Madunaghat | 397 | 19:00 | 387 | 15:00
| Bhulta | 397 | 05:00 | 382 | 11:00 | Meghnaghat | 381 | 05:00 | 368 | 16:00
| Bibiana | 391 | 02:00 | 381 | 11:00 | Payra | 411 | 05:00 | 402 | 16:00
| BIPTC | 403 | 06:00 | 395 | 18:30 | Rahanpur | 393 | 06:00 | 385 | 13:00
| Bogura | 380 | 06:00 | 370 | 13:00 | Rampal | 400 | 05:00 | 384 | 22:00
| Gopalganj | 396 | 05:00 | 360 | 17:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 229 | 01:00 | 217 | 10:00 | Haripur | 229 | 02:00 | 219 | 12:00
| AKSML | 238 | 00:00 | 223 | 08:00 | Hasnabad | 229 | 04:00 | 218 | 12:00
| Aminbazar | 229 | 05:00 | 215 | 16:00 | Hathazari | 240 | 18:30 | 233 | 12:00
| Ashuganj | 233 | 07:00 | 225 | 10:00 | Ishurdi | 232 | 00:00 | 225 | 12:00
| Ashuganj-400 | 234 | 5:00 | 224 | 13:00 | Jhenaidah | 226 | 06:00 | 215 | 12:00
| Baghabari | 229 | 05:00 | 222 | 11:00 | Kaliakoir | 229 | 05:00 | 218 | 10:00
| Barapukuria | 222 | 20:00 | 215 | 13:00 | Keranigonj | 228 | 05:00 | 216 | 10:00
| Barapukuria-230 | 221 | 21:00 | 216 | 14:00 | Khulna(S) | 228 | 05:00 | 217 | 13:00
| Barishal | 236 | 06:00 | 229 | 15:00 | Madunaghat | 240 | 19:00 | 234 | 10:00
| Bheramara | 230 | 00:00 | 223 | 12:00 | Maniknagar | 230 | 05:00 | 220 | 11:00
| Bhulta | 231 | 05:00 | 221 | 11:00 | Meghnaghat | 238 | 00:00 | 229 | 10:00
| Bibiana | 227 | 19:00 | 220 | 09:00 | Meghnaghat-400 | 233 | 05:00 | 224 | 10:00
| BIPTC | 232 | 05:00 | 223 | 12:00 | Mirsorai | 240 | 19:00 | 226 | 13:00
| Bogura | 230 | 01:00 | 224 | 13:00 | Rajshahi | 234 | 06:00 | 224 | 13:00
| Bogura-400 | 232 | 05:00 | 226 | 12:00 | Rampal | 228 | 06:00 | 218 | 13:00
| Borhanuddin | 239 | 06:00 | 234 | 14:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 239 | 19:00 | 226 | 10:00 | Rampura | 230 | 04:00 | 218 | 12:00
| Cumilla(N) | 229 | 19:00 | 220 | 12:00 | Shikalbaha | 240 | 19:00 | 230 | 10:00
| Faridpur | 234 | 06:00 | 226 | 12:00 | Shyampur | 229 | 04:00 | 218 | 11:00
| Fenchuganj | 230 | 07:00 | 224 | 11:00 | Siddhirganj | 232 | 04:00 | 222 | 11:00
| Ghorashal | 232 | 00:00 | 230 | 08:00 | Sirajgonj | 237 | 04:00 | 233 | 11:00
| Ghorashal-230 | 228 | 05:00 | 217 | 10:00 | Sreepur | 230 | 07:00 | 220 | 15:00
| Gopalganj | 235 | 07:00 | 226 | 13:00 | Tongi | 227 | 04:00 | 215 | 11:00
| GPH | 240 | 19:00 | 230 | 09:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 135 | 05:00 | 125 | 12:00 | Kushtia | 134 | 01:00 | 129 | 18:30
| Agargaon | 135 | 04:00 | 127 | 10:00 | Lalbag | 135 | 05:00 | 126 | 10:00
| Agrabad | 135 | 18:30 | 130 | 10:00 | Lalmonirhat | 132 | 21:00 | 125 | 13:00
| AKS | 134 | 18:30 | 129 | 16:00 | Madanganj | 129 | 18:30 | 121 | 10:00
| Aminbazar | 139 | 02:00 | 124 | 14:00 | Madaripur | 130 | 00:00 | 126 | 13:00
| Amnura | 137 | 00:00 | 123 | 22:00 | Madartek | 135 | 07:00 | 125 | 11:00
| Ashuganj | 137 | 05:00 | 135 | 11:00 | Madunaghat | 138 | 18:30 | 131 | 10:00
| Bagerhat | 131 | 06:00 | 122 | 23:00 | Magura | 134 | 06:00 | 125 | 18:30
| Bakulia | 137 | 19:00 | 132 | 10:00 | Mahasthangarh | 136 | 05:00 | 131 | 13:00
| Banani | 135 | 05:00 | 124 | 12:00 | Manikganj | 125 | 18:30 | 116 | 12:00
| Bangabhaban | 131 | 07:00 | 122 | 12:00 | Maniknagar | 131 | 05:00 | 122 | 12:00
| Barapukuria | 138 | 20:00 | 131 | 13:00 | Matarbari | 123 | 07:00 | 118 | 00:00
| Barguna | 139 | 00:00 | 133 | 09:00 | Matuail | 130 | 19:00 | 124 | 10:00
| Barishal | 131 | 06:00 | 125 | 13:00 | Millgate | 132 | 04:00 | 122 | 12:00
| Barishal-230 | 131 | 04:00 | 126 | 13:00 | Mirpur | 137 | 05:00 | 127 | 10:00
| Baroaulia | 137 | 18:30 | 132 | 12:00 | Mirzapur | 127 | 00:00 | 119 | 16:00
| Baroirhat | 130 | 18:30 | 122 | 23:00 | Mithapukur | 135 | 20:00 | 127 | 13:00
| Bashundhara | 135 | 04:00 | 122 | 12:00 | MI_Cement | 134 | 05:00 | 125 | 10:00
| BashundharaCement | 127 | 19:00 | 121 | 10:00 | Modern | 135 | 18:30 | 131 | 13:00
| Beanibazar | 128 | 06:00 | 123 | 18:00 | Mogbazar | 135 | 03:00 | 125 | 12:00
| Benapole | 131 | 06:00 | 121 | 18:30 | Mongla | 130 | 06:00 | 123 | 12:00
| Bhaluka | 128 | 04:00 | 122 | 15:00 | Motijheel | 131 | 07:00 | 122 | 12:00
| Bhandaria | 126 | 07:00 | 119 | 22:00 | Munshiganj | 128 | 04:00 | 123 | 10:00
| Bhangura | 137 | 04:00 | 132 | 12:00 | Mymensingh | 135 | 19:00 | 118 | 19:30
| Bheramara | 136 | 06:00 | 133 | 11:00 | Naogaon | 136 | 00:00 | 122 | 23:00
| Bheramara(GK) | 136 | 06:00 | 132 | 12:00 | Narail | 132 | 04:00 | 123 | 18:00
| Bhulta | 120 | 04:00 | 113 | 12:00 | Narinda | 131 | 5:00 | 122 | 12:00
| Bog-Sherpur | 137 | 06:00 | 132 | 12:00 | Narshingdi | 121 | 19:00 | 113 | 10:00
| Bogura | 139 | 06:00 | 132 | 10:00 | Natore | 135 | 05:00 | 130 | 13:00
| Bogura-230 | 139 | 01:00 | 134 | 13:00 | Nawabganj | 135 | 06:00 | 126 | 10:00
| Brahmanbaria | 130 | 07:00 | 122 | 23:00 | Netrakona | 134 | 00:00 | 121 | 14:00
| Cantonment | 135 | 04:00 | 126 | 10:00 | New | 131 | 04:00 | 123 | 11:00
| Chandpur | 136 | 18:30 | 122 | 15:00 | Niamatpur | 131 | 06:00 | 127 | 12:00
| Chandraghona | 137 | 19:00 | 133 | 10:00 | Noapara | 133 | 05:00 | 126 | 12:00
| Chapai | 130 | 06:00 | 125 | 13:00 | Pabna | 135 | 04:00 | 130 | 12:00
| Charsaidpur | 130 | 19:00 | 122 | 13:00 | Palashbari | 133 | 20:00 | 127 | 13:00
| Chauddagram | 130 | 18:30 | 120 | 15:00 | Panchagarh | 135 | 21:00 | 118 | 13:00
| Chhatak | 129 | 05:00 | 124 | 19:30 | Patuakhali | 139 | 00:00 | 133 | 04:00
| Chowmuhani | 128 | 18:00 | 114 | 13:00 | Payra | 137 | 00:00 | 134 | 10:00
| Chuadanga | 129 | 06:00 | 118 | 18:30 | PHP | 130 | 07:00 | 122 | 23:00
| Coxsbazar | 124 | 18:00 | 118 | 13:00 | Postogola | 137 | 01:00 | 128 | 10:00
| Cumilla(N) | 132 | 18:30 | 126 | 11:00 | Purbachal | 135 | 04:00 | 122 | 10:00
| Cumilla(S) | 131 | 19:00 | 123 | 15:00 | Purbasadipur | 135 | 21:00 | 122 | 13:00
| Daudkandi | 127 | 18:30 | 120 | 14:00 | Rahanpur | 133 | 05:00 | 130 | 12:00
| Dhaka | 135 | 05:00 | 125 | 12:00 | Rahim | 129 | 06:00 | 123 | 12:00
| Dhamrai | 131 | 05:00 | 119 | 12:00 | Rajbari | 130 | 05:00 | 123 | 13:00
| Dhanmondi | 135 | 06:00 | 125 | 13:00 | Rajendrapur | 127 | 19:30 | 114 | 12:00
| Dohazari | 132 | 18:30 | 127 | 13:00 | Rajshahi | 135 | 05:00 | 131 | 10:00
| Faridpur | 131 | 05:00 | 126 | 13:00 | Rajshahi-230 | 134 | 00:00 | 119 | 13:00
| Fatullah | 134 | 05:00 | 126 | 10:00 | Ramganj | 129 | 18:30 | 116 | 15:00
| Fenchuganj | 135 | 06:00 | 132 | 00:00 | Rampur | 136 | 18:00 | 130 | 14:00
| Feni | 130 | 18:30 | 120 | 01:00 | Rampura | 134 | 04:00 | 124 | 12:00
| Ghatail | 129 | 00:00 | 121 | 01:00 | Rangamati | 135 | 19:00 | 131 | 13:00
| Ghorashal | 135 | 00:00 | 130 | 12:00 | Rangpur | 134 | 21:00 | 125 | 13:00
| Goalpara | 135 | 05:00 | 127 | 18:00 | Ruppur | 136 | 03:00 | 132 | 13:00
| Gollamari | 135 | 06:00 | 128 | 13:00 | Saidpur | 135 | 19:30 | 125 | 13:00
| Gopalganj | 132 | 05:00 | 126 | 22:00 | Satkhira | 133 | 06:00 | 124 | 18:30
| Gopalganj-400 | 132 | 05:00 | 127 | 12:00 | Satmasjid | 135 | 05:00 | 126 | 10:00
| Gulshan | 134 | 03:00 | 125 | 12:00 | Savar | 137 | 19:00 | 127 | 14:00
| Halishahar | 137 | 19:00 | 131 | 10:00 | SevenRings | 136 | 05:00 | 130 | 10:00
| Haripur | 129 | 07:00 | 123 | 12:00 | ShahCement | 130 | 19:00 | 122 | 13:00
| HaripurSBU | 129 | 06:00 | 123 | 12:00 | Shahjadpur | 143 | 04:00 | 136 | 10:00
| Hasnabad | 135 | 03:00 | 127 | 10:00 | Shahjibazar | 132 | 07:00 | 125 | 23:00
| Hathazari | 140 | 18:30 | 135 | 10:00 | Shahmirpur | 137 | 19:00 | 132 | 13:00
| Ishurdi | 136 | 00:00 | 133 | 12:00 | Shariatpur | 131 | 06:00 | 124 | 22:00
| Jaldhaka | 133 | 21:00 | 122 | 13:00 | Sherpur | 137 | 10:00 | 127 | 01:00
| Jamalpur | 139 | 00:00 | 130 | 01:00 | Shikalbaha | 125 | 00:00 | 120 | 13:00
| Jashore | 130 | 04:00 | 123 | 18:30 | Shikalbaha-230 | 136 | 18:30 | 131 | 10:00
| Jhenaidah | 134 | 03:00 | 126 | 18:30 | Shitalakhya | 134 | 05:00 | 125 | 10:00
| Jhenaidah-230 | 135 | 06:00 | 127 | 18:30 | Sholosohor | 136 | 19:00 | 131 | 10:00
| Joydebpur | 136 | 18:00 | 124 | 13:00 | Shyampur | 131 | 01:00 | 125 | 11:00
| Joypurhat | 129 | 05:00 | 121 | 18:30 | Shyampur-230 | 133 | 04:00 | 124 | 11:00
| Juldah | 137 | 19:00 | 132 | 08:00 | Siddhirganj | 130 | 05:00 | 124 | 10:00
| Kabirpur | 130 | 02:00 | 118 | 11:00 | Sirajganj | 135 | 03:00 | 129 | 12:00
| Kachua | 134 | 19:00 | 122 | 15:00 | Sonargaon | 129 | 19:00 | 121 | 12:00
| Kaliakoir | 132 | 05:00 | 122 | 10:00 | Sreemongol | 132 | 07:00 | 127 | 18:00
| Kallyanpur | 130 | 01:00 | 124 | 16:00 | Sreepur | 130 | 04:00 | 125 | 13:00
| Kalurghat | 137 | 19:30 | 132 | 10:00 | Srinagar | 134 | 05:00 | 126 | 12:00
| Kamrangirchar | 134 | 05:00 | 123 | 12:00 | SSM | 140 | 08:00 | 136 | 11:00
| Kaptai | 133 | 7:00 | 128 | 16:00 | Sunamganj | 127 | 06:00 | 122 | 13:00
| Kazla | 130 | 04:00 | 122 | 12:00 | Sylhet | 131 | 08:00 | 126 | 22:00
| Keranigonj | 135 | 05:00 | 127 | 10:00 | Sylhet-132 | 130 | 06:00 | 127 | 12:00
| Khagrachori | 134 | 07:00 | 129 | 15:00 | Tangail | 127 | 19:00 | 119 | 01:00
| Khulna | 135 | 05:00 | 127 | 13:00 | Thakurgaon | 137 | 21:00 | 119 | 13:00
| Khulna(S) | 136 | 06:00 | 128 | 13:00 | TK | 136 | 18:30 | 132 | 12:00
| Khulshi | 135 | 19:00 | 129 | 16:00 | Tongi | 134 | 04:00 | 125 | 11:00
| Kishoreganj | 130 | 04:00 | 124 | 23:00 | Ullahpara | 138 | 02:00 | 132 | 12:00
| Kodda | 130 | 18:30 | 113 | 11:00 | Ullon | 134 | 05:00 | 125 | 13:00
| KSRM | 138 | 18:30 | 132 | 02:00 | Uttara | 137 | 05:00 | 127 | 10:00
| Kulaura | 134 | 08:00 | 131 | 01:00 | UttaraNew | 137 | 04:00 | 128 | 10:00
| Kurigram | 133 | 21:00 | 124 | 07:00 | Zigatola | 134 | 05:00 | 127 | 12:00

## L-Curve
Date | 2024-10-20
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1630 | 6248 | 6214 | 12462 |  |  |  | QF-LDC-11
0:30 | 1534 | 6094.5 | 5999 | 12093.5 | Date: | 2024-10-20
1:00 | 1438 | 5941 | 5784 | 11725
1:30 | 1414 | 5830.5 | 5669 | 11499.5
2:00 | 1390 | 5720 | 5554 | 11274
2:30 | 1423 | 5670 | 5442.5 | 11112.5 | [5 empty] | Gen. at Eve. Peak | 13654 | 13654 MW (19:00 )
3:00 | 1456 | 5620 | 5331 | 10951 | [6 empty] | 19:00
3:30 | 1468 | 5567.5 | 5236.5 | 10804 | [5 empty] | Gen. at Day Peak | 12174 | 12174 MW (12:00 )
4:00 | 1480 | 5515 | 5142 | 10657 | [6 empty] | 12:00
4:30 | 1485 | 5463 | 5053.5 | 10516.5 | [5 empty] | Highest Generation | 13654
5:00 | 1490 | 5411 | 4965 | 10376 | [6 empty] | 19:00
5:30 | 1520 | 5319.5 | 4942 | 10261.5
6:00 | 1550 | 5228 | 4919 | 10147
6:30 | 1404 | 5426.5 | 4938 | 10364.5
7:00 | 1258 | 5625 | 4957 | 10582
7:30 | 1370 | 5469.5 | 5042 | 10511.5
8:00 | 1482 | 5314 | 5127 | 10441
8:30 | 1642 | 5422.5 | 5252 | 10674.5
9:00 | 1802 | 5531 | 5377 | 10908
9:30 | 1822 | 5670 | 5472.5 | 11142.5
10:00 | 1842 | 5809 | 5568 | 11377
10:30 | 1812 | 5887.5 | 5635.5 | 11523
11:00 | 1782 | 5966 | 5703 | 11669
11:30 | 1733 | 6150.5 | 5771 | 11921.5
12:00 | 1684 | 6335 | 5839 | 12174
12:30 | 1671 | 6363.5 | 5889 | 12252.5
13:00 | 1658 | 6392 | 5939 | 12331
13:30 | 1579 | 6437 | 5895.5 | 12332.5
14:00 | 1500 | 6482 | 5852 | 12334
14:30 | 1539 | 6479 | 5884.5 | 12363.5
15:00 | 1578 | 6476 | 5917 | 12393
15:30 | 1586 | 6442.5 | 5854 | 12296.5
16:00 | 1594 | 6409 | 5791 | 12200
16:30 | 1529 | 6423.5 | 5656 | 12079.5
17:00 | 1464 | 6438 | 5521 | 11959
17:30 | 1427 | 6753.5 | 5795.5 | 12549
18:00 | 1390 | 7069 | 6070 | 13139
18:30 | 1339 | 7216 | 6180.5 | 13396.5
19:00 | 1288 | 7363 | 6291 | 13654
19:30 | 1372 | 7063 | 6411 | 13474
20:00 | 1410 | 6962 | 6411 | 13373 |  |  |  | Executive Engineer
20:30 | 1443 | 6800 | 6436.5 | 13236.5 |  |  |  | Network Operation Division
21:00 | 1476 | 6638 | 6462 | 13100
21:30 | 1486 | 6541.5 | 6403 | 12944.5
22:00 | 1496 | 6445 | 6344 | 12789 |  |  |  |  | Page 6 of 7
22:30 | 1519 | 6378 | 6324.5 | 12702.5
23:00 | 1542 | 6311 | 6305 | 12616
23:30 | 1586 | 6279.5 | 6259.5 | 12539
24:00 | 1630 | 6248 | 6214 | 12462
13654 MW (19:00 )
12174 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-10-20 |  | Energy |  | 289326202
[16 empty] | 2024-10-20 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3221 | 920 | 1809 | 0 | 1481 | 3181 | 216 | 0 | 427 | 92 | 1109 | 0 | 6 | 0
0:30 | 3297 | 914.5 | 1838.5 | 0 | 1207.5 | 3157 | 216 | 0 | 300.5 | 87 | 1072.5 | 0 | 3 | 19.1 |  |  | Date: | 44123
1:00 | 3373 | 909 | 1868 | 0 | 934 | 3133 | 216 | 0 | 174 | 82 | 1036 | 0 | 0 | 38.2
1:30 | 3310 | 911.5 | 1860.5 | 0 | 813 | 3136 | 215 | 0 | 137.5 | 81 | 1034.5 | 0 | 0.5 | 36.29 | [8 empty] | Total Energy | 289.3262 | 289.3262 | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 3247 | 914 | 1853 | 0 | 692 | 3139 | 214 | 0 | 101 | 80 | 1033 | 0 | 1 | 34.38 | [8 empty] | Energy not Served | 0.8572 | 0.8572
2:30 | 3261.5 | 917.5 | 1844.5 | 0 | 615 | 3067.5 | 213 | 0 | 70.5 | 84 | 1034.5 | 0 | 4.5 | 31.0375 | [8 empty] | Energy Requirement | 290.1834 | 290.1834
3:00 | 3276 | 921 | 1836 | 0 | 538 | 2996 | 212 | 0 | 40 | 88 | 1036 | 0 | 8 | 27.695
3:30 | 3240.5 | 920.5 | 1840 | 0 | 514 | 2912 | 211.5 | 0 | 32 | 87 | 1034 | 0 | 12.5 | 27.2175 | [7 empty] | Shortage
4:00 | 3205 | 920 | 1844 | 0 | 490 | 2828 | 211 | 0 | 24 | 86 | 1032 | 0 | 17 | 26.74
4:30 | 3219 | 920 | 1865.5 | 0 | 456 | 2694.5 | 211 | 0 | 20 | 84 | 1033 | 0 | 13.5 | 13.37
5:00 | 3233 | 920 | 1887 | 0 | 422 | 2561 | 211 | 0 | 16 | 82 | 1034 | 0 | 10 | 0
5:30 | 3199 | 919.5 | 1842 | 0 | 408.5 | 2539.5 | 211.5 | 0 | 16 | 78 | 1034 | 0.5 | 13 | 0
6:00 | 3165 | 919 | 1797 | 0 | 395 | 2518 | 212 | 0 | 16 | 74 | 1034 | 1 | 16 | 0
6:30 | 3207 | 920 | 1908 | 0 | 413 | 2523.5 | 212.5 | 0 | 16 | 75 | 1033.5 | 40.5 | 15.5 | 0 | [6 empty] | Coal
7:00 | 3249 | 921 | 2019 | 0 | 431 | 2529 | 213 | 0 | 16 | 76 | 1033 | 80 | 15 | 0
7:30 | 3243 | 921 | 1865.5 | 0 | 440.5 | 2547.5 | 213.5 | 0 | 24 | 74 | 1033.5 | 141 | 8 | 0 | [5 empty] | Oil
8:00 | 3237 | 921 | 1712 | 0 | 450 | 2566 | 214 | 0 | 32 | 72 | 1034 | 202 | 1 | 0
8:30 | 3266 | 920.5 | 1713 | 0 | 523 | 2594 | 214.5 | 0 | 40 | 71 | 1034.5 | 297.5 | 0.5 | 0
9:00 | 3295 | 920 | 1714 | 0 | 596 | 2622 | 215 | 0 | 48 | 70 | 1035 | 393 | 0 | 0
9:30 | 3315.5 | 920 | 1728 | 0 | 627.5 | 2714.5 | 215 | 0 | 48 | 73 | 1034.5 | 466 | 0.5 | 0
10:00 | 3336 | 920 | 1742 | 0 | 659 | 2807 | 215 | 0 | 48 | 76 | 1034 | 539 | 1 | 0
10:30 | 3312.5 | 920 | 1692.5 | 0 | 751 | 2887.5 | 215.5 | 0 | 48 | 77 | 1035.5 | 583 | 0.5 | 15
11:00 | 3289 | 920 | 1643 | 0 | 843 | 2968 | 216 | 0 | 48 | 78 | 1037 | 627 | 0 | 30
11:30 | 3299 | 920 | 1707.5 | 0 | 937.5 | 3024.5 | 216 | 0 | 75 | 82 | 1035 | 625 | 0 | 61
12:00 | 3309 | 920 | 1772 | 0 | 1032 | 3081 | 216 | 0 | 102 | 86 | 1033 | 623 | 0 | 92
12:30 | 3312 | 920 | 1823 | 0 | 1037 | 3113.5 | 216 | 0 | 100.5 | 88 | 1035 | 603 | 4.5 | 87.065
13:00 | 3315 | 920 | 1874 | 0 | 1042 | 3146 | 216 | 0 | 99 | 90 | 1037 | 583 | 9 | 82.13
13:30 | 3315 | 920 | 1874 | 0 | 1042 | 3146 | 216 | 0 | 99 | 90 | 1037 | 583 | 9 | 82.13
14:00 | 3315 | 920 | 1874 | 0 | 1042 | 3146 | 216 | 0 | 99 | 90 | 1037 | 583 | 9 | 82.13
14:30 | 3281.5 | 920 | 1957 | 0 | 1133.5 | 3160.5 | 215 | 0 | 102 | 87 | 1038.5 | 461.5 | 5.5 | 82.6075
15:00 | 3248 | 920 | 2040 | 0 | 1225 | 3175 | 214 | 0 | 105 | 84 | 1040 | 340 | 2 | 83.085
15:30 | 3244.5 | 920 | 2033 | 0 | 1238.5 | 3171.5 | 214 | 0 | 99.5 | 83 | 1038.5 | 253 | 1 | 79.7425
16:00 | 3241 | 920 | 2026 | 0 | 1252 | 3168 | 214 | 0 | 94 | 82 | 1037 | 166 | 0 | 76.4
16:30 | 3232.5 | 920 | 2030.5 | 0 | 1284 | 3079.5 | 214 | 0 | 106 | 79 | 1034.5 | 96.5 | 3 | 67.3275
17:00 | 3224 | 920 | 2035 | 0 | 1316 | 2991 | 214 | 0 | 118 | 76 | 1032 | 27 | 6 | 58.255
17:30 | 3258.5 | 920 | 2046 | 0 | 1661 | 3030.5 | 213.5 | 0 | 285 | 81 | 1033.5 | 13.5 | 6.5 | 72.58
18:00 | 3293 | 920 | 2057 | 0 | 2006 | 3070 | 213 | 0 | 452 | 86 | 1035 | 0 | 7 | 86.905
18:30 | 3191 | 920 | 1951 | 0 | 2254 | 3156 | 213 | 0 | 581.5 | 87 | 1035 | 0 | 8 | 79.9525
19:00 | 3089 | 920 | 1845 | 0 | 2502 | 3242 | 213 | 0 | 711 | 88 | 1035 | 0 | 9 | 73
19:30 | 3061 | 920 | 1861 | 0 | 2224 | 3242 | 213 | 0 | 718 | 88 | 1145 | 0 | 2 | 63.5
20:00 | 3076 | 920 | 1807 | 0 | 2179 | 3253 | 214 | 0 | 704 | 88 | 1132 | 0 | 0 | 54
20:30 | 3077 | 920 | 1819.5 | 0 | 2068.5 | 3272.5 | 214.5 | 0 | 642 | 87 | 1135.5 | 0 | 0 | 51
21:00 | 3078 | 920 | 1832 | 0 | 1958 | 3292 | 215 | 0 | 580 | 86 | 1139 | 0 | 0 | 48
21:30 | 3146 | 920.5 | 1779.5 | 0 | 1812.5 | 3292 | 215 | 0 | 553 | 87 | 1139 | 0 | 0 | 24
22:00 | 3214 | 921 | 1727 | 0 | 1667 | 3292 | 215 | 0 | 526 | 88 | 1139 | 0 | 0 | 0
22:30 | 3212.5 | 920.5 | 1722.5 | 0 | 1605 | 3291.5 | 215.5 | 0 | 507.5 | 88 | 1139.5 | 0 | 0 | 0
23:00 | 3211 | 920 | 1718 | 0 | 1543 | 3291 | 216 | 0 | 489 | 88 | 1140 | 0 | 0 | 0
23:30 | 3216 | 920 | 1763.5 | 0 | 1512 | 3236 | 216 | 0 | 458 | 90 | 1124.5 | 0 | 3 | 0 |  |  | Max Temp. in Dhaka |  | 33.1°C
24:00 | 3221 | 920 | 1809 | 0 | 1481 | 3181 | 216 | 0 | 427 | 92 | 1109 | 0 | 6 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on X13: Author:

## Generation
2024-10-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 136 | 134 | 132 | 131 | 131 | 132 | 133 | 134 | 135 | 135 | 136 | 136 | 136 | 135 | 134 | 134 | 134 | 133 |  | 133 | 133 | 134 | 135 | 135 | 136 | 136 | 3214805
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1936000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [8 empty] | 4 | 8 | 8 | 8 | 13 | 17 | 16 | 17 | 17 | 23 |  | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 247780
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 |  | 15 | 16 | 16 |  |  | 10 | 8 |  | 1 | [9 empty] | 102330
6 | Sikalbaha 225MW CCPP (Gas) | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 152 | 151 | 151 | 151 | 149 | 149 | 148 | 148 | 149 | 148 | 148 |  | 148 | 148 | 148 | 148 | 148 | 147 | 148 | 3584603
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 85 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 544301
12 | Hathazari 100 MW peaking PP | 64 | 40 | 24 | 8 | 0 | [6 empty] | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 40 | 645936
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 4 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 123781
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 29 | 29 | 0 | [16 empty] | 29 | 29 | 29 | 29 | 29 | 30 | 30 | 236944
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 335 | 335 | 335 | 335 | 330 | 330 | 332 | 331 | 332 | 335 |  | 290 | 280 | 280 | 280 | 300 | 290 | 290 | 7429631
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 18 | 45 | 82 | 97 | 117 | 125 | 120 | 128 |  | 192 | 80 | 30 | 30 | 30 | 30 | 32 | 1181782
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 45 | 73 | 73 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 869818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 570 | 570 | 570 | 520 | 440 | 400 | 402 | 404 | 402 | 470 | 500 | 536 | 580 | 612 | 608 | 608 | 612 | 608 |  | 610 | 611 | 610 | 610 | 610 | 612 | 610 | 13025453
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 40 | 42 | 42 | 41 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 43 | 43 | 40 | 43 | 43 | 43 | 1023120
33 | Ashuganj 225 MW CCPP | 217 | 217 | 217 | 217 | 217 | 217 | 218 | 214 | 217 | 214 | 216 | 216 | 212 | 213 | 214 | 214 | 213 | 213 |  | 218 | 213 | 215 | 216 | 214 | 215 | 216 | 5241000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 280 | 280 | 280 | 280 | 280 | 365 | 335 | 310 | 320 | 310 | 310 | 325 | 285 | 285 | 280 | 280 | 325 |  | 300 | 290 | 280 | 280 | 330 | 330 | 315 | 7654800
| Ashuganj 420 MW CCPP(East) | 335 | 295 | 295 | 295 | 295 | 300 | 330 | 320 | 300 | 340 | 330 | 335 | 330 | 295 | 295 | 295 | 295 | 335 |  | 295 | 285 | 285 | 285 | 340 | 340 | 330 | 7660300
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 126240
36 | Chandpur 150 MW CCPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 70 | 70 | 50 | 50 | 50 | 1472460
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 372 | 388 | 417 | 416 | 416 | 381 | 348 | 352 | 352 | 387 | 411 | 406 | 404 | 402 | 398 | 405 | 406 | 402 |  | 370 | 370 | 370 | 368 | 370 | 370 | 370 | 9428400
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 180 | 180 | 180 |  |  | 0 | 4494541
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 450 | 450 | 450 | 450 | 350 | 350 | 350 | 350 | 350 | 350 | 400 | 400 | 450 | 450 | 450 | 450 | 450 |  | 450 | 380 | 380 | 380 | 380 | 380 | 400 | 9736500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 16 | 16 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 12 | 11 |  | 12 | 13 | 14 | 16 | 18 | 18 | 18 | 355200
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 21 | 34 | 42 | 48 | 49 | 47 | 39 | 21 | 14 | 1 | [9 empty] | 316160
44 | Fenchugonj CCPP Phase-1 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 669000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 704400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 59 | 59 | 60 | 62 | 62 | 62 | 60 | 59 | 59 | 60 | 59 | 57 | 57 | 57 | 57 | 58 | 60 |  | 58 | 60 | 60 | 61 | 58 | 59 | 57 | 1388928
48 | Shahjibazar 86 MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 83 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 2049600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 209 | 209 | 209 | 208 | 212 | 212 | 213 | 213 | 209 | 207 | 206 | 205 | 205 | 203 | 203 | 205 | 205 | 205 |  | 207 | 209 | 208 | 209 | 209 | 209 | 208 | 5188480
51 | Sylhet 20 MW GTPP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 363000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 89712
55 | Fenchugonj 51 MW PP (Barakatullah) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 50 | 50 | 50 | 50 | 49 | 49 | 51 | 51 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1204800
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 280656
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 280 | 280 | 290 | 300 | 300 | 295 | 305 | 310 | 275 | 305 | 310 | 300 | 310 | 295 | 300 | 320 |  | 280 | 305 | 285 | 285 | 295 | 290 | 315 | 7257000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 17 | 0 | [7 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 427056
59 | Tangail Palli Power Gen 22 MW | [15 empty] | 6 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 15 | 18 | 150960
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 82 | 80 | 88 | 86 | 82 | 74 | 76 | 72 | 70 | 76 | 78 | 86 | 90 | 86 | 84 | 82 | 76 | 86 |  | 88 | 88 | 88 | 86 | 88 | 88 | 92 | 1975680
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 37 | 37 | 38 | 37 | 37 | 10 | 2 | 2 | 2 | 3 | 2 | 3 | 2 | 2 | 5 | 8 |  | 15 | 20 | 20 | 27 | 35 | 36 | 30 | 478080
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 4 | 12 | 12 | 12 |  | 12 | 14 | 15 | 16 | 17 | 17 | 17 | 305290
69 | Summit Ashulia | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 |  | 17 | 17 | 18 | 18 | 18 | 18 | 19 | 464400
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 502560
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 23 | 23 | 601920
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 30 | 24 | 24 | 24 | 30 | 18 | 24 | 30 | 24 | 28 |  | 28 | 28 | 28 | 28 | 30 | 31 | 33 | 711300
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 70 | 70 | 70 | 70 | 98 |  | 106 | 74 | 52 | 52 | 52 | 52 | 52 | 1015740
| Chowmuhani 113 MW | 42 | 34 | 27 | 31 | 26 | 28 | 28 | 28 | 28 | 29 | 29 | 39 | 30 | 27 | 29 | 33 | 57 | 67 |  | 77 | 78 | 78 | 78 | 79 | 77 | 78 | 1090320
| Manikgonj 162MW PP(MPGL) | [10 empty] | 35 | 72 | 72 | 72 | 72 | 72 | 72 | 162 |  | 162 | 162 | 162 | 108 | 54 | 54 | 72 | 1205280
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 17 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 34 |  | 34 | 34 | 34 | 25 | 25 | 17 | 8 | 376800
79 | Kodda 150 MW PP | 64 | 32 | 16 | 16 | 16 | 16 | 16 | 32 | 48 | 48 | 48 | 48 | 42 | 63 | 62 | 47 | 48 | 100 |  | 145 | 145 | 130 | 112 | 112 | 112 | 64 | 1466880
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [7 empty] | 6 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 137520
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 35 | 35 | 35 | 88 |  | 88 | 88 | 88 | 70 | 70 | 52 | 17 | 1024320
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 4 | 3 | 4 | 4 | 2 | 2 | 1 | [10 empty] | 25320
| Jodiac Power | [8 empty] | 14 | 17 | 17 | 17 | 17 | 21 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 489076
| Karnaphuli Power Ltd. | [17 empty] | 7 |  | 20 | 34 | 34 | 34 | 17 | 17 | 35 | 205745
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 16 | 16 | 16 | 16 | 16 | [7 empty] | 4 | 10 | 16 | 16 | 16 | 16 | 0 | 135360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 36 | 36 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 26 | 832896
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 944432
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | [14 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 86832
95 | Patenga 50MW PP (Baraka) | 5 | 0 | [6 empty] | 7 | 19 | 19 | 19 |  | 2 | 19 |  |  |  |  | 18 | 19 | 19 | 19 | 12 |  | 0 | 197310
96 | Chattogram 108 MW PP (ECPV) | 19 | 19 | 19 | 19 | 0 |  |  |  | 2 | 19 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 19 |  | 19 | 19 | 18 | 19 | 19 | 19 | 18 | 364800
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [14 empty] | 4 | 15 | 15 | 15 |  | 55 | 40 | 40 | 15 | 15 |  | 0 | 199282
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 |  | 55 | 17 | 17 | 17 | 17 | 17 | 55 | 316799
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 |  | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 3663900
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 11950
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 400932
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 97 | 97 | 97 | 97 | 97 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 134 | 134 | 127 | 135 | 144 |  | 154 | 154 | 154 | 154 | 154 | 154 | 126 | 3004800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 30 | 17 | 17 | 17 | 16 | 16 | 16 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 35 | 44 | 57 | 95 |  | 113 | 113 | 111 | 96 | 78 | 78 | 78 | 1145232
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 25 | 12 | 12 | 12 | 12 | 12 | 12 | 50 | 50 | 63 | 72 | 72 | 63 | 63 | 50 | 50 | 75 |  | 88 | 75 | 86 | 36 | 36 | 36 | 50 | 1072320
116 | Chandpur 200 MW (Desh energy) | 120 | 120 | 120 | 85 | 85 | 68 | 68 | 68 | 68 | 69 | 99 | 100 | 100 | 100 | 100 | 100 | 100 | 125 |  | 181 | 140 | 136 | 100 | 100 | 100 | 103 | 2553600
117 | Ashuganj 150 MW PP (Midland) | [10 empty] | 10 | 32 | 45 | 50 | 50 | 50 | 50 | 58 |  | 74 | 80 | 80 | 85 | 10 | 10 | 15 | 682472
118 | Bibiyana-III 400 MW CCPP | 371 | 335 | 335 | 310 | 331 | 335 | 335 | 377 | 386 | 386 | 386 | 388 | 389 | 390 | 390 | 374 | 373 | 372 |  | 339 | 342 | 341 | 341 | 341 | 342 | 370 | 9011000
| Jamalpur 115 MW PP (United) | 57 | 57 | 58 | 58 | 58 | 58 | 67 | 67 | 77 | 77 | 77 | 77 | 76 | 67 | 76 | 76 | 78 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 77 | 1804800
| Anwara 300 MW PP (United) | 51 | 52 | 52 | 52 | 15 | 15 | 15 | 15 | 15 | 15 | 45 | 45 | 45 | 102 | 102 | 105 | 105 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1216909
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 0 |  | 1 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 247680
| Anlima Energy Ltd. | 35 | 35 | 0 | [7 empty] | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 20 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 440345
| Bhairob 54.5 MW | 17 | 17 | 0 | [18 empty] | 6 | 17 | 17 | 17 | 17 | 115560
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 10 | 17 | 22 | 27 | 27 | 24 | 21 | 15 | 6 | 1 | [9 empty] | 160114
| Chandpur 115(Doreen) | 61 | 40 | 40 | 40 | 34 | 34 | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 52 |  | 91 | 92 | 91 | 92 | 92 | 61 | 17 | 1128960
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432360
| Mirsharai 150 MW (Oil) | 11 | 0 | [15 empty] | 36 |  | 160 | 160 | 160 | 54 | 54 | 17 | 17 | 511855
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 1 | 8 | 17 | 10 | 16 | 15 | 1 | 0 | 1 | 0 | 0 | 9 | 7 | 2 | 0 | 6 | 7 |  | 9 | 2 | 0 | 0 | 0 | 0 | 6 | 118560
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 13 | 13 | 22 | 54 | 69 | 68 | 56 | 53 | 38 | 20 | 4 | [9 empty] | 410864
| Matarbari 2*600 MW (CPGCL) | 211 | 216 | 216 | 216 | 217 | 214 | 217 | 217 | 217 | 214 | 215 | 215 | 216 | 215 | 214 | 214 | 213 | 217 |  | 212 | 216 | 214 | 214 | 215 | 216 | 215 | 5221818
| Meghnaghat (Reliance) 718MW CCPP | 6 | 24 | 24 | 70 | 93 | 96 | 340
| Sreepur 150 MW | [11 empty] | 15 | 18 | 2 | 4 | 8 | 11 | [8 empty] | 0 | 58800
120
121 | Eastern Zone Total | 5941 | 5720 | 5620 | 5515 | 5411 | 5228 | 5625 | 5314 | 5531 | 5809 | 5966 | 6335 | 6392 | 6482 | 6476 | 6409 | 6438 | 7069 |  | 7363 | 7063 | 6962 | 6638 | 6445 | 6311 | 6248 | 148994250
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 10 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 109440
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 10 | 27 | 56 | 74 | 84 | 86 | 83 | 51 | 38 | 24 | 5 | [9 empty] | 544320
132 | Rampal 1320 MW (BIFPCL) | 507 | 508 | 509 | 508 | 510 | 510 | 516 | 511 | 509 | 509 | 508 | 507 | 506 | 510 | 509 | 507 | 506 | 504 |  | 619 | 614 | 619 | 624 | 622 | 618 | 511 | 12814550
133 | United Payra Power Ltd. | 150 | 100 | 17 | 0 | [6 empty] | 9 | 17 | 17 | 54 | 54 | 54 | 54 | 137 |  | 150 | 137 | 150 | 150 | 150 | 150 | 150 | 1536000
| Bhola Nutan Biddut BD LTD (GAS) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 111 | 111 | 112 | 110 | 125 | 130 | 164 | 220 | 220 | 220 | 220 |  | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 3854740
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [21 empty] | 16 | 16 | 16 | 16 | 0 | 52128
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 250 | 200 | 200 | 200 | 200 | 200 | 250 | 250 | 286 | 307 | 307 | 307 | 307 | 250 | 307 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 6611000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3740
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 134 | 100 | 127 | 127 | 127 | 127 | 127 | 127 | 127 |  | 100 | 100 | 100 | 100 | 127 | 127 | 127 | 3066000
141 | Bhola 33 MW PP (Venture) | 9 | 9 | 8 | 8 | 8 | 7 | 6 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 5 | 6 | 8 |  | 8 | 9 | 9 | 10 | 10 | 10 | 10 | 178859
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP | [16 empty] | 20 | 50 |  | 57 | 54 | 54 | 54 |  |  |  | 215040
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
147 | Bheramara HVDC | 909 | 914 | 921 | 920 | 920 | 919 | 921 | 921 | 920 | 920 | 920 | 920 | 920 | 921 | 920 | 920 | 920 | 920 |  | 920 | 920 | 920 | 920 | 921 | 920 | 920 | 22180363
148 | Bheramara 410 MW CCPP | 343 | 343 | 343 | 343 | 343 | 300 | 300 | 300 | 347 | 348 | 346 | 342 | 331 | 290 | 315 | 310 | 302 | 289 |  | 285 | 281 | 281 | 280 | 280 | 282 | 287 | 7811712
149 | Payra 1320 MW | 1244 | 1244 | 1100 | 1040 | 900 | 900 | 900 | 940 | 1000 | 1070 | 1200 | 1244 | 1244 | 1244 | 1244 | 1240 | 1120 | 1140 |  | 1200 | 1200 | 1210 | 1244 | 1244 | 1244 | 1244 | 29444700
150
151 | Barapukuria TPP Unit-1 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 65 | 63 | 63 | 60 | 63 | 62 | 60 | 64 |  | 64 | 64 | 63 | 63 | 64 | 64 | 64 | 1465309
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5594000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 5 |  | 37 | 37 | 37 | 38 | 38 | 37 | 37 | 233956
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 4 | 2 | 1 | 0 | [9 empty] | 34320
157 | Sirajganj 68 MW Solar Park | [6 empty] | 3 | 18 | 40 | 51 | 60 | 64 | 59 | 50 | 40 | 15 | 2 | [9 empty] | 404250
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 214 | 214 | 170 | 170 | 170 | 170 | 170 | 170 | 140 | 140 | 140 | 152 | 200 | 198 | 194 | 190 | 184 |  | 180 | 180 | 182 | 184 | 183 | 184 | 184 | 4384636
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 414 | 341 | 335 | 330 | 339 | 338 | 317 | 350 | 350 | 347 | 316 | 321 | 414 | 353 | 414 | 414 | 414 | 414 |  | 318 | 353 | 319 | 336 | 350 | 345 | 414 | 8698181
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | 6 | 0
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 164862
166 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | [17 empty] | 27 |  | 45 | 45 | 46 | 45 | 45 | 44 | 44 | 265300
169 | Santahar 50 MW Peaking PP | [17 empty] | 15 |  | 28 | 30 | 30 | 30 | 30 | 30 | 15 | 174592
170 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
171 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 95 |  | 87 | 95 | 95 | 95 | 95 | 96 | 96 | 617616
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [17 empty] | 35 |  | 108 | 50 | 50 | 35 | 35 |  | 0 | 340704
173 | Confidence Power Bogura Unit-1 113 MW | 70 | 0 | [12 empty] | 10 | 35 | 35 | 100 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 945216
175 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | 34 | 0 | [15 empty] | 106 |  | 108 | 111 | 111 | 112 | 49 | 49 | 70 | 605232
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 |  | 2 | 5 | 6 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 35754
| Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 36 |  | 90 | 94 | 95 | 95 | 54 | 54 | 54 | 463872
| Intraco Solar 30 MW | [6 empty] | 3 | 10 | 18 | 25 | 28 | 25 | 27 | 23 | 16 | 7 | 1 | [9 empty] | 187867
178 | Adani Power Jharkhanda Ltd | 1036 | 1033 | 1036 | 1032 | 1034 | 1034 | 1033 | 1034 | 1035 | 1034 | 1037 | 1033 | 1037 | 1037 | 1040 | 1037 | 1032 | 1035 |  | 1035 | 1145 | 1132 | 1139 | 1139 | 1140 | 1109 | 25434533
| Teesta Solar Limited | [6 empty] | 26 | 66 | 119 | 153 | 180 | 185 | 174 | 141 | 101 | 48 | 8 | [9 empty] | 1197360