## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-10-27 | Sunday
|  | Date (day): | 2024-10-27 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12903.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14073 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-10-26 | 2024-10-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 405 | 409 | 400 | 410
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 7 | 15 | 15 | 15 | 40 |  | Fuel shortage
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 13 | 13 | 62 |  | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 329 | 332 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 0 | 8 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 30 | 35 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 96 | 150 | 48 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 17 | 35 | 20 |  | Fuel shortage
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 43 | 44 | 44 |  | 36 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 23 | 23 | 23 |  | 10 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 15 | 33 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 17 | 26 | 16 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 18 | 96 | 30 | 95 | 205 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 15 | 87 | 34 | 149
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 105 | 52 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 16 | 0 | 17 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 108 | 54 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 6 | 36 | 36 | 36 |  | 19 | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1598 | 2046 | 1730 | 2213 | 2830 | 825
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 9 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 19 | 19 | 31 |  | Fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 212 | 215 | 215 | 215 |  | 15
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 223 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 40 | 63 | 56 | 85 |  | 13 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 84 | 51 | 85 |  | 17 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 100 | 50 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 15 | 10 | 25
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 20 | 20 | 88 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 65 | 52 | 50 | 95 | 205 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 35 | 35 | 51 | 3 |  | Fuel shortage
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 34 | 76 |  | Fuel shortage
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 31 | 35 | 35 | 35 | 81 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 160 | 35 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 612 | 612 | 612 | 612 |  | 612 | Unit-2 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 3 | 0 | 42 | 60 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 0 | 0 | 0 | 0 | 1150 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1341 | 1684 | 1551 | 1875 | 1990 | 987
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 215 | 214 | 215 | 215
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 290 | 320 | 320 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 393 | 393 | 350 | 350 |  |  | FGMO
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 36 | 43 | 43
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 22 | 25 | 25 | 25 | 35 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 26 | 8 | 26 | 169 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  |  | Gas shortage
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 26 | 104 | 100 | 100 | 50 |  | Fuel shortage
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 43 | 30 | 43 |  | 9 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 70 | 93 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 108 | 200 | 100 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 54 | 78 | 66 | 86
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 27 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 10 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 57 | 106 | 106 | 106 |  | 8 | Engine problem
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 30 | 45 | 29 | 45 | 68 |  | Fuel shortage
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 91 | 34 | 92 | 23 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 73 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1523 | 1808 | 1653 | 1828 | 438 | 390
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 31 | 31 | 30 | 30 | 172 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 87 | 87 | 85 | 95 | 105 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 56 | 55 | 55 | 60 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 14 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 6 | 18
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 0 | 35 | 19 |  | Fuel shortage
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 0 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 188 | 186 | 227.6 | 233 | 172 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 28 | 28 | 28 | 28 |  | 42 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract Expired
90 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 30 | 33 | 35 | 35 | 15 |  | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 58 | 60 | 60
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 86 | 86 | 86
94 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 204 | 204 | 210 | 210 |  | 21 | Machine problem
96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 15 | 12 | 15 | 15 | 5 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 315 | 320 |  |  | FGMO
99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 373 | 386 | 385 | 385
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 30 | 40 | 130 |  | 383 | ST Under maint
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1297 | 1340 | 1392 | 1487 | 20 | 847
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 911 | 910 | 910 | 910
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 0 | 35 |  | 19 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 30 | 60 |  | 49 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 357 | 365 | 365 | 45 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 17 | 88 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 504 | 625 | 520 | 620 | 614 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1799 | 1977 | 1942 | 2007 | 1329 | 68
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 32 | 110
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 5 | 10 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 127 | 127 | 132 | 132 |  | 62 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1140 | 1244 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 150 | 150 | 150
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  | 307 | Under maint
118 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1492 | 1831 | 1788 | 1866 | 0 | 369
119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 35 | 38 |  | 14 | Engine problem
121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 10 | 0 | 24 |  | 47 | Engine problem
122 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 46 | 28 | 46
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 160 | 214 | 210 | 210
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 390 | 343 | 414 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 22 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 8 |  | 3 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 97 | 50 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 95 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1032 | 1012 | 1010 | 1010
135 | Sirajganj 68 MW Solar Park |  | Solar | NWPGCL | 68 | 68 | 68 | 18 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 57 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1664 | 1972 | 2064 | 2101 | 611 | 93
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 65 | 65 | 65 | 65 |  | 20
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 102 | 113 | 113
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 115 | 0 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 4 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 56 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 297 | 452 | 556 | 463 | 40 | 209
| Total |  |  |  |  | 27791 | 27086 | 11199 | 13296 | 12903.6 | 14073 | 7430 | 3788
A. |  | 2024-10-26 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 13296 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 9122 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13480 | MW
3 | Day peak Generation : |  |  | 11199 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12901.15 | MW
4 | Evening peak Generation : |  |  | 13296 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 176 | MW
5 | Total Energy Generation : |  | 272.2099 | MKWHr | By Solar | 2.4512 | MKWHr
| By Gas : | 126.3921 | MKWHr |  | By Oil: | 31.2373 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 60.3459 | MKWHr |  | By Hydro: | 5.1582 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 23.1709 | MKWHr |  | By Wind: | 0.21168 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7430 | MW | Dhaka | 4886.75 | 4847.75 |  | 39 |  | 18:00 |  | 500
|  |  | For Plants S/D or M/C prob = |  |  | 3788 | MW | Chittagong | 1368.5 | 1368.5 |  | 0 |  | 19:00 |  | 173
|  |  | Total = |  |  | 11218 | MW | Khulna | 1534 | 1534 |  | 0 |  | 19:30 |  | 175.72
7 | Total Gas Supplied : |  | 914.15 | MMCFD | **Import Adani: | Taka | 153159708.49 | Rajshahi | 1069.4 | 1069.4 |  | 0 |  | 20:00 |  | 160.44
8 | Fuel Cost : | i) Gas : | Taka | 379423256.77 | ii) Oil : | Taka | 567836055.25 | Comilla | 1320 | 1305 |  | 15 |  | 21:00 |  | 117
|  | iii) Coal : | Taka | 422545840.65 | Total | Taka | 1522964861.16 | Mymensingh | 1103 | 981 |  | 122 |  | 22:00 |  | 107.915
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 13858.35 | MKWHr. | Sylhet | 579 | 579 |  | 0 |  | 23:00 |  | 88.815
| ii) During Peak Demand : |  |  | 1478 | MW (W to E) at | 19:30 | hrs | Barisal | 410.5 | 410.5 |  | 0 |  | 24:00 |  | 55.39
| iii) Maximum : |  |  | 1350 | MW at | 13:00 | hrs | Rangpur | 630 | 630 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.5°C |  |  | Total | 12901.15 | 12725.15 |  | 176
B. |  | 2024-10-27 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 215 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14073 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12800 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 292.7648 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10402 | MW at | 6:00 | 80 | 25 | 25 | 25 | 20 | 15 | 10 | 0 | 15
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7978 | MKWHr. | ii) HVDC Flow at Peak Time |  | 910 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.4448 | MKWHr. | iii) Maximum HVDC Flow : |  | 911 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.24 |  | (b) Today: | 102.94 |  | (c) Rule Curve: |  | 108.5
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-10-26 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 16 | 33 | 0 | 0 | 133 | 80 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 216 | 26 | 50 | 43 | 24 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 0 | 12 | 62 | 48 | 0 | 0 | 0 | 28 | 30 | 0 | 37 | 120 | 0 | 56 | 86 | 0 | 210 | 15 | 0 | 0 | 275 | 20 | 5 | 0 | 0 | 0 | 0 | 97 | 0 | 16 | 0 | 12 | 133 | 0 | 385 | 58 | 17 | 0 | 0 | 65 | 17 | 0 | 70 | 28 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 17 | 395 | 0 | 0 | 570 | 30 | 0 | 0 | 0 | 0 | 48 | 0 |  | 910 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 67 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 511 | 0 | 0 | 935 | 0 | 0 | 0 | 0 | 0 |  | 5573 | 5063 | 10636 | 3543 | 910 | 1795 | 0 | 606 | 2478 | 213 | 0 | 64 | 62 | 935 | 0 | 30 | 0 | 103.29
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 16 | 33 | 0 | 0 | 133 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 216 | 26 | 50 | 43 | 24 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 0 | 12 | 60 | 47 | 0 | 0 | 0 | 28 | 30 | 0 | 37 | 120 | 0 | 59 | 86 | 0 | 210 | 15 | 0 | 0 | 285 | 20 | 5 | 0 | 0 | 0 | 0 | 97 | 0 | 16 | 0 | 0 | 100 | 0 | 384 | 56 | 17 | 0 | 0 | 15 | 0 | 0 | 52 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 395 | 0 | 0 | 550 | 27 | 0 | 0 | 0 | 0 | 76 | 0 |  | 911 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 67 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 0 | 0 | 842 | 0 | 0 | 0 | 0 | 0 |  | 5402 | 4829 | 10231 | 3570 | 911 | 1740 | 0 | 424 | 2396 | 213 | 0 | 48 | 60 | 842 | 0 | 27 | 0 | 103.28
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 16 | 33 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 217 | 8 | 70 | 43 | 25 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 58 | 48 | 0 | 0 | 0 | 28 | 30 | 0 | 37 | 120 | 0 | 59 | 61 | 0 | 210 | 15 | 0 | 0 | 285 | 20 | 5 | 0 | 0 | 0 | 0 | 75 | 0 | 16 | 0 | 0 | 100 | 0 | 383 | 45 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 0 | 0 | 525 | 19 | 0 | 0 | 0 | 0 | 310 | 0 |  | 910 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 67 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511 | 0 | 0 | 832 | 0 | 0 | 0 | 0 | 0 |  | 5310 | 4700 | 10010 | 3455 | 910 | 1876 | 0 | 341 | 2273 | 214 | 0 | 32 | 58 | 832 | 0 | 19 | 0 | 103.27
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 16 | 33 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 216 | 8 | 70 | 43 | 25 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 56 | 48 | 0 | 0 | 0 | 28 | 30 | 0 | 37 | 120 | 0 | 59 | 61 | 0 | 211 | 15 | 0 | 0 | 280 | 20 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 16 | 0 | 0 | 100 | 0 | 383 | 45 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 320 | 0 | 0 | 455 | 28 | 0 | 0 | 0 | 0 | 285 | 0 |  | 911 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 67 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 845 | 0 | 0 | 0 | 0 | 0 |  | 5143 | 4489 | 9632 | 3368 | 911 | 1782 | 0 | 330 | 2082 | 214 | 0 | 16 | 56 | 845 | 0 | 28 | 0 | 103.26
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 16 | 33 | 0 | 0 | 135 | 80 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 0 | 217 | 8 | 75 | 43 | 26 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 56 | 48 | 0 | 0 | 0 | 28 | 30 | 0 | 5 | 120 | 0 | 58 | 61 | 0 | 211 | 15 | 0 | 0 | 280 | 20 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 16 | 0 | 0 | 51 | 0 | 335 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 275 | 0 | 0 | 400 | 28 | 0 | 0 | 0 | 0 | 764 | 0 |  | 910 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 67 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 836 | 0 | 0 | 0 | 0 | 0 |  | 5186 | 4245 | 9431 | 3074 | 910 | 2150 | 0 | 257 | 1889 | 215 | 0 | 16 | 56 | 836 | 0 | 28 | 0 | 103.25
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 16 | 33 | 0 | 0 | 135 | 80 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 350 | 0 | 216 | 8 | 75 | 43 | 26 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 48 | 0 | 0 | 0 | 28 | 30 | 0 | 5 | 120 | 0 | 40 | 61 | 0 | 211 | 15 | 0 | 0 | 305 | 20 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 16 | 0 | 0 | 51 | 0 | 383 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 250 | 0 | 0 | 370 | 25 | 0 | 0 | 0 | 0 | 89 | 0 |  | 911 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 67 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 828 | 0 | 0 | 0 | 0 | 0 |  | 4668 | 4454 | 9122 | 3254 | 911 | 1623 | 0 | 258 | 1942 | 215 | 0 | 16 | 50 | 828 | 0 | 25 | 0 | 103.24
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 16 | 16 | 2 | 0 | 135 | 80 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 310 | 0 | 217 | 8 | 75 | 43 | 25 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 48 | 48 | 0 | 0 | 0 | 28 | 30 | 0 | 18 | 120 | 0 | 59 | 86 | 0 | 211 | 15 | 0 | 0 | 290 | 20 | 5 | 0 | 0 | 0 | 0 | 70 | 0 | 16 | 4 | 0 | 51 | 0 | 383 | 45 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 28 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 2 | 18 | 0 | 393 | 0 | 0 | 370 | 20 | 0 | 0 | 0 | 12 | 0 | 0 |  | 910 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 378 | 2 | 0 | 831 | 5 | 0 | 0 | 2 | 3 |  | 4891 | 4775 | 9666 | 3552 | 910 | 1648 | 0 | 281 | 2085 | 215 | 0 | 32 | 48 | 831 | 44 | 20 | 0 | 103.23
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 16 | 16 | 8 | 0 | 135 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 320 | 0 | 217 | 8 | 70 | 43 | 25 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 46 | 0 | 0 | 0 | 28 | 30 | 0 | 31 | 120 | 0 | 60 | 86 | 0 | 210 | 15 | 0 | 0 | 290 | 20 | 5 | 0 | 0 | 0 | 0 | 85 | 0 | 16 | 0 | 0 | 51 | 0 | 385 | 45 | 17 | 0 | 2 | 0 | 0 | 0 | 34 | 29 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 8 | 17 | 0 | 393 | 0 | 0 | 370 | 8 | 0 | 0 | 0 | 34 | 0 | 0 |  | 911 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1100 | 220 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 377 | 4 | 0 | 831 | 27 | 0 | 0 | 3 | 16 |  | 4958 | 4832 | 9790 | 3549 | 911 | 1671 | 0 | 302 | 2082 | 215 | 0 | 32 | 40 | 831 | 149 | 8 | 0 | 103.22
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 16 | 16 | 17 | 0 | 135 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 212 | 8 | 50 | 34 | 25 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46 | 46 | 0 | 0 | 0 | 28 | 30 | 0 | 37 | 163 | 0 | 60 | 83 | 0 | 209 | 15 | 0 | 0 | 300 | 20 | 5 | 0 | 0 | 0 | 0 | 87 | 0 | 16 | 14 | 0 | 51 | 0 | 340 | 45 | 52 | 0 | 3 | 0 | 0 | 0 | 34 | 29 | 0 | 0 | 3 | 12 | 0 | 0 | 0 | 0 | 19 | 31 | 0 | 350 | 0 | 0 | 405 | 3 | 0 | 0 | 0 | 16 | 0 | 0 |  | 911 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1160 | 180 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 407 | 3 | 0 | 1002 | 21 | 0 | 0 | 9 | 8 |  | 4934 | 5012 | 9946 | 3349 | 911 | 1651 | 0 | 365 | 2207 | 215 | 0 | 32 | 46 | 1002 | 165 | 3 | 0 | 103.21
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 16 | 16 | 17 | 0 | 134 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 345 | 0 | 210 | 8 | 51 | 38 | 23 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 42 | 0 | 0 | 0 | 28 | 30 | 0 | 37 | 120 | 0 | 58 | 86 | 0 | 207 | 15 | 0 | 0 | 280 | 20 | 5 | 0 | 0 | 0 | 0 | 87 | 0 | 16 | 18 | 0 | 51 | 0 | 343 | 46 | 52 | 0 | 4 | 30 | 15 | 0 | 17 | 29 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 13 | 34 | 0 | 350 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 65 | 0 | 0 |  | 910 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 180 | 0 | 0 | 2 | 72 | 0 | 0 | 0 | 454 | 6 | 0 | 1037 | 18 | 0 | 0 | 25 | 57 |  | 5108 | 5038 | 10146 | 3298 | 910 | 1594 | 0 | 409 | 2259 | 214 | 0 | 80 | 50 | 1037 | 295 | 0 | 0 | 103.2
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 17 | 15 | 17 | 0 | 134 | 80 | 0 | 0 | 1 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 212 | 45 | 50 | 29 | 22 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 52 | 32 | 0 | 0 | 1 | 28 | 30 | 0 | 37 | 163 | 0 | 59 | 83 | 0 | 206 | 15 | 0 | 0 | 300 | 15 | 2 | 0 | 0 | 0 | 0 | 87 | 0 | 15 | 12 | 10 | 63 | 2 | 387 | 55 | 52 | 0 | 4 | 30 | 17 | 3 | 17 | 28 | 12 | 0 | 16 | 12 | 0 | 5 | 0 | 0 | 31 | 34 | 0 | 393 | 17 | 0 | 600 | 0 | 0 | 0 | 0 | 70 | 0 | 0 |  | 910 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1100 | 180 | 0 | 0 | 2 | 84 | 0 | 0 | 0 | 456 | 2 | 0 | 1035 | 39 | 0 | 0 | 39 | 64 |  | 5524 | 5144 | 10668 | 3445 | 910 | 1684 | 0 | 472 | 2393 | 214 | 0 | 99 | 52 | 1035 | 364 | 0 | 0 | 103.19
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 7 | 329 | 0 | 0 | 0 | 8 | 96 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 22 | 23 | 20 | 15 | 17 | 0 | 132 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 310 | 0 | 215 | 45 | 50 | 26 | 22 | 0 | 43 | 0 | 0 | 27 | 0 | 0 | 0 | 10 | 54 | 31 | 0 | 0 | 1 | 28 | 30 | 0 | 30 | 163 | 0 | 59 | 83 | 0 | 204 | 15 | 0 | 0 | 290 | 20 | 2 | 0 | 18 | 0 | 0 | 87 | 0 | 15 | 9 | 50 | 108 | 26 | 373 | 55 | 52 | 0 | 4 | 65 | 17 | 17 | 57 | 30 | 12 | 0 | 16 | 14 | 17 | 31 | 0 | 0 | 31 | 34 | 6 | 393 | 36 | 0 | 612 | 3 | 0 | 0 | 0 | 73 | 0 | 0 |  | 911 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1140 | 220 | 0 | 0 | 2 | 84 | 0 | 0 | 0 | 504 | 4 | 0 | 1032 | 56 | 0 | 0 | 18 | 57 |  | 5947 | 5252 | 11199 | 3394 | 911 | 1744 | 0 | 831 | 2491 | 212 | 0 | 172 | 54 | 1032 | 355 | 3 | 0 | 103.18
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 329 | 0 | 0 | 0 | 8 | 95 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 22 | 23 | 23 | 15 | 17 | 0 | 132 | 80 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 310 | 0 | 211 | 45 | 50 | 28 | 21 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 12 | 58 | 31 | 0 | 0 | 1 | 28 | 30 | 0 | 36 | 163 | 0 | 58 | 86 | 0 | 204 | 10 | 0 | 0 | 300 | 20 | 0 | 0 | 43 | 0 | 0 | 87 | 0 | 15 | 16 | 50 | 175 | 65 | 373 | 57 | 52 | 0 | 4 | 174 | 17 | 17 | 106 | 40 | 12 | 0 | 0 | 50 | 72 | 35 | 0 | 0 | 30 | 34 | 36 | 393 | 36 | 0 | 612 | 36 | 0 | 0 | 0 | 35 | 0 | 0 |  | 910 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1244 | 220 | 0 | 0 | 1 | 69 | 0 | 0 | 0 | 504 | 3 | 0 | 1032 | 60 | 0 | 0 | 22 | 60 |  | 6419 | 5300 | 11719 | 3367 | 910 | 1726 | 0 | 1253 | 2595 | 212 | 0 | 176 | 58 | 1032 | 354 | 36 | 0 | 103.17
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 0 | 0 | 0 | 50 | 326 | 0 | 0 | 0 | 8 | 95 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 23 | 23 | 23 | 16 | 17 | 0 | 134 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 211 | 45 | 50 | 32 | 21 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 12 | 62 | 30 | 0 | 0 | 2 | 28 | 30 | 0 | 36 | 163 | 0 | 57 | 86 | 0 | 204 | 10 | 0 | 0 | 295 | 20 | 0 | 0 | 34 | 0 | 0 | 87 | 0 | 15 | 15 | 50 | 200 | 92 | 373 | 57 | 52 | 0 | 3 | 184 | 17 | 17 | 106 | 33 | 12 | 0 | 0 | 39 | 72 | 35 | 0 | 0 | 17 | 34 | 36 | 393 | 36 | 0 | 612 | 0 | 0 | 0 | 0 | 34 | 0 | 0 |  | 910 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1120 | 220 | 0 | 0 | 2 | 70 | 0 | 0 | 0 | 506 | 7 | 0 | 1031 | 59 | 0 | 0 | 25 | 89 |  | 6421 | 5202 | 11623 | 3367 | 910 | 1708 | 0 | 1319 | 2473 | 214 | 0 | 176 | 62 | 1031 | 363 | 0 | 0 | 103.19
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 325 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 0 | 23 | 23 | 16 | 17 | 0 | 134 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 37 | 51 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 325 | 0 | 210 | 45 | 50 | 34 | 21 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 12 | 62 | 30 | 0 | 0 | 0 | 28 | 30 | 0 | 36 | 163 | 0 | 57 | 86 | 0 | 202 | 10 | 0 | 0 | 305 | 20 | 2 | 0 | 37 | 0 | 0 | 86 | 0 | 22 | 11 | 50 | 144 | 87 | 388 | 56 | 35 | 0 | 2 | 200 | 17 | 17 | 106 | 28 | 12 | 0 | 0 | 28 | 72 | 35 | 0 | 0 | 16 | 34 | 36 | 393 | 17 | 0 | 612 | 1 | 0 | 0 | 0 | 20 | 0 | 0 |  | 910 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1170 | 220 | 0 | 22 | 2 | 46 | 0 | 0 | 0 | 509 | 4 | 0 | 1034 | 29 | 0 | 0 | 16 | 36 |  | 6390 | 5248 | 11638 | 3443 | 910 | 1732 | 0 | 1297 | 2526 | 214 | 0 | 208 | 62 | 1034 | 211 | 1 | 0 | 103.15
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 328 | 0 | 0 | 0 | 0 | 95 | 11 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 0 | 23 | 23 | 16 | 17 | 0 | 135 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 4 | 37 | 51 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 212 | 45 | 50 | 34 | 22 | 0 | 43 | 0 | 30 | 50 | 0 | 0 | 0 | 12 | 58 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 36 | 163 | 0 | 40 | 86 | 0 | 204 | 10 | 0 | 0 | 300 | 20 | 2 | 0 | 48 | 0 | 0 | 86 | 0 | 34 | 0 | 70 | 104 | 92 | 388 | 56 | 35 | 0 | 1 | 51 | 17 | 17 | 106 | 28 | 12 | 0 | 0 | 8 | 72 | 35 | 0 | 0 | 4 | 34 | 21 | 350 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 31 | 0 | 0 |  | 910 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 180 | 0 | 100 | 1 | 23 | 0 | 0 | 0 | 511 | 3 | 0 | 1028 | 19 | 0 | 0 | 10 | 31 |  | 6171 | 5177 | 11348 | 3325 | 910 | 1653 | 0 | 1232 | 2558 | 215 | 0 | 238 | 58 | 1028 | 131 | 0 | 0 | 103.14
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 420 | 0 | 0 | 0 | 15 | 328 | 0 | 0 | 0 | 0 | 95 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 18 | 23 | 23 | 16 | 17 | 0 | 135 | 80 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 37 | 68 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 310 | 0 | 214 | 45 | 50 | 35 | 23 | 0 | 43 | 0 | 43 | 43 | 0 | 0 | 0 | 12 | 62 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 36 | 163 | 0 | 58 | 86 | 0 | 205 | 10 | 0 | 0 | 305 | 20 | 2 | 0 | 47 | 0 | 0 | 87 | 0 | 37 | 1 | 88 | 105 | 93 | 340 | 57 | 35 | 0 | 0 | 52 | 17 | 17 | 106 | 28 | 12 | 0 | 0 | 1 | 72 | 35 | 0 | 0 | 1 | 42 | 36 | 380 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 2 | 0 | 0 |  | 910 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 127 | 6 | 10 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 220 | 0 | 137 | 0 | 2 | 0 | 0 | 0 | 509 | 0 | 0 | 1012 | 4 | 0 | 0 | 2 | 38 |  | 6194 | 5230 | 11424 | 3346 | 910 | 1703 | 0 | 1309 | 2545 | 215 | 0 | 271 | 62 | 1012 | 51 | 0 | 0 | 103.13
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 330 | 0 | 0 | 0 | 0 | 136 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 18 | 23 | 23 | 24 | 26 | 0 | 135 | 80 | 0 | 0 | 17 | 223 | 0 | 0 | 0 |  | 12 | 63 | 84 | 0 | 0 | 19 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 214 | 45 | 50 | 36 | 25 | 0 | 43 | 0 | 43 | 43 | 0 | 0 | 0 | 12 | 78 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 36 | 163 | 0 | 58 | 86 | 0 | 205 | 10 | 0 | 0 | 300 | 20 | 2 | 0 | 47 | 0 | 0 | 87 | 0 | 54 | 0 | 100 | 150 | 95 | 385 | 57 | 105 | 17 | 0 | 52 | 33 | 17 | 106 | 35 | 12 | 0 | 0 | 0 | 108 | 35 | 0 | 0 | 0 | 66 | 36 | 393 | 160 | 0 | 612 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 909 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 34 | 25 | 0 | 127 | 9 | 48 | 0 | 0 | 0 | 22 | 5 | 85 | 0 | 0 | 35 | 0 | 24 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 2 | 0 | 53 | 0 | 0 | 90 | 1200 | 220 | 0 | 137 | 0 | 0 | 72 | 0 | 0 | 618 | 0 | 0 | 1013 | 0 | 0 | 0 | 0 | 0 |  | 6821 | 5905 | 12726 | 3507 | 909 | 1776 | 0 | 1846 | 2665 | 215 | 0 | 716 | 78 | 1013 | 0 | 1 | 500 | 103.12
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 333 | 0 | 0 | 0 | 0 | 150 | 13 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 20 | 23 | 23 | 30 | 26 | 0 | 135 | 80 | 0 | 0 | 25 | 223 | 0 | 0 | 0 |  | 12 | 63 | 84 | 0 | 0 | 19 | 0 | 14 | 0 | 0 | 0 | 280 | 0 | 213 | 26 | 50 | 36 | 25 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 12 | 76 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 33 | 163 | 0 | 58 | 86 | 0 | 204 | 12 | 0 | 0 | 280 | 20 | 5 | 0 | 92 | 0 | 0 | 87 | 0 | 81 | 0 | 100 | 200 | 102 | 386 | 56 | 105 | 17 | 0 | 51 | 35 | 17 | 106 | 45 | 12 | 0 | 0 | 0 | 108 | 35 | 0 | 0 | 0 | 90 | 36 | 393 | 160 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 911 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 37 | 53 | 0 | 127 | 9 | 80 | 0 | 0 | 0 | 46 | 5 | 97 | 0 | 0 | 46 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 87 | 0 | 102 | 0 | 0 | 110 | 1230 | 220 | 0 | 150 | 0 | 0 | 110 | 0 | 0 | 624 | 0 | 0 | 1014 | 0 | 0 | 0 | 0 | 0 |  | 6987 | 6232 | 13219 | 3523 | 911 | 1682 | 0 | 2283 | 2701 | 215 | 0 | 814 | 76 | 1014 | 0 | 0 | 173 | 103.09
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 332 | 0 | 0 | 0 | 0 | 150 | 13 | 0 | 0 | 0 | 30 | 55 | 35 | 0 | 20 | 23 | 23 | 33 | 26 | 0 | 135 | 80 | 0 | 0 | 25 | 223 | 0 | 0 | 0 |  | 12 | 63 | 84 | 0 | 0 | 19 | 0 | 15 | 0 | 0 | 0 | 290 | 0 | 214 | 26 | 50 | 36 | 25 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 12 | 78 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 33 | 163 | 0 | 58 | 86 | 0 | 204 | 12 | 0 | 0 | 285 | 20 | 5 | 0 | 96 | 0 | 0 | 87 | 0 | 87 | 0 | 100 | 200 | 104 | 386 | 56 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 45 | 12 | 30 | 0 | 0 | 108 | 35 | 0 | 0 | 0 | 91 | 36 | 393 | 160 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 910 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 35 | 50 | 0 | 127 | 10 | 80 | 0 | 0 | 0 | 32 | 10 | 97 | 0 | 0 | 46 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 70 | 0 | 102 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 625 | 0 | 0 | 1012 | 0 | 0 | 0 | 0 | 0 |  | 7064 | 6232 | 13296 | 3565 | 910 | 1699 | 0 | 2301 | 2716 | 215 | 0 | 800 | 78 | 1012 | 0 | 0 | 175.72 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 332 | 0 | 0 | 0 | 8 | 150 | 13 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 21 | 23 | 23 | 33 | 26 | 0 | 135 | 80 | 0 | 0 | 25 | 224 | 0 | 0 | 0 |  | 12 | 63 | 84 | 0 | 0 | 19 | 0 | 18 | 0 | 0 | 0 | 285 | 0 | 217 | 26 | 50 | 36 | 26 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 12 | 78 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 163 | 0 | 59 | 86 | 0 | 206 | 12 | 0 | 0 | 280 | 20 | 5 | 0 | 96 | 0 | 0 | 86 | 0 | 91 | 0 | 100 | 200 | 10 | 385 | 56 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 47 | 12 | 44 | 0 | 0 | 108 | 35 | 0 | 0 | 0 | 92 | 36 | 370 | 160 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 910 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 30 | 50 | 0 | 127 | 10 | 110 | 0 | 0 | 0 | 46 | 10 | 97 | 0 | 0 | 47 | 0 | 30 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 35 | 0 | 111 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 626 | 0 | 0 | 1009 | 0 | 0 | 0 | 0 | 0 |  | 6982 | 6180 | 13162 | 3525 | 910 | 1668 | 0 | 2230 | 2717 | 215 | 0 | 810 | 78 | 1009 | 0 | 0 | 160.44 | 103.1
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 330 | 0 | 0 | 0 | 8 | 150 | 13 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 22 | 23 | 23 | 33 | 26 | 0 | 135 | 80 | 0 | 0 | 25 | 224 | 0 | 0 | 0 |  | 12 | 63 | 84 | 0 | 0 | 19 | 0 | 22 | 0 | 0 | 0 | 315 | 0 | 213 | 26 | 50 | 37 | 26 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 12 | 78 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 36 | 163 | 0 | 57 | 86 | 0 | 207 | 12 | 0 | 0 | 310 | 12 | 5 | 0 | 97 | 0 | 0 | 87 | 0 | 105 | 0 | 100 | 200 | 10 | 387 | 57 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 47 | 12 | 45 | 14 | 0 | 54 | 35 | 0 | 0 | 0 | 92 | 36 | 330 | 54 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 910 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 25 | 42 | 0 | 127 | 10 | 110 | 0 | 0 | 0 | 46 | 18 | 97 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 35 | 0 | 111 | 0 | 0 | 70 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 624 | 0 | 0 | 1017 | 0 | 0 | 0 | 0 | 0 |  | 6793 | 6135 | 12928 | 3505 | 910 | 1740 | 0 | 2051 | 2715 | 215 | 0 | 697 | 78 | 1017 | 0 | 0 | 117 | 103.09
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 150 | 13 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 21 | 23 | 23 | 33 | 26 | 0 | 134 | 80 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 12 | 63 | 84 | 0 | 0 | 19 | 0 | 27 | 0 | 0 | 0 | 285 | 0 | 215 | 26 | 50 | 37 | 26 | 0 | 43 | 0 | 43 | 51 | 0 | 0 | 0 | 12 | 78 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 58 | 86 | 0 | 207 | 12 | 0 | 0 | 295 | 12 | 5 | 0 | 97 | 0 | 0 | 87 | 0 | 103 | 0 | 89 | 200 | 38 | 385 | 57 | 105 | 17 | 0 | 52 | 33 | 17 | 106 | 47 | 12 | 45 | 15 | 0 | 17 | 35 | 0 | 0 | 0 | 92 | 36 | 330 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 909 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 25 | 42 | 0 | 127 | 10 | 110 | 0 | 0 | 0 | 46 | 18 | 97 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 35 | 0 | 111 | 0 | 0 | 70 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 625 | 0 | 0 | 1008 | 0 | 0 | 0 | 0 | 0 |  | 6648 | 6089 | 12737 | 3482 | 909 | 1660 | 0 | 2010 | 2716 | 214 | 0 | 660 | 78 | 1008 | 0 | 0 | 107.915 | 103.08
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 150 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 23 | 33 | 17 | 0 | 133 | 80 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 8 | 63 | 84 | 0 | 0 | 19 | 0 | 31 | 0 | 0 | 0 | 345 | 0 | 212 | 26 | 50 | 37 | 26 | 0 | 43 | 0 | 43 | 43 | 0 | 0 | 0 | 12 | 78 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 58 | 86 | 0 | 207 | 0 | 0 | 0 | 305 | 12 | 5 | 0 | 73 | 0 | 0 | 87 | 0 | 83 | 0 | 50 | 200 | 80 | 387 | 57 | 35 | 17 | 0 | 52 | 17 | 17 | 106 | 47 | 12 | 45 | 16 | 0 | 17 | 35 | 0 | 0 | 0 | 62 | 36 | 330 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 910 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 25 | 41 | 0 | 127 | 10 | 110 | 0 | 0 | 0 | 46 | 0 | 99 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 50 | 1244 | 220 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 625 | 0 | 0 | 1014 | 0 | 0 | 0 | 0 | 0 |  | 6415 | 6042 | 12457 | 3486 | 910 | 1724 | 0 | 1673 | 2716 | 213 | 0 | 643 | 78 | 1014 | 0 | 0 | 88.815 | 103.07
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 328 | 0 | 0 | 0 | 0 | 150 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 23 | 33 | 8 | 0 | 133 | 80 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 0 | 63 | 84 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 345 | 0 | 211 | 26 | 70 | 37 | 25 | 0 | 43 | 0 | 43 | 51 | 0 | 0 | 0 | 12 | 76 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 57 | 86 | 0 | 208 | 0 | 0 | 0 | 320 | 12 | 5 | 0 | 45 | 0 | 0 | 87 | 0 | 71 | 0 | 50 | 132 | 77 | 387 | 58 | 17 | 0 | 0 | 52 | 17 | 17 | 106 | 38 | 12 | 45 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 30 | 36 | 330 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 911 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 21 | 36 | 0 | 127 | 10 | 110 | 0 | 0 | 0 | 45 | 0 | 99 | 0 | 0 | 30 | 0 | 30 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 50 | 1244 | 220 | 0 | 150 | 0 | 0 | 50 | 0 | 0 | 508 | 0 | 0 | 1010 | 0 | 0 | 0 | 0 | 0 |  | 6233 | 5889 | 12122 | 3549 | 911 | 1710 | 0 | 1436 | 2599 | 213 | 0 | 618 | 76 | 1010 | 0 | 0 | 55.39 | 103.06
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810000 | 0 |  | 0 | 10189000 | 0 | 0 | 0 | 349842 | 7695176 | 0 | 0 | 0 | 50544 | 2005920 | 101000 | 0 | 0 | 0 | 259200 | 272404 | 270132 | 0 | 521400 | 537840 | 478800 | 602500 | 311040 | 0 | 3230204 | 1928000 | 0 | 0 | 191525 | 5239385 | 0 | 0 | 0 |  | 92640 | 612336 | 704381 | 0 | 0 | 125280 | 0 | 475200 | 0 | 0 | 0 | 7905200 | 0 | 5204000 | 652364 | 1357900 | 885672 | 576000 | 0 | 867376 | 0 | 364672 | 680026 | 0 | 0 | 0 | 279850 | 1444800 | 843840 | 0 | 0 | 5400 | 679000 | 701400 | 0 | 685440 | 3650727 | 0 | 1346304 | 1935360 | 0 | 5177070 | 294000 | 0 | 0 | 7211000 | 453240 | 91728 | 0 | 797891 | 0 | 0 | 2023200 | 0 | 915120 | 101520 | 969600 | 2960160 | 976872 | 9358000 | 1272000 | 1083840 | 102872 | 26641 | 1244509 | 398682 | 232510 | 1711140 | 820680 | 168000 | 198200 | 83520 | 191880 | 799200 | 499309 | 0 | 0 | 178821 | 980160 | 462240 | 8826000 | 702545 | 0 | 13030908 | 211680 | 0 | 0 | 0 | 395182 | 1599400 | 0 |  | 21797818 | 0 | 8246592 | 0 | 0 | 0 | 0 | 0 | 177120 | 253952 | 0 | 3010000 | 188445 | 618048 | 0 | 0 | 0 | 256995 | 59329 | 644992 | 0 | 0 | 232187 | 0 | 173770 | 0 | 0 | 165240 | 1535563 | 0 | 4164000 | 0 | 0 | 4382355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8750036 | 0 | 0 | 325248 | 0 | 582374 | 0 | 21715 | 524832 | 29455400 | 5321080 | 0 | 1256400 | 18000 | 506880 | 537024 | 0 | 0 | 12160000 | 40646 | 0 | 23170909 | 305280 | 0 | 3557 | 218250 | 437420 |  | 142668400 | 129541457 | 272209857 | 84290692 | 21797818 | 42101428 | 0 | 25049064 | 60345871 | 5158204 | 0 | 6188199 | 1444800 | 23170909 | 2451192 | 211680 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28252800 | 0 |  | 0 | 32401020 | 0 | 0 | 0 | 6164216.04 | 23470286.8 | 0 | 0 | 0 | 907264.8 | 38954966.4 | 1883650 | 0 | 0 | 0 | 4732992 | 4293087.04 | 4940714.28 | 0 | 391050 | 0 | 0 | 0 | 5570726.4 | 0 | 0 | 0 | 0 | 0 | 3627483.5 | 16713638.15 | 0 | 0 | 0 |  | 1629537.6 | 10783236.96 | 12615463.71 | 0 | 0 | 2062108.8 | 0 | 0 | 0 | 0 | 0 | 22055508 | 0 | 17277280 | 2185419.4 | 4386017 | 2984714.64 | 2522880 | 0 | 3478177.76 | 0 | 6531275.52 | 12281269.56 | 0 | 0 | 0 | 209887.5 | 9477888 | 2624342.4 | 0 | 0 | 0 | 2648100 | 2616222 | 0 | 3118752 | 12485486.34 | 0 | 7471987.2 | 10102579.2 | 0 | 14444025.3 | 1934520 | 0 | 0 | 22281990 | 339930 | 69713.28 | 0 | 16276976.4 | 0 | 0 | 38865672 | 0 | 16115263.2 | 0 | 17268576 | 51358776 | 16196537.76 | 24798700 | 24244320 | 20332838.4 | 1845523.68 | 0 | 20347722.15 | 7750378.08 | 4171229.4 | 32699885.4 | 15929398.8 | 2992080 | 527212 | 1425686.4 | 0 | 14617368 | 8378405.02 | 0 | 0 | 0 | 17662483.2 | 7830345.6 | 26213220 | 9891833.6 | 0 | 90825428.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 61251868.58 | 0 | 24327446.4 | 0 | 0 | 0 | 0 | 0 | 3331627.2 | 4776837.12 | 0 | 9511600 | 893229.3 | 10655147.52 | 0 | 0 | 0 | 4602780.45 | 1088687.15 | 10842315.52 | 0 | 0 | 4158469.17 | 0 | 3112220.7 | 0 | 0 | 125086.68 | 16937259.89 | 0 | 35144160 | 0 | 0 | 14461771.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25550105.12 | 0 | 0 | 6446415.36 | 0 | 11600890.08 | 0 | 0 | 10412666.88 | 190870992 | 16548558.8 | 0 | 24311340 | 0 | 0 | 9317366.4 | 0 | 0 | 88768000 | 0 | 0 | 153159708.49 | 0 | 0 | 0 | 0 | 0 |  | 851488067.43 | 742206550.31 | 1593694617.74 | 247855058.85 | 61251868.58 | 131568197.92 | 0 | 457146341.75 | 422545840.65 | 0 | 0 | 110689713.5 | 9477888 | 153159708.49 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 7 | 329 | 0 | 0 | 0 | 8 | 96 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 22 | 23 | 20 | 15 | 17 | 0 | 132 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 310 | 0 | 215 | 45 | 50 | 26 | 22 | 0 | 43 | 0 | 0 | 27 | 0 | 0 | 0 | 10 | 54 | 31 | 0 | 0 | 1 | 28 | 30 | 0 | 30 | 163 | 0 | 59 | 83 | 0 | 204 | 15 | 0 | 0 | 290 | 20 | 2 | 0 | 18 | 0 | 0 | 87 | 0 | 15 | 9 | 50 | 108 | 26 | 373 | 55 | 52 | 0 | 4 | 65 | 17 | 17 | 57 | 30 | 12 | 0 | 16 | 14 | 17 | 31 | 0 | 0 | 31 | 34 | 6 | 393 | 36 | 0 | 612 | 3 | 0 | 0 | 0 | 73 | 0 | 0 |  | 911 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1140 | 220 | 0 | 0 | 2 | 84 | 0 | 0 | 0 | 504 | 4 | 0 | 1032 | 56 | 0 | 0 | 18 | 57 |  | 11199 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 332 | 0 | 0 | 0 | 0 | 150 | 13 | 0 | 0 | 0 | 30 | 55 | 35 | 0 | 20 | 23 | 23 | 33 | 26 | 0 | 135 | 80 | 0 | 0 | 25 | 223 | 0 | 0 | 0 | 0 | 12 | 63 | 84 | 0 | 0 | 19 | 0 | 15 | 0 | 0 | 0 | 290 | 0 | 214 | 26 | 50 | 36 | 25 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 12 | 78 | 31 | 0 | 0 | 0 | 28 | 30 | 0 | 33 | 163 | 0 | 58 | 86 | 0 | 204 | 12 | 0 | 0 | 285 | 20 | 5 | 0 | 96 | 0 | 0 | 87 | 0 | 87 | 0 | 100 | 200 | 104 | 386 | 56 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 45 | 12 | 30 | 0 | 0 | 108 | 35 | 0 | 0 | 0 | 91 | 36 | 393 | 160 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 910 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 35 | 50 | 0 | 127 | 10 | 80 | 0 | 0 | 0 | 32 | 10 | 97 | 0 | 0 | 46 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 70 | 0 | 102 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 625 | 0 | 0 | 1012 | 0 | 0 | 0 | 0 | 0 |  | 13296 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 21 | 23 | 23 | 33 | 25 | 0 | 135 | 80 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 18 | 85 | 85 | 0 | 20 | 19 | 0 | 25 | 0 | 0 |  | 320 | 0 | 215 | 26 | 70 | 43 | 25 | 0 | 43 | 0 | 43 | 52 | 0 | 0 |  | 12 | 86 | 30 | 0 | 0 | 0 | 28 | 30 | 0 | 35 | 163 | 0 | 60 | 86 | 0 | 210 | 15 | 0 | 0 | 320 | 20 | 5 | 0 | 95 | 0 | 0 | 95 | 0 | 149 | 0 | 100 | 200 | 100 | 385 | 55 | 105 | 17 | 0 | 95 | 51 | 34 | 106 | 45 | 12 | 130 | 17 | 0 | 162 | 35 | 0 | 35 | 0 | 92 | 36 | 350 | 160 | 0 | 612 | 60 | 0 | 0 | 0 |  |  |  |  | 910 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 132 | 10 | 110 | 0 | 0 | 0 | 38 | 24 | 95 | 0 | 0 | 46 | 0 | 30 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 0 | 1010 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 21 | 23 | 23 | 33 | 16 | 0 | 135 | 80 | 0 | 0 | 25 | 225 |  | 0 | 0 | 0 | 6 | 56 | 51 | 0 | 20 | 19 | 0 | 10 | 0 | 0 | 0 | 320 | 0 | 215 | 8 | 50 | 43 | 25 | 0 | 43 | 0 | 30 | 52 | 0 | 0 |  | 12 | 66 | 30 | 0 | 0 | 1.6 | 28 | 30 | 0 | 35 | 163 | 0 | 60 | 86 | 0 | 210 | 15 | 0 | 0 | 315 | 20 | 5 | 0 | 30 | 0 | 0 | 85 | 0 | 34 | 20 | 50 | 100 | 100 | 385 | 55 | 52 | 17 | 5 | 50 | 35 | 17 | 106 | 29 | 12 | 40 | 17 | 50 | 54 | 35 | 0 | 0 | 35 | 34 | 36 | 350 | 35 | 0 | 612 | 42 | 0 | 0 | 0 | 70 |  |  |  | 910 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 132 | 10 | 32 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 28 | 0 | 22 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 8 | 95 | 1244 | 220 |  | 150 | 6 | 100 | 0 | 0 | 0 | 520 | 30 | 0 | 1010 | 170 | 0 |  | 29 | 47 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 21 | 23 | 23 | 32 | 8 | 0 | 136 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 290 | 0 | 215 | 8 | 50 | 37 | 25 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 0 | 12 | 50 | 26 | 0 | 0 | 1 | 28 | 30 | 0 | 0 | 163 | 0 | 60 | 86 | 0 | 208 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 0 | 0 | 0 | 86 | 0 | 36 | 10 | 50 | 51 | 2 | 375 | 57 | 17 | 0 | 0 | 52 | 17 | 5 | 70 | 28 | 12 | 40 | 0 | 13 | 17 | 35 | 0 | 0 | 13 | 17 | 36 | 350 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 911 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1220 | 220 | 0 | 100 | 2 | 34 | 0 | 0 | 0 | 517 | 11 | 0 | 1014 | 33 | 0 | 0 | 25 | 45 | 0 |  |  |  | 126392120 | 21797818 | 0 | 60345871 | 31237263 | 1444800 | 2451192 | 211680 | 5158204 |  |  |  | 249038948
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 126.3921 | 21.7978 | 0 | 60.3459 | 31.2373 | 1.4448 | 2.4512 | 0.21168 | 5.1582
| Minimum Generation |  | 9122 | 6:00
| Highest Generation |  | 13296 | 19:30 | [129 empty] | 0 | [76 empty] | 249.0389
| Day Peak Generation |  | 11199 | 12:00
| Evening Peak Generation |  | 13296 | 19:30 | [206 empty] | 202699852
| HVDC Max Flow |  | 911 | 2:00 | [206 empty] | 202.6999
| HVDC EvPeak Flow |  | 910 | 19:30
| Load factor L.F |  | 85.3% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-10-27
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-10-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11199 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 10402
Evening Peak Generation : |  |  | 13296 | MW Hour : | 19:30 | Available Max Generation : |  | 14073
E.P. Demand (at gen end) : |  |  | 13480 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 14300
Maximum Generation : |  |  | 13296 | MW Hour : | 19:30 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 272.2099 | System Load Factor : | 85.3% | Load Shed : |  | 215
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1350 | MW at | 13:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-10-27
Actual : |  | 102.94 | Ft.(MSL) , | Rule curve : | 108.5 | Ft.( MSL )
Gas Consumed : |  | Total = | 914.15 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 379423256.77 | Adani : | 153159708.49
|  |  | Coal : | 422545840.65 | Oil: | 567836055.25 | Total: | 1522964861.16
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 39 | 936:00 | 4792.4408 |  |  | 80 | -0.2332%
Chittagong Area |  | 0 | 0:00 | 1318.3256 |  |  | 25 | 1.867%
Khulna Area |  | 0 | 0:00 | 1847.1228 |  |  | 25 | 2.316%
Rajshahi Area |  | 0 | 0:00 | 1605.8585 |  |  | 25 | 2.792%
Cumilla Area |  | 15 | 360:00 | 1321.145 |  |  | 20 | 2.496%
Mymensingh Area |  | 122 | 2928:00 | 982.8015 |  |  | 15 | 2.91%
Sylhet Area |  | 0 | 0:00 | 550.6738 |  |  | 10 | 2.121%
Barisal Area |  | 0 | 0:00 | 459.1188 |  |  | 0 | 2.985%
Rangpur Area |  | 0 | 0:00 | 897.9513 |  |  | 15 | 2.975%
Total |  | 176 |  | 13775.4381 |  |  | 215
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:16 | 17:13 | Sherpur 132/33kV S/S Transformer- 03 HT Project Work S/D Due to Development work
08:16 | 17:14 | Sherpur 132/33kV S/S Transformer- 03 LT Project Work S/D Due to Development work
08:16 | 17:10 | Sherpur 132/33kV S/S Transformer- 04 LT Project Work S/D
08:16 | 17:09 | Sherpur 132/33kV S/S Transformer- 04 HT Project Work S/D
08:19 | 16:27 | Chandraghona-Rangamati 132 kV Ckt-2 Scheduled S/D from Rangamati 132/33kV end Due to
Annual deadline checking and from Chandraghona 132/33kV end Due to Annual maintenance
| 08:20 | Rangpur 132/33kV S/S T-2 (404T) LT is restored.
| 08:20 | Rangpur 132/33kV S/S T-2 (404T) HT is restored.
08:20 |  | Sherpur 132/33kV S/S Transformer- 01 HT Project Work S/D Due to Development work
08:20 |  | Sherpur 132/33kV S/S Transformer- 02 HT Project Work S/D Due to Development work
08:30 | 12:23 | Ashuganj 230/132/33kV S/S TR-OAT-12 LT Project Work S/D Due to As per instruction of
NLDC.
08:30 | 12:26 | Ashuganj 230/132/33kV S/S TR-OAT-12 HT Project Work S/D Due to As per instruction of
NLDC.
08:32 | 10:59 | Sylhet (South) S/S Trafo-2 LT Scheduled S/D Due to PDB Work |  |  |  |  | 22.0MW load interrup.
08:35 | 13:32 | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to 33 kv T - 4 Renuvenation work by |  |  |  |  | 2.0MW load interrup.
Kps.
08:36 | 13:30 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to 33 kv T-4 Renuvenation work by KPS. |  |  |  |  | 2.0MW load interrup.
08:36 | 13:30 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to 33 kv T-4 Renuvenation work by KPS. |  |  |  |  | 2.0MW load interrup.
08:37 | 18:39 | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to Annual
maintenance and deadline checking.
08:40 | 16:58 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D Due to Annual Maintenance
08:40 | 13:32 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to 33 kv T-4 Renuvenation work by KPS.
08:41 | 17:00 | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D Due to Annual Maintenance
08:42 | 13:30 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to 33 kv T-4 Renuvenation work by KPS.
08:44 | 12:59 | Aminbazar 400/230/132kV S/S 230 kv Bus 02 Scheduled S/D
08:49 | 13:15 | Aminbazar-Keraniganj 230kV Ckt-2 Project Work S/D from Keranigonj 230/132/33kV end Due to
Development work in Aminbazar S/S. and from Aminbazar 400/230/132kVend.
| 09:03 | Baroaulia-Hathazari 132 kV Ckt-1 is restored.
09:11 | 12:13 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end Due to Annual
maintenance work.
09:22 | 18:32 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 LT Scheduled S/D Due to Annual
Maintenance
09:23 | 18:32 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 HT Scheduled S/D Due to Annual
Maintenance
09:25 |  | Chauddagram-Cumilla(S) 132 kV Ckt-2 Scheduled S/D from Cumilla(S) 132/33kV end Due to
Annual Maintenance and from Chauddagram 132/33kV end Due to Line Checking (Yearly
Maintenance).
09:27 | 18:34 | Payra 400/132/33kV S/S FROM AUXILIARY TRANSFORMER Scheduled S/D Due to Annual
Maintenance
09:31 | 17:06 | Agargaon-Bhasantek 132kV Ckt-1 Scheduled S/D from Cantonment 132/33kV end Due to Agargaon
-Cantonment Ckt-1 S/d for Annual Maintenance Agargaon end . and from Agargaon 230/132kV
end Due to Annual Maintenance
11:10 | 12:12 | Haripur 230/132kV S/S Auto TR-1 LT Forced S/D Due to Red Hot Maintenance at 132 KV CB y
phase top clamp.
11:10 | 12:12 | Haripur 230/132kV S/S Auto TR-1 HT Forced S/D Due to Red Hot Maintenance at 132 KV CB y
phase top clamp.
11:12 | 12:54 | Baghabari-Ishurdi 230 kV Ckt-1 Scheduled S/D from Ishurdi 230/132kV end. and from
Baghabari 230/132kV end Due to ঈশ্বরদী প্রান্তে সংরক্ষণ কাজের জন্য
11:26 | 12:47 | Ishurdi 230/132kV S/S 230 kV Bus 2 Scheduled S/D Due to annual maintanance
12:00 |  | Day peak Generation is 11199 MW.
| 12:35 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-01 (704T) HT is restored.
| 12:37 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-01 (704T) LT is restored.
| 14:03 | Rampur 230/132/33 S/S TR-1 HT is restored.
| 14:18 | Rampur 230/132/33 S/S TR-1 LT is restored.
| 14:20 | BIPTC S/S Baharampur-3 is restored.
| 15:15 | Rampura 230/132kV S/S NLDC Trafo HT is restored.
17:45 | 18:06 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent protection relay P142, Trip
circuit Relay relays Due to Due to 33kv sholla & kusumhati feeder.
19:30 |  | Evening Peak Generation = 13,296MW and Loadshed = 176MW
06:00 |  | Minimum Generation is 10402 MW
06:55 |  | Rampur 230/132/33 S/S ATR-01 (706T) HT Scheduled S/D Due to Annual Maintenance
07:42 |  | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to For Annual Maintenance.
07:43 |  | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to For Annual Maintenance.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-10-26
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 409 | 9810000
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10189000
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 349842 | Fuel shortage
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 101000 | Fuel shortage
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7695176
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 50544 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 30 | 259200 | Fuel shortage
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2005920
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 272404
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 270132 | Fuel shortage
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 43 | 1059240 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 23 | 478800 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 602500
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 26 | 311040 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 96 | 797891 | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 87 | 915120 | Fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1083840
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 83520 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 799200 | Fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 178821
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 462240 | Fuel shortage
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 1599400 | On test.
| Dhaka area Total |  |  |  | 5915 | 2046 | 39374830
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 191525
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 101520
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 125280 | Fuel shortage
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 215 | 5158204
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 223 | 5239385
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 102872 | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 63 | 612336 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 704381 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 969600
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 475200
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26641
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1244509 | Fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 398682 | Fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 232510 | Fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 168000 | Fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 499309 | Fuel shortage
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 160 | 702545
55 | SS Power I |  | IPP | 2*612 | 1224 | 612 | 13030908 | Coal shortage
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 211680
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 0 | 0 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1684 | 30195087
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 214 | 5204000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7905200
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 393 | 8826000 | Gas shortage
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 885672 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 25 | 576000 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 652364 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 867376 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 104 | 976872 | Fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 364672 | Engine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1357900 | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2960160
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 78 | 1444800
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 680026
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 279850 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1711140 | Engine problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 45 | 820680 | Fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 91 | 980160 | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 395182
| Cumilla Area Total |  |  |  | 2917 | 1808 | 36888054
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 31 | 843840 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5400
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 2023200 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 56 | 1272000 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 191880
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 92640 | Fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 0 | Fuel shortage
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 646 | 186 | 4428960
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 28 | 679000 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 701400 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3650727
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 33 | 685440 | Engine problem
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 91728 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 58 | 1346304
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1935360
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 204 | 5177070 | Machine problem.
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 12 | 294000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 20 | 453240 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7211000 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 386 | 9358000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 30 | 198200 | Sync at 19:05
| Sylhet Area Total |  |  |  | 2417 | 1340 | 31781469
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 910 | 21797818
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 177120 | Engine problem
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 253952 | Fuel shortage
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 357 | 8246592 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 506880
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 625 | 12160000 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1977 | 43142362
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 618048 | Engine problem
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 188445 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 127 | 3010000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 29455400
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5321080
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1256400
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Under maint.
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3557
| Barisal Area Total |  |  |  | 2236 | 1831 | 39852930
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 32 | 256995 | Engine problem
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 10 | 59329 | Engine problem
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 46 | 232187 | Engine problem
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 4382355
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 343 | 8750036 | FGMO
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 173770 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 165240 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 644992 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 325248 | High Voltage
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 524832
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 18000
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1012 | 23170909
135 | Sirajganj 68 MW Solar Park |  | NWPGCL | 68 | 68 | 0 | 218250
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 437420
| Rajshahi Area Total |  |  |  | 3449 | 1972 | 39359563
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 65 | 1535563
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4164000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 102 | 582374
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 21715
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 537024
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 40646
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 305280
| Rangpur Area Total |  |  |  | 950 | 452 | 7186602
| Total |  |  |  | 27086 | 13296 | 272209857
| Eastern Grid Total |  |  |  | 16752 | 7064 | 142668400
| Western Grid Total |  |  |  | 10334 | 6232 | 129541457
| National Grid Total |  |  |  | 27086 | 13296 | 272209857
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-10-26
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9081.25 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3643.9 | MW
i) Dhaka area |  |  | 4847.75 |  | MW | i) Khulna area |  |  |  | 1534 | MW
ii) Chattogram area |  |  | 1368.5 |  | MW | ii) Barishal area |  |  |  | 410.5 | MW
iii) Cumilla area |  |  | 1305 |  | MW | iii) Rajshahi area |  |  |  | 1069.4 | MW
iv) Mymensingh area |  |  | 981 |  | MW | iv) Rangpur area |  |  |  | 630 | MW
v) Sylhet area |  |  | 579 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12725.15 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 7 | 00:00 | 67 | Jashore | 118 | 18:30 | 133 | Rajbari | 70 | 18:30
2 | AKSML | 113 | 14:00 | 68 | Jhenaidah | 111 | 18:30 | 134 | Rajendrapur | 90 | 18:00
3 | Aftabnagar | 52 | 13:00 | 69 | Joydebpur | 173 | 15:00 | 135 | Rajshahi | 87 | 18:30
4 | Agargaon | 107 | 18:30 | 70 | Joypurhat | 40 | 18:00 | 136 | Rajshahi-230 | 65 | 13:00
5 | Agrabad | 120 | 12:00 | 71 | Juldah | 15 | 15:00 | 137 | Ramganj | 110 | 21:00
6 | Amnura | 39 | 21:00 | 72 | KSRM | 31 | 12:00 | 138 | Rampur | 40 | 18:30
7 | Ashuganj | 76 | 01:00 | 73 | Kabirpur | 253 | 18:30 | 139 | Rangamati | 16 | 18:30
8 | BSRM | 67 | 06:00 | 74 | Kachua | 76 | 18:00 | 140 | Rangpur | 115 | 18:30
9 | Bagerhat | 83 | 19:00 | 75 | Kallyanpur | 99 | 18:00 | 141 | Ruppur | 4.2 | 12:00
10 | Bakulia | 100 | 18:30 | 76 | Kalurghat | 36 | 15:00 | 142 | SSM | 0 | 00:00
11 | Banani | 56.4 | 13:00 | 77 | Kamrangirchar | 59.4 | 13:00 | 143 | Saidpur | 80 | 18:30
12 | Bangabhaban | 13 | 11:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 108 | 18:30
13 | Barapukuria | 46 | 18:00 | 79 | Kazla | 111 | 13:00 | 145 | Satmasjid | 101 | 13:00
14 | Barguna | 20 | 20:00 | 80 | Keranigonj | 74 | 19:00 | 146 | Savar | 202 | 12:00
15 | Barishal | 112 | 12:00 | 81 | Khagrachori | 30 | 19:00 | 147 | SevenRings | 11.08 | 01:00
16 | Barishal-230 | 80 | 18:30 | 82 | Khulna | 75 | 12:00 | 148 | ShahCement | 29 | 02:00
17 | Baroaulia | 81 | 14:00 | 83 | Khulshi | 173 | 18:30 | 149 | Shahjadpur | 79 | 18:30
18 | Baroirhat | 65 | 19:00 | 84 | Kishoreganj | 138 | 00:00 | 150 | Shahjibazar | 132 | 22:00
19 | Bashundhara | 162 | 18:00 | 85 | Kodda | 296 | 21:00 | 151 | Shahmirpur | 46 | 01:00
20 | BashundharaCement | 1 | 17:00 | 86 | Kulaura | 46 | 18:30 | 152 | Shariatpur | 77 | 21:00
21 | Beanibazar | 68 | 18:30 | 87 | Kurigram | 46 | 18:00 | 153 | Sherpur | 112 | 18:00
22 | Benapole | 52 | 19:30 | 88 | Kushtia | 122 | 19:00 | 154 | Shikalbaha | 22 | 19:00
23 | Bhaluka | 128 | 15:00 | 89 | Lalbag | 90 | 13:00 | 155 | Shitalakhya | 82.4 | 12:00
24 | Bhandaria | 49 | 22:00 | 90 | Lalmonirhat | 48 | 18:00 | 156 | Sholosohor | 45 | 15:00
25 | Bhangura | 31 | 18:00 | 91 | MI_Cement | 17.2 | 12:00 | 157 | Shyampur | 176 | 13:00
26 | Bheramara(GK) | 53 | 18:30 | 92 | Madanganj | 34 | 00:00 | 158 | Siddhirganj | 120 | 15:00
27 | Bhulta | 241 | 18:30 | 93 | Madaripur | 98 | 19:00 | 159 | Sirajganj | 78 | 19:30
28 | Bog-Sherpur | 50 | 18:30 | 94 | Madartek | 71.43 | 22:00 | 160 | Sonargaon | 86 | 18:00
29 | Bogura | 118 | 19:00 | 95 | Madunaghat | 55 | 18:00 | 161 | Sreemongol | 74 | 19:00
30 | Borhanuddin | 79 | 22:00 | 96 | Magura | 59 | 18:00 | 162 | Sreepur | 72 | 15:00
31 | Brahmanbaria | 175 | 20:00 | 97 | Mahasthangarh | 80 | 21:00 | 163 | Srinagar | 45.4 | 21:00
32 | Cantonment | 114 | 12:00 | 98 | Manikganj | 107 | 18:00 | 164 | Sunamganj | 50 | 00:00
33 | Chandpur | 68 | 18:00 | 99 | Maniknagar | 56 | 13:00 | 165 | Sylhet | 44 | 19:00
34 | Chandraghona | 34 | 19:00 | 100 | Matarbari | 46 | 21:00 | 166 | Sylhet-132 | 122 | 12:00
35 | Chapai | 44 | 21:00 | 101 | Matuail | 64 | 12:00 | 167 | TK | 34 | 18:30
36 | Charsaidpur | 37 | 23:00 | 102 | Millgate | 120 | 12:00 | 168 | Tangail | 174 | 21:00
37 | Chauddagram | 64 | 20:00 | 103 | Mirpur | 129 | 18:00 | 169 | Thakurgaon | 65 | 18:30
38 | Chhatak | 31 | 19:00 | 104 | Mirsorai | 5 | 16:00 | 170 | Tongi | 121 | 12:00
39 | Chowmuhani | 224 | 18:30 | 105 | Mirzapur | 46 | 18:00 | 171 | Ullahpara | 31 | 20:00
40 | Chuadanga | 104 | 18:30 | 106 | Mithapukur | 38 | 18:30 | 172 | Ullon | 50 | 15:00
41 | Coxsbazar | 112 | 18:30 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 88 | 13:00
42 | Cumilla(N) | 160 | 19:30 | 108 | Mogbazar | 94.7 | 14:00 | 174 | UttaraNew | 51 | 12:00
43 | Cumilla(S) | 160 | 18:30 | 109 | Mongla | 38 | 16:00 | 175 | Zigatola | 94 | 18:00
44 | Daudkandi | 159 | 20:00 | 110 | Motijheel | 42 | 13:00
45 | Dhaka | 34 | 13:00 | 111 | Munshiganj | 98 | 23:00
46 | Dhamrai | 118 | 19:30 | 112 | Mymensingh | 198 | 20:00
47 | Dhanmondi | 113 | 18:00 | 113 | Naogaon | 85 | 18:30
48 | Dohazari | 104 | 15:00 | 114 | Narail | 54 | 19:00
49 | Faridpur | 151 | 18:00 | 115 | Narinda | 66 | 13:00
50 | Fatullah | 88 | 12:00 | 116 | Narshingdi | 169 | 05:00
51 | Fenchuganj | 41 | 12:00 | 117 | Natore | 114 | 18:30
52 | Feni | 104 | 18:00 | 118 | Nawabganj | 43 | 20:00
53 | GPH | 98 | 22:00 | 119 | Netrakona | 112 | 21:00
54 | Ghatail | 56 | 18:00 | 120 | New | 54.6 | 12:00
55 | Ghorashal | 60 | 23:00 | 121 | Niamatpur | 41 | 18:30
56 | Goalpara | 20 | 18:00 | 122 | Noapara | 38 | 18:30
57 | Gollamari | 74 | 13:00 | 123 | PHP | 5 | 05:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-10-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 381 | 02:00 | 369 | 11:00 | Kaliakoir | 369 | 02:00 | 359 | 10:00
| Ashuganj | 405 | 7:00 | 384 | 12:00 | Madunaghat | 391 | 01:00 | 384 | 11:00
| Bhulta | 396 | 07:00 | 384 | 10:00 | Meghnaghat | 378 | 05:00 | 368 | 10:00
| Bibiana | 393 | 01:00 | 383 | 12:00 | Payra | 408 | 03:00 | 402 | 13:00
| BIPTC | 400 | 15:00 | 391 | 13:00 | Rahanpur | 400 | 05:00 | 392 | 13:00
| Bogura | 387 | 20:00 | 378 | 13:00 | Rampal | 401 | 05:00 | 387 | 14:00
| Gopalganj | 397 | 05:00 | 383 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 229 | 05:00 | 218 | 11:00 | Haripur | 226 | 01:00 | 220 | 10:00
| AKSML | 239 | 20:00 | 229 | 05:00 | Hasnabad | 227 | 04:00 | 218 | 15:00
| Aminbazar | 228 | 20:00 | 218 | 10:00 | Hathazari | 236 | 13:00 | 230 | 10:00
| Ashuganj | 231 | 07:00 | 227 | 00:00 | Ishurdi | 233 | 05:00 | 226 | 15:00
| Ashuganj-400 | 235 | 7:00 | 225 | 12:00 | Jhenaidah | 227 | 06:00 | 214 | 18:30
| Baghabari | 229 | 05:00 | 224 | 11:00 | Kaliakoir | 230 | 04:00 | 220 | 11:00
| Barapukuria | 225 | 05:00 | 218 | 13:00 | Keranigonj | 228 | 04:00 | 216 | 11:00
| Barapukuria-230 | 220 | 22:00 | 214 | 7:00 | Khulna(S) | 229 | 05:00 | 217 | 18:30
| Barishal | 236 | 17:00 | 230 | 12:00 | Madunaghat | 236 | 14:00 | 231 | 11:00
| Bheramara | 230 | 05:00 | 223 | 11:00 | Maniknagar | 229 | 00:00 | 221 | 10:00
| Bhulta | 230 | 03:00 | 222 | 10:00 | Meghnaghat | 238 | 03:00 | 230 | 10:00
| Bibiana | 226 | 20:00 | 220 | 16:00 | Meghnaghat-400 | 231 | 04:00 | 224 | 10:00
| BIPTC | 233 | 05:00 | 223 | 18:30 | Mirsorai | 239 | 19:30 | 228 | 10:00
| Bogura | 233 | 05:00 | 228 | 13:00 | Rajshahi | 231 | 06:00 | 224 | 15:00
| Bogura-400 | 236 | 05:00 | 230 | 15:00 | Rampal | 228 | 05:00 | 218 | 18:30
| Borhanuddin | 241 | 08:00 | 235 | 15:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 238 | 20:00 | 227 | 10:00 | Rampura | 234 | 00:00 | 219 | 11:00
| Cumilla(N) | 228 | 20:00 | 222 | 10:00 | Shikalbaha | 237 | 18:00 | 228 | 10:00
| Faridpur | 233 | 04:00 | 225 | 15:00 | Shyampur | 228 | 04:00 | 218 | 15:00
| Fenchuganj | 229 | 12:00 | 224 | 00:00 | Siddhirganj | 231 | 07:00 | 223 | 11:00
| Ghorashal | 230 | 00:00 | 228 | 16:00 | Sirajgonj | 238 | 03:00 | 234 | 13:00
| Ghorashal-230 | 227 | 04:00 | 218 | 11:00 | Sreepur | 229 | 08:00 | 221 | 11:00
| Gopalganj | 234 | 05:00 | 226 | 15:00 | Tongi | 226 | 01:00 | 217 | 10:00
| GPH | 237 | 20:00 | 228 | 10:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 136 | 07:00 | 129 | 10:00 | Kushtia | 135 | 05:00 | 128 | 18:30
| Agargaon | 135 | 03:00 | 127 | 11:00 | Lalbag | 135 | 04:00 | 126 | 10:00
| Agrabad | 135 | 20:00 | 128 | 10:00 | Lalmonirhat | 134 | 19:30 | 128 | 09:00
| AKS | 133 | 18:00 | 129 | 09:00 | Madanganj | 127 | 08:00 | 123 | 06:00
| Aminbazar | 138 | 19:30 | 126 | 10:00 | Madaripur | 132 | 06:00 | 126 | 13:00
| Amnura | 139 | 19:30 | 129 | 12:00 | Madartek | 135 | 04:00 | 128 | 11:00
| Ashuganj | 137 | 05:00 | 135 | 00:00 | Madunaghat | 136 | 18:00 | 130 | 10:00
| Bagerhat | 132 | 06:00 | 121 | 18:00 | Magura | 135 | 06:00 | 125 | 18:30
| Bakulia | 135 | 20:00 | 130 | 10:00 | Mahasthangarh | 139 | 05:00 | 134 | 13:00
| Banani | 135 | 01:00 | 129 | 11:00 | Manikganj | 125 | 20:00 | 120 | 09:00
| Bangabhaban | 130 | 03:00 | 122 | 15:00 | Maniknagar | 129 | 03:00 | 124 | 11:00
| Barapukuria | 140 | 05:00 | 134 | 13:00 | Matarbari | 126 | 15:00 | 117 | 00:00
| Barguna | 141 | 17:00 | 131 | 14:00 | Matuail | 129 | 04:00 | 125 | 11:00
| Barishal | 131 | 20:00 | 124 | 13:00 | Millgate | 132 | 04:00 | 124 | 11:00
| Barishal-230 | 131 | 05:00 | 124 | 15:00 | Mirpur | 137 | 05:00 | 32 | 17:00
| Baroaulia | 136 | 18:00 | 131 | 04:00 | Mirzapur | 128 | 03:00 | 122 | 15:00
| Baroirhat | 131 | 13:00 | 119 | 00:00 | Mithapukur | 138 | 19:30 | 131 | 13:00
| Bashundhara | 136 | 04:00 | 123 | 10:00 | MI_Cement | 133 | 05:00 | 125 | 11:00
| BashundharaCement | 127 | 08:00 | 123 | 06:00 | Modern | 135 | 20:00 | 129 | 10:00
| Beanibazar | 127 | 07:00 | 123 | 18:30 | Mogbazar | 137 | 07:00 | 130 | 11:00
| Benapole | 134 | 04:00 | 120 | 18:30 | Mongla | 132 | 05:00 | 120 | 18:30
| Bhaluka | 128 | 01:00 | 122 | 23:00 | Motijheel | 130 | 03:00 | 122 | 15:00
| Bhandaria | 126 | 20:00 | 119 | 15:00 | Munshiganj | 128 | 20:00 | 124 | 00:00
| Bhangura | 139 | 03:00 | 134 | 11:00 | Mymensingh | 135 | 11:00 | 119 | 19:30
| Bheramara | 135 | 03:00 | 132 | 11:00 | Naogaon | 139 | 05:00 | 129 | 08:00
| Bheramara(GK) | 135 | 03:00 | 132 | 15:00 | Narail | 134 | 04:00 | 123 | 18:30
| Bhulta | 123 | 18:00 | 117 | 23:00 | Narinda | 125 | 20:00 | 120 | 09:00
| Bog-Sherpur | 139 | 02:00 | 134 | 11:00 | Narshingdi | 129 | 09:00 | 115 | 11:00
| Bogura | 142 | 20:00 | 137 | 13:00 | Natore | 137 | 05:00 | 132 | 12:00
| Bogura-230 | 141 | 05:00 | 137 | 13:00 | Nawabganj | 135 | 04:00 | 127 | 11:00
| Brahmanbaria | 131 | 08:00 | 123 | 00:00 | Netrakona | 134 | 04:00 | 126 | 21:00
| Cantonment | 135 | 03:00 | 126 | 11:00 | New | 134 | 05:00 | 125 | 11:00
| Chandpur | 136 | 13:00 | 121 | 03:00 | Niamatpur | 134 | 03:00 | 130 | 13:00
| Chandraghona | 136 | 18:00 | 132 | 10:00 | Noapara | 136 | 06:00 | 124 | 18:00
| Chapai | 133 | 03:00 | 129 | 13:00 | Pabna | 136 | 03:00 | 131 | 15:00
| Charsaidpur | 128 | 06:00 | 124 | 10:00 | Palashbari | 138 | 20:00 | 131 | 10:00
| Chauddagram | 131 | 13:00 | 121 | 02:00 | Panchagarh | 138 | 19:30 | 124 | 12:00
| Chhatak | 128 | 05:00 | 123 | 18:30 | Patuakhali | 139 | 19:00 | 131 | 10:00
| Chowmuhani | 128 | 14:00 | 115 | 00:00 | Payra | 138 | 17:00 | 133 | 10:00
| Chuadanga | 132 | 05:00 | 116 | 18:00 | PHP | 131 | 13:00 | 120 | 00:00
| Coxsbazar | 125 | 16:00 | 118 | 00:00 | Postogola | 134 | 03:00 | 127 | 11:00
| Cumilla(N) | 132 | 13:00 | 127 | 00:00 | Purbachal | 135 | 01:00 | 124 | 11:00
| Cumilla(S) | 132 | 20:00 | 124 | 00:00 | Purbasadipur | 138 | 20:00 | 125 | 12:00
| Daudkandi | 126 | 06:00 | 121 | 10:00 | Rahanpur | 136 | 04:00 | 133 | 12:00
| Dhaka | 136 | 03:00 | 129 | 15:00 | Rahim | 128 | 05:00 | 124 | 00:00
| Dhamrai | 131 | 04:00 | 124 | 11:00 | Rajbari | 129 | 06:00 | 124 | 18:30
| Dhanmondi | 136 | 03:00 | 129.6 | 15:00 | Rajendrapur | 128 | 19:00 | 118 | 09:00
| Dohazari | 133 | 18:00 | 127 | 10:00 | Rajshahi | 136 | 03:00 | 131 | 14:00
| Faridpur | 131 | 07:00 | 126 | 15:00 | Rajshahi-230 | 135 | 04:00 | 125 | 12:00
| Fatullah | 133 | 20:00 | 126 | 11:00 | Ramganj | 130 | 13:00 | 116 | 03:00
| Fenchuganj | 134 | 07:00 | 131 | 23:00 | Rampur | 134 | 19:00 | 130 | 09:00
| Feni | 131 | 13:00 | 120 | 00:00 | Rampura | 135 | 02:00 | 126 | 00:00
| Ghatail | 131 | 06:00 | 122 | 18:00 | Rangamati | 135 | 18:00 | 130 | 10:00
| Ghorashal | 135 | 03:00 | 132 | 15:00 | Rangpur | 137 | 19:30 | 129 | 12:00
| Goalpara | 137 | 05:00 | 126 | 18:30 | Ruppur | 137 | 04:00 | 133 | 18:00
| Gollamari | 136 | 05:00 | 129 | 18:00 | Saidpur | 139 | 20:00 | 130 | 08:00
| Gopalganj | 132 | 04:00 | 126 | 18:30 | Satkhira | 134 | 04:00 | 122 | 18:30
| Gopalganj-400 | 132 | 05:00 | 127 | 15:00 | Satmasjid | 135 | 04:00 | 127 | 11:00
| Gulshan | 135 | 07:00 | 129 | 10:00 | Savar | 135 | 02:00 | 125 | 10:00
| Halishahar | 135 | 18:00 | 128 | 10:00 | SevenRings | 135 | 04:00 | 131 | 23:00
| Haripur | 129 | 01:00 | 125 | 10:00 | ShahCement | 128 | 06:00 | 124 | 10:00
| HaripurSBU | 1260 | 18:30 | 122 | 00:00 | Shahjadpur | 140 | 08:00 | 130 | 01:00
| Hasnabad | 133 | 01:00 | 128 | 10:00 | Shahjibazar | 131 | 10:00 | 126 | 00:00
| Hathazari | 138 | 19:30 | 134 | 11:00 | Shahmirpur | 135 | 18:00 | 130 | 11:00
| Ishurdi | 137 | 05:00 | 133 | 15:00 | Shariatpur | 130 | 04:00 | 125 | 14:00
| Jaldhaka | 136 | 20:00 | 127 | 08:00 | Sherpur | 137 | 12:00 | 124 | 18:00
| Jamalpur | 138 | 11:00 | 128 | 18:00 | Shikalbaha | 125 | 19:00 | 119 | 10:00
| Jashore | 133 | 05:00 | 121 | 18:30 | Shikalbaha-230 | 136 | 18:00 | 130 | 10:00
| Jhenaidah | 136 | 04:00 | 127 | 18:00 | Shitalakhya | 133 | 05:00 | 125 | 11:00
| Jhenaidah-230 | 136 | 05:00 | 125 | 18:30 | Sholosohor | 135 | 18:00 | 129 | 10:00
| Joydebpur | 135 | 13:00 | 125 | 15:00 | Shyampur | 131 | 19:30 | 123 | 10:00
| Joypurhat | 131 | 04:00 | 127 | 13:00 | Shyampur-230 | 133 | 04:00 | 126 | 11:00
| Juldah | 135 | 18:00 | 131 | 00:00 | Siddhirganj | 129 | 02:00 | 124 | 11:00
| Kabirpur | 131 | 01:00 | 122 | 09:00 | Sirajganj | 138 | 05:00 | 133 | 14:00
| Kachua | 134 | 13:00 | 122 | 00:00 | Sonargaon | 129 | 01:00 | 123 | 00:00
| Kaliakoir | 133 | 04:00 | 125 | 09:00 | Sreemongol | 131 | 08:00 | 127 | 00:00
| Kallyanpur | 131 | 01:00 | 125 | 11:00 | Sreepur | 130 | 08:00 | 125 | 15:00
| Kalurghat | 136 | 19:30 | 130 | 10:00 | Srinagar | 134 | 05:00 | 127 | 11:00
| Kamrangirchar | 135 | 05:00 | 123 | 12:00 | SSM | 140 | 18:00 | 136 | 00:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 126 | 09:00 | 121 | 23:00
| Kazla | 130 | 05:00 | 123 | 11:00 | Sylhet | 130 | 09:00 | 126 | 23:00
| Keranigonj | 135 | 04:00 | 127 | 11:00 | Sylhet-132 | 129 | 07:00 | 127 | 00:00
| Khagrachori | 134 | 18:00 | 130 | 10:00 | Tangail | 127 | 05:00 | 122 | 18:00
| Khulna | 134 | 06:00 | 129 | 18:00 | Thakurgaon | 141 | 20:00 | 125 | 13:00
| Khulna(S) | 137 | 05:00 | 127 | 18:30 | TK | 136 | 19:30 | 130 | 10:00
| Khulshi | 134 | 20:00 | 127 | 10:00 | Tongi | 135 | 01:00 | 127 | 12:00
| Kishoreganj | 131 | 05:00 | 124 | 23:00 | Ullahpara | 138 | 04:00 | 134 | 12:00
| Kodda | 131 | 18:00 | 117 | 09:00 | Ullon | 135 | 01:00 | 129 | 11:00
| KSRM | 136 | 18:00 | 130 | 10:00 | Uttara | 136 | 03:00 | 128 | 10:00
| Kulaura | 133 | 09:00 | 130 | 00:00 | UttaraNew | 137 | 04:00 | 123 | 11:00
| Kurigram | 134 | 04:00 | 128 | 09:00 | Zigatola | 135 | 05:00 | 126 | 11:00

## L-Curve
Date | 2024-10-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1828 | 6233 | 5889 | 12122 |  |  |  | QF-LDC-11
0:30 | 1718 | 5903 | 5476 | 11379 | Date: | 2024-10-26
1:00 | 1608 | 5573 | 5063 | 10636
1:30 | 1562 | 5487.5 | 4946 | 10433.5
2:00 | 1516 | 5402 | 4829 | 10231
2:30 | 1536 | 5356 | 4764.5 | 10120.5 | [5 empty] | Gen. at Eve. Peak | 13296 | 13296 MW (19:30 )
3:00 | 1556 | 5310 | 4700 | 10010 | [6 empty] | 19:30
3:30 | 1543 | 5226.5 | 4594.5 | 9821 | [5 empty] | Gen. at Day Peak | 11199 | 11199 MW (12:00 )
4:00 | 1530 | 5143 | 4489 | 9632 | [6 empty] | 12:00
4:30 | 1513 | 5164.5 | 4367 | 9531.5 | [5 empty] | Highest Generation | 13296
5:00 | 1496 | 5186 | 4245 | 9431 | [6 empty] | 19:30
5:30 | 1531 | 4927 | 4349.5 | 9276.5
6:00 | 1566 | 4668 | 4454 | 9122
6:30 | 1496 | 4779.5 | 4614.5 | 9394
7:00 | 1426 | 4891 | 4775 | 9666
7:30 | 1389 | 4924.5 | 4803.5 | 9728
8:00 | 1352 | 4958 | 4832 | 9790
8:30 | 1486 | 4946 | 4922 | 9868
9:00 | 1620 | 4934 | 5012 | 9946
9:30 | 1684 | 5021 | 5025 | 10046
10:00 | 1748 | 5108 | 5038 | 10146
10:30 | 1736 | 5316 | 5091 | 10407
11:00 | 1724 | 5524 | 5144 | 10668
11:30 | 1611 | 5735.5 | 5198 | 10933.5
12:00 | 1498 | 5947 | 5252 | 11199
12:30 | 1424 | 6183 | 5276 | 11459
13:00 | 1350 | 6419 | 5300 | 11719
13:30 | 1442 | 6420 | 5251 | 11671
14:00 | 1534 | 6421 | 5202 | 11623
14:30 | 1526 | 6405.5 | 5225 | 11630.5
15:00 | 1518 | 6390 | 5248 | 11638
15:30 | 1535 | 6280.5 | 5212.5 | 11493
16:00 | 1552 | 6171 | 5177 | 11348
16:30 | 1501 | 6182.5 | 5203.5 | 11386
17:00 | 1450 | 6194 | 5230 | 11424
17:30 | 1474 | 6507.5 | 5567.5 | 12075
18:00 | 1498 | 6821 | 5905 | 12726
18:30 | 1527 | 6904 | 6068.5 | 12972.5
19:00 | 1556 | 6987 | 6232 | 13219
19:30 | 1478 | 7064 | 6232 | 13296
20:00 | 1498 | 6982 | 6180 | 13162 |  |  |  | Executive Engineer
20:30 | 1561 | 6887.5 | 6157.5 | 13045 |  |  |  | Network Operation Division
21:00 | 1624 | 6793 | 6135 | 12928
21:30 | 1641 | 6720.5 | 6112 | 12832.5
22:00 | 1658 | 6648 | 6089 | 12737 |  |  |  |  | Page 6 of 7
22:30 | 1730 | 6531.5 | 6065.5 | 12597
23:00 | 1802 | 6415 | 6042 | 12457
23:30 | 1815 | 6324 | 5965.5 | 12289.5
24:00 | 1828 | 6233 | 5889 | 12122
13296 MW (19:30 )
11199 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-10-26 |  | Energy |  | 272209857
[16 empty] | 2024-10-26 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3549 | 911 | 1710 | 0 | 1436 | 2599 | 213 | 0 | 618 | 76 | 1010 | 0 | 0 | 55.39
0:30 | 3546 | 910.5 | 1752.5 | 0 | 1021 | 2538.5 | 213 | 0 | 341 | 69 | 972.5 | 0 | 15 | 27.695 |  |  | Date: | 44129
1:00 | 3543 | 910 | 1795 | 0 | 606 | 2478 | 213 | 0 | 64 | 62 | 935 | 0 | 30 | 0
1:30 | 3556.5 | 910.5 | 1767.5 | 0 | 515 | 2437 | 213 | 0 | 56 | 61 | 888.5 | 0 | 28.5 | 0 | [8 empty] | Total Energy | 272.2099 | 272.2099 | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 3570 | 911 | 1740 | 0 | 424 | 2396 | 213 | 0 | 48 | 60 | 842 | 0 | 27 | 0 | [8 empty] | Energy not Served | 1.181 | 1.181
2:30 | 3512.5 | 910.5 | 1808 | 0 | 382.5 | 2334.5 | 213.5 | 0 | 40 | 59 | 837 | 0 | 23 | 0 | [8 empty] | Energy Requirement | 273.3909 | 273.3909
3:00 | 3455 | 910 | 1876 | 0 | 341 | 2273 | 214 | 0 | 32 | 58 | 832 | 0 | 19 | 0
3:30 | 3411.5 | 910.5 | 1829 | 0 | 335.5 | 2177.5 | 214 | 0 | 24 | 57 | 838.5 | 0 | 23.5 | 0 | [7 empty] | Shortage
4:00 | 3368 | 911 | 1782 | 0 | 330 | 2082 | 214 | 0 | 16 | 56 | 845 | 0 | 28 | 0
4:30 | 3221 | 910.5 | 1966 | 0 | 293.5 | 1985.5 | 214.5 | 0 | 16 | 56 | 840.5 | 0 | 28 | 0
5:00 | 3074 | 910 | 2150 | 0 | 257 | 1889 | 215 | 0 | 16 | 56 | 836 | 0 | 28 | 0
5:30 | 3164 | 910.5 | 1886.5 | 0 | 257.5 | 1915.5 | 215 | 0 | 16 | 53 | 832 | 0 | 26.5 | 0
6:00 | 3254 | 911 | 1623 | 0 | 258 | 1942 | 215 | 0 | 16 | 50 | 828 | 0 | 25 | 0
6:30 | 3403 | 910.5 | 1635.5 | 0 | 269.5 | 2013.5 | 215 | 0 | 24 | 49 | 829.5 | 22 | 22.5 | 0 | [6 empty] | Coal
7:00 | 3552 | 910 | 1648 | 0 | 281 | 2085 | 215 | 0 | 32 | 48 | 831 | 44 | 20 | 0
7:30 | 3550.5 | 910.5 | 1659.5 | 0 | 291.5 | 2083.5 | 215 | 0 | 32 | 44 | 831 | 96.5 | 14 | 0 | [5 empty] | Oil
8:00 | 3549 | 911 | 1671 | 0 | 302 | 2082 | 215 | 0 | 32 | 40 | 831 | 149 | 8 | 0
8:30 | 3449 | 911 | 1661 | 0 | 333.5 | 2144.5 | 215 | 0 | 32 | 43 | 916.5 | 157 | 5.5 | 0
9:00 | 3349 | 911 | 1651 | 0 | 365 | 2207 | 215 | 0 | 32 | 46 | 1002 | 165 | 3 | 0
9:30 | 3323.5 | 910.5 | 1622.5 | 0 | 387 | 2233 | 214.5 | 0 | 56 | 48 | 1019.5 | 230 | 1.5 | 0
10:00 | 3298 | 910 | 1594 | 0 | 409 | 2259 | 214 | 0 | 80 | 50 | 1037 | 295 | 0 | 0
10:30 | 3371.5 | 910 | 1639 | 0 | 440.5 | 2326 | 214 | 0 | 89.5 | 51 | 1036 | 329.5 | 0 | 0
11:00 | 3445 | 910 | 1684 | 0 | 472 | 2393 | 214 | 0 | 99 | 52 | 1035 | 364 | 0 | 0
11:30 | 3419.5 | 910.5 | 1714 | 0 | 651.5 | 2442 | 213 | 0 | 135.5 | 53 | 1033.5 | 359.5 | 1.5 | 0
12:00 | 3394 | 911 | 1744 | 0 | 831 | 2491 | 212 | 0 | 172 | 54 | 1032 | 355 | 3 | 0
12:30 | 3380.5 | 910.5 | 1735 | 0 | 1042 | 2543 | 212 | 0 | 174 | 56 | 1032 | 354.5 | 19.5 | 0
13:00 | 3367 | 910 | 1726 | 0 | 1253 | 2595 | 212 | 0 | 176 | 58 | 1032 | 354 | 36 | 0
13:30 | 3367 | 910 | 1726 | 0 | 1253 | 2595 | 212 | 0 | 176 | 58 | 1032 | 354 | 36 | 0
14:00 | 3367 | 910 | 1726 | 0 | 1253 | 2595 | 212 | 0 | 176 | 58 | 1032 | 354 | 36 | 0
14:30 | 3405 | 910 | 1729 | 0 | 1275 | 2560.5 | 213 | 0 | 192 | 60 | 1033 | 282.5 | 18.5 | 0
15:00 | 3443 | 910 | 1732 | 0 | 1297 | 2526 | 214 | 0 | 208 | 62 | 1034 | 211 | 1 | 0
15:30 | 3384 | 910 | 1692.5 | 0 | 1264.5 | 2542 | 214.5 | 0 | 223 | 60 | 1031 | 171 | 0.5 | 0
16:00 | 3325 | 910 | 1653 | 0 | 1232 | 2558 | 215 | 0 | 238 | 58 | 1028 | 131 | 0 | 0
16:30 | 3335.5 | 910 | 1678 | 0 | 1270.5 | 2551.5 | 215 | 0 | 254.5 | 60 | 1020 | 91 | 0 | 0
17:00 | 3346 | 910 | 1703 | 0 | 1309 | 2545 | 215 | 0 | 271 | 62 | 1012 | 51 | 0 | 0
17:30 | 3426.5 | 909.5 | 1739.5 | 0 | 1577.5 | 2605 | 215 | 0 | 493.5 | 70 | 1012.5 | 25.5 | 0.5 | 250
18:00 | 3507 | 909 | 1776 | 0 | 1846 | 2665 | 215 | 0 | 716 | 78 | 1013 | 0 | 1 | 500
18:30 | 3515 | 910 | 1729 | 0 | 2064.5 | 2683 | 215 | 0 | 765 | 77 | 1013.5 | 0 | 0.5 | 336.5
19:00 | 3523 | 911 | 1682 | 0 | 2283 | 2701 | 215 | 0 | 814 | 76 | 1014 | 0 | 0 | 173
19:30 | 3565 | 910 | 1699 | 0 | 2301 | 2716 | 215 | 0 | 800 | 78 | 1012 | 0 | 0 | 166.72
20:00 | 3525 | 910 | 1668 | 0 | 2230 | 2717 | 215 | 0 | 810 | 78 | 1009 | 0 | 0 | 160.44
20:30 | 3515 | 910 | 1704 | 0 | 2140.5 | 2716 | 215 | 0 | 753.5 | 78 | 1013 | 0 | 0 | 138.72
21:00 | 3505 | 910 | 1740 | 0 | 2051 | 2715 | 215 | 0 | 697 | 78 | 1017 | 0 | 0 | 117
21:30 | 3493.5 | 909.5 | 1700 | 0 | 2030.5 | 2715.5 | 214.5 | 0 | 678.5 | 78 | 1012.5 | 0 | 0 | 112.4575
22:00 | 3482 | 909 | 1660 | 0 | 2010 | 2716 | 214 | 0 | 660 | 78 | 1008 | 0 | 0 | 107.915
22:30 | 3484 | 909.5 | 1692 | 0 | 1841.5 | 2716 | 213.5 | 0 | 651.5 | 78 | 1011 | 0 | 0 | 98.365
23:00 | 3486 | 910 | 1724 | 0 | 1673 | 2716 | 213 | 0 | 643 | 78 | 1014 | 0 | 0 | 88.815
23:30 | 3517.5 | 910.5 | 1717 | 0 | 1554.5 | 2657.5 | 213 | 0 | 630.5 | 77 | 1012 | 0 | 0 | 72.1025 |  |  | Max Temp. in Dhaka |  | 33.5°C
24:00 | 3549 | 911 | 1710 | 0 | 1436 | 2599 | 213 | 0 | 618 | 76 | 1010 | 0 | 0 | 55.39
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on X13: Author:

## Generation
2024-10-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 133 | 133 | 134 | 134 | 135 | 135 | 135 | 135 | 135 | 134 | 134 | 132 | 132 | 134 | 134 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 134 | 133 | 133 | 3230204
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1928000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [10 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 191525
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 |  | 14 | 18 | 12 | 9 | 16 | 15 | 11 |  | 1 | [9 empty] | 101520
6 | Sikalbaha 225MW CCPP (Gas) | 228 | 226 | 228 | 227 | 228 | 228 | 228 | 226 | 224 | 220 | 219 | 222 | 221 | 220 | 220 | 222 | 221 | 223 |  | 223 | 223 | 224 | 224 | 225 | 225 | 224 | 5239385
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [14 empty] | 51 | 51 | 68 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 704381
12 | Hathazari 100 MW peaking PP | [11 empty] | 40 | 37 | 37 | 37 | 37 | 37 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 612336
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 102872
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [15 empty] | 30 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 364672
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 290 | 290 | 250 | 335 | 335 | 335 | 280 | 280 | 332 | 329 | 329 | 326 | 325 | 328 | 328 | 330 |  | 333 | 332 | 332 | 330 | 335 | 280 | 328 | 7695176
18 | Kodda 300 MW PP Unit-2 (Summit) | [11 empty] | 18 | 43 | 34 | 37 | 48 | 47 | 47 |  | 92 | 96 | 96 | 97 | 97 | 73 | 45 | 797891
19 | Ashuganj 195 MW PP (APSCL-United) | 26 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 652364
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 570 | 550 | 525 | 455 | 400 | 370 | 370 | 370 | 405 | 450 | 600 | 612 | 612 | 612 | 612 | 612 | 612 | 612 |  | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 13030908
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 38 | 29 | 26 | 28 | 32 | 34 | 34 | 35 | 36 |  | 36 | 36 | 36 | 37 | 37 | 37 | 37 | 885672
33 | Ashuganj 225 MW CCPP | 216 | 216 | 217 | 216 | 217 | 216 | 217 | 217 | 212 | 210 | 212 | 215 | 211 | 211 | 210 | 212 | 214 | 214 |  | 213 | 214 | 217 | 213 | 215 | 212 | 211 | 5204000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 280 | 350 | 310 | 320 | 320 | 345 | 310 | 310 | 310 | 310 | 325 | 310 | 310 | 310 |  | 280 | 290 | 285 | 315 | 285 | 345 | 345 | 7905200
| Ashuganj 420 MW CCPP(East) | 395 | 395 | 320 | 320 | 275 | 250 | 393 | 393 | 350 | 350 | 393 | 393 | 393 | 393 | 393 | 350 | 380 | 393 |  | 393 | 393 | 370 | 330 | 330 | 330 | 330 | 8826000
35 | Ashuganj 55 MW PP (Precision) | 24 | 24 | 25 | 25 | 26 | 26 | 25 | 25 | 25 | 23 | 22 | 22 | 21 | 21 | 21 | 22 | 23 | 25 |  | 25 | 25 | 26 | 26 | 26 | 26 | 25 | 576000
36 | Chandpur 150 MW CCPP | 50 | 50 | 70 | 70 | 75 | 75 | 75 | 70 | 50 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 1357900
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 413 | 411 | 407 | 401 | 358 | 369 | 402 | 401 | 382 | 410 | 405 | 405 | 404 | 404 | 400 | 400 | 400 | 402 |  | 410 | 409 | 409 | 406 | 410 | 407 | 405 | 9810000
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 400 | 360 | 320 | 320 | 420 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 420 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10189000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 48 | 47 | 48 | 48 | 48 | 48 | 48 | 46 | 46 | 42 | 32 | 31 | 31 | 30 | 30 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 843840
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 24 | 12 | 15 | 12 | 14 | 50 | 39 | 28 | 8 | 1 | [9 empty] | 191880
44 | Fenchugonj CCPP Phase-1 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 679000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 701400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 59 | 59 | 59 | 58 | 40 | 59 | 60 | 60 | 58 | 59 | 59 | 58 | 57 | 57 | 40 | 58 | 58 |  | 58 | 58 | 59 | 57 | 58 | 58 | 57 | 1346304
48 | Shahjibazar 86 MW PP (Shahjibazar) | 86 | 86 | 61 | 61 | 61 | 61 | 86 | 86 | 83 | 86 | 83 | 83 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1935360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 210 | 210 | 210 | 211 | 211 | 211 | 211 | 210 | 209 | 207 | 206 | 204 | 204 | 204 | 202 | 204 | 205 | 205 |  | 204 | 204 | 206 | 207 | 207 | 207 | 208 | 5177070
51 | Sylhet 20 MW GTPP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 10 | 10 | 10 | 10 | 10 | 10 |  | 12 | 12 | 12 | 12 | 12 |  | 0 | 294000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 |  |  | 2 | 2 | 2 | 2 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 91728
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 453240
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 285 | 285 | 280 | 280 | 305 | 290 | 290 | 300 | 280 | 300 | 290 | 300 | 295 | 305 | 300 | 305 | 300 |  | 280 | 285 | 280 | 310 | 295 | 305 | 320 | 7211000
| Bibiyana South 400 MW | [20 empty] | 30 | 44 | 45 | 45 | 45 | 45 | 198200
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 270132
59 | Tangail Palli Power Gen 22 MW | [15 empty] | 4 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 8 | 0 | 92640
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 62 | 60 | 58 | 56 | 56 | 50 | 48 | 40 | 46 | 50 | 52 | 54 | 58 | 62 | 62 | 58 | 62 | 78 |  | 76 | 78 | 78 | 78 | 78 | 78 | 76 | 1444800
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 36 | 8 | 2 | 3 | 2 | 3 | 5 | 2 | 2 | 2 | 3 | 10 |  | 14 | 15 | 18 | 22 | 27 | 31 | 3 | 475200
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 279850
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 23 |  |  | 18 | 18 |  | 20 | 20 | 21 | 22 | 21 | 23 | 23 | 521400
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 537840
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 20 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 478800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 24 |  | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 602500
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 70 | 52 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 57 | 106 | 106 | 106 | 106 | 106 | 106 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 1711140
| Chowmuhani 113 MW | 28 | 29 | 29 | 29 | 29 | 29 | 28 | 29 | 29 | 29 | 28 | 30 | 40 | 33 | 28 | 28 | 28 | 35 |  | 45 | 45 | 47 | 47 | 47 | 47 | 38 | 820680
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 72 | 72 | 72 | 72 | 72 | 108 |  | 108 | 108 | 108 | 54 | 17 | 17 | 17 | 799200
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 |  | 26 | 26 | 26 | 26 | 26 | 17 | 8 | 311040
79 | Kodda 150 MW PP | 64 | 48 | 32 | 16 | 16 | 16 | 32 | 32 | 32 | 80 | 82 | 96 | 95 | 95 | 95 | 95 | 95 | 136 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2005920
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 8 | 8 | [7 empty] | 27 | 52 | 52 | 52 | 50 | 43 | 43 |  | 52 | 52 | 52 | 52 | 51 | 43 | 51 | 680026
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 |  |  | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 35 | 35 | 35 | 105 |  | 105 | 105 | 105 | 105 | 105 | 35 | 17 | 1083840
| Kaptai 7 MW Solar PP | [7 empty] | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 26641
| Jodiac Power | 17 | [7 empty] | 0 | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 33 |  | 35 | 35 | 35 | 35 | 33 | 17 | 17 | 398682
| Karnaphuli Power Ltd. | [10 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 232510
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [15 empty] | 11 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 101000
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [8 empty] | 3 | 15 | 16 | 16 | [10 empty] | 14 | 15 | 16 | 0 | 83520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 37 | 37 | 37 | 37 | 5 | 5 | 18 | 31 | 37 | 37 | 37 | 30 | 36 | 36 | 36 | 36 | 36 | 36 |  | 33 | 33 | 34 | 36 |  |  | 0 | 685440
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 5 | 5 | 5 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 867376
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 8 | 8 | 8 | 8 | [7 empty] | 8 | 8 | 8 |  | 0 | 50544
95 | Patenga 50MW PP (Baraka) | [16 empty] | 1 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 125280
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [14 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 7 | 30 | 50 | 55 | 55 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 349842
100 | Manikganj 55 MW PP (Northern) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 55 | 55 | 55 | 17 |  |  | 0 | 272404
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3650727
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 0 | 0 | 0 | [9 empty] | 5400
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 30 | 35 | 35 | 35 |  | 0 | 259200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 97 | 75 | 65 | 65 | 65 | 70 | 85 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 87 | 87 |  | 87 | 87 | 86 | 87 | 87 | 87 | 87 | 2023200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 15 | 22 | 34 | 37 | 54 |  | 81 | 87 | 91 | 105 | 103 | 83 | 71 | 915120
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | [9 empty] | 10 | 50 | 50 | 50 | 50 | 70 | 88 | 100 |  | 100 | 100 | 100 | 100 | 89 | 50 | 50 | 969600
116 | Chandpur 200 MW (Desh energy) | 133 | 100 | 100 | 100 | 51 | 51 | 51 | 51 | 51 | 51 | 63 | 108 | 175 | 200 | 144 | 104 | 105 | 150 |  | 200 | 200 | 200 | 200 | 200 | 200 | 132 | 2960160
117 | Ashuganj 150 MW PP (Midland) | [10 empty] | 2 | 26 | 65 | 92 | 87 | 92 | 93 | 95 |  | 102 | 104 | 10 | 10 | 38 | 80 | 77 | 976872
118 | Bibiyana-III 400 MW CCPP | 385 | 384 | 383 | 383 | 335 | 383 | 383 | 385 | 340 | 343 | 387 | 373 | 373 | 373 | 388 | 388 | 340 | 385 |  | 386 | 386 | 385 | 387 | 385 | 387 | 387 | 9358000
| Jamalpur 115 MW PP (United) | 58 | 56 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 46 | 55 | 55 | 57 | 57 | 56 | 56 | 57 | 57 |  | 56 | 56 | 56 | 57 | 57 | 57 | 58 | 1272000
| Anwara 300 MW PP (United) | 65 | 15 | [7 empty] | 30 | 30 | 65 | 174 | 184 | 200 | 51 | 52 | 52 |  | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 1244509
| Juldah unit-2 (Acorn) | [10 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 168000
| Anlima Energy Ltd. | 17 | [9 empty] | 5 | 31 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 499309
| Bhairob 54.5 MW | [25 empty] | 0 | 0
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 8 | 19 | 13 | 31 | 31 | 30 | 17 | 16 | 4 | 1 | [9 empty] | 178821
| Chandpur 115(Doreen) | 17 | 17 | 17 | 16 | 17 | 18 | 18 | 17 | 31 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 42 | 66 |  | 90 | 91 | 92 | 92 | 92 | 62 | 30 | 980160
| Kanchan Purbachal Power Generation Ltd. | 17 | [10 empty] | 6 | 36 | 36 | 36 | 21 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 462240
| Mirsharai 150 MW (Oil) | [10 empty] | 17 | 36 | 36 | 36 | 17 | 17 | 17 | 160 |  | 160 | 160 | 160 | 54 | 17 | 17 | 17 | 702545
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 30 | 27 | 19 | 28 | 28 | 25 | 20 | 8 | 3 | 0 | 0 | 3 | 36 | 0 | 1 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211680
| Sonagazi 75 MW Solar Plant | [5 empty] | 0 | 12 | 34 | 16 | 65 | 70 | 73 | 35 | 34 | 20 | 31 | 2 | [9 empty] | 395182
Matarbari 2*600 MW (CPGCL)
| Meghnaghat (Reliance) 718MW CCPP | 48 | 76 | 310 | 285 | 764 | 89 | [19 empty] | 0 | 1599400
| Sreepur 150 MW | [25 empty] | 0 | 0
120
121 | Eastern Zone Total | 5573 | 5402 | 5310 | 5143 | 5186 | 4668 | 4891 | 4958 | 4934 | 5108 | 5524 | 5947 | 6419 | 6421 | 6390 | 6171 | 6194 | 6821 |  | 6987 | 7064 | 6982 | 6793 | 6648 | 6415 | 6233 | 142668400
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | [16 empty] | 3 | 34 |  | 37 | 35 | 30 | 25 | 25 | 25 | 21 | 177120
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 7 | 30 | 56 | 72 | 84 | 84 | 69 | 70 | 46 | 23 | 2 | [9 empty] | 506880
132 | Rampal 1320 MW (BIFPCL) | 511 | 509 | 511 | 510 | 382 | 385 | 378 | 377 | 407 | 454 | 456 | 504 | 504 | 506 | 509 | 511 | 509 | 618 |  | 624 | 625 | 626 | 624 | 625 | 625 | 508 | 12160000
133 | United Payra Power Ltd. | 17 | [13 empty] | 22 | 100 | 137 | 137 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1256400
| Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 180 | 180 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 180 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5321080
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 10 | 48 |  | 80 | 80 | 110 | 110 | 110 | 110 | 110 | 618048
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3557
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 127 | 127 | 127 | 127 | 93 | 93 | 127 | 127 | 93 | 93 | 93 | 127 | 127 | 127 | 127 | 127 | 127 | 127 |  | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 3010000
141 | Bhola 33 MW PP (Venture) | 10 | 10 | 8 | 9 | 7 | 8 | 6 | 6 | 5 | 6 | 6 | 5 | 7 | 7 | 7 | 6 | 6 | 9 |  | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 188445
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP | [17 empty] | 25 |  | 53 | 50 | 50 | 42 | 42 | 41 | 36 | 253952
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
147 | Bheramara HVDC | 910 | 911 | 910 | 911 | 910 | 911 | 910 | 911 | 911 | 910 | 910 | 911 | 910 | 910 | 910 | 910 | 910 | 909 |  | 911 | 910 | 910 | 910 | 909 | 910 | 911 | 21797818
148 | Bheramara 410 MW CCPP | 300 | 330 | 360 | 310 | 250 | 260 | 388 | 385 | 380 | 300 | 375 | 300 | 300 | 300 | 353 | 300 | 300 | 357 |  | 357 | 357 | 355 | 358 | 355 | 368 | 367 | 8246592
149 | Payra 1320 MW | 1160 | 1100 | 1000 | 880 | 870 | 950 | 1100 | 1100 | 1160 | 1120 | 1100 | 1140 | 1244 | 1120 | 1170 | 1200 | 1190 | 1200 |  | 1230 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 29455400
150
151 | Barapukuria TPP Unit-1 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 65 | 65 | 65 | 67 | 65 | 65 | 65 | 65 | 65 | 64 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1535563
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4164000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 22 |  | 46 | 32 | 46 | 46 | 46 | 46 | 45 | 256995
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 0 | [9 empty] | 18000
157 | Sirajganj 68 MW Solar Park | [6 empty] | 2 | 3 | 9 | 25 | 39 | 18 | 22 | 25 | 16 | 10 | 2 | [9 empty] | 218250
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 214 | 170 | 140 | 140 | 140 | 140 | 140 | 178 | 160 | 160 | 160 | 140 | 140 | 160 | 160 | 160 | 191 |  | 214 | 214 | 180 | 180 | 180 | 180 | 180 | 4382355
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 414 | 321 | 317 | 332 | 332 | 414 | 414 | 414 | 355 | 358 | 353 | 390 | 350 | 340 | 354 | 320 | 353 | 389 |  | 333 | 343 | 312 | 348 | 314 | 364 | 364 | 8750036
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | [17 empty] | 5 |  | 5 | 10 | 10 | 18 | 18 |  |  | 59329
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 165240
166 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | [17 empty] | 35 |  | 46 | 46 | 47 | 45 | 45 | 45 | 30 | 232187
169 | Santahar 50 MW Peaking PP | [17 empty] | 24 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 173770
170 | Natore 52 MW PP (Rajlanka)
171 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 8 | 8 | 8 | 8 | 8 | 85 |  | 97 | 97 | 97 | 97 | 97 | 99 | 99 | 644992
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [17 empty] | 2 |  | 87 | 70 | 35 | 35 | 35 | 35 | 35 | 325248
173 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 90 |  | 110 | 113 | 113 | 70 | 70 | 50 | 50 | 524832
175 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [17 empty] | 53 |  | 102 | 102 | 111 | 111 | 111 | 56 | 49 | 582374
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 4 |  | 4 | 2 | 3 | 1 | 1 | 0 | 0 | [9 empty] | 21715
| Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 72 |  | 110 | 115 | 115 | 75 | 75 | 50 | 50 | 537024
| Intraco Solar 30 MW | [6 empty] | 2 | 4 | 3 | 6 | 2 | 4 | 3 | 7 | 4 | 3 | 0 | [9 empty] | 40646
178 | Adani Power Jharkhanda Ltd | 935 | 842 | 832 | 845 | 836 | 828 | 831 | 831 | 1002 | 1037 | 1035 | 1032 | 1032 | 1031 | 1034 | 1028 | 1012 | 1013 |  | 1014 | 1012 | 1009 | 1017 | 1008 | 1014 | 1010 | 23170909
| Teesta Solar Limited | [6 empty] | 5 | 27 | 21 | 18 | 39 | 56 | 60 | 59 | 29 | 19 | 4 | [9 empty] | 305280