## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-10-30 | Wednesday
|  | Date (day): | 2024-10-30 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12304.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13623 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-10-29 | 2024-10-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 403 | 415 | 400 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 15 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 13 | 13 | 62 |  | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 295 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 0 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 147 | 64 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 17 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 17 | 35 | 20 |  | Fuel shortage
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 38 | 44 | 44 |  | 36 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 23 | 23 |  | 10 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 30 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 17 | 34 | 16 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 64 | 250 | 45 | 300 |  |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 130 | 72 | 132 | 17 |  | Fuel shortage
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 52 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 17 | 0 | 104 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 90 | 35 | 90 | 72 |  | Fuel shortage
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 36 | 36 | 36 | 36 |  | 19 | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1680 | 2229 | 1736 | 2323 | 2710 | 825
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 19 | 19 | 31 |  | Fuel shortage
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 176 | 175 | 175 | 175 | 55 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 222 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 44 | 71 | 56 | 72 |  | 26 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 58 | 84 | 51 | 85 |  | 17 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 100 | 50 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 10 | 5 | 10
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 69 | 52 | 52 | 52 | 248 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 17 | 35 | 19 |  | Fuel shortage
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 35 | 35 | 81 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 160 | 35 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 |  | Coal shortage
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 4 | 5 | 5 | 10 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 0 | 0 | 0 | 0 | 1150 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1411 | 1651 | 1433 | 1661 | 2753 | 373
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 209 | 213 | 215 | 215
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 310 | 320 | 320 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 360 | 395 | 350 | 350 |  |  | FGMO
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 41 | 43 | 43
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 75 | 115 | 100 | 115 | 35 |  | Fuel shortage
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 27 | 43 | 30 | 43 |  | 9 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 51 | 50 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 34 | 17 | 34 | 166 |  | Fuel shortage
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 62 | 72 | 66 | 86
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 25 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 106 | 17 | 106
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 18 | 17 | 17 | 96 |  | Fuel shortage
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 74 | 35 | 75 | 40 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 68 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1407 | 1597 | 1429 | 1580 | 687 | 384
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 10 | 11 | 10 | 20 | 182 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 77 | 77 | 68 | 68 | 132 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 48 | 57 | 57 | 58 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 37 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 0 | 24
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 28 | 0 | 35 | 19 |  | Fuel shortage
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 0 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 173 | 164 | 186.6 | 204 | 182 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 28 | 28 | 28 | 28 |  | 42 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract Expired
90 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 |  | 6 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 54 | 60 | 60
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 11 | 10 | 86
94 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 202 | 208 | 210 | 210 |  | 21 | Machine problem
96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 20 | 20 |  | 5 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 285 | 315 | 320 |  |  | FGMO
99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 387 | 385 | 385
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 360 | 370 | 380 | 380
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1585 | 1551 | 1606 | 1687 | 70 | 464
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 914 | 774 | 939 | 939
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 3 | 25 | 0 | 35 |  | 19 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 51 | 30 | 60 |  | 49 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 305 | 273 | 290 | 280 | 130 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 509 | 621 | 360 | 620 | 614 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1801 | 1744 | 1719 | 1934 | 1431 | 68
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 16 | 16
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 5 | 10 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 123 | 127 | 132 | 132 |  | 62 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1200 | 1244 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  | 307 | Under maint
118 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1581 | 1799 | 1639 | 1772 | 0 | 369
119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 45 | 35 | 45 |  | 7 | Engine problem
121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 26 | 0 | 24 |  | 47 | Engine problem
122 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 28 | 46
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 169 | 163 | 180 | 190
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 387 | 414 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 22 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 5 | 8 |  | 3 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 50 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 9 | 113 | 113 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 35 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1017 | 1016 | 1000 | 1000
135 | Sirajganj 68 MW Solar Park |  | Solar | NWPGCL | 68 | 68 | 68 | 39 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 70 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1766 | 2034 | 1964 | 2078 | 611 | 86
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 62 | 62 | 65 | 65 |  | 20
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 60 | 34 | 34
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 72 | 115 | 115 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 110 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 455 | 407 | 592 | 384 | 40 | 209
| Total |  |  |  |  | 27791 | 27086 | 11859 | 13176 | 12304.6 | 13623 | 8484 | 2778
A. |  | 2024-10-29 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 13176 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 10626 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14000 | MW
3 | Day peak Generation : |  |  | 11859 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13369.92 | MW
4 | Evening peak Generation : |  |  | 13176 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 787 | MW
5 | Total Energy Generation : |  | 288.7636 | MKWHr | By Solar | 3.5765 | MKWHr
| By Gas : | 128.3903 | MKWHr |  | By Oil: | 40.5281 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 64.4113 | MKWHr |  | By Hydro: | 4.2163 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 24.4326 | MKWHr |  | By Wind: | 0.05664 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 8484 | MW | Dhaka | 5199.82 | 5029.82 |  | 170 |  | 18:00 |  | 960
|  |  | For Plants S/D or M/C prob = |  |  | 2778 | MW | Chittagong | 1228.5 | 1198.5 |  | 30 |  | 19:00 |  | 823
|  |  | Total = |  |  | 11262 | MW | Khulna | 1582.8 | 1462.8 |  | 120 |  | 19:30 |  | 787
7 | Total Gas Supplied : |  | 908.07 | MMCFD | **Import Adani: | Taka | 161499314.14 | Rajshahi | 1241.8 | 1191.8 |  | 50 |  | 20:00 |  | 753
8 | Fuel Cost : | i) Gas : | Taka | 381408085.476 | ii) Oil : | Taka | 740148204.07 | Comilla | 1279 | 1154 |  | 125 |  | 21:00 |  | 744.9
|  | iii) Coal : | Taka | 449966080.68 | Total | Taka | 1733021684.366 | Mymensingh | 1057 | 927 |  | 130 |  | 22:00 |  | 739.17
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 12416.25 | MKWHr. | Sylhet | 574 | 514 |  | 60 |  | 23:00 |  | 929.215
| ii) During Peak Demand : |  |  | 1164 | MW (W to E) at | 19:30 | hrs | Barisal | 432 | 390 |  | 42 |  | 24:00 |  | 1122.125
| iii) Maximum : |  |  | 1094 | MW at | 18:00 | hrs | Rangpur | 775 | 715 |  | 60
10 | Maximum Temperature in Dhaka was |  |  |  | 34.2°C |  |  | Total | 13369.92 | 12582.92 |  | 787
B. |  | 2024-10-30 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 34.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 357 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13623 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12400 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 306.8223 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10925 | MW at | 6:00 | 37 | 38 | 62 | 62 | 47 | 39 | 17 | 19 | 36
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6216 | MKWHr. | ii) HVDC Flow at Peak Time |  | 774 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.5302 | MKWHr. | iii) Maximum HVDC Flow : |  | 922 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.38 |  | (b) Today: | 102.19 |  | (c) Rule Curve: |  | 108.7
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-10-29 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 322 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 0 | 0 | 133 | 40 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 0 | 62 | 69 | 0 | 0 | 19 | 0 | 31 | 0 | 0 | 0 | 340 | 0 | 213 | 8 | 50 | 42 | 24 | 0 | 43 | 0 | 44 | 52 | 0 | 0 | 0 | 18 | 66 | 33 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 55 | 41 | 0 | 207 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 195 | 0 | 0 | 87 | 0 | 86 | 0 | 50 | 51 | 81 | 385 | 58 | 17 | 0 | 0 | 52 | 35 | 17 | 17 | 19 | 12 | 320 | 16 | 0 | 17 | 35 | 0 | 17 | 0 | 22 | 36 | 393 | 17 | 0 | 614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 912 | 0 | 289 | 0 | 0 | 0 | 0 | 0 | 20 | 46 | 0 | 132 | 10 | 16 | 0 | 0 | 0 | 46 | 18 | 0 | 0 | 0 | 37 | 0 | 15 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 501 | 0 | 0 | 1015 | 0 | 0 | 0 | 0 | 0 |  | 6403 | 5799 | 12202 | 3784 | 912 | 1719 | 0 | 1517 | 2594 | 173 | 0 | 422 | 66 | 1015 | 0 | 0 | 169.99 | 102.43
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 320 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 0 | 0 | 133 | 40 | 0 | 0 | 8 | 228 | 0 | 0 | 0 |  | 0 | 62 | 68 | 0 | 0 | 19 | 0 | 36 | 0 | 0 | 0 | 310 | 0 | 216 | 8 | 50 | 42 | 24 | 0 | 43 | 0 | 44 | 52 | 0 | 0 | 0 | 18 | 68 | 33 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 130 | 0 | 55 | 41 | 0 | 206 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 195 | 0 | 0 | 87 | 0 | 48 | 0 | 50 | 51 | 83 | 383 | 58 | 17 | 0 | 0 | 52 | 35 | 17 | 17 | 18 | 12 | 320 | 0 | 0 | 17 | 35 | 0 | 17 | 0 | 21 | 36 | 393 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 912 | 0 | 289 | 0 | 0 | 0 | 0 | 0 | 20 | 46 | 0 | 100 | 10 | 16 | 0 | 0 | 0 | 46 | 18 | 0 | 0 | 0 | 21 | 0 | 15 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 1244 | 180 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 509 | 0 | 0 | 1017 | 0 | 0 | 0 | 0 | 0 |  | 6282 | 5626 | 11908 | 3729 | 912 | 1541 | 0 | 1463 | 2600 | 173 | 0 | 405 | 68 | 1017 | 0 | 0 | 145.16 | 102.42
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 315 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 0 | 0 | 132 | 40 | 0 | 0 | 8 | 227 | 0 | 0 | 0 |  | 0 | 62 | 0 | 0 | 0 | 6 | 0 | 37 | 0 | 0 | 0 | 285 | 0 | 215 | 8 | 50 | 42 | 24 | 0 | 43 | 0 | 44 | 52 | 0 | 0 | 0 | 18 | 66 | 33 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 130 | 0 | 55 | 41 | 0 | 206 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 45 | 0 | 0 | 87 | 0 | 51 | 0 | 50 | 51 | 83 | 371 | 58 | 17 | 0 | 0 | 52 | 35 | 17 | 17 | 13 | 12 | 320 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 21 | 36 | 393 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 912 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 20 | 41 | 0 | 100 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 66 | 0 | 170 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 1244 | 180 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 515 | 0 | 0 | 1015 | 0 | 0 | 0 | 0 | 0 |  | 5898 | 5489 | 11387 | 3698 | 912 | 1539 | 0 | 1178 | 2607 | 172 | 0 | 200 | 66 | 1015 | 0 | 0 | 117.465 | 102.41
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 0 | 0 | 134 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 300 | 0 | 214 | 8 | 50 | 42 | 24 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 18 | 68 | 33 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 130 | 0 | 55 | 41 | 0 | 209 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 87 | 0 | 51 | 0 | 50 | 51 | 50 | 335 | 58 | 17 | 0 | 0 | 52 | 35 | 0 | 17 | 18 | 12 | 320 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 21 | 36 | 393 | 17 | 0 | 613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 912 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 15 | 41 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 1244 | 180 | 0 | 150 | 0 | 0 | 74 | 0 | 0 | 510 | 0 | 0 | 1014 | 0 | 0 | 0 | 0 | 0 |  | 5643 | 5376 | 11019 | 3665 | 912 | 1544 | 0 | 952 | 2601 | 174 | 0 | 89 | 68 | 1014 | 0 | 0 | 101.23 | 102.4
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 0 | 0 | 135 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 310 | 0 | 214 | 8 | 50 | 42 | 24 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 18 | 62 | 33 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 130 | 0 | 55 | 41 | 0 | 209 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 87 | 0 | 51 | 0 | 50 | 51 | 0 | 310 | 58 | 17 | 0 | 0 | 52 | 35 | 0 | 17 | 18 | 12 | 320 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 21 | 36 | 393 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 913 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 501 | 0 | 0 | 1015 | 0 | 0 | 0 | 0 | 0 |  | 5566 | 5204 | 10770 | 3632 | 913 | 1617 | 0 | 732 | 2591 | 175 | 0 | 33 | 62 | 1015 | 0 | 0 | 0 | 102.39
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 0 | 0 | 135 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 290 | 0 | 215 | 8 | 50 | 42 | 24 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 18 | 60 | 33 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 130 | 0 | 55 | 41 | 0 | 209 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 87 | 0 | 51 | 0 | 50 | 51 | 0 | 312 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 12 | 320 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 16 | 36 | 393 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 913 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 512 | 0 | 0 | 1012 | 0 | 0 | 0 | 0 | 0 |  | 5429 | 5197 | 10626 | 3655 | 913 | 1608 | 0 | 568 | 2602 | 175 | 0 | 33 | 60 | 1012 | 0 | 0 | 0 | 102.38
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 2 | 0 | 136 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 315 | 0 | 215 | 8 | 50 | 42 | 14 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 18 | 54 | 26 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 58 | 41 | 0 | 209 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 87 | 0 | 51 | 3 | 50 | 51 | 0 | 314 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 12 | 320 | 0 | 6 | 17 | 0 | 0 | 0 | 3 | 17 | 36 | 370 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 10 | 0 | 0 |  | 912 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 9 | 0 | 0 | 0 | 510 | 3 | 0 | 1017 | 14 | 0 | 0 | 6 | 11 |  | 5452 | 5318 | 10770 | 3649 | 912 | 1695 | 0 | 571 | 2598 | 176 | 0 | 33 | 54 | 1017 | 65 | 0 | 85.95 | 102.37
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 22 | 23 | 33 | 8 | 0 | 136 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 315 | 0 | 214 | 8 | 50 | 40 | 5 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 18 | 52 | 25 | 0 | 0 | 1 | 28 | 30 | 0 | 0 | 163 | 0 | 58 | 41 | 0 | 209 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 87 | 0 | 51 | 9 | 50 | 51 | 2 | 313 | 58 | 17 | 0 | 1 | 49 | 19 | 0 | 17 | 19 | 12 | 320 | 0 | 19 | 17 | 1 | 0 | 0 | 11 | 17 | 36 | 350 | 17 | 0 | 611 | 0 | 0 | 0 | 0 | 30 | 0 | 0 |  | 913 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 35 | 1244 | 220 | 0 | 54 | 1 | 32 | 0 | 0 | 0 | 511 | 7 | 0 | 1019 | 37 | 0 | 0 | 20 | 37 |  | 5465 | 5356 | 10821 | 3589 | 913 | 1515 | 0 | 703 | 2599 | 176 | 0 | 49 | 52 | 1019 | 206 | 0 | 94.545 | 102.37
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 22 | 23 | 33 | 17 | 0 | 136 | 40 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 212 | 8 | 51 | 39 | 5 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 18 | 50 | 24 | 0 | 0 | 1 | 28 | 30 | 0 | 0 | 163 | 0 | 58 | 41 | 0 | 206 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 88 | 0 | 51 | 15 | 50 | 51 | 35 | 370 | 58 | 52 | 0 | 3 | 52 | 35 | 0 | 17 | 18 | 12 | 320 | 0 | 31 | 17 | 35 | 0 | 0 | 20 | 30 | 32 | 350 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 49 | 0 | 0 |  | 912 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 35 | 1220 | 220 | 0 | 54 | 3 | 54 | 0 | 0 | 0 | 511 | 17 | 0 | 1012 | 84 | 0 | 0 | 34 | 62 |  | 5702 | 5441 | 11143 | 3622 | 912 | 1509 | 0 | 858 | 2576 | 176 | 0 | 52 | 50 | 1012 | 376 | 0 | 44.885 | 102.37
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 22 | 25 | 33 | 17 | 0 | 136 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 42 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 335 | 0 | 211 | 8 | 50 | 38 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 52 | 10 | 0 | 0 | 2 | 28 | 30 | 0 | 0 | 163 | 0 | 57 | 41 | 0 | 205 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 30 | 0 | 0 | 88 | 0 | 60 | 17 | 50 | 51 | 72 | 387 | 58 | 52 | 0 | 4 | 69 | 35 | 3 | 17 | 19 | 12 | 330 | 0 | 40 | 17 | 35 | 0 | 0 | 26 | 34 | 36 | 350 | 36 | 0 | 612 | 1 | 0 | 0 | 0 | 62 | 0 | 0 |  | 913 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 34 | 0 | 4 | 35 | 1200 | 220 | 0 | 17 | 2 | 48 | 0 | 0 | 0 | 509 | 24 | 0 | 1015 | 131 | 0 | 0 | 46 | 81 |  | 5888 | 5418 | 11306 | 3639 | 913 | 1477 | 0 | 883 | 2553 | 176 | 0 | 110 | 52 | 1015 | 487 | 1 | 42.02 | 102.36
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 25 | 300 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 15 | 22 | 25 | 32 | 17 | 0 | 136 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 42 | 51 | 0 | 0 | 15 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 210 | 8 | 50 | 38 | 5 | 0 | 43 | 0 | 29 | 8 | 0 | 0 | 0 | 18 | 58 | 10 | 0 | 0 | 2 | 28 | 30 | 0 | 0 | 163 | 0 | 57 | 41 | 0 | 205 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 64 | 0 | 0 | 88 | 0 | 70 | 14 | 50 | 51 | 76 | 388 | 58 | 52 | 0 | 4 | 69 | 35 | 17 | 17 | 18 | 12 | 340 | 0 | 45 | 17 | 35 | 0 | 0 | 29 | 34 | 29 | 350 | 36 | 0 | 612 | 2 | 0 | 0 | 0 | 68 | 0 | 0 |  | 912 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 34 | 0 | 6 | 35 | 1200 | 220 | 0 | 17 | 3 | 72 | 0 | 0 | 0 | 510 | 29 | 0 | 1018 | 100 | 0 | 0 | 36 | 93 |  | 6193 | 5465 | 11658 | 3661 | 912 | 1583 | 0 | 993 | 2554 | 176 | 0 | 200 | 58 | 1018 | 501 | 2 | 326.61 | 102.36
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 15 | 22 | 25 | 32 | 17 | 0 | 136 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 44 | 58 | 0 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 209 | 8 | 51 | 38 | 5 | 0 | 43 | 0 | 27 | 8 | 0 | 0 | 0 | 18 | 62 | 10 | 0 | 0 | 2 | 28 | 30 | 0 | 0 | 163 | 0 | 54 | 41 | 0 | 202 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 64 | 0 | 0 | 77 | 0 | 70 | 18 | 50 | 51 | 75 | 387 | 47 | 52 | 0 | 4 | 69 | 35 | 17 | 17 | 18 | 12 | 360 | 0 | 37 | 35 | 35 | 0 | 0 | 30 | 34 | 36 | 360 | 36 | 0 | 612 | 4 | 0 | 0 | 0 | 68 | 0 | 0 |  | 914 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 123 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 9 | 0 | 34 | 0 | 1 | 35 | 1200 | 220 | 0 | 17 | 5 | 70 | 72 | 0 | 0 | 509 | 6 | 0 | 1017 | 110 | 0 | 0 | 39 | 70 |  | 6256 | 5603 | 11859 | 3699 | 914 | 1656 | 0 | 1102 | 2553 | 176 | 0 | 216 | 62 | 1017 | 460 | 4 | 516.655 | 102.35
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 297 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 15 | 22 | 25 | 32 | 17 | 0 | 136 | 40 | 0 | 0 | 4 | 220 | 0 | 0 | 0 |  | 0 | 44 | 66 | 0 | 0 | 19 | 0 | 4 | 0 | 0 | 0 | 315 | 0 | 211 | 8 | 51 | 39 | 5 | 0 | 43 | 0 | 31 | 8 | 0 | 0 | 0 | 18 | 58 | 8 | 0 | 0 | 2 | 28 | 30 | 0 | 0 | 163 | 0 | 54 | 41 | 0 | 204 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 64 | 0 | 0 | 81 | 0 | 68 | 18 | 50 | 51 | 73 | 389 | 47 | 52 | 0 | 4 | 70 | 35 | 17 | 17 | 18 | 12 | 372 | 0 | 42 | 35 | 35 | 0 | 10 | 28 | 34 | 36 | 393 | 36 | 0 | 606 | 7 | 0 | 0 | 0 | 64 | 0 | 0 |  | 914 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 123 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 61 | 0 | 170 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 34 | 0 | 5 | 35 | 1244 | 220 | 0 | 17 | 1 | 80 | 115 | 0 | 0 | 508 | 26 | 0 | 1014 | 118 | 0 | 0 | 33 | 91 |  | 6310 | 5769 | 12079 | 3742 | 914 | 1655 | 0 | 1177 | 2589 | 176 | 0 | 235 | 58 | 1014 | 512 | 7 | 497.555 | 102.35
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 298 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 16 | 22 | 25 | 32 | 17 | 0 | 134 | 40 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 52 | 64 | 0 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 209 | 8 | 50 | 39 | 5 | 0 | 43 | 0 | 37 | 8 | 0 | 0 | 0 | 18 | 68 | 8 | 0 | 0 | 2 | 28 | 30 | 0 | 0 | 163 | 0 | 53 | 11 | 0 | 202 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 64 | 0 | 0 | 77 | 0 | 68 | 14 | 50 | 51 | 73 | 389 | 47 | 52 | 0 | 3 | 70 | 35 | 17 | 34 | 17 | 12 | 372 | 0 | 19 | 35 | 35 | 0 | 17 | 23 | 36 | 36 | 393 | 36 | 0 | 611 | 6 | 0 | 0 | 0 | 51 | 0 | 0 |  | 913 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 130 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 61 | 0 | 170 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 34 | 0 | 4 | 35 | 1244 | 220 | 0 | 17 | 3 | 72 | 115 | 0 | 0 | 508 | 14 | 0 | 1021 | 114 | 0 | 0 | 42 | 76 |  | 6280 | 5764 | 12044 | 3737 | 913 | 1628 | 0 | 1202 | 2594 | 174 | 0 | 264 | 68 | 1021 | 437 | 6 | 559.63 | 102.36
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 298 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 17 | 22 | 25 | 24 | 17 | 0 | 134 | 40 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 0 | 53 | 63 | 0 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 210 | 8 | 50 | 37 | 5 | 0 | 43 | 0 | 36 | 8 | 0 | 0 | 0 | 18 | 68 | 7 | 0 | 0 | 1 | 28 | 30 | 0 | 0 | 163 | 0 | 53 | 11 | 0 | 204 | 0 | 0 | 0 | 305 | 13 | 0 | 0 | 64 | 0 | 0 | 77 | 0 | 67 | 10 | 50 | 51 | 72 | 389 | 47 | 35 | 0 | 2 | 70 | 35 | 17 | 20 | 17 | 12 | 372 | 1 | 22 | 35 | 35 | 0 | 17 | 16 | 50 | 36 | 393 | 17 | 0 | 610 | 10 | 0 | 0 | 0 | 34 | 0 | 0 |  | 913 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 10 | 21 | 0 | 130 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 61 | 0 | 170 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 1230 | 220 | 0 | 17 | 2 | 47 | 115 | 0 | 0 | 511 | 16 | 0 | 1015 | 81 | 0 | 0 | 21 | 53 |  | 6199 | 5634 | 11833 | 3722 | 913 | 1618 | 0 | 1176 | 2582 | 174 | 0 | 247 | 68 | 1015 | 308 | 10 | 799.335 | 102.34
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 298 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 17 | 15 | 25 | 32 | 17 | 0 | 134 | 40 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 6 | 59 | 63 | 0 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 209 | 8 | 50 | 35 | 5 | 0 | 43 | 0 | 36 | 8 | 0 | 0 | 0 | 18 | 68 | 10 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 55 | 11 | 0 | 204 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 64 | 0 | 0 | 77 | 0 | 68 | 5 | 62 | 51 | 80 | 390 | 47 | 35 | 0 | 1 | 52 | 35 | 17 | 40 | 17 | 12 | 372 | 16 | 10 | 35 | 35 | 0 | 17 | 7 | 51 | 36 | 393 | 17 | 0 | 610 | 7 | 0 | 0 | 0 | 18 | 0 | 0 |  | 914 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 15 | 30 | 0 | 123 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 72 | 0 | 34 | 0 | 1 | 35 | 1200 | 220 | 0 | 17 | 1 | 22 | 115 | 0 | 0 | 365 | 7 | 0 | 1008 | 33 | 0 | 0 | 11 | 13 |  | 6211 | 5368 | 11579 | 3718 | 914 | 1621 | 0 | 1258 | 2408 | 174 | 0 | 274 | 68 | 1008 | 129 | 7 | 798.38 | 102.33
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 295 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 17 | 15 | 25 | 30 | 17 | 0 | 134 | 40 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 18 | 61 | 67 | 0 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 213 | 8 | 50 | 38 | 5 | 0 | 43 | 0 | 24 | 8 | 0 | 0 | 0 | 5 | 60 | 10 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 120 | 0 | 58 | 11 | 0 | 202 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 90 | 0 | 0 | 80 | 0 | 74 | 0 | 100 | 59 | 87 | 386 | 48 | 35 | 0 | 0 | 52 | 35 | 17 | 106 | 17 | 0 | 372 | 16 | 0 | 35 | 35 | 0 | 17 | 1 | 51 | 29 | 393 | 17 | 0 | 612 | 8 | 0 | 0 | 0 | 2 | 0 | 0 |  | 913 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 15 | 33 | 0 | 80 | 7 | 16 | 0 | 0 | 0 | 36 | 5 | 77 | 0 | 0 | 21 | 0 | 6 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 113 | 0 | 38 | 0 | 0 | 90 | 1200 | 180 | 0 | 17 | 0 | 3 | 115 | 0 | 0 | 369 | 1 | 0 | 1006 | 6 | 0 | 0 | 1 | 3 |  | 6223 | 5297 | 11520 | 3562 | 913 | 1417 | 0 | 1541 | 2413 | 174 | 0 | 409 | 60 | 1006 | 17 | 8 | 792.65 | 102.33
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 295 | 0 | 0 | 0 | 8 | 106 | 0 | 0 | 0 | 0 | 42 | 35 | 17 | 0 | 16 | 15 | 25 | 30 | 25 | 0 | 134 | 40 | 0 | 0 | 25 | 219 | 0 | 0 | 0 |  | 12 | 63 | 67 | 0 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 212 | 8 | 50 | 39 | 5 | 0 | 43 | 0 | 43 | 34 | 0 | 0 | 0 | 15 | 70 | 10 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 44 | 11 | 0 | 207 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 135 | 0 | 0 | 77 | 0 | 100 | 0 | 100 | 149 | 95 | 386 | 48 | 88 | 10 | 0 | 52 | 35 | 17 | 106 | 18 | 12 | 366 | 7 | 0 | 72 | 35 | 0 | 17 | 0 | 54 | 36 | 393 | 160 | 0 | 612 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 770 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 127 | 10 | 16 | 0 | 0 | 0 | 38 | 5 | 93 | 0 | 0 | 44 | 0 | 15 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 1200 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 610 | 0 | 0 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 6896 | 5799 | 12695 | 3663 | 770 | 1603 | 0 | 2051 | 2655 | 174 | 0 | 688 | 70 | 1016 | 0 | 5 | 960 | 102.31
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 268 | 0 | 0 | 0 | 8 | 148 | 11 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 16 | 22 | 25 | 30 | 25 | 0 | 135 | 40 | 0 | 0 | 25 | 222 | 0 | 0 | 0 |  | 0 | 63 | 84 | 0 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 212 | 8 | 50 | 41 | 5 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 9 | 70 | 10 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 54 | 11 | 0 | 208 | 0 | 0 | 0 | 280 | 8 | 2 | 0 | 212 | 0 | 0 | 77 | 0 | 115 | 0 | 100 | 122 | 117 | 387 | 48 | 88 | 17 | 0 | 52 | 35 | 17 | 106 | 18 | 12 | 366 | 0 | 0 | 90 | 35 | 0 | 17 | 0 | 73 | 36 | 393 | 160 | 0 | 612 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 770 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 27 | 37 | 0 | 127 | 10 | 16 | 0 | 0 | 0 | 45 | 28 | 94 | 0 | 0 | 47 | 0 | 22 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 35 | 0 | 0 | 113 | 1230 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 |  | 7109 | 5929 | 13038 | 3667 | 770 | 1606 | 0 | 2231 | 2695 | 175 | 0 | 798 | 70 | 1021 | 0 | 5 | 823 | 102.28
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 295 | 0 | 0 | 0 | 8 | 147 | 13 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 16 | 22 | 25 | 30 | 34 | 0 | 135 | 40 | 0 | 0 | 25 | 222 | 0 | 0 | 0 |  | 0 | 71 | 84 | 0 | 0 | 19 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 213 | 8 | 50 | 41 | 5 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 18 | 72 | 11 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 54 | 11 | 0 | 208 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 250 | 0 | 0 | 77 | 0 | 130 | 0 | 100 | 34 | 115 | 387 | 48 | 88 | 17 | 0 | 52 | 35 | 17 | 106 | 18 | 12 | 370 | 0 | 0 | 90 | 35 | 0 | 28 | 0 | 74 | 36 | 395 | 160 | 0 | 612 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 774 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 25 | 51 | 0 | 127 | 10 | 48 | 0 | 0 | 0 | 45 | 26 | 94 | 0 | 0 | 47 | 0 | 22 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 113 | 0 | 60 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 0 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 7192 | 5984 | 13176 | 3726 | 774 | 1592 | 0 | 2292 | 2709 | 175 | 0 | 815 | 72 | 1016 | 0 | 5 | 787 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 295 | 0 | 0 | 0 | 8 | 147 | 13 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 16 | 22 | 25 | 30 | 34 | 0 | 135 | 40 | 0 | 0 | 25 | 222 | 0 | 0 | 0 |  | 0 | 71 | 84 | 0 | 0 | 19 | 0 | 14 | 0 | 0 | 0 | 310 | 0 | 213 | 8 | 50 | 41 | 5 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 18 | 72 | 11 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 55 | 11 | 0 | 206 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 258 | 0 | 0 | 78 | 0 | 131 | 0 | 100 | 34 | 115 | 387 | 48 | 88 | 17 | 0 | 52 | 35 | 17 | 106 | 18 | 12 | 370 | 0 | 0 | 90 | 35 | 0 | 32 | 0 | 74 | 36 | 393 | 160 | 0 | 612 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 774 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 27 | 44 | 0 | 127 | 10 | 48 | 0 | 0 | 0 | 47 | 28 | 94 | 0 | 0 | 46 | 0 | 22 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 113 | 0 | 70 | 0 | 0 | 38 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 0 | 1017 | 0 | 0 | 0 | 0 | 0 |  | 7194 | 5918 | 13112 | 3716 | 774 | 1593 | 0 | 2241 | 2709 | 175 | 0 | 813 | 72 | 1017 | 0 | 2 | 753 | 102.29
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 288 | 0 | 0 | 0 | 0 | 147 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 17 | 22 | 25 | 32 | 34 | 0 | 136 | 40 | 0 | 0 | 25 | 222 | 0 | 0 | 0 |  | 0 | 71 | 82 | 0 | 0 | 19 | 0 | 16 | 0 | 0 | 0 | 300 | 0 | 213 | 8 | 50 | 41 | 5 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 18 | 72 | 15 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 55 | 11 | 0 | 207 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 266 | 0 | 0 | 76 | 0 | 131 | 0 | 100 | 34 | 102 | 387 | 48 | 88 | 17 | 0 | 52 | 35 | 17 | 106 | 18 | 12 | 366 | 0 | 0 | 72 | 35 | 0 | 35 | 0 | 74 | 36 | 370 | 0 | 0 | 613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 918 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 26 | 40 | 0 | 127 | 10 | 48 | 0 | 0 | 0 | 46 | 22 | 94 | 0 | 0 | 39 | 0 | 22 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 113 | 0 | 70 | 0 | 0 | 38 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 624 | 0 | 0 | 1019 | 0 | 0 | 0 | 0 | 0 |  | 6935 | 6055 | 12990 | 3677 | 918 | 1610 | 0 | 2173 | 2713 | 176 | 0 | 632 | 72 | 1019 | 0 | 0 | 744.9 | 102.28
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 288 | 0 | 0 | 0 | 0 | 147 | 13 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 22 | 25 | 33 | 34 | 0 | 136 | 40 | 0 | 0 | 25 | 222 | 0 | 0 | 0 |  | 0 | 71 | 82 | 0 | 0 | 19 | 0 | 23 | 0 | 0 | 0 | 330 | 0 | 210 | 8 | 50 | 42 | 5 | 0 | 43 | 0 | 43 | 8 | 0 | 0 | 0 | 18 | 74 | 15 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 55 | 11 | 0 | 206 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 228 | 0 | 0 | 77 | 0 | 113 | 0 | 100 | 34 | 100 | 387 | 48 | 88 | 17 | 0 | 52 | 35 | 17 | 106 | 18 | 12 | 366 | 0 | 0 | 35 | 35 | 0 | 35 | 0 | 74 | 36 | 370 | 0 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 917 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 26 | 40 | 0 | 127 | 10 | 48 | 0 | 0 | 0 | 42 | 22 | 94 | 0 | 0 | 39 | 0 | 22 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 70 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 0 | 1020 | 0 | 0 | 0 | 0 | 0 |  | 6781 | 6065 | 12846 | 3704 | 917 | 1637 | 0 | 1979 | 2711 | 176 | 0 | 628 | 74 | 1020 | 0 | 0 | 739.17 | 102.27
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 288 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 25 | 33 | 17 | 0 | 134 | 40 | 0 | 0 | 23 | 227 | 0 | 0 | 0 |  | 0 | 71 | 83 | 0 | 0 | 19 | 0 | 27 | 0 | 0 | 0 | 290 | 0 | 212 | 8 | 50 | 40 | 5 | 0 | 43 | 0 | 44 | 8 | 0 | 0 | 0 | 18 | 74 | 17 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 56 | 11 | 0 | 206 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 196 | 0 | 0 | 77 | 0 | 94 | 0 | 50 | 34 | 104 | 385 | 47 | 35 | 17 | 0 | 52 | 35 | 17 | 106 | 19 | 12 | 366 | 5 | 0 | 17 | 35 | 0 | 35 | 0 | 66 | 36 | 370 | 17 | 0 | 613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 918 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 26 | 40 | 0 | 127 | 10 | 16 | 0 | 0 | 0 | 47 | 22 | 94 | 0 | 0 | 39 | 0 | 22 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 113 | 0 | 70 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 0 | 1017 | 0 | 0 | 0 | 0 | 0 |  | 6505 | 6022 | 12527 | 3671 | 918 | 1623 | 0 | 1687 | 2711 | 174 | 0 | 652 | 74 | 1017 | 0 | 0 | 929.215 | 102.26
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 285 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 22 | 25 | 33 | 8 | 0 | 133 | 40 | 0 | 0 | 8 | 228 | 0 | 0 | 0 |  | 0 | 70 | 83 | 0 | 0 | 19 | 0 | 28 | 0 | 0 | 0 | 320 | 0 | 213 | 8 | 50 | 39 | 5 | 0 | 43 | 0 | 44 | 8 | 0 | 0 | 0 | 18 | 74 | 17 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 55 | 11 | 0 | 205 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 198 | 0 | 0 | 67 | 0 | 91 | 0 | 50 | 23 | 105 | 387 | 48 | 17 | 0 | 0 | 52 | 35 | 17 | 106 | 17 | 12 | 366 | 16 | 0 | 17 | 35 | 0 | 35 | 0 | 35 | 36 | 370 | 17 | 0 | 616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 922 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 26 | 40 | 0 | 127 | 10 | 16 | 0 | 0 | 0 | 47 | 18 | 94 | 0 | 0 | 32 | 0 | 22 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 364 | 0 | 0 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 6390 | 5735 | 12125 | 3702 | 922 | 1657 | 0 | 1550 | 2457 | 173 | 0 | 574 | 74 | 1016 | 0 | 0 | 1122.125 | 102.25
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9648000 | 0 |  | 0 | 10434300 | 0 | 0 | 0 | 671384 | 7261312 | 0 | 0 | 0 | 35136 | 1500480 | 43000 | 0 | 0 | 0 | 259200 | 272074 | 275365 | 0 | 454200 | 511920 | 616300 | 762500 | 324960 | 0 | 3244315 | 972000 | 0 | 0 | 216966 | 5180697 | 0 | 0 | 0 |  | 36720 | 1074576 | 1139909 | 0 | 0 | 334560 | 0 | 409440 | 0 | 0 | 0 | 7943500 | 0 | 5119000 | 217455 | 1190770 | 951264 | 247200 | 0 | 925432 | 0 | 630624 | 742310 | 0 | 0 | 0 | 408050 | 1530240 | 399360 | 0 | 0 | 11350 | 670000 | 699720 | 0 | 0 | 3731645 | 0 | 1313952 | 669120 | 0 | 5146190 | 0 | 0 | 0 | 7233500 | 311328 | 58000 | 0 | 2559273 | 0 | 0 | 1975200 | 0 | 1830240 | 120285 | 1523520 | 1327200 | 1719563 | 9252000 | 1256400 | 1054080 | 88655 | 24480 | 1249527 | 821067 | 319490 | 1145700 | 437640 | 288000 | 8310200 | 85440 | 268310 | 799200 | 765273 | 0 | 328680 | 194401 | 971520 | 848160 | 9205000 | 834691 | 0 | 14699998 | 56640 | 0 | 0 | 0 | 456445 | 0 | 0 |  | 21621600 | 0 | 7104096 | 0 | 0 | 0 | 0 | 0 | 284640 | 565760 | 0 | 3061000 | 196049 | 413952 | 0 | 0 | 0 | 443284 | 161865 | 736864 | 0 | 0 | 326615 | 0 | 181108 | 0 | 0 | 195948 | 1505454 | 0 | 4171000 | 0 | 0 | 4031273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9166545 | 0 | 0 | 1499424 | 0 | 966076 | 0 | 33097 | 1205376 | 31409400 | 5354000 | 0 | 2041200 | 24240 | 523440 | 1916160 | 0 | 0 | 12625450 | 160468 | 0 | 24432574 | 848160 | 0 | 3659 | 277504 | 630700 |  | 150645602 | 138117981 | 288763583 | 89805580 | 21621600 | 38584686 | 0 | 32647691 | 64411302 | 4216315 | 0 | 7880416 | 1530240 | 24432574 | 3576539 | 56640 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27786240 | 0 |  | 0 | 33181074 | 0 | 0 | 0 | 11829786.08 | 22147001.6 | 0 | 0 | 0 | 630691.2 | 29139321.6 | 801950 | 0 | 0 | 0 | 4732992 | 4287886.24 | 5036425.85 | 0 | 340650 | 0 | 0 | 0 | 5820033.6 | 0 | 0 | 0 | 0 | 0 | 4109336.04 | 16526423.43 | 0 | 0 | 0 |  | 645904.8 | 18923283.36 | 20415770.19 | 0 | 0 | 5506857.6 | 0 | 0 | 0 | 0 | 0 | 22162365 | 0 | 16995080 | 728474.25 | 3846187.1 | 3205759.68 | 1082736 | 0 | 3710982.32 | 0 | 11294475.84 | 13406118.6 | 0 | 0 | 0 | 306037.5 | 10038374.4 | 1242009.6 | 0 | 0 | 0 | 2613000 | 2609955.6 | 0 | 0 | 12762225.9 | 0 | 7292433.6 | 3492806.4 | 0 | 14357870.1 | 0 | 0 | 0 | 22351515 | 233496 | 44080 | 0 | 52209169.2 | 0 | 0 | 37943592 | 0 | 32230526.4 | 0 | 27133891.2 | 23026920 | 28510354.54 | 24517800 | 23946984 | 19774540.8 | 1590470.7 | 0 | 20429766.45 | 15961542.48 | 5731650.6 | 21894327 | 8494592.4 | 5129280 | 22105132 | 1458460.8 | 0 | 14617368 | 12841280.94 | 0 | 5873511.6 | 0 | 17506790.4 | 14367830.4 | 27338850 | 11752449.28 | 0 | 102458986.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60756696 | 0 | 20957083.2 | 0 | 0 | 0 | 0 | 0 | 5354078.4 | 10641945.6 | 0 | 9672760 | 929272.26 | 7136532.48 | 0 | 0 | 0 | 7939216.44 | 2970222.75 | 12386683.84 | 0 | 0 | 5849674.65 | 0 | 3243644.28 | 0 | 0 | 148332.636 | 16605157.62 | 0 | 35203240 | 0 | 0 | 13303200.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26766311.4 | 0 | 0 | 29718583.68 | 0 | 19244233.92 | 0 | 0 | 23914659.84 | 203532912 | 16650940 | 0 | 39497220 | 0 | 0 | 33245376 | 0 | 0 | 92165785 | 0 | 0 | 161499314.14 | 0 | 0 | 0 | 0 | 0 |  | 944483677.73 | 859333077.036 | 1803816754.766 | 259751747.946 | 60756696 | 121656337.53 | 0 | 600237437.84 | 449966080.68 | 0 | 0 | 139910766.23 | 10038374.4 | 161499314.14 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 15 | 22 | 25 | 32 | 17 | 0 | 136 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 44 | 58 | 0 | 0 | 19 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 209 | 8 | 51 | 38 | 5 | 0 | 43 | 0 | 27 | 8 | 0 | 0 | 0 | 18 | 62 | 10 | 0 | 0 | 2 | 28 | 30 | 0 | 0 | 163 | 0 | 54 | 41 | 0 | 202 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 64 | 0 | 0 | 77 | 0 | 70 | 18 | 50 | 51 | 75 | 387 | 47 | 52 | 0 | 4 | 69 | 35 | 17 | 17 | 18 | 12 | 360 | 0 | 37 | 35 | 35 | 0 | 0 | 30 | 34 | 36 | 360 | 36 | 0 | 612 | 4 | 0 | 0 | 0 | 68 | 0 | 0 |  | 914 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 123 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 9 | 0 | 34 | 0 | 1 | 35 | 1200 | 220 | 0 | 17 | 5 | 70 | 72 | 0 | 0 | 509 | 6 | 0 | 1017 | 110 | 0 | 0 | 39 | 70 |  | 11859 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 295 | 0 | 0 | 0 | 8 | 147 | 13 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 16 | 22 | 25 | 30 | 34 | 0 | 135 | 40 | 0 | 0 | 25 | 222 | 0 | 0 | 0 | 0 | 0 | 71 | 84 | 0 | 0 | 19 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 213 | 8 | 50 | 41 | 5 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 18 | 72 | 11 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 54 | 11 | 0 | 208 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 250 | 0 | 0 | 77 | 0 | 130 | 0 | 100 | 34 | 115 | 387 | 48 | 88 | 17 | 0 | 52 | 35 | 17 | 106 | 18 | 12 | 370 | 0 | 0 | 90 | 35 | 0 | 28 | 0 | 74 | 36 | 395 | 160 | 0 | 612 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 774 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 25 | 51 | 0 | 127 | 10 | 48 | 0 | 0 | 0 | 45 | 26 | 94 | 0 | 0 | 47 | 0 | 22 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 113 | 0 | 60 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 0 | 1016 | 0 | 0 | 0 | 0 | 0 |  | 13176 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 149 | 13 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 21 | 23 | 23 | 33 | 25 | 0 | 135 | 40 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 24 | 72 | 85 | 0 | 0 | 19 | 0 | 10 | 0 | 0 |  | 320 | 0 | 215 | 8 | 50 | 43 | 5 | 0 | 43 | 0 | 43 | 52 | 0 | 0 |  | 18 | 86 | 20 | 0 | 0 | 0 | 28 | 30 | 0 | 0 | 163 | 0 | 60 | 86 | 0 | 210 | 0 | 0 | 0 | 320 | 20 | 5 | 0 | 300 | 0 | 0 | 68 | 0 | 132 | 0 | 100 | 34 | 115 | 385 | 57 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 17 | 12 | 380 | 0 | 0 | 90 | 35 | 0 | 35 | 0 | 75 | 36 | 350 | 160 | 0 | 612 | 10 | 0 | 0 | 0 |  |  |  |  | 939 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 132 | 10 | 16 | 0 | 0 | 0 | 45 | 24 | 95 | 0 | 0 | 46 | 0 | 30 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 34 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 0 | 1000 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 0 | 64 | 13 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 21 | 23 | 23 | 33 | 16 | 0 | 135 | 40 | 0 | 0 | 25 | 225 |  | 0 | 0 | 0 | 0 | 56 | 51 | 0 | 0 | 19 | 0 | 5 | 0 | 0 | 0 | 320 | 0 | 215 | 8 | 50 | 43 | 5 | 0 | 43 | 0 | 30 | 25 | 0 | 0 |  | 18 | 66 | 10 | 0 | 0 | 1.6 | 28 | 30 | 0 | 0 | 163 | 0 | 60 | 10 | 0 | 210 | 0 | 0 | 0 | 315 | 20 | 5 | 0 | 45 | 0 | 0 | 68 | 0 | 72 | 20 | 50 | 17 | 100 | 385 | 57 | 52 | 17 | 5 | 52 | 17 | 17 | 17 | 17 | 12 | 380 | 17 | 50 | 35 | 35 | 0 | 0 | 35 | 35 | 36 | 350 | 35 | 0 | 612 | 5 | 0 | 0 | 0 | 70 |  |  |  | 939 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 132 | 10 | 16 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 28 | 0 | 22 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 34 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 115 | 0 | 0 | 360 | 30 | 0 | 1000 | 170 | 0 |  | 29 | 47 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 270 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 22 | 25 | 32 | 8 | 0 | 136 | 40 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 48 | 68 | 0 | 0 | 19 | 0 | 8 | 0 | 0 | 0 | 285 | 0 | 215 | 8 | 50 | 42 | 20 | 0 | 43 | 0 | 43 | 25 | 0 | 0 | 0 | 18 | 52 | 25 | 0 | 0 | 1 | 0 | 30 | 0 | 0 | 163 | 0 | 40 | 11 | 0 | 209 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 45 | 0 | 0 | 57 | 0 | 52 | 10 | 50 | 17 | 72 | 312 | 48 | 17 | 0 | 2 | 52 | 35 | 17 | 52 | 20 | 12 | 366 | 0 | 15 | 17 | 35 | 0 | 0 | 11 | 18 | 17 | 350 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 922 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 113 | 0 | 34 | 0 | 1 | 35 | 1244 | 220 | 0 | 17 | 1 | 33 | 115 | 0 | 0 | 368 | 9 | 0 | 1017 | 56 | 0 | 0 | 20 | 37 | 0 |  |  |  | 128390266 | 21621600 | 0 | 64411302 | 40528107 | 1530240 | 3576539 | 56640 | 4216315 |  |  |  | 264331009
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 128.3903 | 21.6216 | 0 | 64.4113 | 40.5281 | 1.5302 | 3.5765 | 0.05664 | 4.2163
| Minimum Generation |  | 10626 | 6:00
| Highest Generation |  | 13176 | 19:30 | [129 empty] | 0 | [76 empty] | 264.331
| Day Peak Generation |  | 11859 | 12:00
| Evening Peak Generation |  | 13176 | 19:30 | [206 empty] | 202699852
| HVDC Max Flow |  | 922 | 24:00 | [206 empty] | 202.6999
| HVDC EvPeak Flow |  | 774 | 19:30
| Load factor L.F |  | 91.32% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-10-30
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-10-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11859 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 10925
Evening Peak Generation : |  |  | 13176 | MW Hour : | 19:30 | Available Max Generation : |  | 13623
E.P. Demand (at gen end) : |  |  | 14000 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 13176 | MW Hour : | 19:30 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 288.7636 | System Load Factor : | 91.32% | Load Shed : |  | 357
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1094 | MW at | 18:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-10-30
Actual : |  | 102.19 | Ft.(MSL) , | Rule curve : | 108.7 | Ft.( MSL )
Gas Consumed : |  | Total = | 908.07 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 381408085.476 | Adani : | 161499314.14
|  |  | Coal : | 449966080.68 | Oil: | 740148204.07 | Total: | 1733021684.366
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 170 | 4080:00 | 4695.4665 |  |  | 37 | 0.7946%
Chittagong Area |  | 30 | 720:00 | 1291.088 |  |  | 38 | 2.961%
Khulna Area |  | 120 | 2880:00 | 1808.7915 |  |  | 62 | 3.425%
Rajshahi Area |  | 50 | 1200:00 | 1572.379 |  |  | 62 | 3.916%
Cumilla Area |  | 125 | 3000:00 | 1293.6804 |  |  | 47 | 3.611%
Mymensingh Area |  | 130 | 3120:00 | 962.2882 |  |  | 39 | 4.038%
Sylhet Area |  | 60 | 1440:00 | 539.2681 |  |  | 17 | 3.223%
Barisal Area |  | 42 | 1008:00 | 449.5289 |  |  | 19 | 4.116%
Rangpur Area |  | 60 | 1440:00 | 879.1971 |  |  | 36 | 4.105%
Total |  | 787 |  | 13491.6877 |  |  | 357
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
8:17 | 17:40 | Chattak-Sylhet 132 kV Ckt-1 Scheduled S/D from Chhatak 132/33kV end Due to Annual Maintenance of
Sylhet -chhatak Ckt-1. and from Sylhet 132/33kV end Due to Yearly Maintenance
- | 8:19 | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT is restored.
8:20 | 15:07 | Bogura 230/132kV S/S T-03 HT Scheduled S/D Due to Annual Maintenance
8:20 | 16:18 | Lalmonirhat 132/33kV S/S Transformer T-2 415T HT Scheduled S/D Due to T2 x former S/D for annual maintenance.
- | 8:20 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT is restored.
8:20 | 15:07 | Bogura 230/132kV S/S T-03 LT Scheduled S/D Due to Annual Maintenance
- | 8:21 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT is restored.
- | 8:22 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT is restored.
8:23 | 14:40 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to 33kV Busbar maintenance work at Transformer -2 side. |  |  |  |  | 45.0MW load interrup.
work done by PBS.
8:23 | 14:47 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33kV Busbar maintenance work at Transformer -2 side , |  |  |  |  | 45.0MW load interrup.
work will be executed by PBS.
8:25 | 15:22 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Annual Maintenance
8:26 | 15:20 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Annual Maintenance
8:35 | 16:52 | Ashuganj-Shahjibazar 132kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to Shoutdown taken
by Ashugonj s/s
8:37 | 16:26 | Barishal 230/132kV S/S ATR-2 LT Scheduled S/D Due to Annual maintenance
8:38 | 16:28 | Barishal 230/132kV S/S ATR-2 HT Scheduled S/D Due to Annual maintenance
8:53 | 16:16 | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to Annual Maintenance
9:08 | 15:42 | Fenchuganj-Fenchuganj 132 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Annual maintenance
9:13 | 17:30 | Mymensingh-Netrokona 132kV Ckt-2 Scheduled S/D from Netrakona 132/33kV end Due to A/M
9:20 | 16:12 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Scheduled S/D Due to Annual Maintenance
9:20 | 16:11 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Scheduled S/D Due to Annual Maintenance
9:24 | 15:00 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Conductor armaring
work between tower number 65-66
9:26 | 12:58 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end. and from Gopalganj 400/132kVend.
9:31 | 13:29 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to S/D From Aminbazar
End and from Aminbazar 400/230/132kV end Due to Annual Maintenance
10:24 | 15:19 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to According to NLDC
10:35 | 15:10 | Hasnabad 132/33kV S/S Keraniganj-2 (Pre- Aourahati) Scheduled S/D Due to Hydraulic oil cable of Circuit
Breaker replacement.
- | 12:49 | Niamatpur 132/33kV S/S Main Bus is restored.
13:00 | 13:40 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end. and from Gopalganj 400/132kVend.
14:08 | 15:31 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Project Work S/D from Gopalganj 400/132kV end. and from
Faridpur 132/33kV end Due to Instruction by ALDC for SCADA work.
- | 14:52 | Sholosohor 132/33kV S/S TRAFO-01 HT is restored.
- | 14:52 | Sholosohor 132/33kV S/S TRAFO-01 LT is restored.
15:46 | 17:11 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Project Work S/D from Faridpur 132/33kV end Due to Instruction by ALDC
for SCADA work.
15:47 | 17:10 | Gopalganj 400/132kV S/S 230kV Faridpur CKT-02 Scheduled S/D
16:06 | 6:16 | Narshingdi 132/33kV S/S 132 kV Main Bus-2 Project Work S/D Due to Jumper Connection for T-4 Transformer
Installation.
- | 17:11 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT is restored.
- | 17:12 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT is restored.
19:30 | - | Evening peak Generation is 13176 MW
20:20 | 23:54 | BIPTC S/S Baharampur-2 Forced S/D Due to Shutdown is taken from Baharampur end
6:28 | - | Narshingdi 132/33kV S/S 132 kV Main Bus-1 Project Work S/D Due to Transformer-4 isstallation works.
7:31 | - | Agargaon-Bhasantek 132kV Ckt-1 Scheduled S/D from Cantonment 132/33kV end Due to Agargaon -Cantonment
Ckt-1 S/d for Annual Maintenance Agargaon end . and from Agargaon 230/132kV end Due to Annual Maintenance.
7:50 | - | Savar 132/33kV S/S Bus-B Scheduled S/D Due to Hot spot maintenance of L-39, L-42 & Bus Coupler B bus
DS by Dhaka pbs-3

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-10-29
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 415 | 9648000
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10434300
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 671384
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 43000 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 295 | 7261312 | DP High
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 35136 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 259200 | Fuel shortage
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 147 | 1500480
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 272074
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 275365 | Fuel shortage
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 966120 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 616300 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 762500
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 34 | 324960 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 250 | 2559273 | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 130 | 1830240 | Engine problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1054080 | Engine problem
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 85440 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 799200 | Fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 194401
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 848160 | Fuel shortage
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 2229 | 40440925
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 216966
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 120285
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 334560 | Fuel shortage
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 175 | 4216315
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5180697
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 88655 | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 71 | 1074576 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 1139909 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1523520
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 409440
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24480
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1249527 | Fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 821067 | Fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 319490 | Fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 288000 | Fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 765273 | Fuel shortage
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 160 | 834691
55 | SS Power I |  | IPP | 2*612 | 1224 | 612 | 14699998 | Coal shortage
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 5 | 56640
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 0 | 0 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1651 | 33364089
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 5119000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7943500
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 395 | 9205000
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 951264 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 5 | 247200 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217455 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 925432 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 115 | 1719563 | Fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 630624 | Engine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1190770 | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 1327200 | Fuel shortage
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 72 | 1530240
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 742310
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 408050 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1145700 | Engine problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 18 | 437640 | Fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 74 | 971520 | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 456445
| Cumilla Area Total |  |  |  | 2917 | 1597 | 35168913
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 11 | 399360 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11350
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 77 | 1975200 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 48 | 1256400 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 268310
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 36720 | Fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 28 | 328680 | Fuel shortage
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 646 | 164 | 4276020
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 28 | 670000 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 699720 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3731645
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 58000 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 54 | 1313952 | Gas shortage
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 11 | 669120 | Gas shortage
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 208 | 5146190 | Machine problem.
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 311328 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7233500 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 387 | 9252000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 370 | 8310200
| Sylhet Area Total |  |  |  | 2417 | 1551 | 37395655
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 774 | 21621600
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 284640 | Engine problem
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 51 | 565760 | Engine problem
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 273 | 7104096 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 523440
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 621 | 12625450 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1744 | 42724986
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 413952 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 196049 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 127 | 3061000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 31409400
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5354000
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 2041200
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Under maint.
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3659
| Barisal Area Total |  |  |  | 2236 | 1799 | 42479260
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 45 | 443284 | Engine problem
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 26 | 161865 | Machine problem.
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 47 | 326615
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 163 | 4031273 | Gas shortage
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 387 | 9166545 | FGMO
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 181108 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 195948 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 736864 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1499424
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1205376
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 24240
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1016 | 24432574
135 | Sirajganj 68 MW Solar Park |  | NWPGCL | 68 | 68 | 0 | 277504
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 630700
| Rajshahi Area Total |  |  |  | 3449 | 2034 | 43313320
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 62 | 1505454
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4171000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 60 | 966076 | Fuel shortage
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33097
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1916160
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 160468
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 848160
| Rangpur Area Total |  |  |  | 950 | 407 | 9600415
| Total |  |  |  | 27086 | 13176 | 288763583
| Eastern Grid Total |  |  |  | 16752 | 7192 | 150645602
| Western Grid Total |  |  |  | 10334 | 5984 | 138117981
| National Grid Total |  |  |  | 27086 | 13176 | 288763583
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-10-29
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8823.32 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3759.6 | MW
i) Dhaka area |  |  | 5029.82 |  | MW | i) Khulna area |  |  |  | 1462.8 | MW
ii) Chattogram area |  |  | 1198.5 |  | MW | ii) Barishal area |  |  |  | 390 | MW
iii) Cumilla area |  |  | 1154 |  | MW | iii) Rajshahi area |  |  |  | 1191.8 | MW
iv) Mymensingh area |  |  | 927 |  | MW | iv) Rangpur area |  |  |  | 715 | MW
v) Sylhet area |  |  | 514 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12582.92 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 2 | 00:00 | 67 | Jashore | 122 | 20:00 | 133 | Rajbari | 68 | 18:00
2 | AKSML | 129 | 08:00 | 68 | Jhenaidah | 112 | 20:00 | 134 | Rajendrapur | 98 | 20:00
3 | Aftabnagar | 58 | 13:00 | 69 | Joydebpur | 188 | 20:00 | 135 | Rajshahi | 110 | 21:00
4 | Agargaon | 116 | 13:00 | 70 | Joypurhat | 48 | 00:00 | 136 | Rajshahi-230 | 74 | 13:00
5 | Agrabad | 104 | 19:30 | 71 | Juldah | 16 | 09:00 | 137 | Ramganj | 92 | 05:00
6 | Amnura | 48 | 18:00 | 72 | KSRM | 26 | 11:00 | 138 | Rampur | 43 | 00:00
7 | Ashuganj | 89 | 02:00 | 73 | Kabirpur | 265 | 09:00 | 139 | Rangamati | 16 | 18:00
8 | BSRM | 9 | 02:00 | 74 | Kachua | 76 | 22:00 | 140 | Rangpur | 117 | 13:00
9 | Bagerhat | 74 | 00:00 | 75 | Kallyanpur | 108 | 19:00 | 141 | Ruppur | 7 | 16:00
10 | Bakulia | 98 | 18:00 | 76 | Kalurghat | 38 | 10:00 | 142 | SSM | 9 | 00:00
11 | Banani | 70 | 13:00 | 77 | Kamrangirchar | 66.4 | 18:30 | 143 | Saidpur | 85 | 14:00
12 | Bangabhaban | 22 | 10:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 114 | 18:00
13 | Barapukuria | 51 | 20:00 | 79 | Kazla | 115 | 12:00 | 145 | Satmasjid | 97 | 19:30
14 | Barguna | 18 | 00:00 | 80 | Keranigonj | 80 | 18:30 | 146 | Savar | 200 | 21:00
15 | Barishal | 103 | 13:00 | 81 | Khagrachori | 30 | 18:00 | 147 | SevenRings | 12.38 | 14:00
16 | Barishal-230 | 78 | 00:00 | 82 | Khulna | 84 | 13:00 | 148 | ShahCement | 30 | 00:00
17 | Baroaulia | 70 | 10:00 | 83 | Khulshi | 159 | 20:00 | 149 | Shahjadpur | 86 | 19:00
18 | Baroirhat | 69 | 19:30 | 84 | Kishoreganj | 130 | 01:00 | 150 | Shahjibazar | 123 | 00:00
19 | Bashundhara | 181 | 18:00 | 85 | Kodda | 279 | 22:00 | 151 | Shahmirpur | 56 | 00:00
20 | BashundharaCement | 11 | 01:00 | 86 | Kulaura | 44 | 21:00 | 152 | Shariatpur | 71 | 22:00
21 | Beanibazar | 62 | 21:00 | 87 | Kurigram | 44 | 19:30 | 153 | Sherpur | 108 | 19:30
22 | Benapole | 56 | 21:00 | 88 | Kushtia | 132 | 18:30 | 154 | Shikalbaha | 28 | 01:00
23 | Bhaluka | 124 | 09:00 | 89 | Lalbag | 87 | 13:00 | 155 | Shitalakhya | 80.7 | 16:00
24 | Bhandaria | 46 | 00:00 | 90 | Lalmonirhat | 45 | 18:00 | 156 | Sholosohor | 45 | 11:00
25 | Bhangura | 35 | 18:00 | 91 | MI_Cement | 11 | 03:00 | 157 | Shyampur | 178 | 11:00
26 | Bheramara(GK) | 55 | 20:00 | 92 | Madanganj | 38 | 00:00 | 158 | Siddhirganj | 123 | 12:00
27 | Bhulta | 255 | 00:00 | 93 | Madaripur | 94 | 21:00 | 159 | Sirajganj | 92 | 19:00
28 | Bog-Sherpur | 54 | 00:00 | 94 | Madartek | 79.5 | 23:00 | 160 | Sonargaon | 85 | 19:00
29 | Bogura | 137 | 00:00 | 95 | Madunaghat | 60 | 18:30 | 161 | Sreemongol | 63 | 00:00
30 | Borhanuddin | 76 | 00:00 | 96 | Magura | 51 | 21:00 | 162 | Sreepur | 69 | 09:00
31 | Brahmanbaria | 160 | 01:00 | 97 | Mahasthangarh | 64 | 18:30 | 163 | Srinagar | 44.72 | 19:00
32 | Cantonment | 114 | 18:00 | 98 | Manikganj | 113 | 20:00 | 164 | Sunamganj | 50 | 00:00
33 | Chandpur | 60 | 20:00 | 99 | Maniknagar | 70 | 13:00 | 165 | Sylhet | 44 | 18:30
34 | Chandraghona | 31 | 21:00 | 100 | Matarbari | 45 | 00:00 | 166 | Sylhet-132 | 118 | 12:00
35 | Chapai | 49 | 18:00 | 101 | Matuail | 70 | 16:00 | 167 | TK | 31.5 | 23:00
36 | Charsaidpur | 33 | 13:00 | 102 | Millgate | 128 | 12:00 | 168 | Tangail | 166 | 18:30
37 | Chauddagram | 64 | 19:30 | 103 | Mirpur | 145 | 18:00 | 169 | Thakurgaon | 78 | 18:30
38 | Chhatak | 29 | 00:00 | 104 | Mirsorai | 6 | 18:00 | 170 | Tongi | 142 | 10:00
39 | Chowmuhani | 223 | 18:30 | 105 | Mirzapur | 34 | 21:00 | 171 | Ullahpara | 42 | 18:00
40 | Chuadanga | 94 | 21:00 | 106 | Mithapukur | 40 | 18:00 | 172 | Ullon | 51 | 18:00
41 | Coxsbazar | 112 | 20:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 86 | 12:00
42 | Cumilla(N) | 155 | 00:00 | 108 | Mogbazar | 123.4 | 15:00 | 174 | UttaraNew | 52 | 12:00
43 | Cumilla(S) | 154 | 18:00 | 109 | Mongla | 38 | 00:00 | 175 | Zigatola | 86 | 18:00
44 | Daudkandi | 140 | 00:00 | 110 | Motijheel | 46 | 14:00
45 | Dhaka | 42 | 13:00 | 111 | Munshiganj | 101 | 20:00
46 | Dhamrai | 124 | 21:00 | 112 | Mymensingh | 226 | 20:00
47 | Dhanmondi | 125 | 13:00 | 113 | Naogaon | 96 | 00:00
48 | Dohazari | 101 | 20:00 | 114 | Narail | 46 | 00:00
49 | Faridpur | 135 | 00:00 | 115 | Narinda | 66 | 16:00
50 | Fatullah | 91 | 15:00 | 116 | Narshingdi | 164 | 00:00
51 | Fenchuganj | 38 | 18:00 | 117 | Natore | 127 | 22:00
52 | Feni | 96 | 20:00 | 118 | Nawabganj | 48.4 | 18:30
53 | GPH | 52 | 11:00 | 119 | Netrakona | 95 | 20:00
54 | Ghatail | 46 | 06:00 | 120 | New | 55.8 | 12:00
55 | Ghorashal | 53 | 21:00 | 121 | Niamatpur | 53 | 20:00
56 | Goalpara | 28 | 18:00 | 122 | Noapara | 39 | 18:30
57 | Gollamari | 74 | 00:00 | 123 | PHP | 4 | 18:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-10-29 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 381 | 02:00 | 369 | 10:00 | Kaliakoir | 368 | 02:00 | 354 | 10:00
| Ashuganj | 406 | 7:00 | 389 | 10:00 | Madunaghat | 399 | 02:00 | 387 | 00:00
| Bhulta | 395 | 20:00 | 381 | 10:00 | Meghnaghat | 378 | 20:00 | 366 | 10:00
| Bibiana | 391 | 02:00 | 382 | 10:00 | Payra | 407 | 18:00 | 401 | 13:00
| BIPTC | 400 | 19:30 | 390 | 23:00 | Rahanpur | 398 | 17:00 | 393 | 11:00
| Bogura | 385 | 17:00 | 379 | 11:00 | Rampal | 398 | 08:00 | 388 | 12:00
| Gopalganj | 393 | 06:00 | 383 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 227 | 02:00 | 216 | 10:00 | Haripur | 227 | 19:30 | 219 | 12:00
| AKSML | 234 | 18:00 | 227 | 08:00 | Hasnabad | 227 | 18:00 | 216 | 10:00
| Aminbazar | 227 | 05:00 | 212 | 14:00 | Hathazari | 237 | 19:00 | 231 | 05:00
| Ashuganj | 233 | 10:00 | 225 | 09:00 | Ishurdi | 235 | 18:30 | 227 | 12:00
| Ashuganj-400 | 234 | 7:00 | 225 | 12:00 | Jhenaidah | 228 | 08:00 | 219 | 13:00
| Baghabari | 229 | 18:00 | 223 | 13:00 | Kaliakoir | 229 | 19:30 | 219 | 10:00
| Barapukuria | 224 | 17:00 | 218 | 07:00 | Keranigonj | 226 | 02:00 | 215 | 10:00
| Barapukuria-230 | 225 | 17:00 | 219 | 07:00 | Khulna(S) | 229 | 06:00 | 220 | 22:00
| Barishal | 235 | 17:00 | 230 | 00:00 | Madunaghat | 236 | 02:00 | 230 | 10:00
| Bheramara | 233 | 18:30 | 225 | 12:00 | Maniknagar | 227 | 01:00 | 219 | 10:00
| Bhulta | 229 | 02:00 | 221 | 10:00 | Meghnaghat | 236 | 00:00 | 228 | 12:00
| Bibiana | 224 | 02:00 | 219 | 11:00 | Meghnaghat-400 | 231 | 20:00 | 223 | 10:00
| BIPTC | 234 | 18:00 | 224 | 13:00 | Mirsorai | 240 | 18:00 | 227 | 10:00
| Bogura | 233 | 03:00 | 230 | 08:00 | Rajshahi | 235 | 19:00 | 224 | 12:00
| Bogura-400 | 236 | 17:00 | 231 | 11:00 | Rampal | 228 | 06:00 | 220 | 13:00
| Borhanuddin | 240 | 08:00 | 236 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 238 | 18:00 | 227 | 10:00 | Rampura | 227 | 05:00 | 218 | 11:00
| Cumilla(N) | 229 | 18:00 | 219 | 10:00 | Shikalbaha | 236 | 18:00 | 229 | 05:00
| Faridpur | 231 | 03:00 | 225 | 12:00 | Shyampur | 228 | 20:00 | 218 | 10:00
| Fenchuganj | 228 | 08:00 | 222 | 12:00 | Siddhirganj | 229 | 05:00 | 222 | 10:00
| Ghorashal | 232 | 18:00 | 225 | 15:00 | Sirajgonj | 239 | 19:30 | 234 | 10:00
| Ghorashal-230 | 228 | 19:30 | 218 | 11:00 | Sreepur | 230 | 06:00 | 223 | 11:00
| Gopalganj | 232 | 05:00 | 227 | 12:00 | Tongi | 227 | 19:30 | 215 | 12:00
| GPH | 237 | 18:30 | 228 | 10:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 137 | 02:00 | 129 | 11:00 | Kushtia | 135 | 07:00 | 130 | 13:00
| Agargaon | 134 | 02:00 | 126 | 10:00 | Lalbag | 133 | 02:00 | 124 | 12:00
| Agrabad | 134 | 18:00 | 129 | 09:00 | Lalmonirhat | 131 | 04:00 | 125 | 07:00
| AKS | 133 | 18:00 | 128 | 09:00 | Madanganj | 128 | 18:00 | 121 | 10:00
| Aminbazar | 137 | 03:00 | 124 | 09:00 | Madaripur | 132 | 06:00 | 126 | 12:00
| Amnura | 145 | 07:00 | 126 | 00:00 | Madartek | 136 | 02:00 | 128 | 14:00
| Ashuganj | 137 | 18:30 | 133 | 10:00 | Madunaghat | 136 | 18:30 | 131 | 05:00
| Bagerhat | 135 | 08:00 | 125 | 00:00 | Magura | 136 | 08:00 | 129 | 13:00
| Bakulia | 135 | 18:00 | 129 | 10:00 | Mahasthangarh | 139 | 17:00 | 133 | 10:00
| Banani | 136 | 03:00 | 127 | 12:00 | Manikganj | 126 | 19:00 | 117 | 14:00
| Bangabhaban | 128 | 04:00 | 121 | 12:00 | Maniknagar | 129 | 06:00 | 120 | 13:00
| Barapukuria | 137 | 17:00 | 131 | 07:00 | Matarbari | 126 | 15:00 | 116 | 23:00
| Barguna | 139 | 02:00 | 132 | 12:00 | Matuail | 129 | 20:00 | 123 | 10:00
| Barishal | 130 | 19:30 | 125 | 12:00 | Millgate | 132 | 02:00 | 122 | 12:00
| Barishal-230 | 130 | 07:00 | 125 | 12:00 | Mirpur | 135 | 05:00 | 127 | 10:00
| Baroaulia | 136 | 19:30 | 132 | 00:00 | Mirzapur | 126 | 00:00 | 119 | 22:00
| Baroirhat | 132 | 18:00 | 117 | 00:00 | Mithapukur | 135 | 02:00 | 129 | 10:00
| Bashundhara | 136 | 03:00 | 122 | 11:00 | MI_Cement | 133 | 20:00 | 125 | 10:00
| BashundharaCement | 128 | 18:00 | 121 | 10:00 | Modern | 135 | 18:30 | 129 | 09:00
| Beanibazar | 126 | 07:00 | 122 | 00:00 | Mogbazar | 137 | 02:00 | 10 | 14:00
| Benapole | 133 | 08:00 | 126 | 00:00 | Mongla | 132 | 08:00 | 124 | 00:00
| Bhaluka | 128 | 06:00 | 122 | 10:00 | Motijheel | 128 | 04:00 | 122 | 10:00
| Bhandaria | 126 | 17:00 | 121 | 12:00 | Munshiganj | 128 | 18:00 | 121 | 12:00
| Bhangura | 137 | 03:00 | 133 | 12:00 | Mymensingh | 133 | 06:00 | 117 | 18:30
| Bheramara | 136 | 18:30 | 132 | 12:00 | Naogaon | 138 | 06:00 | 125 | 00:00
| Bheramara(GK) | 136 | 18:00 | 133 | 00:00 | Narail | 137 | 08:00 | 130 | 13:00
| Bhulta | 119 | 04:00 | 114 | 13:00 | Narinda | 126 | 19:00 | 117 | 14:00
| Bog-Sherpur | 139 | 02:00 | 134 | 10:00 | Narshingdi | 120 | 17:00 | 115 | 00:00
| Bogura | 140 | 02:00 | 136 | 11:00 | Natore | 136 | 06:00 | 132 | 11:00
| Bogura-230 | 141 | 04:00 | 133 | 18:00 | Nawabganj | 134 | 06:00 | 126 | 10:00
| Brahmanbaria | 129 | 18:00 | 124 | 01:00 | Netrakona | 131 | 00:00 | 118 | 22:00
| Cantonment | 133 | 02:00 | 126 | 10:00 | New | 132 | 07:00 | 123 | 09:00
| Chandpur | 136 | 18:00 | 117 | 01:00 | Niamatpur | 133 | 17:00 | 130 | 00:00
| Chandraghona | 136 | 18:00 | 131 | 10:00 | Noapara | 136 | 06:00 | 129 | 00:00
| Chapai | 131 | 17:00 | 127 | 00:00 | Pabna | 135 | 02:00 | 132 | 10:00
| Charsaidpur | 128 | 18:00 | 121 | 10:00 | Palashbari | 135 | 17:00 | 129 | 10:00
| Chauddagram | 130 | 18:00 | 118 | 00:00 | Panchagarh | 137 | 02:00 | 117 | 11:00
| Chhatak | 127 | 06:00 | 121 | 13:00 | Patuakhali | 140 | 18:00 | 130 | 13:00
| Chowmuhani | 122 | 18:00 | 110 | 01:00 | Payra | 139 | 22:00 | 133 | 13:00
| Chuadanga | 131 | 06:00 | 122 | 14:00 | PHP | 130 | 18:00 | 116 | 00:00
| Coxsbazar | 124 | 11:00 | 117 | 23:00 | Postogola | 134 | 19:30 | 127 | 10:00
| Cumilla(N) | 133 | 18:00 | 125 | 00:00 | Purbachal | 137 | 02:00 | 122 | 10:00
| Cumilla(S) | 133 | 18:00 | 123 | 00:00 | Purbasadipur | 134 | 17:00 | 120 | 07:00
| Daudkandi | 128 | 18:00 | 121 | 00:00 | Rahanpur | 135 | 17:00 | 133 | 00:00
| Dhaka | 136 | 01:00 | 129 | 12:00 | Rahim | 126 | 02:00 | 122 | 10:00
| Dhamrai | 130 | 19:30 | 122 | 10:00 | Rajbari | 128 | 05:00 | 125 | 12:00
| Dhanmondi | 137.5 | 04:00 | 128 | 13:00 | Rajendrapur | 129 | 19:30 | 118 | 10:00
| Dohazari | 133 | 17:00 | 125 | 06:00 | Rajshahi | 136 | 19:00 | 130 | 13:00
| Faridpur | 130 | 05:00 | 127 | 00:00 | Rajshahi-230 | 136 | 20:00 | 122 | 00:00
| Fatullah | 133 | 20:00 | 125 | 12:00 | Ramganj | 131 | 18:00 | 112 | 01:00
| Fenchuganj | 134 | 08:00 | 130 | 01:00 | Rampur | 134 | 18:00 | 129 | 10:00
| Feni | 130 | 18:00 | 119 | 00:00 | Rampura | 137 | 05:00 | 128 | 11:00
| Ghatail | 128 | 03:00 | 116 | 18:30 | Rangamati | 135 | 18:30 | 130 | 10:00
| Ghorashal | 137 | 18:00 | 131 | 13:00 | Rangpur | 138 | 06:00 | 126 | 07:00
| Goalpara | 137 | 06:00 | 130 | 00:00 | Ruppur | 138 | 19:00 | 133 | 12:00
| Gollamari | 136 | 08:00 | 131 | 12:00 | Saidpur | 136 | 03:00 | 124 | 07:00
| Gopalganj | 132 | 04:00 | 127 | 12:00 | Satkhira | 133 | 06:00 | 126 | 22:00
| Gopalganj-400 | 131 | 06:00 | 127 | 13:00 | Satmasjid | 133 | 01:00 | 126 | 12:00
| Gulshan | 136 | 04:00 | 128 | 12:00 | Savar | 137 | 20:00 | 127 | 09:00
| Halishahar | 135 | 18:30 | 129 | 09:00 | SevenRings | 136 | 18:00 | 130 | 10:00
| Haripur | 128 | 18:00 | 124 | 12:00 | ShahCement | 128 | 18:00 | 121 | 10:00
| HaripurSBU | 128 | 18:00 | 124 | 12:00 | Shahjadpur | 140 | 03:00 | 136 | 12:00
| Hasnabad | 134 | 19:30 | 127 | 11:00 | Shahjibazar | 129 | 07:00 | 124 | 13:00
| Hathazari | 137 | 20:00 | 134 | 00:00 | Shahmirpur | 136 | 18:00 | 131 | 10:00
| Ishurdi | 138 | 19:00 | 133 | 12:00 | Shariatpur | 130 | 05:00 | 126 | 00:00
| Jaldhaka | 133 | 03:00 | 122 | 08:00 | Sherpur | 135 | 05:00 | 117 | 18:30
| Jamalpur | 136 | 05:00 | 120 | 18:30 | Shikalbaha | 125 | 18:00 | 119 | 10:00
| Jashore | 135 | 08:00 | 126 | 22:00 | Shikalbaha-230 | 135 | 17:00 | 120 | 20:00
| Jhenaidah | 136 | 05:00 | 129 | 22:00 | Shitalakhya | 133 | 20:00 | 125 | 10:00
| Jhenaidah-230 | 136 | 08:00 | 130 | 00:00 | Sholosohor | 135 | 18:00 | 130 | 10:00
| Joydebpur | 134 | 18:00 | 125 | 10:00 | Shyampur | 137 | 07:00 | 123 | 10:00
| Joypurhat | 129 | 17:00 | 123 | 00:00 | Shyampur-230 | 132 | 19:30 | 125 | 10:00
| Juldah | 136 | 18:00 | 129 | 09:00 | Siddhirganj | 129 | 18:00 | 123 | 10:00
| Kabirpur | 130 | 02:00 | 120 | 10:00 | Sirajganj | 138 | 05:00 | 132 | 10:00
| Kachua | 130 | 17:00 | 118 | 01:00 | Sonargaon | 128 | 19:30 | 122 | 09:00
| Kaliakoir | 132 | 19:00 | 123 | 10:00 | Sreemongol | 128 | 05:00 | 125 | 00:00
| Kallyanpur | 129 | 04:00 | 124 | 12:00 | Sreepur | 130 | 06:00 | 125 | 11:00
| Kalurghat | 136 | 18:00 | 130 | 10:00 | Srinagar | 133 | 05:00 | 126 | 13:00
| Kamrangirchar | 133 | 07:00 | 122 | 13:00 | SSM | 139 | 17:00 | 136 | 10:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 125 | 07:00 | 120 | 12:00
| Kazla | 128 | 03:00 | 120 | 13:00 | Sylhet | 128 | 07:00 | 126 | 00:00
| Keranigonj | 134 | 06:00 | 127 | 10:00 | Sylhet-132 | 128 | 06:00 | 126 | 00:00
| Khagrachori | 133 | 08:00 | 129 | 10:00 | Tangail | 126 | 00:00 | 115 | 18:30
| Khulna | 136 | 06:00 | 130 | 13:00 | Thakurgaon | 140 | 02:00 | 118 | 11:00
| Khulna(S) | 137 | 06:00 | 131 | 00:00 | TK | 135 | 15:00 | 131 | 07:00
| Khulshi | 133 | 18:00 | 128 | 10:00 | Tongi | 133 | 04:00 | 125 | 10:00
| Kishoreganj | 130 | 06:00 | 124 | 10:00 | Ullahpara | 138 | 03:00 | 133 | 10:00
| Kodda | 133 | 18:00 | 119 | 10:00 | Ullon | 137 | 04:00 | 128 | 12:00
| KSRM | 136 | 17:00 | 130 | 10:00 | Uttara | 136 | 05:00 | 127 | 12:00
| Kulaura | 131 | 04:00 | 128 | 13:00 | UttaraNew | 135 | 02:00 | 127 | 10:00
| Kurigram | 133 | 03:00 | 124 | 08:00 | Zigatola | 134 | 06:00 | 127 | 10:00

## L-Curve
Date | 2024-10-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1540 | 6390 | 5735 | 12125 |  |  |  | QF-LDC-11
0:30 | 1499 | 6396.5 | 5767 | 12163.5 | Date: | 2024-10-29
1:00 | 1458 | 6403 | 5799 | 12202
1:30 | 1446 | 6342.5 | 5712.5 | 12055
2:00 | 1434 | 6282 | 5626 | 11908
2:30 | 1447 | 6090 | 5557.5 | 11647.5 | [5 empty] | Gen. at Eve. Peak | 13176 | 13176 MW (19:30 )
3:00 | 1460 | 5898 | 5489 | 11387 | [6 empty] | 19:30
3:30 | 1462 | 5770.5 | 5432.5 | 11203 | [5 empty] | Gen. at Day Peak | 11859 | 11859 MW (12:00 )
4:00 | 1464 | 5643 | 5376 | 11019 | [6 empty] | 12:00
4:30 | 1462 | 5604.5 | 5290 | 10894.5 | [5 empty] | Highest Generation | 13176
5:00 | 1460 | 5566 | 5204 | 10770 | [6 empty] | 19:30
5:30 | 1483 | 5497.5 | 5200.5 | 10698
6:00 | 1506 | 5429 | 5197 | 10626
6:30 | 1463 | 5440.5 | 5257.5 | 10698
7:00 | 1420 | 5452 | 5318 | 10770
7:30 | 1428 | 5458.5 | 5337 | 10795.5
8:00 | 1436 | 5465 | 5356 | 10821
8:30 | 1570 | 5583.5 | 5398.5 | 10982
9:00 | 1704 | 5702 | 5441 | 11143
9:30 | 1714 | 5795 | 5429.5 | 11224.5
10:00 | 1724 | 5888 | 5418 | 11306
10:30 | 1659 | 6040.5 | 5441.5 | 11482
11:00 | 1594 | 6193 | 5465 | 11658
11:30 | 1593 | 6224.5 | 5534 | 11758.5
12:00 | 1592 | 6256 | 5603 | 11859
12:30 | 1585 | 6283 | 5686 | 11969
13:00 | 1578 | 6310 | 5769 | 12079
13:30 | 1574 | 6295 | 5766.5 | 12061.5
14:00 | 1570 | 6280 | 5764 | 12044
14:30 | 1577 | 6239.5 | 5699 | 11938.5
15:00 | 1584 | 6199 | 5634 | 11833
15:30 | 1609 | 6205 | 5501 | 11706
16:00 | 1634 | 6211 | 5368 | 11579
16:30 | 1605 | 6217 | 5332.5 | 11549.5
17:00 | 1576 | 6223 | 5297 | 11520
17:30 | 1335 | 6559.5 | 5548 | 12107.5
18:00 | 1094 | 6896 | 5799 | 12695
18:30 | 1149 | 7002.5 | 5864 | 12866.5
19:00 | 1204 | 7109 | 5929 | 13038
19:30 | 1164 | 7192 | 5984 | 13176
20:00 | 1146 | 7194 | 5918 | 13112 |  |  |  | Executive Engineer
20:30 | 1234 | 7064.5 | 5986.5 | 13051 |  |  |  | Network Operation Division
21:00 | 1322 | 6935 | 6055 | 12990
21:30 | 1365 | 6858 | 6060 | 12918
22:00 | 1408 | 6781 | 6065 | 12846 |  |  |  |  | Page 6 of 7
22:30 | 1432 | 6643 | 6043.5 | 12686.5
23:00 | 1456 | 6505 | 6022 | 12527
23:30 | 1498 | 6447.5 | 5878.5 | 12326
24:00 | 1540 | 6390 | 5735 | 12125
13176 MW (19:30 )
11859 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-10-29 |  | Energy |  | 288763583
[15 empty] | Date: | 2024-10-29 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3702 | 922 | 1657 | 0 | 1550 | 2457 | 173 | 0 | 574 | 74 | 1016 | 0 | 0 | 1122.125
0:30 | 3743 | 917 | 1688 | 0 | 1533.5 | 2525.5 | 173 | 0 | 498 | 70 | 1015.5 | 0 | 0 | 646.0575 |  |  | Date: | 44132
1:00 | 3784 | 912 | 1719 | 0 | 1517 | 2594 | 173 | 0 | 422 | 66 | 1015 | 0 | 0 | 169.99
1:30 | 3756.5 | 912 | 1630 | 0 | 1490 | 2597 | 173 | 0 | 413.5 | 67 | 1016 | 0 | 0 | 157.575 | [8 empty] | Total Energy | 288.7636 | 288.7636 | Total Energy Gen 288.764 MKWHr Energy Not Served 11.315 MKWHr Energy Requirement 300.079 MKWHr
2:00 | 3729 | 912 | 1541 | 0 | 1463 | 2600 | 173 | 0 | 405 | 68 | 1017 | 0 | 0 | 145.16 | [8 empty] | Energy not Served | 11.3151 | 11.3151
2:30 | 3713.5 | 912 | 1540 | 0 | 1320.5 | 2603.5 | 172.5 | 0 | 302.5 | 67 | 1016 | 0 | 0 | 131.3125 | [8 empty] | Energy Requirement | 300.0787 | 300.0787
3:00 | 3698 | 912 | 1539 | 0 | 1178 | 2607 | 172 | 0 | 200 | 66 | 1015 | 0 | 0 | 117.465
3:30 | 3681.5 | 912 | 1541.5 | 0 | 1065 | 2604 | 173 | 0 | 144.5 | 67 | 1014.5 | 0 | 0 | 109.3475 | [7 empty] | Shortage
4:00 | 3665 | 912 | 1544 | 0 | 952 | 2601 | 174 | 0 | 89 | 68 | 1014 | 0 | 0 | 101.23
4:30 | 3648.5 | 912.5 | 1580.5 | 0 | 842 | 2596 | 174.5 | 0 | 61 | 65 | 1014.5 | 0 | 0 | 50.615
5:00 | 3632 | 913 | 1617 | 0 | 732 | 2591 | 175 | 0 | 33 | 62 | 1015 | 0 | 0 | 0
5:30 | 3643.5 | 913 | 1612.5 | 0 | 650 | 2596.5 | 175 | 0 | 33 | 61 | 1013.5 | 0 | 0 | 0
6:00 | 3655 | 913 | 1608 | 0 | 568 | 2602 | 175 | 0 | 33 | 60 | 1012 | 0 | 0 | 0
6:30 | 3652 | 912.5 | 1651.5 | 0 | 569.5 | 2600 | 175.5 | 0 | 33 | 57 | 1014.5 | 32.5 | 0 | 42.975 | [6 empty] | Coal
7:00 | 3649 | 912 | 1695 | 0 | 571 | 2598 | 176 | 0 | 33 | 54 | 1017 | 65 | 0 | 85.95
7:30 | 3619 | 912.5 | 1605 | 0 | 637 | 2598.5 | 176 | 0 | 41 | 53 | 1018 | 135.5 | 0 | 90.2475 | [5 empty] | Oil
8:00 | 3589 | 913 | 1515 | 0 | 703 | 2599 | 176 | 0 | 49 | 52 | 1019 | 206 | 0 | 94.545
8:30 | 3605.5 | 912.5 | 1512 | 0 | 780.5 | 2587.5 | 176 | 0 | 50.5 | 51 | 1015.5 | 291 | 0 | 69.715
9:00 | 3622 | 912 | 1509 | 0 | 858 | 2576 | 176 | 0 | 52 | 50 | 1012 | 376 | 0 | 44.885
9:30 | 3630.5 | 912.5 | 1493 | 0 | 870.5 | 2564.5 | 176 | 0 | 81 | 51 | 1013.5 | 431.5 | 0.5 | 43.4525
10:00 | 3639 | 913 | 1477 | 0 | 883 | 2553 | 176 | 0 | 110 | 52 | 1015 | 487 | 1 | 42.02
10:30 | 3650 | 912.5 | 1530 | 0 | 938 | 2553.5 | 176 | 0 | 155 | 55 | 1016.5 | 494 | 1.5 | 184.315
11:00 | 3661 | 912 | 1583 | 0 | 993 | 2554 | 176 | 0 | 200 | 58 | 1018 | 501 | 2 | 326.61
11:30 | 3680 | 913 | 1619.5 | 0 | 1047.5 | 2553.5 | 176 | 0 | 208 | 60 | 1017.5 | 480.5 | 3 | 421.6325
12:00 | 3699 | 914 | 1656 | 0 | 1102 | 2553 | 176 | 0 | 216 | 62 | 1017 | 460 | 4 | 516.655
12:30 | 3720.5 | 914 | 1655.5 | 0 | 1139.5 | 2571 | 176 | 0 | 225.5 | 60 | 1015.5 | 486 | 5.5 | 538.1425
13:00 | 3742 | 914 | 1655 | 0 | 1177 | 2589 | 176 | 0 | 235 | 58 | 1014 | 512 | 7 | 559.63
13:30 | 3742 | 914 | 1655 | 0 | 1177 | 2589 | 176 | 0 | 235 | 58 | 1014 | 512 | 7 | 559.63
14:00 | 3742 | 914 | 1655 | 0 | 1177 | 2589 | 176 | 0 | 235 | 58 | 1014 | 512 | 7 | 559.63
14:30 | 3732 | 913.5 | 1636.5 | 0 | 1176.5 | 2585.5 | 175 | 0 | 241 | 63 | 1014.5 | 410 | 8.5 | 679.4825
15:00 | 3722 | 913 | 1618 | 0 | 1176 | 2582 | 174 | 0 | 247 | 68 | 1015 | 308 | 10 | 799.335
15:30 | 3720 | 913.5 | 1619.5 | 0 | 1217 | 2495 | 174 | 0 | 260.5 | 68 | 1011.5 | 218.5 | 8.5 | 798.8575
16:00 | 3718 | 914 | 1621 | 0 | 1258 | 2408 | 174 | 0 | 274 | 68 | 1008 | 129 | 7 | 798.38
16:30 | 3640 | 913.5 | 1519 | 0 | 1399.5 | 2410.5 | 174 | 0 | 341.5 | 64 | 1007 | 73 | 7.5 | 795.515
17:00 | 3562 | 913 | 1417 | 0 | 1541 | 2413 | 174 | 0 | 409 | 60 | 1006 | 17 | 8 | 792.65
17:30 | 3612.5 | 841.5 | 1510 | 0 | 1796 | 2534 | 174 | 0 | 548.5 | 65 | 1011 | 8.5 | 6.5 | 876.325
18:00 | 3663 | 770 | 1603 | 0 | 2051 | 2655 | 174 | 0 | 688 | 70 | 1016 | 0 | 5 | 960
18:30 | 3665 | 770 | 1604.5 | 0 | 2141 | 2675 | 174.5 | 0 | 743 | 70 | 1018.5 | 0 | 5 | 891.5
19:00 | 3667 | 770 | 1606 | 0 | 2231 | 2695 | 175 | 0 | 798 | 70 | 1021 | 0 | 5 | 823
19:30 | 3726 | 774 | 1592 | 0 | 2292 | 2709 | 175 | 0 | 815 | 72 | 1016 | 0 | 5 | 788
20:00 | 3716 | 774 | 1593 | 0 | 2241 | 2709 | 175 | 0 | 813 | 72 | 1017 | 0 | 2 | 753
20:30 | 3696.5 | 846 | 1601.5 | 0 | 2207 | 2711 | 175.5 | 0 | 722.5 | 72 | 1018 | 0 | 1 | 748.95
21:00 | 3677 | 918 | 1610 | 0 | 2173 | 2713 | 176 | 0 | 632 | 72 | 1019 | 0 | 0 | 744.9
21:30 | 3690.5 | 917.5 | 1623.5 | 0 | 2076 | 2712 | 176 | 0 | 630 | 73 | 1019.5 | 0 | 0 | 742.035
22:00 | 3704 | 917 | 1637 | 0 | 1979 | 2711 | 176 | 0 | 628 | 74 | 1020 | 0 | 0 | 739.17
22:30 | 3687.5 | 917.5 | 1630 | 0 | 1833 | 2711 | 175 | 0 | 640 | 74 | 1018.5 | 0 | 0 | 834.1925
23:00 | 3671 | 918 | 1623 | 0 | 1687 | 2711 | 174 | 0 | 652 | 74 | 1017 | 0 | 0 | 929.215
23:30 | 3686.5 | 920 | 1640 | 0 | 1618.5 | 2584 | 173.5 | 0 | 613 | 74 | 1016.5 | 0 | 0 | 1025.67 |  |  | Max Temp. in Dhaka |  | 34.2°C
24:00 | 3702 | 922 | 1657 | 0 | 1550 | 2457 | 173 | 0 | 574 | 74 | 1016 | 0 | 0 | 1122.125
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 288.764 MKWHr Energy Not Served 11.315 MKWHr Energy Requirement 300.079 MKWHr
Note on X13: Author:

## Generation
2024-10-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 133 | 133 | 132 | 134 | 135 | 135 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 134 | 134 | 134 | 134 | 134 |  | 135 | 135 | 135 | 136 | 136 | 134 | 133 | 3244315
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | [9 empty] | 4 | 8 | 8 | 8 | 8 | 25 |  | 25 | 25 | 25 | 25 | 25 | 23 | 8 | 216966
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 9 | 15 | 17 | 14 | 18 | 18 | 14 | 10 | 5 | 0 | [9 empty] | 120285
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 228 | 227 | 227 | 227 | 227 | 227 | 227 | 226 | 221 | 221 | 220 | 220 | 220 | 219 | 219 | 211 | 219 |  | 222 | 222 | 222 | 222 | 222 | 227 | 228 | 5180697
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 69 | 68 | [8 empty] | 51 | 58 | 66 | 64 | 63 | 63 | 67 | 67 |  | 84 | 84 | 84 | 82 | 82 | 83 | 83 | 1139909
12 | Hathazari 100 MW peaking PP | 62 | 62 | 62 | [5 empty] | 3 | 42 | 42 | 44 | 44 | 52 | 53 | 59 | 61 | 63 |  | 63 | 71 | 71 | 71 | 71 | 71 | 70 | 1074576
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 10 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 88655
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 44 | 44 | 44 | [7 empty] | 29 | 27 | 31 | 37 | 36 | 36 | 24 | 43 |  | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 630624
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 322 | 320 | 315 | 314 | 310 | 310 | 310 | 310 | 300 | 300 | 300 | 300 | 297 | 298 | 298 | 298 | 295 | 295 |  | 268 | 295 | 295 | 288 | 288 | 288 | 285 | 7261312
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 195 | 45 | [6 empty] | 30 | 64 | 64 | 64 | 64 | 64 | 64 | 90 | 135 |  | 212 | 250 | 258 | 266 | 228 | 196 | 198 | 2559273
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217455
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 614 | 612 | 612 | 613 | 612 | 612 | 612 | 611 | 612 | 612 | 612 | 612 | 606 | 611 | 610 | 610 | 612 | 612 |  | 612 | 612 | 612 | 613 | 612 | 613 | 616 | 14699998
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 39 | 38 | 38 | 38 | 39 | 39 | 37 | 35 | 38 | 39 |  | 41 | 41 | 41 | 41 | 42 | 40 | 39 | 951264
33 | Ashuganj 225 MW CCPP | 213 | 216 | 215 | 214 | 214 | 215 | 215 | 214 | 212 | 211 | 210 | 209 | 211 | 209 | 210 | 209 | 213 | 212 |  | 212 | 213 | 213 | 213 | 210 | 212 | 213 | 5119000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 340 | 310 | 285 | 300 | 310 | 290 | 315 | 315 | 315 | 335 | 320 | 315 | 315 | 315 | 315 | 320 | 285 | 310 |  | 310 | 310 | 310 | 300 | 330 | 290 | 320 | 7943500
| Ashuganj 420 MW CCPP(East) | 393 | 393 | 393 | 393 | 393 | 393 | 370 | 350 | 350 | 350 | 350 | 360 | 393 | 393 | 393 | 393 | 393 | 393 |  | 393 | 395 | 393 | 370 | 370 | 370 | 370 | 9205000
35 | Ashuganj 55 MW PP (Precision) | 24 | 24 | 24 | 24 | 24 | 24 | 14 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 247200
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 50 | 50 | 51 | 51 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1190770
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 408 | 413 | 417 | 400 | 377 | 381 | 371 | 371 | 373 | 373 | 401 | 403 | 403 | 401 | 401 | 403 | 406 | 404 |  | 407 | 415 | 410 | 405 | 406 | 407 | 407 | 9648000
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 380 | 380 | 380 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10434300
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 33 | 33 | 33 | 33 | 33 | 33 | 26 | 25 | 24 | 10 | 10 | 10 | 8 | 8 | 7 | 10 | 10 | 10 |  | 10 | 11 | 11 | 15 | 15 | 17 | 17 | 399360
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 19 | 31 | 40 | 45 | 37 | 42 | 19 | 22 | 10 | 0 | [9 empty] | 268310
44 | Fenchugonj CCPP Phase-1 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 670000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 699720
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 55 | 55 | 55 | 55 | 58 | 58 | 58 | 57 | 57 | 54 | 54 | 53 | 53 | 55 | 58 | 44 |  | 54 | 54 | 55 | 55 | 55 | 56 | 55 | 1313952
48 | Shahjibazar 86 MW PP (Shahjibazar) | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 669120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 207 | 206 | 206 | 209 | 209 | 209 | 209 | 209 | 206 | 205 | 205 | 202 | 204 | 202 | 204 | 204 | 202 | 207 |  | 208 | 208 | 206 | 207 | 206 | 206 | 205 | 5146190
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 58000
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 8 | 13 | 13 | 13 | 13 | 13 | 13 | 311328
57 | Bibiana-II 341 MW CCPP (Summit) | 315 | 300 | 280 | 280 | 300 | 305 | 300 | 290 | 300 | 310 | 305 | 305 | 300 | 305 | 305 | 300 | 275 | 295 |  | 280 | 285 | 280 | 290 | 290 | 285 | 305 | 7233500
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 330 | 340 | 360 | 372 | 372 | 372 | 372 | 372 | 366 |  | 366 | 370 | 370 | 366 | 366 | 366 | 366 | 8310200
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 35 | 35 | 35 | 17 | 17 | 17 | 275365
59 | Tangail Palli Power Gen 22 MW | [15 empty] | 6 | 18 | 12 |  | 0 | 0 | 0 |  |  |  | 0 | 36720
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 66 | 68 | 66 | 68 | 62 | 60 | 54 | 52 | 50 | 52 | 58 | 62 | 58 | 68 | 68 | 68 | 60 | 70 |  | 70 | 72 | 72 | 72 | 74 | 74 | 74 | 1530240
64 | Malancha, Ctg. EPZ (United) | 31 | 36 | 37 | 39 | 40 | 40 | 35 | 6 | 2 | 2 | 2 | 2 | 4 | 2 | 2 | 2 | 2 | 2 |  | 2 | 10 | 14 | 16 | 23 | 27 | 28 | 409440
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 5 | 15 |  | 9 | 18 | 18 | 18 | 18 | 18 | 18 | 408050
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 15 | 15 | 15 | 15 | 16 | 17 | 17 | 17 | 16 |  | 16 | 16 | 16 | 17 | 17 | 17 | 19 | 454200
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 15 | 15 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511920
71 | Maona 33 MW PP(Summit) | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 616300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 24 | 32 | 30 | 30 |  | 30 | 30 | 30 | 32 | 33 | 33 | 33 | 762500
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 20 | 40 | 106 | 106 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 1145700
| Chowmuhani 113 MW | 19 | 18 | 13 | 18 | 18 | 18 | 18 | 19 | 18 | 19 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 18 |  | 18 | 18 | 18 | 18 | 18 | 19 | 17 | 437640
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 72 |  | 90 | 90 | 90 | 72 | 35 | 17 | 17 | 799200
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 |  | 25 | 34 | 34 | 34 | 34 | 17 | 8 | 324960
79 | Kodda 150 MW PP | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 42 | 48 | 48 | 48 | 47 | 47 | 47 | 106 |  | 148 | 147 | 147 | 147 | 147 | 147 | 81 | 1500480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 34 |  | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 742310
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 35 | 35 | 35 | 88 |  | 88 | 88 | 88 | 88 | 88 | 35 | 17 | 1054080
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 24480
| Jodiac Power | 35 | 35 | 35 | 35 | 35 |  |  | 19 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 821067
| Karnaphuli Power Ltd. | 17 | 17 | 17 | [6 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 319490
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 11 | 13 | 13 | 13 | 13 |  | 0 | 43000
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 16 | [13 empty] | 1 | 16 | 16 | 7 | [6 empty] | 5 | 16 | 85440
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 925432
94 | Gagnagar 102 MW PP (Digital Power) | [12 empty] | 8 | 8 |  |  |  | 8 |  | 8 | 8 | 8 |  |  |  | 0 | 35136
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 6 | [6 empty] | 1 | 15 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 334560
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 15 | [7 empty] | 25 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 671384
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 17 | 35 |  | 55 | 55 | 55 | 35 | 17 |  | 0 | 272074
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3731645
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 11350
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 35 | 42 |  | 35 | 35 | 35 | 17 |  |  | 0 | 259200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 88 | 88 | 77 | 81 | 77 | 77 | 77 | 80 | 77 |  | 77 | 77 | 78 | 76 | 77 | 77 | 67 | 1975200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 86 | 48 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 60 | 70 | 70 | 68 | 68 | 67 | 68 | 74 | 100 |  | 115 | 130 | 131 | 131 | 113 | 94 | 91 | 1830240
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 62 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 1523520
116 | Chandpur 200 MW (Desh energy) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 59 | 149 |  | 122 | 34 | 34 | 34 | 34 | 34 | 23 | 1327200
117 | Ashuganj 150 MW PP (Midland) | 81 | 83 | 83 | 50 |  |  |  | 2 | 35 | 72 | 76 | 75 | 73 | 73 | 72 | 80 | 87 | 95 |  | 117 | 115 | 115 | 102 | 100 | 104 | 105 | 1719563
118 | Bibiyana-III 400 MW CCPP | 385 | 383 | 371 | 335 | 310 | 312 | 314 | 313 | 370 | 387 | 388 | 387 | 389 | 389 | 389 | 390 | 386 | 386 |  | 387 | 387 | 387 | 387 | 387 | 385 | 387 | 9252000
| Jamalpur 115 MW PP (United) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 47 | 47 | 47 | 47 | 47 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 47 | 48 | 1256400
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 |  |  | 49 | 52 | 69 | 69 | 69 | 70 | 70 | 70 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1249527
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 288000
| Anlima Energy Ltd. | 35 | 35 | 35 | 35 | 35 |  |  | 1 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 765273
| Bhairob 54.5 MW | 17 | 17 | [10 empty] | 10 | 17 | 17 | 17 | 17 | 17 |  | 17 | 28 | 32 | 35 | 35 | 35 | 35 | 328680
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 11 | 20 | 26 | 29 | 30 | 28 | 23 | 16 | 7 | 1 | [9 empty] | 194401
| Chandpur 115(Doreen) | 22 | 21 | 21 | 21 | 21 | 16 | 17 | 17 | 30 | 34 | 34 | 34 | 34 | 36 | 50 | 51 | 51 | 54 |  | 73 | 74 | 74 | 74 | 74 | 66 | 35 | 971520
| Kanchan Purbachal Power Generation Ltd. | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 32 | 36 | 29 | 36 | 36 | 36 | 36 | 36 | 29 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 848160
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 160 |  | 160 | 160 | 160 |  |  | 17 | 17 | 834691
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 4 | 7 | 6 | 10 | 7 | 8 | 5 |  | 5 | 5 | 2 | 0 | 0 | 0 | 0 | 56640
| Sonagazi 75 MW Solar Plant | [5 empty] | 0 | 10 | 30 | 49 | 62 | 68 | 68 | 64 | 51 | 34 | 18 | 2 | [9 empty] | 456445
Matarbari 2*600 MW (CPGCL)
Meghnaghat (Reliance) 718MW CCPP
Sreepur 150 MW
120
121 | Eastern Zone Total | 6403 | 6282 | 5898 | 5643 | 5566 | 5429 | 5452 | 5465 | 5702 | 5888 | 6193 | 6256 | 6310 | 6280 | 6199 | 6211 | 6223 | 6896 |  | 7109 | 7192 | 7194 | 6935 | 6781 | 6505 | 6390 | 150645602
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | 20 | 20 | 20 | 15 | [7 empty] | 3 | 10 | 10 | 10 | 15 | 15 | 20 |  | 27 | 25 | 27 | 26 | 26 | 26 | 26 | 284640
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 9 | 32 | 54 | 48 | 72 | 70 | 80 | 72 | 47 | 22 | 3 | [9 empty] | 523440
132 | Rampal 1320 MW (BIFPCL) | 501 | 509 | 515 | 510 | 501 | 512 | 510 | 511 | 511 | 509 | 510 | 509 | 508 | 508 | 511 | 365 | 369 | 610 |  | 621 | 621 | 621 | 624 | 622 | 622 | 364 | 12625450
133 | United Payra Power Ltd. | 150 | 150 | 150 | 150 | 54 | 17 | 17 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2041200
| Bhola Nutan Biddut BD LTD (GAS) | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5354000
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | [5 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 48 | 48 | 48 | 48 | 16 | 16 | 413952
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3659
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 132 | 100 | 100 | 100 | 100 | 127 | 127 | 127 | 127 | 123 | 123 | 123 | 123 | 130 | 130 | 123 | 80 | 127 |  | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 3061000
141 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 9 | 9 | 7 | 7 | 6 | 6 | 5 | 6 | 5 | 7 | 7 | 7 | 7 | 7 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 196049
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP | 46 | 46 | 41 | 41 | [9 empty] | 17 | 21 | 30 | 33 | 34 |  | 37 | 51 | 44 | 40 | 40 | 40 | 40 | 565760
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
147 | Bheramara HVDC | 912 | 912 | 912 | 912 | 913 | 913 | 912 | 913 | 912 | 913 | 912 | 914 | 914 | 913 | 913 | 914 | 913 | 770 |  | 770 | 774 | 774 | 918 | 917 | 918 | 922 | 21621600
148 | Bheramara 410 MW CCPP | 289 | 289 | 298 | 302 | 310 | 315 | 315 | 314 | 305 | 305 | 305 | 305 | 293 | 293 | 290 | 284 | 250 | 272 |  | 273 | 273 | 272 | 273 | 272 | 272 | 272 | 7104096
149 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1220 | 1200 | 1200 | 1200 | 1244 | 1244 | 1230 | 1200 | 1200 | 1200 |  | 1230 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 31409400
150
151 | Barapukuria TPP Unit-1 | 65 | 65 | 66 | 64 | 64 | 64 | 62 | 63 | 63 | 62 | 62 | 62 | 61 | 61 | 61 | 63 | 62 | 63 |  | 62 | 62 | 62 | 62 | 63 | 62 | 63 | 1505454
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4171000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 46 | 46 | [14 empty] | 36 | 38 |  | 45 | 45 | 47 | 46 | 42 | 47 | 47 | 443284
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 2 | 3 | 5 | 1 | 3 | 2 | 1 | 0 | [9 empty] | 24240
157 | Sirajganj 68 MW Solar Park | [6 empty] | 6 | 20 | 34 | 46 | 36 | 39 | 33 | 42 | 21 | 11 | 1 | [9 empty] | 277504
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 174 | 174 | 174 | 174 | 175 | 179 | 183 | 150 | 150 | 150 | 150 | 169 | 177 | 171 | 169 | 165 | 140 | 147 |  | 161 | 163 | 162 | 163 | 162 | 162 | 163 | 4031273
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 414 | 319 | 336 | 340 | 352 | 340 | 414 | 353 | 341 | 300 | 340 | 414 | 414 | 414 | 404 | 412 | 316 | 396 |  | 414 | 387 | 389 | 394 | 414 | 401 | 414 | 9166545
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | 18 | 18 | [14 empty] | 5 | 5 |  | 28 | 26 | 28 | 22 | 22 | 22 | 18 | 161865
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 195948
166 | Amnura 50 MW PP(Sinha)
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | 37 | 21 | [13 empty] | 7 | 21 | 44 |  | 47 | 47 | 46 | 39 | 39 | 39 | 32 | 326615
169 | Santahar 50 MW Peaking PP | 15 | 15 | [14 empty] | 6 | 15 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 181108
170 | Natore 52 MW PP (Rajlanka)
171 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 77 | 93 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 736864
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 50 | [8 empty] | 9 | 35 | 35 | 35 | 72 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1499424
173 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 90 | 113 |  | 113 | 113 | 38 | 38 | 35 | 35 | 35 | 1205376
175 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 38 | 34 |  | 35 | 60 | 70 | 70 | 70 | 70 | 34 | 966076
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 3 | 4 | 6 | 1 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 33097
| Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 74 | [7 empty] | 72 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1916160
| Intraco Solar 30 MW | [6 empty] | 3 | 7 | 17 | 24 | 29 | 6 | 26 | 14 | 16 | 7 | 1 | [9 empty] | 160468
178 | Adani Power Jharkhanda Ltd | 1015 | 1017 | 1015 | 1014 | 1015 | 1012 | 1017 | 1019 | 1012 | 1015 | 1018 | 1017 | 1014 | 1021 | 1015 | 1008 | 1006 | 1016 |  | 1021 | 1016 | 1017 | 1019 | 1020 | 1017 | 1016 | 24432574
| Teesta Solar Limited | [6 empty] | 14 | 37 | 84 | 131 | 100 | 110 | 118 | 114 | 81 | 33 | 6 | [9 empty] | 848160