## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-11-02 | Saturday
|  | Date (day): | 2024-11-02 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12007.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13162 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-11-01 | 2024-11-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 404 | 413 | 400 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 15 | 15 | 25
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 13 | 13 | 62 |  | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 140 | 202 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 330 | 300 | 330
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 0 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 63 | 148 | 48 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 17 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 17 | 35 | 20 |  | Fuel shortage
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 44 | 41 | 43 | 43 |  | 37 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 32 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 34 | 16 | 34 | 18 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 30 | 30 | 100 | 270 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 87 | 72 | 100 | 49 |  | Fuel shortage
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 70 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 2 | 0 | 16 | 88 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 90 | 17 | 90 | 72 |  | Fuel shortage
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 18 | 36 | 36 | 36 |  | 19 | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1461 | 2165 | 1646 | 2074 | 2987 | 832
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 8 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 40 | 26 | 40 |  | 10 | Engine problem
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 176 | 175 | 176 | 176 | 54 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 226 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 48 | 71 | 70 | 71 |  | 27 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 67 | 84 | 84 | 84 |  | 18 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 88 | 50 | 88 |  | 12 | Engine problem
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 25 | 20 | 10 | 20
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 17 | 25 | 25 | 83 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 50 | 52 | 52 | 52 | 248 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 35 | 35 | 19 |  | Fuel shortage
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 51 | 17 | 17 | 51 | 65 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 54 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 460 | 418 | 400 | 415 | 809 |  | Coal shortage
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 10 | 5 | 10 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 0 | 0 | 0 | 0 | 1150 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1286 | 1370 | 1271 | 1523 | 2877 | 397
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 216 | 214 | 215 | 215
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 310 | 300 | 310 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 393 | 393 | 400 | 400
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 41 | 40 | 40 | 40
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 5 | 10 | 10 | 10 | 45 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 45 | 38 | 45 | 150 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 43 | 50 | 40 | 100 | 50 |  | Fuel shortage
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 42 | 42 | 42 | 42 |  | 10 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 18 | 34 | 17 | 34 | 166 |  | Fuel shortage
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 62 | 66 | 66 | 86
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 34 | 34 | 43 |  | 9 | Engine problem
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 15 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 66 | 106 | 52 | 106
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 67 | 77 | 47 | 77 | 36 |  | Fuel shortage
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 87 | 35 | 90 | 25 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 68 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1550 | 1624 | 1525 | 1717 | 585 | 386
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 25 | 33 | 28 | 40 | 162 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 96 | 96 | 96 | 96 | 104 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 56 | 55 | 56 | 59 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 29 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 18 | 0 | 18
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 35 | 19 |  | Fuel shortage
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 0 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 231 | 220 | 247.6 | 245 | 162 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 130 | 163 | 163
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract Expired
90 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 |  | 6 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 57 | 55 | 60 | 60
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 11 | 11 | 10 | 11 | 75 |  | Gas shortage
94 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 208 | 207 | 210 | 210 |  | 21 | Machine problem
96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 13 | 13 |  | 12 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 290 | 300 | 300 |  |  | FGMO
99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 383 | 385 | 385 |  |  | FGMO
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 340 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1468 | 1466 | 1581 | 1582 | 140 | 499
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 923 | 777 | 940 | 940
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 15 | 21 | 20 | 35 |  | 19 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 14 | 37 | 30 | 50 |  | 59 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 270 | 370 | 300 | 350 | 60 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 0 | 17 | 88 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 68 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 373 | 627 | 370 | 620 | 614 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1663 | 1849 | 1760 | 2012 | 1344 | 78
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 16 |  |  | fuel shoprtage
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 9 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 127 | 123 | 100 | 123 |  | 71 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1200 | 1200 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  | 307 | Under maint
118 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1530 | 1718 | 1607 | 1763 | 0 | 378
119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 38 | 38 | 35 | 45 |  | 7 | Engine problem
121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 20 | 0 | 25 |  | 46 | Engine problem
122 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 30 | 35 | 26 | 40 |  | 10 | Engine problem
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 181 | 160 | 170 | 170 | 40 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 336 | 320 | 414 | 414
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 22 | 28 | 22 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 5 | 8 |  | 3 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 50 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 24 | 35 | 113 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 113 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 735 | 729 | 730 | 730
135 | Sirajganj 68 MW Solar Park |  | Solar | NWPGCL | 68 | 68 | 68 | 44 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 102 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1557 | 1501 | 1760 | 1783 | 703 | 95
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 64 | 64 | 65 | 65 |  | 20
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 120 | 170 | 170 | 170 |  | 104 | Machine problem
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 40 | 113 | 113
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 95 | 115 | 54 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 123 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 453 | 389 | 610 | 463 | 40 | 209
| Total |  |  |  |  | 27791 | 27086 | 11199 | 12302 | 12007.6 | 13162 | 8838 | 2874
A. |  | 2024-11-01 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 12310 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 10233 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12302 | MW
3 | Day peak Generation : |  |  | 11199 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11885.87 | MW
4 | Evening peak Generation : |  |  | 12302 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 274.8461 | MKWHr | By Solar | 3.2074 | MKWHr
| By Gas : | 125.8282 | MKWHr |  | By Oil: | 42.9793 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 58.3699 | MKWHr |  | By Hydro: | 4.0454 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 16.8873 | MKWHr |  | By Wind: | 0.08112 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 8838 | MW | Dhaka | 4283.77 | 4283.77 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2874 | MW | Chittagong | 1119.5 | 1119.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 11712 | MW | Khulna | 1480 | 1480 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 910.28 | MMCFD | **Import Adani: | Taka | 111624874.53 | Rajshahi | 1137.6 | 1137.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 376110331.148 | ii) Oil : | Taka | 786070750.34 | Comilla | 1250 | 1250 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 406838865.79 | Total | Taka | 1680644821.808 | Mymensingh | 1008 | 1008 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 11381.7 | MKWHr. | Sylhet | 527 | 527 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 760 | MW (W to E) at | 19:00 | hrs | Barisal | 417 | 417 |  | 0 |  | 24:00 |  | 246
| iii) Maximum : |  |  | 760 | MW at | 19:00 | hrs | Rangpur | 663 | 663 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.9°C |  |  | Total | 11885.87 | 11885.87 |  | 0
B. |  | 2024-11-02 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.9°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13162 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11400 | MW
4 | Reserve(Generation end) |  |  |  | 162 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 290.2518 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9970 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8655 | MKWHr. | ii) HVDC Flow at Peak Time |  | 777 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.5821 | MKWHr. | iii) Maximum HVDC Flow : |  | 923 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 101.6 |  | (b) Today: | 101.35 |  | (c) Rule Curve: |  | 109

## YesterdayGen
2024-11-01 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 210 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 33 | 8 | 0 | 136 | 40 | 0 | 0 | 20 | 222 | 0 | 0 | 0 |  | 6 | 71 | 84 | 0 | 0 | 20 | 0 | 29 | 0 | 0 | 0 | 350 | 0 | 213 | 8 | 50 | 43 | 5 | 0 | 51 | 0 | 43 | 8 | 0 | 0 | 0 | 18 | 76 | 31 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 163 | 0 | 58 | 11 | 0 | 205 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 35 | 0 | 50 | 17 | 68 | 336 | 57 | 105 | 0 | 0 | 52 | 35 | 17 | 17 | 29 | 12 | 395 | 0 | 0 | 17 | 20 | 0 | 17 | 0 | 34 | 36 | 350 | 17 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 922 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 19 | 31 | 0 | 127 | 9 | 0 | 0 | 0 | 0 | 30 | 7 | 95 | 0 | 0 | 25 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 105 | 0 | 111 | 0 | 0 | 113 | 1244 | 220 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 367 | 0 | 0 | 730 | 0 | 0 | 0 | 0 | 0 |  | 5946 | 5390 | 11336 | 3554 | 922 | 1680 | 0 | 1277 | 2429 | 176 | 0 | 492 | 76 | 730 | 0 | 0 | 1684.62 | 101.65
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 210 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 25 | 33 | 8 | 0 | 136 | 40 | 0 | 0 | 25 | 223 | 0 | 0 | 0 |  | 4 | 71 | 84 | 0 | 0 | 19 | 0 | 30 | 0 | 0 | 0 | 350 | 0 | 213 | 8 | 50 | 43 | 5 | 0 | 51 | 0 | 43 | 8 | 0 | 0 | 0 | 18 | 72 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 163 | 0 | 55 | 11 | 0 | 205 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 35 | 0 | 50 | 17 | 87 | 336 | 57 | 105 | 0 | 0 | 52 | 35 | 17 | 52 | 28 | 12 | 395 | 0 | 0 | 17 | 17 | 0 | 17 | 0 | 34 | 36 | 350 | 17 | 0 | 582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 922 | 0 | 279 | 0 | 0 | 0 | 0 | 0 | 19 | 31 | 0 | 127 | 9 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 105 | 0 | 111 | 0 | 0 | 113 | 1244 | 220 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 370 | 0 | 0 | 735 | 0 | 0 | 0 | 0 | 0 |  | 5984 | 5298 | 11282 | 3547 | 922 | 1681 | 0 | 1329 | 2430 | 176 | 0 | 390 | 72 | 735 | 0 | 0 | 1115.44 | 101.64
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 180 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 25 | 32 | 8 | 0 | 136 | 40 | 0 | 0 | 25 | 223 | 0 | 0 | 0 |  | 6 | 71 | 84 | 0 | 0 | 29 | 0 | 30 | 0 | 0 | 0 | 310 | 0 | 214 | 8 | 50 | 43 | 5 | 0 | 51 | 0 | 43 | 8 | 0 | 0 | 0 | 18 | 76 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 163 | 0 | 55 | 11 | 0 | 205 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 34 | 0 | 50 | 17 | 84 | 336 | 57 | 105 | 0 | 0 | 52 | 35 | 17 | 52 | 28 | 12 | 400 | 0 | 0 | 17 | 17 | 0 | 17 | 0 | 33 | 36 | 350 | 17 | 0 | 582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 922 | 0 | 279 | 0 | 0 | 0 | 0 | 0 | 19 | 31 | 0 | 127 | 10 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 1244 | 220 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 371 | 0 | 0 | 731 | 0 | 0 | 0 | 0 | 0 |  | 5885 | 5306 | 11191 | 3477 | 922 | 1677 | 0 | 1344 | 2430 | 176 | 0 | 358 | 76 | 731 | 0 | 0 | 963.595 | 101.63
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 183 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 25 | 32 | 8 | 0 | 136 | 40 | 0 | 0 | 25 | 227 | 0 | 0 | 0 |  | 6 | 71 | 84 | 0 | 0 | 33 | 0 | 20 | 0 | 0 | 0 | 310 | 0 | 217 | 8 | 50 | 43 | 5 | 0 | 51 | 0 | 43 | 8 | 0 | 0 | 0 | 18 | 72 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 163 | 0 | 56 | 11 | 0 | 205 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 35 | 0 | 50 | 17 | 85 | 335 | 56 | 105 | 0 | 0 | 52 | 35 | 17 | 52 | 28 | 12 | 395 | 0 | 0 | 17 | 17 | 0 | 17 | 0 | 34 | 36 | 350 | 17 | 0 | 582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 923 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 19 | 31 | 0 | 127 | 10 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 1244 | 220 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 371 | 0 | 0 | 734 | 0 | 0 | 0 | 0 | 0 |  | 5869 | 5283 | 11152 | 3507 | 923 | 1624 | 0 | 1350 | 2430 | 176 | 0 | 336 | 72 | 734 | 0 | 0 | 571.09 | 101.62
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 183 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 25 | 33 | 8 | 0 | 136 | 40 | 0 | 0 | 25 | 227 | 0 | 0 | 0 |  | 6 | 71 | 84 | 0 | 0 | 33 | 0 | 20 | 0 | 0 | 0 | 330 | 0 | 214 | 8 | 50 | 43 | 5 | 0 | 51 | 0 | 43 | 8 | 0 | 0 | 0 | 18 | 76 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 120 | 0 | 56 | 11 | 0 | 207 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 30 | 0 | 0 | 95 | 0 | 35 | 0 | 50 | 17 | 84 | 321 | 57 | 105 | 0 | 0 | 52 | 35 | 17 | 52 | 28 | 12 | 400 | 0 | 0 | 17 | 17 | 0 | 17 | 0 | 34 | 36 | 350 | 17 | 0 | 582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 922 | 0 | 289 | 0 | 0 | 0 | 0 | 0 | 19 | 27 | 0 | 127 | 10 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 113 | 0 | 111 | 0 | 0 | 95 | 1244 | 220 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 372 | 0 | 0 | 736 | 0 | 0 | 0 | 0 | 0 |  | 5854 | 5216 | 11070 | 3528 | 922 | 1544 | 0 | 1331 | 2431 | 176 | 0 | 326 | 76 | 736 | 0 | 0 | 315.15 | 101.61
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 182 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 25 | 33 | 8 | 0 | 136 | 40 | 0 | 0 | 20 | 226 | 0 | 0 | 0 |  | 6 | 71 | 84 | 0 | 0 | 33 | 0 | 23 | 0 | 0 | 0 | 310 | 0 | 217 | 8 | 50 | 43 | 5 | 0 | 51 | 0 | 43 | 25 | 0 | 0 | 0 | 18 | 66 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 120 | 0 | 61 | 11 | 0 | 206 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 30 | 0 | 0 | 95 | 0 | 35 | 0 | 50 | 17 | 65 | 311 | 57 | 105 | 0 | 0 | 52 | 35 | 17 | 52 | 28 | 12 | 400 | 1 | 0 | 17 | 17 | 0 | 17 | 0 | 34 | 36 | 393 | 17 | 0 | 582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 922 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 19 | 27 | 0 | 127 | 8 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 113 | 0 | 50 | 0 | 0 | 50 | 1244 | 220 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 372 | 0 | 0 | 733 | 0 | 0 | 0 | 0 | 0 |  | 5878 | 5081 | 10959 | 3572 | 922 | 1515 | 0 | 1219 | 2431 | 176 | 0 | 325 | 66 | 733 | 0 | 0 | 230.155 | 101.6
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 |  | 0 | 380 | 0 | 0 | 0 | 30 | 182 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 25 | 10 | 8 | 0 | 134 | 40 | 0 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 71 | 84 | 0 | 0 | 33 | 0 | 25 | 0 | 0 | 0 | 290 | 0 | 216 | 36 | 50 | 43 | 5 | 0 | 51 | 0 | 43 | 25 | 0 | 0 | 0 | 18 | 62 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 120 | 0 | 59 | 11 | 0 | 206 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 35 | 3 | 50 | 17 | 51 | 311 | 57 | 70 | 0 | 1 | 49 | 35 | 17 | 52 | 28 | 12 | 400 | 14 | 3 | 17 | 17 | 0 | 17 | 4 | 35 | 0 | 400 | 17 | 0 | 582 | 22 | 0 | 0 | 0 | 5 | 0 | 0 |  | 918 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 19 | 27 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 1140 | 180 | 0 | 17 | 0 | 7 | 55 | 0 | 0 | 374 | 1 | 0 | 733 | 10 | 0 | 0 | 3 | 9 |  | 5707 | 4817 | 10524 | 3479 | 918 | 1443 | 0 | 1000 | 2329 | 174 | 0 | 318 | 62 | 733 | 46 | 22 | 101.23 | 101.59
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 |  | 0 | 380 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 22 | 25 | 33 | 8 | 0 | 135 | 40 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 70 | 84 | 0 | 0 | 26 | 0 | 27 | 0 | 0 | 0 | 290 | 0 | 216 | 36 | 70 | 43 | 5 | 0 | 51 | 0 | 43 | 25 | 0 | 0 | 0 | 18 | 56 | 29 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 120 | 0 | 58 | 11 | 0 | 206 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 35 | 9 | 50 | 17 | 51 | 300 | 58 | 70 | 0 | 2 | 50 | 35 | 17 | 52 | 29 | 12 | 400 | 14 | 11 | 17 | 17 | 0 | 17 | 11 | 35 | 25 | 393 | 17 | 0 | 500 | 5 | 0 | 0 | 0 | 18 | 0 | 0 |  | 922 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 14 | 27 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 1110 | 180 | 0 | 17 | 1 | 23 | 54 | 0 | 0 | 377 | 7 | 0 | 736 | 4 | 0 | 0 | 12 | 34 |  | 5580 | 4845 | 10425 | 3342 | 922 | 1448 | 0 | 1054 | 2220 | 175 | 0 | 335 | 56 | 736 | 132 | 5 | 62 | 101.58
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 340 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 25 | 33 | 26 | 0 | 136 | 40 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 60 | 84 | 0 | 0 | 26 | 0 | 29 | 0 | 0 | 0 | 290 | 0 | 215 | 36 | 50 | 43 | 5 | 0 | 51 | 0 | 43 | 25 | 0 | 0 | 0 | 18 | 56 | 27 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 120 | 0 | 40 | 11 | 0 | 207 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 35 | 14 | 50 | 17 | 48 | 333 | 58 | 35 | 0 | 2 | 50 | 35 | 17 | 52 | 29 | 12 | 400 | 14 | 17 | 17 | 17 | 0 | 17 | 19 | 34 | 36 | 370 | 17 | 0 | 500 | 0 | 0 | 0 | 0 | 38 | 0 | 0 |  | 922 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 14 | 16 | 0 | 81 | 5 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 1040 | 180 | 0 | 17 | 2 | 37 | 54 | 0 | 0 | 373 | 9 | 0 | 736 | 36 | 0 | 0 | 33 | 59 |  | 5502 | 4731 | 10233 | 3273 | 922 | 1397 | 0 | 943 | 2147 | 176 | 0 | 316 | 56 | 736 | 267 | 0 | 45 | 101.57
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 |  | 0 | 340 | 0 | 0 | 0 | 30 | 0 | 0 | 99 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 25 | 33 | 17 | 0 | 136 | 40 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 61 | 66 | 0 | 0 | 26 | 0 | 20 | 0 | 0 | 0 | 290 | 0 | 214 | 36 | 50 | 42 | 5 | 0 | 51 | 0 | 43 | 34 | 0 | 0 | 0 | 16 | 54 | 27 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 120 | 0 | 40 | 11 | 0 | 208 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 35 | 9 | 50 | 17 | 31 | 385 | 58 | 35 | 0 | 3 | 50 | 35 | 17 | 52 | 29 | 12 | 350 | 0 | 34 | 17 | 17 | 0 | 17 | 26 | 34 | 17 | 340 | 17 | 0 | 501 | 0 | 0 | 0 | 0 | 56 | 0 | 0 |  | 923 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 14 | 16 | 0 | 81 | 5 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 8 | 65 | 0 | 130 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 180 | 0 | 17 | 4 | 57 | 35 | 0 | 0 | 373 | 17 | 0 | 736 | 96 | 0 | 0 | 46 | 82 |  | 5546 | 4756 | 10302 | 3347 | 923 | 1388 | 0 | 839 | 2109 | 176 | 0 | 299 | 54 | 736 | 431 | 0 | 0 | 101.56
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 340 | 0 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 22 | 22 | 17 | 32 | 25 | 0 | 136 | 40 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 4 | 45 | 70 | 0 | 0 | 27 | 0 | 24 | 0 | 0 | 0 | 310 | 0 | 212 | 36 | 50 | 41 | 5 | 0 | 51 | 0 | 43 | 34 | 0 | 0 | 0 | 18 | 60 | 25 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 120 | 0 | 40 | 11 | 0 | 208 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 30 | 0 | 0 | 97 | 0 | 34 | 13 | 50 | 17 | 40 | 385 | 57 | 35 | 0 | 2 | 50 | 35 | 17 | 52 | 29 | 12 | 350 | 0 | 32 | 17 | 17 | 0 | 17 | 29 | 34 | 18 | 340 | 17 | 0 | 456 | 0 | 0 | 0 | 0 | 30 | 0 | 0 |  | 922 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 120 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 180 | 0 | 17 | 4 | 64 | 60 | 0 | 0 | 371 | 18 | 0 | 736 | 64 | 0 | 0 | 52 | 97 |  | 5626 | 4858 | 10484 | 3468 | 922 | 1447 | 0 | 897 | 2061 | 176 | 0 | 311 | 60 | 736 | 406 | 0 | 0 | 101.55
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 420 | 0 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 22 | 22 | 17 | 32 | 25 | 0 | 136 | 40 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 48 | 67 | 0 | 0 | 33 | 0 | 25 | 0 | 0 | 0 | 315 | 0 | 216 | 36 | 50 | 41 | 5 | 0 | 51 | 0 | 42 | 25 | 0 | 0 | 0 | 18 | 62 | 25 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 120 | 0 | 57 | 11 | 0 | 208 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 34 | 8 | 50 | 18 | 43 | 387 | 57 | 105 | 0 | 4 | 50 | 35 | 17 | 66 | 67 | 12 | 350 | 0 | 29 | 35 | 51 | 0 | 17 | 30 | 34 | 18 | 393 | 17 | 0 | 460 | 0 | 0 | 0 | 0 | 68 | 0 | 0 |  | 923 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 30 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 120 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 24 | 0 | 34 | 0 | 2 | 35 | 1200 | 180 | 0 | 17 | 2 | 68 | 95 | 0 | 0 | 373 | 15 | 0 | 735 | 123 | 0 | 0 | 44 | 102 |  | 5996 | 5203 | 11199 | 3553 | 923 | 1480 | 0 | 1201 | 2217 | 176 | 0 | 356 | 62 | 735 | 496 | 0 | 0 | 101.54
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 420 | 0 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 16 | 14 | 17 | 31 | 25 | 0 | 134 | 40 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 61 | 84 | 0 | 0 | 33 | 0 | 28 | 0 | 0 | 0 | 315 | 0 | 213 | 36 | 50 | 41 | 15 | 0 | 51 | 0 | 42 | 25 | 0 | 0 | 0 | 15 | 66 | 22 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 163 | 0 | 54 | 11 | 0 | 208 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 34 | 15 | 50 | 97 | 42 | 387 | 57 | 105 | 0 | 4 | 100 | 35 | 17 | 106 | 66 | 12 | 340 | 0 | 41 | 54 | 53 | 0 | 17 | 28 | 35 | 18 | 395 | 17 | 0 | 465 | 0 | 0 | 0 | 0 | 58 | 0 | 0 |  | 923 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 33 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 117 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 105 | 0 | 45 | 0 | 2 | 70 | 1244 | 220 | 0 | 17 | 4 | 73 | 102 | 0 | 0 | 372 | 6 | 0 | 731 | 143 | 0 | 0 | 39 | 92 |  | 6267 | 5539 | 11806 | 3586 | 923 | 1626 | 0 | 1541 | 2262 | 174 | 0 | 391 | 66 | 731 | 506 | 0 | 0 | 101.53
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 |  | 0 | 420 | 0 | 0 | 0 | 30 | 0 | 0 | 79 | 0 | 8 | 63 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 15 | 17 | 30 | 25 | 0 | 133 | 40 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 6 | 68 | 82 | 0 | 3 | 33 | 0 | 28 | 0 | 0 | 0 | 325 | 0 | 207 | 36 | 50 | 40 | 20 | 0 | 51 | 0 | 42 | 25 | 0 | 0 | 0 | 18 | 66 | 24 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 120 | 0 | 53 | 11 | 0 | 206 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 30 | 0 | 0 | 95 | 0 | 33 | 16 | 50 | 31 | 43 | 343 | 56 | 105 | 0 | 1 | 49 | 35 | 17 | 70 | 66 | 12 | 340 | 0 | 34 | 35 | 17 | 0 | 17 | 23 | 34 | 6 | 393 | 17 | 0 | 462 | 0 | 0 | 0 | 0 | 46 | 0 | 0 |  | 923 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 0 | 81 | 7 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 28 | 0 | 22 | 0 | 0 | 8 | 63 | 0 | 117 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 35 | 0 | 103 | 0 | 2 | 35 | 1244 | 180 | 0 | 17 | 3 | 60 | 75 | 0 | 0 | 372 | 9 | 0 | 733 | 118 | 0 | 0 | 43 | 77 |  | 5807 | 5259 | 11066 | 3357 | 923 | 1509 | 0 | 1221 | 2258 | 173 | 0 | 393 | 66 | 733 | 433 | 0 | 0 | 101.55
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 420 | 0 | 0 | 0 | 30 | 21 | 0 | 80 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 16 | 14 | 17 | 31 | 25 | 0 | 133 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 68 | 82 | 0 | 6 | 33 | 0 | 24 | 0 | 0 | 0 | 290 | 0 | 210 | 36 | 50 | 40 | 20 | 0 | 51 | 0 | 35 | 25 | 0 | 0 | 0 | 18 | 62 | 32 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 163 | 0 | 53 | 11 | 0 | 205 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 30 | 0 | 0 | 95 | 0 | 34 | 11 | 50 | 17 | 42 | 342 | 56 | 88 | 0 | 1 | 49 | 35 | 17 | 70 | 67 | 12 | 340 | 0 | 5 | 35 | 17 | 0 | 17 | 16 | 34 | 18 | 393 | 17 | 0 | 462 | 2 | 0 | 0 | 0 | 25 | 0 | 0 |  | 922 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 0 | 81 | 7 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 117 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 35 | 0 | 111 | 0 | 2 | 35 | 1244 | 220 | 0 | 17 | 2 | 45 | 75 | 0 | 0 | 370 | 12 | 0 | 733 | 77 | 0 | 0 | 29 | 56 |  | 5771 | 5199 | 10970 | 3381 | 922 | 1605 | 0 | 1223 | 2257 | 173 | 0 | 330 | 62 | 733 | 282 | 2 | 0 | 101.51
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 420 | 0 | 0 | 0 | 30 | 38 | 0 | 80 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 16 | 14 | 17 | 31 | 25 | 0 | 133 | 40 | 0 | 0 | 6 | 222 | 0 | 0 | 0 |  | 10 | 68 | 82 | 0 | 5 | 33 | 0 | 19 | 0 | 0 | 0 | 290 | 0 | 210 | 8 | 50 | 40 | 12 | 0 | 51 | 0 | 35 | 25 | 0 | 0 | 0 | 18 | 60 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 163 | 0 | 54 | 11 | 0 | 205 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 30 | 0 | 0 | 55 | 0 | 44 | 5 | 76 | 17 | 42 | 343 | 45 | 52 | 0 | 1 | 52 | 35 | 17 | 52 | 67 | 12 | 310 | 0 | 8 | 35 | 17 | 0 | 17 | 7 | 34 | 17 | 393 | 17 | 0 | 430 | 6 | 0 | 0 | 0 | 14 | 0 | 0 |  | 923 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 45 | 0 | 21 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 117 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1244 | 220 | 0 | 17 | 0 | 23 | 0 | 0 | 0 | 371 | 5 | 0 | 724 | 32 | 0 | 0 | 13 | 24 |  | 5630 | 4885 | 10515 | 3450 | 923 | 1550 | 0 | 919 | 2226 | 173 | 0 | 351 | 60 | 724 | 133 | 6 | 0 | 101.5
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 320 | 0 | 0 | 0 | 30 | 260 | 0 | 80 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 20 | 17 | 35 | 0 | 16 | 14 | 17 | 31 | 25 | 0 | 134 | 40 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 18 | 68 | 82 | 0 | 9 | 33 | 0 | 23 | 0 | 0 | 0 | 290 | 0 | 212 | 8 | 50 | 40 | 7 | 0 | 51 | 0 | 35 | 8 | 0 | 0 | 0 | 18 | 58 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 120 | 0 | 55 | 11 | 0 | 205 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 30 | 0 | 0 | 55 | 0 | 17 | 0 | 88 | 17 | 42 | 343 | 45 | 52 | 0 | 0 | 52 | 35 | 17 | 34 | 68 | 12 | 310 | 0 | 0 | 17 | 17 | 0 | 17 | 1 | 50 | 17 | 300 | 17 | 0 | 422 | 7 | 0 | 0 | 0 | 1 | 0 | 0 |  | 922 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 38 | 0 | 55 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 117 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 180 | 0 | 17 | 0 | 4 | 0 | 0 | 0 | 375 | 1 | 0 | 731 | 3 | 0 | 0 | 1 | 3 |  | 5548 | 4642 | 10190 | 3471 | 922 | 1351 | 0 | 903 | 2178 | 174 | 0 | 381 | 58 | 731 | 14 | 7 | 0 | 101.49
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 329 | 0 | 201 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 20 | 14 | 17 | 32 | 34 | 0 | 134 | 40 | 0 | 0 | 14 | 225 | 0 | 0 | 0 |  | 18 | 71 | 84 | 0 | 16 | 40 | 0 | 24 | 0 | 0 | 0 | 312 | 0 | 213 | 45 | 50 | 40 | 7 | 0 | 51 | 0 | 35 | 34 | 0 | 0 | 0 | 8 | 70 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 163 | 0 | 55 | 11 | 0 | 205 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 30 | 0 | 0 | 95 | 0 | 33 | 0 | 88 | 28 | 50 | 387 | 47 | 88 | 10 | 0 | 52 | 35 | 17 | 100 | 75 | 12 | 340 | 0 | 0 | 90 | 17 | 0 | 17 | 0 | 52 | 29 | 393 | 90 | 0 | 420 | 8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 808 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 0 | 123 | 9 | 16 | 0 | 0 | 0 | 38 | 5 | 93 | 0 | 0 | 20 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 167 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 17 | 0 | 22 | 0 | 93 | 0 | 0 | 95 | 1200 | 220 | 0 | 150 | 0 | 0 | 28 | 0 | 0 | 623 | 0 | 0 | 729 | 0 | 0 | 0 | 0 | 0 |  | 6697 | 5481 | 12178 | 3995 | 808 | 1625 | 0 | 1677 | 2474 | 174 | 0 | 618 | 70 | 729 | 0 | 8 | 0 | 101.48
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1559.515 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 330 | 0 | 202 | 0 | 8 | 148 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 19 | 22 | 17 | 32 | 34 | 0 | 135 | 40 | 0 | 0 | 17 | 226 | 0 | 0 | 0 |  | 18 | 71 | 84 | 0 | 17 | 40 | 0 | 20 | 0 | 0 | 0 | 310 | 0 | 214 | 45 | 50 | 40 | 10 | 0 | 51 | 0 | 42 | 34 | 0 | 0 | 0 | 15 | 66 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 130 | 0 | 55 | 11 | 0 | 207 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 87 | 0 | 88 | 34 | 50 | 383 | 56 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 77 | 12 | 340 | 2 | 0 | 90 | 17 | 0 | 17 | 0 | 87 | 36 | 393 | 54 | 0 | 418 | 10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 777 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 21 | 37 | 0 | 123 | 9 | 16 | 0 | 0 | 0 | 38 | 20 | 93 | 0 | 0 | 35 | 0 | 28 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 35 | 0 | 40 | 0 | 0 | 35 | 1200 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 627 | 0 | 0 | 729 | 0 | 0 | 0 | 0 | 0 |  | 6845 | 5457 | 12302 | 4007 | 777 | 1561 | 0 | 1827 | 2479 | 175 | 0 | 671 | 66 | 729 | 0 | 10 | 0 | 101.45
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 326 | 0 | 115 | 0 | 8 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 19 | 22 | 17 | 32 | 34 | 0 | 136 | 40 | 0 | 0 | 17 | 226 | 0 | 0 | 0 |  | 18 | 71 | 84 | 0 | 18 | 40 | 0 | 20 | 0 | 0 | 0 | 345 | 0 | 211 | 45 | 50 | 39 | 10 | 0 | 51 | 0 | 42 | 43 | 0 | 0 | 0 | 12 | 66 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 9 | 163 | 0 | 55 | 11 | 0 | 0 | 0 | 0 | 0 | 330 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 87 | 0 | 88 | 34 | 45 | 387 | 56 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 77 | 12 | 375 | 10 | 0 | 90 | 17 | 0 | 30 | 0 | 92 | 36 | 393 | 54 | 0 | 420 | 13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 777 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 0 | 123 | 10 | 16 | 0 | 0 | 0 | 38 | 23 | 93 | 0 | 0 | 37 | 0 | 28 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1220 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 623 | 0 | 0 | 729 | 0 | 0 | 0 | 0 | 0 |  | 6707 | 5579 | 12286 | 3788 | 777 | 1733 | 0 | 1852 | 2495 | 176 | 0 | 657 | 66 | 729 | 0 | 13 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 325 | 0 | 0 | 0 | 8 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 19 | 23 | 17 | 32 | 34 | 0 | 136 | 40 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 18 | 71 | 84 | 0 | 20 | 26 | 0 | 35 | 0 | 0 | 0 | 350 | 0 | 212 | 30 | 50 | 41 | 10 | 0 | 51 | 0 | 42 | 43 | 0 | 0 | 0 | 18 | 66 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 27 | 163 | 0 | 54 | 83 | 0 | 0 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 30 | 0 | 0 | 97 | 0 | 87 | 0 | 88 | 34 | 45 | 387 | 55 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 77 | 12 | 385 | 12 | 0 | 90 | 17 | 0 | 33 | 0 | 92 | 36 | 393 | 54 | 0 | 408 | 10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 778 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 20 | 36 | 0 | 123 | 10 | 16 | 0 | 0 | 0 | 38 | 23 | 93 | 0 | 0 | 37 | 0 | 28 | 0 | 0 | 8 | 63 | 0 | 170 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1220 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 625 | 0 | 0 | 729 | 0 | 0 | 0 | 0 | 0 |  | 6661 | 5602 | 12263 | 3712 | 778 | 1803 | 0 | 1845 | 2486 | 176 | 0 | 658 | 66 | 729 | 0 | 10 | 0 | 101.46
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 325 | 0 | 0 | 0 | 8 | 134 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 18 | 22 | 17 | 32 | 34 | 0 | 86 | 40 | 0 | 0 | 17 | 224 | 0 | 0 | 0 |  | 18 | 71 | 84 | 0 | 25 | 26 | 0 | 41 | 0 | 0 | 0 | 350 | 0 | 210 | 8 | 70 | 41 | 10 | 0 | 51 | 0 | 42 | 43 | 0 | 0 | 0 | 15 | 66 | 54 | 0 | 0 | 0 | 0 | 30 | 0 | 32 | 163 | 0 | 53 | 83 | 0 | 0 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 30 | 0 | 0 | 97 | 0 | 90 | 0 | 88 | 34 | 45 | 389 | 56 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 78 | 12 | 388 | 16 | 0 | 90 | 17 | 0 | 35 | 0 | 92 | 36 | 393 | 54 | 0 | 407 | 3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 919 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 17 | 36 | 0 | 123 | 10 | 16 | 0 | 0 | 0 | 38 | 24 | 93 | 0 | 0 | 37 | 0 | 28 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 50 | 0 | 68 | 0 | 0 | 70 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 624 | 0 | 0 | 727 | 0 | 0 | 0 | 0 | 0 |  | 6610 | 5691 | 12301 | 3611 | 919 | 1792 | 0 | 1890 | 2509 | 126 | 0 | 658 | 66 | 727 | 0 | 3 | 0 | 101.45
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 148 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 23 | 17 | 32 | 34 | 0 | 86 | 40 | 0 | 0 | 17 | 224 | 0 | 0 | 0 |  | 18 | 71 | 84 | 0 | 25 | 26 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 214 | 8 | 50 | 41 | 10 | 0 | 51 | 0 | 43 | 43 | 0 | 0 | 0 | 18 | 68 | 72 | 0 | 0 | 0 | 0 | 30 | 0 | 33 | 163 | 0 | 55 | 80 | 0 | 0 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 30 | 0 | 0 | 98 | 0 | 108 | 0 | 88 | 34 | 50 | 386 | 56 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 77 | 12 | 400 | 16 | 0 | 35 | 17 | 0 | 35 | 0 | 92 | 36 | 393 | 54 | 0 | 407 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 919 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 17 | 36 | 0 | 123 | 10 | 16 | 0 | 0 | 0 | 38 | 24 | 93 | 0 | 0 | 37 | 0 | 28 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 113 | 0 | 90 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 623 | 0 | 0 | 732 | 0 | 0 | 0 | 0 | 0 |  | 6500 | 5810 | 12310 | 3705 | 919 | 1698 | 0 | 1876 | 2508 | 126 | 0 | 673 | 68 | 732 | 0 | 5 | 0 | 101.44
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 17 | 33 | 17 | 0 | 86 | 40 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 18 | 64 | 84 | 0 | 25 | 26 | 0 | 42 | 0 | 0 | 0 | 330 | 0 | 212 | 8 | 70 | 42 | 10 | 0 | 51 | 0 | 43 | 43 | 0 | 0 | 0 | 18 | 70 | 72 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 163 | 0 | 55 | 11 | 0 | 130 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 30 | 0 | 0 | 98 | 0 | 112 | 0 | 50 | 34 | 52 | 373 | 56 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 78 | 12 | 398 | 0 | 0 | 17 | 17 | 0 | 35 | 0 | 61 | 36 | 393 | 17 | 0 | 407 | 9 | 0 | 0 | 0 | 0 | 0 | 0 |  | 920 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 20 | 37 | 0 | 123 | 10 | 16 | 0 | 0 | 0 | 38 | 24 | 94 | 0 | 0 | 37 | 0 | 28 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 113 | 0 | 90 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 625 | 0 | 0 | 727 | 0 | 0 | 0 | 0 | 0 |  | 6375 | 5847 | 12222 | 3869 | 920 | 1618 | 0 | 1738 | 2511 | 126 | 0 | 634 | 70 | 727 | 0 | 9 | 0 | 101.43
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 17 | 33 | 8 | 0 | 130 | 40 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 18 | 71 | 84 | 0 | 25 | 26 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 215 | 8 | 70 | 42 | 10 | 0 | 51 | 0 | 43 | 25 | 0 | 0 | 0 | 18 | 69 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 163 | 0 | 56 | 11 | 0 | 130 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 30 | 0 | 0 | 97 | 0 | 82 | 0 | 50 | 24 | 45 | 371 | 57 | 105 | 0 | 0 | 52 | 35 | 17 | 106 | 77 | 12 | 400 | 0 | 0 | 17 | 17 | 0 | 19 | 0 | 34 | 18 | 393 | 17 | 0 | 406 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 919 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 20 | 37 | 0 | 127 | 10 | 0 | 0 | 0 | 0 | 37 | 7 | 94 | 0 | 0 | 37 | 0 | 15 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 113 | 0 | 90 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 506 | 0 | 0 | 719 | 0 | 0 | 0 | 0 | 0 |  | 6114 | 5728 | 11842 | 3812 | 919 | 1654 | 0 | 1560 | 2390 | 170 | 0 | 544 | 69 | 719 | 0 | 5 | 246 | 101.42
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9208800 | 0 |  | 0 | 9942500 | 0 | 0 | 0 | 653963 | 4081038 | 0 | 1314000 | 0 | 48672 | 1517280 | 0 | 0 | 0 | 0 | 262188 | 270524 | 275344 | 0 | 472200 | 468360 | 478440 | 760600 | 469891 | 0 | 3073375 | 972000 | 0 | 0 | 352189 | 5308173 | 0 | 0 | 0 |  | 249840 | 1594848 | 1937108 | 0 | 182400 | 728160 | 0 | 679680 | 0 | 0 | 0 | 7877100 | 0 | 5191000 | 535273 | 1281630 | 1014840 | 205920 | 0 | 1149432 | 0 | 1016672 | 579648 | 0 | 0 | 0 | 384580 | 1582080 | 779520 | 0 | 0 | 7350 | 0 | 698640 | 0 | 279648 | 3571691 | 0 | 1285152 | 457920 | 0 | 4698100 | 0 | 0 | 0 | 7231500 | 333840 | 48384 | 0 | 747709 | 0 | 0 | 2236800 | 0 | 1192320 | 100440 | 1416000 | 629760 | 1286327 | 8870000 | 1336800 | 2143027 | 102036 | 18723 | 1268345 | 907588 | 425710 | 1639320 | 1244880 | 297600 | 8934500 | 103392 | 218340 | 802080 | 495545 | 0 | 497160 | 192167 | 1120320 | 686520 | 9065000 | 650690 | 0 | 11749089 | 81120 | 0 | 0 | 0 | 346882 | 0 | 0 |  | 21865454 | 0 | 7473312 | 0 | 0 | 0 | 0 | 0 | 395040 | 589312 | 0 | 2805000 | 199719 | 87456 | 0 | 0 | 0 | 765889 | 115590 | 782272 | 0 | 0 | 515735 | 0 | 372884 | 0 | 0 | 190404 | 1485382 | 0 | 3756000 | 0 | 0 | 4453636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8821963 | 52320 | 0 | 1693152 | 0 | 1510953 | 0 | 12894 | 1491552 | 30739400 | 5276730 | 0 | 1372800 | 28680 | 460800 | 1865664 | 0 | 0 | 10640000 | 113267 | 0 | 16887273 | 725760 | 0 | 3393 | 328500 | 650240 |  | 146317683 | 128528426 | 274846109 | 87476249 | 21865454 | 38351976 | 0 | 32725955 | 58369871 | 4045375 | 0 | 10253320 | 1582080 | 16887273 | 3207436 | 81120 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26521344 | 0 |  | 0 | 31617150 | 0 | 0 | 0 | 11522828.06 | 12447165.9 | 0 | 7029900 | 0 | 873662.4 | 29465577.6 | 0 | 0 | 0 | 0 | 4787552.88 | 4263458.24 | 5036041.76 | 0 | 354150 | 0 | 0 | 0 | 8415747.81 | 0 | 0 | 0 | 0 | 0 | 6670459.66 | 16933071.87 | 0 | 0 | 0 |  | 4394685.6 | 28085273.28 | 34693604.28 | 0 | 3569568 | 11985513.6 | 0 | 0 | 0 | 0 | 0 | 21977109 | 0 | 17234120 | 1793164.55 | 4139664.9 | 3420010.8 | 901929.6 | 0 | 4609222.32 | 0 | 18208595.52 | 10468442.88 | 0 | 0 | 0 | 288435 | 10378444.8 | 2424307.2 | 0 | 0 | 0 | 0 | 2605927.2 | 0 | 1272398.4 | 12215183.22 | 0 | 7132593.6 | 2390342.4 | 0 | 13107699 | 0 | 0 | 0 | 22345335 | 250380 | 36771.84 | 0 | 15253263.6 | 0 | 0 | 42968928 | 0 | 20996755.2 | 0 | 25218960 | 10926336 | 21327301.66 | 23505500 | 25479408 | 40203186.52 | 1830525.84 | 0 | 20737440.75 | 17643510.72 | 7637237.4 | 31327405.2 | 24163120.8 | 5300256 | 23765770 | 1764901.44 | 0 | 14670043.2 | 8315245.1 | 0 | 8884249.2 | 0 | 20188166.4 | 11629648.8 | 26923050 | 9161715.2 | 0 | 81891150.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 61441925.74 | 0 | 22046270.4 | 0 | 0 | 0 | 0 | 0 | 7430702.4 | 11084958.72 | 0 | 8863800 | 946668.06 | 1507741.44 | 0 | 0 | 0 | 13717071.99 | 2121076.5 | 13149992.32 | 0 | 0 | 9236813.85 | 0 | 6678352.44 | 0 | 0 | 144135.828 | 16383763.46 | 0 | 31700640 | 0 | 0 | 14696998.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25760131.96 | 893625.6 | 0 | 33558272.64 | 0 | 30098183.76 | 0 | 0 | 29592391.68 | 199191312 | 16410630.3 | 0 | 26563680 | 0 | 0 | 32369270.4 | 0 | 0 | 77672000 | 0 | 0 | 111624874.53 | 0 | 0 | 0 | 0 | 0 |  | 947579907.53 | 804885284.818 | 1752465192.348 | 255848175.338 | 61441925.74 | 120262155.81 | 0 | 603037016.24 | 406838865.79 | 0 | 0 | 183033734.1 | 10378444.8 | 111624874.53 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 420 | 0 | 0 | 0 | 30 | 0 | 0 | 140 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 22 | 22 | 17 | 32 | 25 | 0 | 136 | 40 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 48 | 67 | 0 | 0 | 33 | 0 | 25 | 0 | 0 | 0 | 315 | 0 | 216 | 36 | 50 | 41 | 5 | 0 | 51 | 0 | 42 | 25 | 0 | 0 | 0 | 18 | 62 | 25 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 120 | 0 | 57 | 11 | 0 | 208 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 34 | 8 | 50 | 18 | 43 | 387 | 57 | 105 | 0 | 4 | 50 | 35 | 17 | 66 | 67 | 12 | 350 | 0 | 29 | 35 | 51 | 0 | 17 | 30 | 34 | 18 | 393 | 17 | 0 | 460 | 0 | 0 | 0 | 0 | 68 | 0 | 0 |  | 923 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 30 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 120 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 24 | 0 | 34 | 0 | 2 | 35 | 1200 | 180 | 0 | 17 | 2 | 68 | 95 | 0 | 0 | 373 | 15 | 0 | 735 | 123 | 0 | 0 | 44 | 102 |  | 11199 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 330 | 0 | 202 | 0 | 8 | 148 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 19 | 22 | 17 | 32 | 34 | 0 | 135 | 40 | 0 | 0 | 17 | 226 | 0 | 0 | 0 | 0 | 18 | 71 | 84 | 0 | 17 | 40 | 0 | 20 | 0 | 0 | 0 | 310 | 0 | 214 | 45 | 50 | 40 | 10 | 0 | 51 | 0 | 42 | 34 | 0 | 0 | 0 | 15 | 66 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 130 | 0 | 55 | 11 | 0 | 207 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 87 | 0 | 88 | 34 | 50 | 383 | 56 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 77 | 12 | 340 | 2 | 0 | 90 | 17 | 0 | 17 | 0 | 87 | 36 | 393 | 54 | 0 | 418 | 10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 777 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 21 | 37 | 0 | 123 | 9 | 16 | 0 | 0 | 0 | 38 | 20 | 93 | 0 | 0 | 35 | 0 | 28 | 0 | 0 | 8 | 64 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 35 | 0 | 40 | 0 | 0 | 35 | 1200 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 627 | 0 | 0 | 729 | 0 | 0 | 0 | 0 | 0 |  | 12302 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 25 | 330 | 0 | 0 | 0 | 8 | 149 | 13 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 20 | 23 | 17 | 33 | 34 | 0 | 136 | 40 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 18 | 71 | 84 | 0 | 25 | 40 | 0 | 20 | 0 | 0 |  | 310 | 0 | 215 | 45 | 50 | 40 | 10 | 0 | 51 | 0 | 42 | 43 | 0 | 0 |  | 18 | 86 | 40 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 163 | 0 | 60 | 11 | 0 | 210 | 0 | 0 | 0 | 300 | 13 | 5 | 0 | 100 | 0 | 0 | 96 | 0 | 100 | 0 | 88 | 34 | 100 | 385 | 56 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 77 | 12 | 400 | 16 | 0 | 90 | 51 | 0 | 35 | 0 | 90 | 36 | 400 | 160 | 0 | 415 | 10 | 0 | 0 | 0 |  |  |  |  | 940 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 35 | 50 | 0 | 123 | 10 | 16 | 0 | 0 | 0 | 45 | 25 | 95 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 0 | 730 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 300 | 0 | 0 | 0 | 0 | 48 | 13 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 20 | 23 | 17 | 33 | 16 | 0 | 136 | 40 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 0 | 70 | 84 | 0 | 25 | 26 | 0 | 10 | 0 | 0 | 0 | 300 | 0 | 215 | 38 | 50 | 40 | 10 | 0 | 51 | 0 | 42 | 34 | 0 | 0 |  | 18 | 66 | 28 | 0 | 0 | 1.6 | 0 | 30 | 0 | 5 | 163 | 0 | 60 | 10 | 0 | 210 | 0 | 0 | 0 | 300 | 13 | 5 | 0 | 30 | 0 | 0 | 96 | 0 | 72 | 20 | 50 | 17 | 40 | 385 | 55 | 70 | 17 | 5 | 52 | 35 | 17 | 52 | 47 | 12 | 400 | 0 | 50 | 17 | 17 | 0 | 17 | 35 | 35 | 36 | 400 | 17 | 0 | 400 | 5 | 0 | 0 | 0 | 70 |  |  |  | 940 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 0 | 100 | 10 | 16 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 26 | 0 | 22 | 0 | 0 | 5 | 65 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 1244 | 220 |  | 17 | 6 | 100 | 54 | 0 | 0 | 370 | 30 | 0 | 730 | 170 | 0 |  | 29 | 47 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 20 | 23 | 17 | 0 | 8 | 0 | 134 | 40 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 25 | 12 | 0 | 13 | 0 | 0 | 0 | 310 | 0 | 216 | 45 | 90 | 33 | 10 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 42 | 50 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 120 | 0 | 60 | 11 | 0 | 130 | 0 | 0 | 0 | 290 | 13 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 6 | 9 | 50 | 17 | 54 | 383 | 57 | 52 | 0 | 0 | 52 | 35 | 17 | 17 | 69 | 12 | 400 | 0 | 16 | 0 | 17 | 0 | 0 | 0 | 34 | 18 | 400 | 17 | 0 | 406 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 919 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1080 | 180 | 0 | 17 | 1 | 29 | 35 | 0 | 0 | 370 | 7 | 0 | 727 | 47 | 0 | 0 | 11 | 30 | 0 |  |  |  | 125828225 | 21865454 | 0 | 58369871 | 42979275 | 1582080 | 3207436 | 81120 | 4045375 |  |  |  | 257958836
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 125.8282 | 21.8655 | 0 | 58.3699 | 42.9793 | 1.5821 | 3.2074 | 0.08112 | 4.0454
| Minimum Generation |  | 10233 | 9:00
| Highest Generation |  | 12310 | 22:00 | [129 empty] | 0 | [76 empty] | 257.9588
| Day Peak Generation |  | 11199 | 12:00
| Evening Peak Generation |  | 12302 | 19:00 | [206 empty] | 202699852
| HVDC Max Flow |  | 923 | 4:00 | [206 empty] | 202.6999
| HVDC EvPeak Flow |  | 777 | 19:00
| Load factor L.F |  | 93.03% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-11-02
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-11-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11199 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 9970
Evening Peak Generation : |  |  | 12302 | MW Hour : | 19:00 | Available Max Generation : |  | 13162
E.P. Demand (at gen end) : |  |  | 12302 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13000
Maximum Generation : |  |  | 12310 | MW Hour : | 22:00 | Reserve(Generation end) |  | 162
Total Gen. (MKWH) : |  |  | 274.8461 | System Load Factor : | 93.03% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 760 | MW at | 19:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-11-02
Actual : |  | 101.35 | Ft.(MSL) , | Rule curve : | 109 | Ft.( MSL )
Gas Consumed : |  | Total = | 910.28 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 376110331.148 | Adani : | 111624874.53
|  |  | Coal : | 406838865.79 | Oil: | 786070750.34 | Total: | 1680644821.808
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4695.4665 |  |  | 0 | 0.7946%
Chittagong Area |  | 0 | 0:00 | 1291.088 |  |  | 0 | 2.961%
Khulna Area |  | 0 | 0:00 | 1808.7915 |  |  | 0 | 3.425%
Rajshahi Area |  | 0 | 0:00 | 1572.379 |  |  | 0 | 3.916%
Cumilla Area |  | 0 | 0:00 | 1293.6804 |  |  | 0 | 3.611%
Mymensingh Area |  | 0 | 0:00 | 962.2882 |  |  | 0 | 4.038%
Sylhet Area |  | 0 | 0:00 | 539.2681 |  |  | 0 | 3.223%
Barisal Area |  | 0 | 0:00 | 449.5289 |  |  | 0 | 4.116%
Rangpur Area |  | 0 | 0:00 | 879.1971 |  |  | 0 | 4.105%
Total |  | 0 |  | 13491.6877 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:00 |  | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Transformer-3 oil centrifuge
08:04 | 18:28 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 Project Work S/D from Sirajganj 132/33kV end Due to Bogura-kaliakor
400kv Double Circuit Transmition line Conductor Stinging . and from Bog-Sherpur 132/33kVend.
08:05 | 18:28 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Project Work S/D from Sirajganj 132/33kV end Due to Bogura-kaliakor
400kv Double Circuit Transmition line Conductor Stinging . and from Bog-Sherpur 132/33kVend.
08:23 |  | BSRM-Mirsharai 230 kV Ckt-1 Project Work S/D from Mirsorai 230/33kV end Due to BSRM-Korerhat 400kV double
circuit line tower erection and stringing work and from BSRM 230/33kV end Due to 400kv ESPNER Project
| 08:27 | Kodda 132/33kV S/S Tr-3 (426T) HT is restored.
| 08:29 | Kodda 132/33kV S/S Tr-3 (426T) LT is restored.
08:29 | 11:43 | Jhenaidah 230/132kV S/S Transformer- 1 LT Scheduled S/D Due to OTI meter i installation
08:32 | 11:43 | Jhenaidah 230/132kV S/S Transformer- 1 HT Scheduled S/D Due to OTI Meter installation
08:34 | 17:22 | Ashuganj-Shahjibazar 132kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to Shutdown taken
by Ashuganj Grid.
08:46 | 17:21 | Ashuganj-Shahjibazar 132kV Ckt-1 Project Work S/D from Ashuganj 230/132/33kV end Due to As per instruction of NLDC
| 08:59 | Madaripur 132/33kV S/S T3-426T LT is restored.
| 08:59 | Madaripur 132/33kV S/S T1-405T HT is restored.
| 08:59 | Madaripur 132/33kV S/S T3-426T HT is restored.
| 08:59 | Madaripur 132/33kV S/S T1-405T LT is restored.
| 09:01 | Kushtia 132/33kV S/S T-1 HT is restored.
| 09:04 | Kushtia 132/33kV S/S T-1 LT is restored.
09:04 | 10:20 | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D
09:05 | 10:19 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D
| 09:14 | Barapukuria-Bogura 230 kV Ckt-2 is restored.
10:44 | 15:40 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Scheduled S/D
12:00 |  | Day Peak Generation: 11199 MW.
13:05 | 13:14 | Haripur-Narsingdi 132kV Ckt-1 Tripped from Haripur 230/132kV end showing 1. Generale Trip, 2. Zone 1 Trip,3.
B Phase Trip relays Due to Unknown, Only Haripur Side Trip
13:10 | 14:20 | Thakurgaon 132/33kV S/S T-1(422T) HT Tripped showing Differential Relay B Phase relays Due to 33kV
Baliadangi Feeder Fault
13:10 | 14:20 | Thakurgaon 132/33kV S/S T-1(422T) LT Tripped showing No Relay Operate relays Due to 33kV Baliadangi Feeder Fault
14:04 |  | Siddirganj CCPP 335 MW GT was sync.
| 15:42 | Barapukuria-Bogura 230 kV Ckt-1 is restored.
15:53 |  | Barapukuria-Bogura 230 kV Ckt-2 Project Work S/D from Barapukuria 230/132/33kV end Due to Project work
and from Bogura 400/230kV end Due to work on Barapukuria SS
16:01 |  | Siddirganj CCPP 335 MW ST was sync.
19:00 |  | Evening Peak Gen. 12302 MW
19:09 |  | Sylhet 225 MW CCPP tripped
03:24 | 03:40 | Natore-Rajshahi 132kV Ckt-2 Tripped from Rajshahi 132/33kV end showing SIEMENS SIPROTEC 7SA52
relays Due to Distance Relay Trip, Distance Relay Zone-1 Trip and from Natore 132/33kV end showing
Phase C,zone 2. relays Due to Distance relay operate.
06:00 |  | Minimum Generation = 99,70MW
06:10 |  | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end.
06:12 | 06:31 | Joypurhat 132/33kV S/S Naogaon Ckt.-2 Project Work S/D Due to Project Work of Niamotpur Grid Sub Station
06:14 |  | Naogaon-Niyamatpur 132kV Ckt-1 Project Work S/D from Niamatpur 132/33kV end Due to T-3,Jack bus
stringing কাজের জন্য।
06:21 |  | Niamatpur 132/33kV S/S Transformer-1(407T) LT Project Work S/D Due to T-3,Jack bus stringing কাজের জন্য। |  |  |  |  | 14.0MW load interrup.
06:21 |  | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Project Work S/D Due to T-3,Jack bus stringing কাজের জন্য। |  |  |  |  | 27.0MW load interrup.
06:22 |  | Daudkandi 132/33kV S/S Transformer-1 HT Forced S/D Due to Emergency maintenance work.
06:22 |  | Niamatpur 132/33kV S/S 132kV Rahanpur Ckt-1 Project Work S/D Due to T-3,Jack bus stringing কাজের জন্য।
06:22 |  | Niamatpur 132/33kV S/S 132 kV Rahanpur Ckt-2 Project Work S/D Due to T-3,Jack bus stringing কাজের জন্য।
06:24 |  | Daudkandi 132/33kV S/S Transformer-1 LT Forced S/D Due to Emergency maintenance work.
06:24 |  | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Project Work S/D Due to T-3,Jack bus stringing কাজের জন্য।
06:24 |  | Niamatpur 132/33kV S/S Transformer-1(407T) HT Project Work S/D Due to T-3,Jack bus stringing কাজের জন্য।
07:00 |  | Agrabad 132/33kV S/S Auxiliary Transformer-02 HT Scheduled S/D Due to Annual Maintenance
07:08 |  | Agrabad 132/33kV S/S MTR-02 (416T) HT Scheduled S/D Due to Annual Maintenance
07:11 |  | Coxsbazar 132/33kV S/S 415T-T2 HT Scheduled S/D Due to Transformer-02 Oil Centrifuging by Project |  |  |  |  | 40.0MW load interrup.
07:17 |  | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to TR-02, 33 kv Bus hotspot Maintenance by PBS
07:17 |  | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to TR-02, 33 kv Bus hotspot maintenance by PBS
07:22 |  | Barishal 132/33kV S/S 132 kV Capacitor Bank Scheduled S/D Due to Annual Maintenance Work
07:38 |  | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Scheduled S/D |  |  |  |  | 20.0MW load interrup.
07:40 |  | Kishoreganj 132/33kV S/S Tr-3 (424T) HT Scheduled S/D |  |  |  |  | 42.0MW load interrup.
07:41 |  | Madaripur 132/33kV S/S T2-415T LT Scheduled S/D Due to Annual Maintenance
07:42 |  | Madaripur 132/33kV S/S T2-415T HT Scheduled S/D Due to Annual Maintenance

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-11-01
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 413 | 9208800
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9942500
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 653963 | low demand.
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 202 | 1314000
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 4081038
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 48672 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 262188 | Fuel shortage
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 148 | 1517280
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 270524
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 275344 | Fuel shortage
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 940560 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 478440 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 760600
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 34 | 469891 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 30 | 747709 | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 87 | 1192320 | Fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2143027
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 2 | 103392 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 802080 | Fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 192167
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 686520 | Fuel shortage
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 2165 | 36091015
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 352189
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 100440
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 728160 | Fuel shortage
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 175 | 4045375
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 226 | 5308173
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 102036 | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 71 | 1594848 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 1937108 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 1416000 | Engine problem
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 679680
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 17 | 182400 | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18723
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1268345 | Fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 907588 | Fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 425710 | Fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 297600 | Fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 495545 | Fuel shortage
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 54 | 650690 | low demand.
55 | SS Power I |  | IPP | 2*612 | 1224 | 418 | 11749089 | Coal shortage
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 10 | 81120
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 0 | 0 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1370 | 32340819
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 214 | 5191000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7877100
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 393 | 9065000
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 1014840 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 10 | 205920 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 535273 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1149432
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 1286327 | Fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 42 | 1016672 | Engine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1281630 | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 629760 | Fuel shortage
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 66 | 1582080
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 579648 | Fuel shortage
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 384580 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1639320 | Engine problem
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 77 | 1244880 | Fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 87 | 1120320 | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 346882
| Cumilla Area Total |  |  |  | 2917 | 1624 | 36150664
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 33 | 779520 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7350
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 96 | 2236800 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 56 | 1336800 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 218340
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 249840 | Fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 497160 | Fuel shortage
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 646 | 220 | 5325810
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 698640 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3571691 | frequency control.
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 279648 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 48384 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1285152
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 11 | 457920 | Gas shortage
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 207 | 4698100
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 333840 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7231500 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 383 | 8870000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8934500
| Sylhet Area Total |  |  |  | 2417 | 1466 | 36409375
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 777 | 21865454
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 395040 | Engine problem
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 37 | 589312 | Engine problem
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 7473312
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 52320 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 460800
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 627 | 10640000 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1849 | 41476238
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 87456 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 9 | 199719 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 123 | 2805000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 30739400 | Machine problem.
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5276730
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1372800
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Under maint.
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3393
| Barisal Area Total |  |  |  | 2236 | 1718 | 40484498
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 765889 | Engine problem
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 115590 | Machine problem.
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Lube Oil porblem
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 515735 | Engine problem
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 160 | 4453636 | Gas shortage
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 320 | 8821963 | FGMO
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 372884 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 190404 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 782272 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 1693152 | High voltage
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 1491552 | High voltage
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28680
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 729 | 16887273
135 | Sirajganj 68 MW Solar Park |  | NWPGCL | 68 | 68 | 0 | 328500
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 650240
| Rajshahi Area Total |  |  |  | 3449 | 1501 | 37097770
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 64 | 1485382 | Machine problem.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 3756000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 40 | 1510953 | low demand.
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 12894
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1865664
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 113267
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 725760
| Rangpur Area Total |  |  |  | 950 | 389 | 9469920
| Total |  |  |  | 27086 | 12302 | 274846109
| Eastern Grid Total |  |  |  | 16752 | 6845 | 146317683
| Western Grid Total |  |  |  | 10334 | 5457 | 128528426
| National Grid Total |  |  |  | 27086 | 12302 | 274846109
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-11-2024
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8188.27 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3697.6 | MW
i) Dhaka area |  |  | 4283.77 |  | MW | i) Khulna area |  |  |  | 1480 | MW
ii) Chattogram area |  |  | 1119.5 |  | MW | ii) Barishal area |  |  |  | 417 | MW
iii) Cumilla area |  |  | 1250 |  | MW | iii) Rajshahi area |  |  |  | 1137.6 | MW
iv) Mymensingh area |  |  | 1008 |  | MW | iv) Rangpur area |  |  |  | 663 | MW
v) Sylhet area |  |  | 527 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11885.87 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 3 | 09:00 | 67 | Jashore | 116 | 18:30 | 133 | Rajbari | 66 | 18:00
2 | AKSML | 115 | 12:00 | 68 | Jhenaidah | 113 | 18:30 | 134 | Rajendrapur | 82 | 18:30
3 | Aftabnagar | 48 | 00:00 | 69 | Joydebpur | 160 | 00:00 | 135 | Rajshahi | 97 | 18:00
4 | Agargaon | 102 | 00:00 | 70 | Joypurhat | 52 | 18:00 | 136 | Rajshahi-230 | 70 | 13:00
5 | Agrabad | 84 | 12:00 | 71 | Juldah | 15 | 20:00 | 137 | Ramganj | 110 | 20:00
6 | Amnura | 51 | 18:00 | 72 | KSRM | 38 | 00:00 | 138 | Rampur | 39 | 04:00
7 | Ashuganj | 89 | 23:00 | 73 | Kabirpur | 225 | 00:00 | 139 | Rangamati | 15 | 18:00
8 | BSRM | 68 | 15:00 | 74 | Kachua | 74 | 21:00 | 140 | Rangpur | 109 | 13:00
9 | Bagerhat | 77 | 18:00 | 75 | Kallyanpur | 102 | 01:00 | 141 | Ruppur | 6.4 | 11:00
10 | Bakulia | 84 | 18:30 | 76 | Kalurghat | 32 | 00:00 | 142 | SSM | 12 | 00:00
11 | Banani | 47.8 | 19:30 | 77 | Kamrangirchar | 58 | 00:00 | 143 | Saidpur | 72 | 18:30
12 | Bangabhaban | 5 | 00:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 110 | 19:00
13 | Barapukuria | 41 | 13:00 | 79 | Kazla | 99 | 13:00 | 145 | Satmasjid | 91 | 19:30
14 | Barguna | 20 | 20:00 | 80 | Keranigonj | 64 | 03:00 | 146 | Savar | 156 | 00:00
15 | Barishal | 97 | 13:00 | 81 | Khagrachori | 30 | 18:00 | 147 | SevenRings | 11.44 | 12:00
16 | Barishal-230 | 82 | 18:00 | 82 | Khulna | 73 | 13:00 | 148 | ShahCement | 26 | 01:00
17 | Baroaulia | 64 | 15:00 | 83 | Khulshi | 143 | 12:00 | 149 | Shahjadpur | 68 | 18:30
18 | Baroirhat | 48 | 18:00 | 84 | Kishoreganj | 136 | 20:00 | 150 | Shahjibazar | 121 | 21:00
19 | Bashundhara | 162 | 12:00 | 85 | Kodda | 232 | 02:00 | 151 | Shahmirpur | 39 | 18:00
20 | BashundharaCement | 12 | 00:00 | 86 | Kulaura | 40 | 18:00 | 152 | Shariatpur | 77 | 21:00
21 | Beanibazar | 64 | 18:00 | 87 | Kurigram | 44 | 18:00 | 153 | Sherpur | 116 | 18:30
22 | Benapole | 55 | 21:00 | 88 | Kushtia | 122 | 18:00 | 154 | Shikalbaha | 21 | 03:00
23 | Bhaluka | 114 | 14:00 | 89 | Lalbag | 78 | 00:00 | 155 | Shitalakhya | 67.5 | 00:00
24 | Bhandaria | 48 | 22:00 | 90 | Lalmonirhat | 41 | 18:00 | 156 | Sholosohor | 37 | 22:00
25 | Bhangura | 33 | 18:00 | 91 | MI_Cement | 17.8 | 13:00 | 157 | Shyampur | 154 | 12:00
26 | Bheramara(GK) | 53 | 18:00 | 92 | Madanganj | 36 | 00:00 | 158 | Siddhirganj | 106 | 00:00
27 | Bhulta | 246 | 00:00 | 93 | Madaripur | 92 | 23:00 | 159 | Sirajganj | 72 | 18:00
28 | Bog-Sherpur | 52 | 18:30 | 94 | Madartek | 92 | 00:00 | 160 | Sonargaon | 80 | 08:00
29 | Bogura | 142 | 18:30 | 95 | Madunaghat | 53 | 01:00 | 161 | Sreemongol | 66 | 18:00
30 | Borhanuddin | 80 | 21:00 | 96 | Magura | 55 | 18:00 | 162 | Sreepur | 64 | 04:00
31 | Brahmanbaria | 172 | 22:00 | 97 | Mahasthangarh | 58 | 19:00 | 163 | Srinagar | 44.4 | 21:00
32 | Cantonment | 102 | 12:00 | 98 | Manikganj | 108 | 18:30 | 164 | Sunamganj | 51 | 18:30
33 | Chandpur | 68 | 18:00 | 99 | Maniknagar | 58 | 00:00 | 165 | Sylhet | 42 | 18:30
34 | Chandraghona | 32 | 19:30 | 100 | Matarbari | 46 | 20:00 | 166 | Sylhet-132 | 98 | 18:00
35 | Chapai | 54 | 20:00 | 101 | Matuail | 58 | 00:00 | 167 | TK | 30.6 | 18:30
36 | Charsaidpur | 43 | 04:00 | 102 | Millgate | 103 | 00:00 | 168 | Tangail | 180 | 18:00
37 | Chauddagram | 63 | 19:30 | 103 | Mirpur | 126 | 12:00 | 169 | Thakurgaon | 72 | 18:30
38 | Chhatak | 30 | 18:30 | 104 | Mirsorai | 56 | 20:00 | 170 | Tongi | 114 | 00:00
39 | Chowmuhani | 219 | 22:00 | 105 | Mirzapur | 34 | 18:00 | 171 | Ullahpara | 34 | 18:00
40 | Chuadanga | 95 | 18:00 | 106 | Mithapukur | 46 | 18:00 | 172 | Ullon | 53 | 12:00
41 | Coxsbazar | 113 | 14:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 75 | 18:00
42 | Cumilla(N) | 158 | 20:00 | 108 | Mogbazar | 101.2 | 12:00 | 174 | UttaraNew | 50 | 00:00
43 | Cumilla(S) | 140 | 00:00 | 109 | Mongla | 32 | 01:00 | 175 | Zigatola | 82 | 00:00
44 | Daudkandi | 129 | 19:00 | 110 | Motijheel | 36 | 20:00
45 | Dhaka | 16 | 10:00 | 111 | Munshiganj | 102 | 23:00
46 | Dhamrai | 100 | 04:00 | 112 | Mymensingh | 196 | 13:00
47 | Dhanmondi | 105 | 12:00 | 113 | Naogaon | 103 | 20:00
48 | Dohazari | 104 | 18:00 | 114 | Narail | 50 | 18:00
49 | Faridpur | 134 | 18:30 | 115 | Narinda | 49.5 | 00:00
50 | Fatullah | 81 | 00:00 | 116 | Narshingdi | 180 | 18:30
51 | Fenchuganj | 35 | 18:00 | 117 | Natore | 122 | 19:30
52 | Feni | 104 | 18:00 | 118 | Nawabganj | 43.6 | 21:00
53 | GPH | 95 | 20:00 | 119 | Netrakona | 113 | 19:00
54 | Ghatail | 60 | 18:00 | 120 | New | 40.1 | 00:00
55 | Ghorashal | 51 | 00:00 | 121 | Niamatpur | 54 | 22:00
56 | Goalpara | 28 | 13:00 | 122 | Noapara | 35 | 18:00
57 | Gollamari | 64 | 05:00 | 123 | PHP | 2 | 02:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-11-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 398 | 11:00 | 378 | 00:00 | Kaliakoir | 373 | 08:00 | 366 | 02:00
| Ashuganj | 409 | 8:16 | 398 | 23:00 | Madunaghat | 402 | 09:00 | 395 | 00:00
| Bhulta | 402 | 17:00 | 392 | 00:00 | Meghnaghat | 383 | 17:00 | 375 | 00:00
| Bibiana | 394 | 19:00 | 387 | 00:00 | Payra | 410 | 08:00 | 404 | 00:00
| BIPTC | 401 | 01:00 | 396 | 21:00 | Rahanpur | 396 | 05:00 | 390 | 20:00
| Bogura | 388 | 04:00 | 381 | 20:00 | Rampal | 402 | 08:00 | 391 | 00:00
| Gopalganj | 399 | 17:00 | 390 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 260 | 18:00 | 231 | 19:30 | Haripur | 232 | 17:00 | 224 | 00:00
| AKSML | 240 | 19:00 | 232 | 00:00 | Hasnabad | 232 | 04:00 | 226 | 00:00
| Aminbazar | 235 | 07:00 | 227 | 06:00 | Hathazari | 238 | 08:00 | 233 | 00:00
| Ashuganj | 236 | 08:00 | 230 | 00:00 | Ishurdi | 235 | 09:00 | 230 | 21:00
| Ashuganj-400 | 236 | 08:00 | 230 | 00:00 | Jhenaidah | 228 | 09:00 | 221 | 22:00
| Baghabari | 231 | 04:00 | 227 | 12:00 | Kaliakoir | 233 | 18:30 | 228 | 02:00
| Barapukuria | 225 | 03:00 | 220 | 17:00 | Keranigonj | 232 | 19:00 | 225 | 00:00
| Barapukuria-230 | 225 | 03:00 | 220 | 17:00 | Khulna(S) | 231 | 17:00 | 221 | 21:00
| Barishal | 237 | 07:00 | 232 | 15:00 | Madunaghat | 238 | 09:00 | 235 | 00:00
| Bheramara | 233 | 18:30 | 227 | 21:00 | Maniknagar | 232 | 18:30 | 224 | 00:00
| Bhulta | 234 | 17:00 | 227 | 00:00 | Meghnaghat | 241 | 17:00 | 234 | 00:00
| Bibiana | 226 | 08:00 | 221 | 02:00 | Meghnaghat-400 | 235 | 19:00 | 229 | 00:00
| BIPTC | 234 | 08:00 | 226 | 21:00 | Mirsorai | 239 | 18:30 | 231 | 00:00
| Bogura | 235 | 18:30 | 232 | 10:00 | Rajshahi | 236 | 17:00 | 228 | 13:00
| Bogura-400 | 238 | 06:00 | 233 | 11:00 | Rampal | 229 | 09:00 | 221 | 21:00
| Borhanuddin | 241 | 17:00 | 237 | 23:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 237 | 18:00 | 231 | 01:00 | Rampura | 232 | 18:30 | 225 | 00:00
| Cumilla(N) | 231 | 17:00 | 224 | 00:00 | Shikalbaha | 237 | 19:00 | 232 | 14:00
| Faridpur | 236 | 08:00 | 228 | 21:00 | Shyampur | 233 | 19:00 | 226 | 00:00
| Fenchuganj | 229 | 05:00 | 223 | 23:00 | Siddhirganj | 235 | 17:00 | 227 | 00:00
| Ghorashal | 235 | 08:00 | 230 | 00:00 | Sirajgonj | 241 | 18:30 | 237 | 01:00
| Ghorashal-230 | 232 | 19:00 | 225 | 00:00 | Sreepur | 234 | 17:00 | 229 | 00:00
| Gopalganj | 235 | 17:00 | 230 | 21:00 | Tongi | 231 | 07:00 | 222 | 00:00
| GPH | 237 | 17:00 | 232 | 14:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 139 | 06:00 | 135 | 00:00 | Kushtia | 136 | 05:00 | 132 | 13:00
| Agargaon | 137 | 08:00 | 132 | 00:00 | Lalbag | 137 | 08:00 | 132 | 00:00
| Agrabad | 135 | 00:00 | 133 | 14:00 | Lalmonirhat | 135 | 05:00 | 128 | 17:00
| AKS | 134 | 08:00 | 132 | 00:00 | Madanganj | 132 | 17:00 | 124 | 00:00
| Aminbazar | 140 | 07:00 | 130 | 03:00 | Madaripur | 132 | 07:00 | 128 | 23:00
| Amnura | 140 | 18:00 | 125 | 19:30 | Madartek | 139 | 17:00 | 134 | 00:00
| Ashuganj | 140 | 08:00 | 136 | 00:00 | Madunaghat | 139 | 17:00 | 135 | 00:00
| Bagerhat | 134 | 10:00 | 125 | 21:00 | Magura | 134 | 06:00 | 128 | 21:00
| Bakulia | 136 | 17:00 | 133 | 14:00 | Mahasthangarh | 139 | 03:00 | 136 | 11:00
| Banani | 139 | 08:00 | 133 | 00:00 | Manikganj | 129 | 22:00 | 122 | 02:00
| Bangabhaban | 132 | 19:00 | 127 | 00:00 | Maniknagar | 132 | 18:30 | 127 | 00:00
| Barapukuria | 138 | 03:00 | 133 | 17:00 | Matarbari | 128 | 08:00 | 120 | 12:00
| Barguna | 139 | 18:30 | 131 | 14:00 | Matuail | 133 | 17:00 | 126.5 | 01:00
| Barishal | 131 | 06:00 | 126 | 23:00 | Millgate | 133 | 06:00 | 129 | 00:00
| Barishal-230 | 132 | 09:00 | 127 | 21:00 | Mirpur | 139 | 08:00 | 133 | 00:00
| Baroaulia | 138 | 17:00 | 132 | 00:00 | Mirzapur | 130 | 22:00 | 123 | 18:00
| Baroirhat | 127 | 09:00 | 122 | 00:00 | Mithapukur | 138 | 06:00 | 132 | 10:00
| Bashundhara | 139 | 19:00 | 129 | 00:00 | MI_Cement | 136 | 18:30 | 131 | 00:00
| BashundharaCement | 132 | 17:00 | 124 | 00:00 | Modern | 137 | 17:00 | 134 | 00:00
| Beanibazar | 128 | 07:00 | 120 | 19:30 | Mogbazar | 139 | 06:00 | 135 | 13:00
| Benapole | 134 | 17:00 | 125 | 21:00 | Mongla | 134 | 17:00 | 125 | 21:00
| Bhaluka | 131 | 08:00 | 125 | 01:00 | Motijheel | 132 | 19:00 | 127 | 00:00
| Bhandaria | 127 | 17:00 | 120 | 22:00 | Munshiganj | 131 | 17:00 | 125 | 00:00
| Bhangura | 138 | 01:00 | 136 | 13:00 | Mymensingh | 136 | 23:00 | 122 | 13:00
| Bheramara | 137 | 08:00 | 134 | 21:00 | Naogaon | 140 | 12:00 | 122 | 20:00
| Bheramara(GK) | 137 | 07:00 | 134 | 21:00 | Narail | 133 | 06:00 | 126 | 21:00
| Bhulta | 122 | 09:00 | 115 | 00:00 | Narinda | 132 | 18:30 | 127 | 00:00
| Bog-Sherpur | 141 | 12:00 | 137 | 07:00 | Narshingdi | 124 | 15:00 | 117 | 00:00
| Bogura | 142 | 03:00 | 138 | 20:00 | Natore | 136 | 03:00 | 133 | 21:00
| Bogura-230 | 142 | 03:00 | 139 | 16:00 | Nawabganj | 136 | 07:00 | 132 | 00:00
| Brahmanbaria | 131 | 08:00 | 124 | 23:00 | Netrakona | 135 | 23:00 | 123 | 17:00
| Cantonment | 136 | 08:00 | 132 | 00:00 | New | 138 | 01:00 | 130 | 00:00
| Chandpur | 128 | 12:00 | 120 | 06:00 | Niamatpur | 132 | 06:00 | 128 | 20:00
| Chandraghona | 139 | 02:00 | 134 | 12:00 | Noapara | 135 | 16:00 | 128 | 23:00
| Chapai | 131 | 06:00 | 126 | 21:00 | Pabna | 137 | 06:00 | 133 | 21:00
| Charsaidpur | 131 | 18:00 | 125 | 00:00 | Palashbari | 137 | 06:00 | 131 | 10:00
| Chauddagram | 129 | 19:00 | 124 | 00:00 | Panchagarh | 136 | 04:00 | 121 | 17:00
| Chhatak | 127 | 00:00 | 118 | 19:30 | Patuakhali | 140 | 00:00 | 130 | 15:00
| Chowmuhani | 125 | 12:00 | 118 | 05:00 | Payra | 137 | 00:00 | 133 | 13:00
| Chuadanga | 130 | 07:00 | 122 | 22:00 | PHP | 128 | 13:00 | 122 | 00:00
| Coxsbazar | 129 | 01:00 | 120 | 12:00 | Postogola | 137 | 08:00 | 133 | 00:00
| Cumilla(N) | 133 | 17:00 | 128 | 00:00 | Purbachal | 139 | 07:00 | 130 | 00:00
| Cumilla(S) | 131 | 08:00 | 126 | 00:00 | Purbasadipur | 135 | 02:00 | 124 | 16:00
| Daudkandi | 130 | 08:00 | 123 | 23:00 | Rahanpur | 134 | 01:00 | 131 | 20:00
| Dhaka | 139 | 17:00 | 134 | 00:00 | Rahim | 131 | 17:00 | 126 | 00:00
| Dhamrai | 132 | 08:00 | 129 | 01:00 | Rajbari | 131 | 08:00 | 126 | 21:00
| Dhanmondi | 139 | 07:00 | 134 | 00:00 | Rajendrapur | 133 | 23:00 | 121 | 03:00
| Dohazari | 134 | 08:00 | 129 | 12:00 | Rajshahi | 137 | 08:00 | 133 | 15:00
| Faridpur | 132 | 08:00 | 128 | 21:00 | Rajshahi-230 | 136 | 06:00 | 121 | 20:00
| Fatullah | 137 | 17:00 | 131 | 00:00 | Ramganj | 125 | 13:00 | 117 | 03:00
| Fenchuganj | 134 | 07:00 | 130 | 23:00 | Rampur | 136 | 02:00 | 133 | 11:00
| Feni | 129 | 13:00 | 123 | 00:00 | Rampura | 139 | 08:00 | 134 | 00:00
| Ghatail | 130 | 00:00 | 123 | 18:00 | Rangamati | 136 | 02:00 | 134 | 10:00
| Ghorashal | 139 | 07:00 | 134 | 01:00 | Rangpur | 136 | 05:00 | 127 | 17:00
| Goalpara | 137 | 17:00 | 129 | 21:00 | Ruppur | 138 | 05:00 | 135 | 00:00
| Gollamari | 136 | 09:00 | 131 | 00:00 | Saidpur | 137 | 05:00 | 126 | 17:00
| Gopalganj | 133 | 06:00 | 129 | 20:00 | Satkhira | 134 | 17:00 | 125 | 21:00
| Gopalganj-400 | 133 | 08:00 | 129 | 23:00 | Satmasjid | 136 | 07:00 | 132 | 00:00
| Gulshan | 138 | 06:00 | 134 | 00:00 | Savar | 139 | 18:00 | 132 | 00:00
| Halishahar | 137 | 08:00 | 133 | 23:00 | SevenRings | 139 | 06:00 | 135 | 00:00
| Haripur | 132 | 17:00 | 126 | 00:00 | ShahCement | 131 | 18:00 | 125 | 00:00
| HaripurSBU | 132 | 17:00 | 126 | 00:00 | Shahjadpur | 141 | 17:00 | 138 | 00:00
| Hasnabad | 137 | 08:00 | 133 | 00:00 | Shahjibazar | 130 | 08:00 | 124 | 23:00
| Hathazari | 139 | 17:00 | 136 | 00:00 | Shahmirpur | 137 | 17:00 | 134 | 11:00
| Ishurdi | 138 | 07:00 | 135 | 21:00 | Shariatpur | 132 | 08:00 | 125 | 22:00
| Jaldhaka | 134 | 04:00 | 125 | 17:00 | Sherpur | 135 | 23:00 | 123 | 18:00
| Jamalpur | 138 | 00:00 | 126 | 17:00 | Shikalbaha | 126 | 08:00 | 122 | 23:00
| Jashore | 135 | 17:00 | 127 | 22:00 | Shikalbaha-230 | 137 | 02:00 | 128 | 08:00
| Jhenaidah | 136 | 08:00 | 130 | 21:00 | Shitalakhya | 136 | 18:30 | 131 | 00:00
| Jhenaidah-230 | 136 | 17:00 | 130 | 21:00 | Sholosohor | 136 | 08:00 | 134 | 05:00
| Joydebpur | 137 | 18:30 | 132 | 00:00 | Shyampur | 133 | 18:30 | 127 | 13:00
| Joypurhat | 129 | 05:00 | 122 | 19:30 | Shyampur-230 | 136 | 19:00 | 130 | 00:00
| Juldah | 138 | 17:00 | 135 | 00:00 | Siddhirganj | 133 | 17:00 | 128 | 00:00
| Kabirpur | 133 | 19:00 | 125 | 16:00 | Sirajganj | 138 | 05:00 | 135 | 13:00
| Kachua | 128 | 17:00 | 122 | 02:00 | Sonargaon | 131 | 17:00 | 125 | 00:00
| Kaliakoir | 135 | 08:00 | 129 | 18:00 | Sreemongol | 130 | 08:00 | 125 | 18:30
| Kallyanpur | 132 | 08:00 | 128 | 01:00 | Sreepur | 132 | 07:00 | 130 | 00:00
| Kalurghat | 137 | 17:00 | 134 | 01:00 | Srinagar | 136 | 17:00 | 132 | 00:00
| Kamrangirchar | 137 | 08:00 | 127 | 00:00 | SSM | 140 | 10:00 | 138 | 00:00
| Kaptai | 139 | 8:00 | 136 | 15:00 | Sunamganj | 126 | 07:00 | 117 | 21:00
| Kazla | 131 | 18:30 | 126 | 00:00 | Sylhet | 130 | 09:00 | 127 | 05:00
| Keranigonj | 137 | 17:00 | 133 | 00:00 | Sylhet-132 | 128 | 00:00 | 123 | 19:30
| Khagrachori | 135 | 06:00 | 134 | 00:00 | Tangail | 130 | 22:00 | 122 | 18:00
| Khulna | 136 | 08:00 | 130 | 23:00 | Thakurgaon | 138 | 04:00 | 121 | 17:00
| Khulna(S) | 137 | 17:00 | 131 | 21:00 | TK | 137 | 17:00 | 134 | 13:00
| Khulshi | 135 | 08:00 | 132 | 04:00 | Tongi | 136 | 07:00 | 129 | 00:00
| Kishoreganj | 133 | 17:00 | 128 | 00:00 | Ullahpara | 139 | 04:00 | 135 | 18:30
| Kodda | 136 | 18:30 | 121 | 03:00 | Ullon | 139 | 17:00 | 134 | 00:00
| KSRM | 138 | 18:00 | 133 | 13:00 | Uttara | 139 | 07:00 | 134 | 00:00
| Kulaura | 132 | 07:00 | 129 | 18:30 | UttaraNew | 139 | 19:00 | 132 | 22:00
| Kurigram | 134 | 03:00 | 125 | 17:00 | Zigatola | 137 | 09:00 | 132 | 00:00

## L-Curve
Date | 2024-11-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1566 | 6114 | 5728 | 11842 |  |  |  | QF-LDC-11
0:30 | 1482 | 6030 | 5559 | 11589 | Date: | 2024-11-01
1:00 | 1398 | 5946 | 5390 | 11336
1:30 | 1372 | 5965 | 5344 | 11309
2:00 | 1346 | 5984 | 5298 | 11282
2:30 | 1340 | 5934.5 | 5302 | 11236.5 | [5 empty] | Gen. at Eve. Peak | 12302 | 12302 MW (19:00 )
3:00 | 1334 | 5885 | 5306 | 11191 | [6 empty] | 19:00
3:30 | 1325 | 5877 | 5294.5 | 11171.5 | [5 empty] | Gen. at Day Peak | 11199 | 11199 MW (12:00 )
4:00 | 1316 | 5869 | 5283 | 11152 | [6 empty] | 12:00
4:30 | 1329 | 5861.5 | 5249.5 | 11111 | [5 empty] | Highest Generation | 12310
5:00 | 1342 | 5854 | 5216 | 11070 | [6 empty] | 22:00
5:30 | 1336 | 5866 | 5148.5 | 11014.5
6:00 | 1330 | 5878 | 5081 | 10959
6:30 | 1252 | 5792.5 | 4949 | 10741.5
7:00 | 1174 | 5707 | 4817 | 10524
7:30 | 1167 | 5643.5 | 4831 | 10474.5
8:00 | 1160 | 5580 | 4845 | 10425
8:30 | 1201 | 5541 | 4788 | 10329
9:00 | 1242 | 5502 | 4731 | 10233
9:30 | 1271 | 5524 | 4743.5 | 10267.5
10:00 | 1300 | 5546 | 4756 | 10302
10:30 | 1313 | 5586 | 4807 | 10393
11:00 | 1326 | 5626 | 4858 | 10484
11:30 | 1363 | 5811 | 5030.5 | 10841.5
12:00 | 1400 | 5996 | 5203 | 11199
12:30 | 1279 | 6131.5 | 5371 | 11502.5
13:00 | 1158 | 6267 | 5539 | 11806
13:30 | 1173 | 6037 | 5399 | 11436
14:00 | 1188 | 5807 | 5259 | 11066
14:30 | 1204 | 5789 | 5229 | 11018
15:00 | 1220 | 5771 | 5199 | 10970
15:30 | 1122 | 5700.5 | 5042 | 10742.5
16:00 | 1024 | 5630 | 4885 | 10515
16:30 | 932 | 5589 | 4763.5 | 10352.5
17:00 | 840 | 5548 | 4642 | 10190
17:30 | 853 | 6122.5 | 5061.5 | 11184
18:00 | 866 | 6697 | 5481 | 12178
18:30 | 813 | 6771 | 5469 | 12240
19:00 | 760 | 6845 | 5457 | 12302
19:30 | 882 | 6707 | 5579 | 12286
20:00 | 888 | 6661 | 5602 | 12263 |  |  |  | Executive Engineer
20:30 | 986 | 6635.5 | 5646.5 | 12282 |  |  |  | Network Operation Division
21:00 | 1084 | 6610 | 5691 | 12301
21:30 | 1153 | 6555 | 5750.5 | 12305.5
22:00 | 1222 | 6500 | 5810 | 12310 |  |  |  |  | Page 6 of 7
22:30 | 1293 | 6437.5 | 5828.5 | 12266
23:00 | 1364 | 6375 | 5847 | 12222
23:30 | 1465 | 6244.5 | 5787.5 | 12032
24:00 | 1566 | 6114 | 5728 | 11842
12302 MW (19:00 )
11199 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-11-01 |  | Energy |  | 274846109
[16 empty] | 2024-11-01 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3812 | 919 | 1654 | 0 | 1560 | 2390 | 170 | 0 | 544 | 69 | 719 | 0 | 5 | 246
0:30 | 3683 | 920.5 | 1667 | 0 | 1418.5 | 2409.5 | 173 | 0 | 518 | 72.5 | 724.5 | 0 | 2.5 | 965.31 |  |  | Date: | 44135
1:00 | 3554 | 922 | 1680 | 0 | 1277 | 2429 | 176 | 0 | 492 | 76 | 730 | 0 | 0 | 1684.62
1:30 | 3550.5 | 922 | 1680.5 | 0 | 1303 | 2429.5 | 176 | 0 | 441 | 74 | 732.5 | 0 | 0 | 1400.03 | [8 empty] | Total Energy | 274.8461 | 274.8461 | Total Energy Gen 274.846 MKWHr Energy Not Served 5.239 MKWHr Energy Requirement 280.085 MKWHr
2:00 | 3547 | 922 | 1681 | 0 | 1329 | 2430 | 176 | 0 | 390 | 72 | 735 | 0 | 0 | 1115.44 | [8 empty] | Energy not Served | 5.239 | 5.239
2:30 | 3512 | 922 | 1679 | 0 | 1336.5 | 2430 | 176 | 0 | 374 | 74 | 733 | 0 | 0 | 1039.5175 | [8 empty] | Energy Requirement | 280.0851 | 280.0851
3:00 | 3477 | 922 | 1677 | 0 | 1344 | 2430 | 176 | 0 | 358 | 76 | 731 | 0 | 0 | 963.595
3:30 | 3492 | 922.5 | 1650.5 | 0 | 1347 | 2430 | 176 | 0 | 347 | 74 | 732.5 | 0 | 0 | 767.3425 | [7 empty] | Shortage
4:00 | 3507 | 923 | 1624 | 0 | 1350 | 2430 | 176 | 0 | 336 | 72 | 734 | 0 | 0 | 571.09
4:30 | 3517.5 | 922.5 | 1584 | 0 | 1340.5 | 2430.5 | 176 | 0 | 331 | 74 | 735 | 0 | 0 | 443.12
5:00 | 3528 | 922 | 1544 | 0 | 1331 | 2431 | 176 | 0 | 326 | 76 | 736 | 0 | 0 | 315.15
5:30 | 3550 | 922 | 1529.5 | 0 | 1275 | 2431 | 176 | 0 | 325.5 | 71 | 734.5 | 0 | 0 | 272.6525
6:00 | 3572 | 922 | 1515 | 0 | 1219 | 2431 | 176 | 0 | 325 | 66 | 733 | 0 | 0 | 230.155
6:30 | 3525.5 | 920 | 1479 | 0 | 1109.5 | 2380 | 175 | 0 | 321.5 | 64 | 733 | 23 | 11 | 165.6925 | [6 empty] | Coal
7:00 | 3479 | 918 | 1443 | 0 | 1000 | 2329 | 174 | 0 | 318 | 62 | 733 | 46 | 22 | 101.23
7:30 | 3410.5 | 920 | 1445.5 | 0 | 1027 | 2274.5 | 174.5 | 0 | 326.5 | 59 | 734.5 | 89 | 13.5 | 81.615 | [5 empty] | Oil
8:00 | 3342 | 922 | 1448 | 0 | 1054 | 2220 | 175 | 0 | 335 | 56 | 736 | 132 | 5 | 62
8:30 | 3307.5 | 922 | 1422.5 | 0 | 998.5 | 2183.5 | 175.5 | 0 | 325.5 | 56 | 736 | 199.5 | 2.5 | 53.5
9:00 | 3273 | 922 | 1397 | 0 | 943 | 2147 | 176 | 0 | 316 | 56 | 736 | 267 | 0 | 45
9:30 | 3310 | 922.5 | 1392.5 | 0 | 891 | 2128 | 176 | 0 | 307.5 | 55 | 736 | 349 | 0 | 22.5
10:00 | 3347 | 923 | 1388 | 0 | 839 | 2109 | 176 | 0 | 299 | 54 | 736 | 431 | 0 | 0
10:30 | 3407.5 | 922.5 | 1417.5 | 0 | 868 | 2085 | 176 | 0 | 305 | 57 | 736 | 418.5 | 0 | 0
11:00 | 3468 | 922 | 1447 | 0 | 897 | 2061 | 176 | 0 | 311 | 60 | 736 | 406 | 0 | 0
11:30 | 3510.5 | 922.5 | 1463.5 | 0 | 1049 | 2139 | 176 | 0 | 333.5 | 61 | 735.5 | 451 | 0 | 0
12:00 | 3553 | 923 | 1480 | 0 | 1201 | 2217 | 176 | 0 | 356 | 62 | 735 | 496 | 0 | 0
12:30 | 3569.5 | 923 | 1553 | 0 | 1371 | 2239.5 | 175 | 0 | 373.5 | 64 | 733 | 501 | 0 | 0
13:00 | 3586 | 923 | 1626 | 0 | 1541 | 2262 | 174 | 0 | 391 | 66 | 731 | 506 | 0 | 0
13:30 | 3586 | 923 | 1626 | 0 | 1541 | 2262 | 174 | 0 | 391 | 66 | 731 | 506 | 0 | 0
14:00 | 3586 | 923 | 1626 | 0 | 1541 | 2262 | 174 | 0 | 391 | 66 | 731 | 506 | 0 | 0
14:30 | 3483.5 | 922.5 | 1615.5 | 0 | 1382 | 2259.5 | 173.5 | 0 | 360.5 | 64 | 732 | 394 | 1 | 0
15:00 | 3381 | 922 | 1605 | 0 | 1223 | 2257 | 173 | 0 | 330 | 62 | 733 | 282 | 2 | 0
15:30 | 3415.5 | 922.5 | 1577.5 | 0 | 1071 | 2241.5 | 173 | 0 | 340.5 | 61 | 728.5 | 207.5 | 4 | 0
16:00 | 3450 | 923 | 1550 | 0 | 919 | 2226 | 173 | 0 | 351 | 60 | 724 | 133 | 6 | 0
16:30 | 3460.5 | 922.5 | 1450.5 | 0 | 911 | 2202 | 173.5 | 0 | 366 | 59 | 727.5 | 73.5 | 6.5 | 0
17:00 | 3471 | 922 | 1351 | 0 | 903 | 2178 | 174 | 0 | 381 | 58 | 731 | 14 | 7 | 0
17:30 | 3733 | 865 | 1488 | 0 | 1290 | 2326 | 174 | 0 | 499.5 | 64 | 730 | 7 | 7.5 | 0
18:00 | 3995 | 808 | 1625 | 0 | 1677 | 2474 | 174 | 0 | 618 | 70 | 729 | 0 | 8 | 0
18:30 | 4001 | 792.5 | 1593 | 0 | 1752 | 2476.5 | 174.5 | 0 | 644.5 | 68 | 729 | 0 | 9 | 0
19:00 | 4007 | 777 | 1561 | 0 | 1827 | 2479 | 175 | 0 | 671 | 66 | 729 | 0 | 10 | 0
19:30 | 3788 | 777 | 1733 | 0 | 1852 | 2495 | 176 | 0 | 657 | 66 | 729 | 0 | 13 | 0
20:00 | 3712 | 778 | 1803 | 0 | 1845 | 2486 | 176 | 0 | 658 | 66 | 729 | 0 | 10 | 0
20:30 | 3661.5 | 848.5 | 1797.5 | 0 | 1867.5 | 2497.5 | 151 | 0 | 658 | 66 | 728 | 0 | 6.5 | 0
21:00 | 3611 | 919 | 1792 | 0 | 1890 | 2509 | 126 | 0 | 658 | 66 | 727 | 0 | 3 | 0
21:30 | 3658 | 919 | 1745 | 0 | 1883 | 2508.5 | 126 | 0 | 665.5 | 67 | 729.5 | 0 | 4 | 0
22:00 | 3705 | 919 | 1698 | 0 | 1876 | 2508 | 126 | 0 | 673 | 68 | 732 | 0 | 5 | 0
22:30 | 3787 | 919.5 | 1658 | 0 | 1807 | 2509.5 | 126 | 0 | 653.5 | 69 | 729.5 | 0 | 7 | 0
23:00 | 3869 | 920 | 1618 | 0 | 1738 | 2511 | 126 | 0 | 634 | 70 | 727 | 0 | 9 | 0
23:30 | 3840.5 | 919.5 | 1636 | 0 | 1649 | 2450.5 | 148 | 0 | 589 | 69.5 | 723 | 0 | 7 | 123 |  |  | Max Temp. in Dhaka |  | 33.9°C
24:00 | 3812 | 919 | 1654 | 0 | 1560 | 2390 | 170 | 0 | 544 | 69 | 719 | 0 | 5 | 246
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 274.846 MKWHr Energy Not Served 5.239 MKWHr Energy Requirement 280.085 MKWHr
Note on X13: Author:

## Generation
2024-11-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 136 | 136 | 136 | 136 | 136 | 136 | 134 | 135 | 136 | 136 | 136 | 136 | 134 | 133 | 133 | 133 | 134 | 134 |  | 135 | 136 | 136 | 86 | 86 | 86 | 130 | 3073375
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 972000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 20 | 25 | 25 | 25 | 25 | 20 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 6 | 8 | 14 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 352189
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 9 | 14 | 9 | 13 | 8 | 15 | 16 | 11 | 5 | 0 | [9 empty] | 100440
6 | Sikalbaha 225MW CCPP (Gas) | 222 | 223 | 223 | 227 | 227 | 226 | 227 | 226 | 225 | 225 | 225 | 225 | 225 | 219 | 222 | 222 | 222 | 225 |  | 226 | 226 | 225 | 224 | 224 | 225 | 224 | 5308173
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 66 | 70 | 67 | 84 | 82 | 82 | 82 | 82 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1937108
12 | Hathazari 100 MW peaking PP | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 60 | 61 | 45 | 48 | 61 | 68 | 68 | 68 | 68 | 71 |  | 71 | 71 | 71 | 71 | 71 | 64 | 71 | 1594848
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 10 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 102036
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 35 | 35 | 35 | 35 |  | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 1016672
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [9 empty] | 99 | 140 | 140 | 140 | 79 | 80 | 80 | 80 | 201 |  | 202 | 115 | [5 empty] | 1314000
17 | Siddhirganj 335 MW CCPP | 210 | 210 | 180 | 183 | 183 | 182 | 182 | [7 empty] | 21 | 38 | 260 | 329 |  | 330 | 326 | 325 | 325 | 335 | 335 | 335 | 4081038
18 | Kodda 300 MW PP Unit-2 (Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 747709
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 8 | 8 | 45 |  | 45 | 45 | 30 | 8 | 8 | 8 | 8 | 535273
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 584 | 582 | 582 | 582 | 582 | 582 | 582 | 500 | 500 | 501 | 456 | 460 | 465 | 462 | 462 | 430 | 422 | 420 |  | 418 | 420 | 408 | 407 | 407 | 407 | 406 | 11749089
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 41 | 41 | 41 | 40 | 40 | 40 | 40 | 40 |  | 40 | 39 | 41 | 41 | 41 | 42 | 42 | 1014840
33 | Ashuganj 225 MW CCPP | 213 | 213 | 214 | 217 | 214 | 217 | 216 | 216 | 215 | 214 | 212 | 216 | 213 | 207 | 210 | 210 | 212 | 213 |  | 214 | 211 | 212 | 210 | 214 | 212 | 215 | 5191000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 350 | 350 | 310 | 310 | 330 | 310 | 290 | 290 | 290 | 290 | 310 | 315 | 315 | 325 | 290 | 290 | 290 | 312 |  | 310 | 345 | 350 | 350 | 310 | 330 | 310 | 7877100
| Ashuganj 420 MW CCPP(East) | 350 | 350 | 350 | 350 | 350 | 393 | 400 | 393 | 370 | 340 | 340 | 393 | 395 | 393 | 393 | 393 | 300 | 393 |  | 393 | 393 | 393 | 393 | 393 | 393 | 393 | 9065000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 20 | 20 | 12 | 7 | 7 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 205920
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 70 | 50 | 70 | 70 | 1281630
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 349 | 340 | 331 | 352 | 355 | 370 | 367 | 366 | 371 | 376 | 400 | 404 | 404 | 366 | 370 | 407 | 401 | 404 |  | 413 | 408 | 407 | 408 | 408 | 398 | 371 | 9208800
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 380 | 380 | 340 | 340 | 340 | 420 | 420 | 420 | 420 | 420 | 320 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9942500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 31 | 32 | 33 | 33 | 34 | 33 | 33 | 29 | 27 | 27 | 25 | 25 | 22 | 24 | 32 | 33 | 33 | 33 |  | 33 | 33 | 33 | 54 | 72 | 72 | 33 | 779520
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 3 | 11 | 17 | 34 | 32 | 29 | 41 | 34 | 5 | 8 | 0 | [9 empty] | 218340
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 698640
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 58 | 55 | 55 | 56 | 56 | 61 | 59 | 58 | 40 | 40 | 40 | 57 | 54 | 53 | 53 | 54 | 55 | 55 |  | 55 | 55 | 54 | 53 | 55 | 55 | 56 | 1285152
48 | Shahjibazar 86 MW PP (Shahjibazar) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 83 | 83 | 80 | 11 | 11 | 457920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 205 | 205 | 205 | 205 | 207 | 206 | 206 | 206 | 207 | 208 | 208 | 208 | 208 | 206 | 205 | 205 | 205 | 205 |  | 207 |  |  |  |  | 130 | 130 | 4698100
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 48384
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 333840
57 | Bibiana-II 341 MW CCPP (Summit) | 315 | 315 | 310 | 280 | 290 | 295 | 280 | 290 | 275 | 285 | 310 | 285 | 285 | 280 | 310 | 285 | 280 | 295 |  | 290 | 330 | 310 | 310 | 295 | 295 | 300 | 7231500
| Bibiyana South 400 MW | 395 | 395 | 400 | 395 | 400 | 400 | 400 | 400 | 400 | 350 | 350 | 350 | 340 | 340 | 340 | 310 | 310 | 340 |  | 340 | 375 | 385 | 388 | 400 | 398 | 400 | 8934500
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 17 |  |  |  |  | 17 |  | 17 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 |  |  |  | 275344
59 | Tangail Palli Power Gen 22 MW | 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 6 | 6 | 10 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 249840
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 76 | 72 | 76 | 72 | 76 | 66 | 62 | 56 | 56 | 54 | 60 | 62 | 66 | 66 | 62 | 60 | 58 | 70 |  | 66 | 66 | 66 | 66 | 68 | 70 | 69 | 1582080
64 | Malancha, Ctg. EPZ (United) | 29 | 30 | 30 | 20 | 20 | 23 | 25 | 27 | 29 | 20 | 24 | 25 | 28 | 28 | 24 | 19 | 23 | 24 |  | 20 | 20 | 35 | 41 | 42 | 42 | 42 | 679680
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 18 | 18 | 15 | 18 | 18 | 18 | 18 | 8 |  | 15 | 12 | 18 | 15 | 18 | 18 | 18 | 384580
69 | Summit Ashulia | 19 | 20 | 20 | 16 | 16 | 16 | 16 | 18 | 20 | 20 | 22 | 22 | 16 | 16 | 16 | 16 | 16 | 20 |  | 19 | 19 | 19 | 18 | 20 | 22 | 22 | 472200
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 14 | 15 | 14 | 14 | 14 | 14 |  | 22 | 22 | 23 | 22 | 23 | 23 | 23 | 468360
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 478440
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 32 | 32 | 33 | 33 | 10 | 33 | 33 | 33 | 32 | 32 | 31 | 30 | 31 | 31 | 31 | 32 |  | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 760600
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 66 | 106 | 70 | 70 | 52 | 34 | 100 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 1639320
| Chowmuhani 113 MW | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 67 | 66 | 66 | 67 | 67 | 68 | 75 |  | 77 | 77 | 77 | 78 | 77 | 78 | 77 | 1244880
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 54 | 35 | 35 | 35 | 17 | 90 |  | 90 | 90 | 90 | 90 | 35 | 17 | 17 | 802080
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 34 |  | 34 | 34 | 34 | 34 | 34 | 17 | 8 | 469891
79 | Kodda 150 MW PP | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 48 | 63 | 63 | 63 | 32 | 32 | 31 | 115 |  | 148 | 132 | 132 | 134 | 148 | 148 | 82 | 1517280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 34 | 34 | 25 | 25 | 25 | 25 | 25 | 8 | 34 |  | 34 | 43 | 43 | 43 | 43 | 43 | 25 | 579648
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 35 | 35 | 35 | 105 | 105 | 105 | 88 | 52 | 52 | 88 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2143027
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 2 | 3 | 2 | 4 | 4 | 1 | 1 | 1 | [10 empty] | 18723
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 907588
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 425710
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [5 empty] | 1 | 14 | 14 | 14 | [10 empty] | 2 | 10 | 12 | 16 | 16 |  |  | 103392
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 9 | 27 | 32 | 33 | 5 | 5 | 279648
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1149432
94 | Gagnagar 102 MW PP (Digital Power) | [13 empty] | 8 | 8 |  |  |  |  | 8 | 8 | 8 | 8 | 8 |  |  | 48672
95 | Patenga 50MW PP (Baraka) | 20 | 19 | 29 | 33 | 33 | 33 | 33 | 26 | 26 | 26 | 27 | 33 | 33 | 33 | 33 | 33 | 33 | 40 |  | 40 | 40 | 26 | 26 | 26 | 26 | 26 | 728160
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 3 | 6 | 5 | 9 | 16 |  | 17 | 18 | 20 | 25 | 25 | 25 | 25 | 182400
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 653963
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 17 | 35 |  | 55 | 55 | 55 | 35 | 17 |  |  | 270524
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 120 | 163 | 163 | 120 | 163 |  | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 3571691
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 7350
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 35 |  | 35 | 35 | 35 | 17 |  |  |  | 262188
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 96 | 96 | 96 | 96 | 95 | 95 | 96 | 96 | 96 | 96 | 97 | 96 | 96 | 95 | 95 | 55 | 55 | 95 |  | 96 | 96 | 97 | 97 | 98 | 98 | 97 | 2236800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 34 | 34 | 33 | 34 | 44 | 17 | 33 |  | 87 | 87 | 87 | 90 | 108 | 112 | 82 | 1192320
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 76 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 50 | 50 | 1416000
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 97 | 31 | 17 | 17 | 17 | 28 |  | 34 | 34 | 34 | 34 | 34 | 34 | 24 | 629760
117 | Ashuganj 150 MW PP (Midland) | 68 | 87 | 84 | 85 | 84 | 65 | 51 | 51 | 48 | 31 | 40 | 43 | 42 | 43 | 42 | 42 | 42 | 50 |  | 50 | 45 | 45 | 45 | 50 | 52 | 45 | 1286327
118 | Bibiyana-III 400 MW CCPP | 336 | 336 | 336 | 335 | 321 | 311 | 311 | 300 | 333 | 385 | 385 | 387 | 387 | 343 | 342 | 343 | 343 | 387 |  | 383 | 387 | 387 | 389 | 386 | 373 | 371 | 8870000
| Jamalpur 115 MW PP (United) | 57 | 57 | 57 | 56 | 57 | 57 | 57 | 58 | 58 | 58 | 57 | 57 | 57 | 56 | 56 | 45 | 45 | 47 |  | 56 | 56 | 55 | 56 | 56 | 56 | 57 | 1336800
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 49 | 50 | 50 | 50 | 50 | 50 | 100 | 49 | 49 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1268345
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 297600
| Anlima Energy Ltd. | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 53 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 495545
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 30 | 33 | 35 | 35 | 35 | 19 | 497160
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 11 | 19 | 26 | 29 | 30 | 28 | 23 | 16 | 7 | 1 | [9 empty] | 192167
| Chandpur 115(Doreen) | 34 | 34 | 33 | 34 | 34 | 34 | 35 | 35 | 34 | 34 | 34 | 34 | 35 | 34 | 34 | 34 | 50 | 52 |  | 87 | 92 | 92 | 92 | 92 | 61 | 34 | 1120320
| Kanchan Purbachal Power Generation Ltd. | 36 | 36 | 36 | 36 | 36 | 36 |  | 25 | 36 | 17 | 18 | 18 | 18 | 6 | 18 | 17 | 17 | 29 |  | 36 | 36 | 36 | 36 | 36 | 36 | 18 | 686520
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 90 |  | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 650690
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 7 | 8 |  | 10 | 13 | 10 | 3 | 5 | 9 | 5 | 81120
| Sonagazi 75 MW Solar Plant | [6 empty] | 5 | 18 | 38 | 56 | 30 | 68 | 58 | 46 | 25 | 14 | 1 | [9 empty] | 346882
Matarbari 2*600 MW (CPGCL)
Meghnaghat (Reliance) 718MW CCPP
Sreepur 150 MW
120
121 | Eastern Zone Total | 5946 | 5984 | 5885 | 5869 | 5854 | 5878 | 5707 | 5580 | 5502 | 5546 | 5626 | 5996 | 6267 | 5807 | 5771 | 5630 | 5548 | 6697 |  | 6845 | 6707 | 6661 | 6610 | 6500 | 6375 | 6114 | 146317683
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 |  | 21 | 20 | 20 | 17 | 17 | 20 | 20 | 395040
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 1 | 17 |  | 17 | 17 | 17 |  |  |  |  | 52320
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 7 | 23 | 37 | 57 | 64 | 68 | 73 | 60 | 45 | 23 | 4 | [9 empty] | 460800
132 | Rampal 1320 MW (BIFPCL) | 367 | 370 | 371 | 371 | 372 | 372 | 374 | 377 | 373 | 373 | 371 | 373 | 372 | 372 | 370 | 371 | 375 | 623 |  | 627 | 623 | 625 | 624 | 623 | 625 | 506 | 10640000
133 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1372800
| Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 180 | 220 | 220 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5276730
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 87456
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [9 empty] | 3393
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 127 | 127 | 127 | 127 | 127 | 127 | 80 | 81 | 81 | 81 | 127 | 127 | 127 | 81 | 81 | 81 | 81 | 123 |  | 123 | 123 | 123 | 123 | 123 | 123 | 127 | 2805000
141 | Bhola 33 MW PP (Venture) | 9 | 9 | 10 | 10 | 10 | 8 | 7 | 6 | 5 | 5 | 5 | 6 | 7 | 7 | 7 | 6 | 6 | 9 |  | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 199719
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP | 31 | 31 | 31 | 31 | 27 | 27 | 27 | 27 | 16 | 16 | 14 | 14 | 16 | 18 | 18 | 14 | 18 | 25 |  | 37 | 35 | 36 | 36 | 36 | 37 | 37 | 589312
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
147 | Bheramara HVDC | 922 | 922 | 922 | 923 | 922 | 922 | 918 | 922 | 922 | 923 | 922 | 923 | 923 | 923 | 922 | 923 | 922 | 808 |  | 777 | 777 | 778 | 919 | 919 | 920 | 919 | 21865454
148 | Bheramara 410 MW CCPP | 278 | 279 | 279 | 286 | 289 | 297 | 310 | 315 | 270 | 270 | 270 | 270 | 338 | 342 | 342 | 344 | 280 | 363 |  | 370 | 368 | 371 | 221 | 326 | 333 | 355 | 7473312
149 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1140 | 1110 | 1040 | 1040 | 1050 | 1200 | 1244 | 1244 | 1244 | 1244 | 1200 | 1200 |  | 1200 | 1220 | 1220 | 1244 | 1244 | 1244 | 1244 | 30739400
150
151 | Barapukuria TPP Unit-1 | 64 | 64 | 63 | 63 | 63 | 63 | 63 | 63 | 64 | 65 | 64 | 64 | 64 | 63 | 64 | 64 | 64 | 64 |  | 64 | 62 | 63 | 64 | 64 | 65 | 64 | 1485382
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 130 | 120 | 120 | 117 | 117 | 117 | 117 | 117 | 167 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3756000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 30 | 30 | 30 | 30 | 24 | 23 | 16 | 22 | 22 | 22 | 31 | 38 | 38 | 38 | 41 | 45 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 765889
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 4 | 4 | 2 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 28680
157 | Sirajganj 68 MW Solar Park | [6 empty] | 3 | 12 | 33 | 46 | 52 | 44 | 39 | 43 | 29 | 13 | 1 | [9 empty] | 328500
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 167 | 168 | 171 | 172 | 175 | 179 | 183 | 180 | 180 | 181 | 181 | 181 | 181 | 140 | 161 | 201 | 160 | 178 |  | 160 | 179 | 194 | 205 | 205 | 214 | 214 | 4453636
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 401 | 354 | 319 | 343 | 337 | 340 | 330 | 360 | 336 | 385 | 351 | 338 | 350 | 340 | 345 |  | 320 | 414 | 414 | 414 | 336 | 353 | 384 | 8821963
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | 7 | [16 empty] | 5 |  | 20 | 23 | 23 | 24 | 24 | 24 | 7 | 115590
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190404
166 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 28 | 28 | 28 | 30 | 33 | 28 |  |  |  | 20 |  | 35 | 37 | 37 | 37 | 37 | 37 | 37 | 515735
169 | Santahar 50 MW Peaking PP | 22 | 22 | 22 | [8 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 28 | 28 | 28 | 28 | 28 | 28 | 15 | 372884
170 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
171 | Chapainawabganj 100 MW Peaking PP | 95 | [14 empty] | 21 | 55 | 93 |  | 93 | 93 | 93 | 93 | 93 | 94 | 94 | 782272
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | 105 | 105 | 113 | 113 | 113 | 113 | 50 | 50 | 35 |  |  | 24 | 105 | 35 | 35 |  |  | 22 |  | 35 | 35 | 35 | 50 | 113 | 113 | 113 | 1693152
173 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 95 | 50 | 35 | 35 |  |  |  | 35 | 70 | 35 | 35 |  |  | 95 |  | 35 | 35 | 35 | 70 | 113 | 113 | 113 | 1491552
175 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | 111 | 111 | 111 | 111 | 111 | 50 | 34 | 34 |  |  |  | 34 | 45 | 103 | 111 |  |  | 93 |  | 40 | 34 | 34 | 68 | 90 | 90 | 90 | 1510953
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 12894
| Energypac Power Venture Thakurgaon Ltd. | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 54 | 54 | 35 | 60 | 95 | 102 | 75 | 75 |  |  | 28 |  | 115 | 115 | 115 | 115 | 75 | 75 | 75 | 1865664
| Intraco Solar 30 MW | [6 empty] | 1 | 7 | 9 | 17 | 18 | 15 | 6 | 9 | 12 | 5 | 1 | [9 empty] | 113267
178 | Adani Power Jharkhanda Ltd | 730 | 735 | 731 | 734 | 736 | 733 | 733 | 736 | 736 | 736 | 736 | 735 | 731 | 733 | 733 | 724 | 731 | 729 |  | 729 | 729 | 729 | 727 | 732 | 727 | 719 | 16887273
| Teesta Solar Limited | [6 empty] | 10 | 4 | 36 | 96 | 64 | 123 | 143 | 118 | 77 | 32 | 3 | [9 empty] | 725760