## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-11-08 | Friday
|  | Date (day): | 2024-11-08 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12320.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13493 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-11-07 | 2024-11-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 409 | 411 | 400 | 412
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 31 | 30 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Under maint.
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 8 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 35 | 54 | 0
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 132 | 48 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 17 | 35 | 20 |  | Fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 17 | 35 | 20 |  | Fuel shortage
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 40 | 42 | 42 |  | 38 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 23 | 23 | 23 | 23 |  | 10 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 31 | 25 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 25 | 25 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 138 | 100 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 97 | 52 | 149 |  | 0
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 52 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 0 | 16 | 88 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 117 | 162 | 100 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 22 | 36 | 36 | 36 |  | 19 | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1698 | 2165 | 1838 | 2424 | 2544 | 902
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 9 | 25 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 174 | 174 | 132 | 132 | 98 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 223 | 225 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 25 | 78 | 50 | 70 |  | 28 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 68 | 78 | 65 | 84 |  | 18 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 100 | 50 | 100 |  | 0 | Engine problem
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 8 | 16 | 30 | 30
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 26 | 40 | 31 | 35 | 73 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 52 | 52 | 52 | 248 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 20 | 35 | 35 | 35 | 19 |  | Fuel shortage
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 41 | 35 | 53 | 63 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 160 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 310 | 312 | 612 | 612 |  | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 0 | 15 | 15 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 0 | 0 | 0 | 0 | 1150 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1107 | 1432 | 1478 | 1724 | 2100 | 988
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 335 | 310 | 310 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 393 | 393 | 400 | 400
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 43 | 43 | 44 | 44
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 189 | 190 | 190 | 190 | 5
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 13 | 27 | 120 | 120 | 30 |  | Fuel shortage
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 43 | 35 | 36 |  | 16 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 103 | 147 | 100 | 200 |  | 0
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 50 | 68 | 66 | 82
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 3 | 77 | 106 | 106 |  | 8 | Engine problem
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 47 | 97 | 35 | 84 | 29 |  | Fuel shortage
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 30 | 92 | 51 | 92 | 23 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 72 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1386 | 1675 | 1690 | 1827 | 255 | 620
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 11 | 15 | 25 | 25 | 177 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 95 | 95 | 96 | 96 | 104 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 56 | 55 | 57 | 58 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 33 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 18 | 6 | 18
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 2 | 17 | 35 | 19 |  | Fuel shortage
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 36 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 256 | 186 | 250.6 | 231 | 177 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | S/D for FGMO work.
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract Expired
90 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 36 | 36 | 36 | 36 | 14 |  | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 |  | 6 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 57 | 60 | 60 | 61
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 86 | 86
94 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 209 | 208 | 210 | 210 |  | 21 | Machine problem
96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 13 | 13 |  | 12 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 295 | 300 | 310 |  |  | FGMO
99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 385 | 385 | 385 |  |  | FGMO
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 357 | 375 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1479 | 1487 | 1525 | 1536 | 34 | 662
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 900 | 900 | 719 | 668
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 19 | 20 | 35 |  | 19 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 30 | 60 |  | 49 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 339 | 321 | 300 | 300 | 110 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 0 | 17 | 88 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 366 | 627 | 375 | 617 | 617 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1689 | 1944 | 1544 | 1697 | 1061 | 68
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 16 | 110
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 5 | 7 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 124 | 127 | 120 | 127 |  | 67 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1160 | 1060 | 1244 | 1244
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 137 | 51 | 137 |  | 13 | Engine problem
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  | 307 | Under maint
118 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1563 | 1631 | 1661 | 1848 | 0 | 387
119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 46 | 45 | 45 |  | 7 | Engine problem
121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 5 | 12 | 0 | 25 |  | 46 | Engine problem
122 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 26 | 43 |  | 7 | Engine problem
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 173 | 177 | 180 | 180 | 30 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 414 | 414 |  |  | FGMO
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 15 | 22 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 5 | 11
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 50 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 94 | 95 | 95 |  | 18 | Engine problem
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 15 | 113 | 113 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 721 | 713 | 730 | 730
135 | Sirajganj 68 MW Solar Park |  | Solar | NWPGCL | 68 | 68 | 68 | 54 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 75 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1499 | 1732 | 1762 | 1781 | 693 | 107
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 65 | 65 | 67 | 67 |  | 18
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 130 | 130 | 130 | 130 |  | 144 | Machine problem
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 68 | 113 | 113
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 48 | 115 | 54 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 26 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 143 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 418 | 378 | 572 | 425 | 40 | 247
| Total |  |  |  |  | 27791 | 27086 | 11095 | 12630 | 12320.6 | 13493 | 6904 | 3981
A. |  | 2024-11-07 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 12630 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 8983 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12630 | MW
3 | Day peak Generation : |  |  | 11095 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12319.13 | MW
4 | Evening peak Generation : |  |  | 12630 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 261.5483 | MKWHr | By Solar | 3.8438 | MKWHr
| By Gas : | 124.6469 | MKWHr |  | By Oil: | 35.9044 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 53.6496 | MKWHr |  | By Hydro: | 3.9874 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 16.3994 | MKWHr |  | By Wind: | 0.00336 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6904 | MW | Dhaka | 4849.03 | 4849.03 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3981 | MW | Chittagong | 1140.7 | 1140.7 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10885 | MW | Khulna | 1456.2 | 1456.2 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 881.39 | MMCFD | **Import Adani: | Taka | 108399855.53 | Rajshahi | 1163.2 | 1163.2 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 372056085.762 | ii) Oil : | Taka | 649938384.41 | Comilla | 1082 | 1082 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 373425415.73 | Total | Taka | 1503819741.432 | Mymensingh | 1011 | 1011 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 9928.05 | MKWHr. | Sylhet | 496 | 496 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 830 | MW (W to E) at | 18:00 | hrs | Barisal | 351 | 351 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 782 | MW at | 22:00 | hrs | Rangpur | 770 | 770 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.0°C |  |  | Total | 12319.13 | 12319.13 |  | 0
B. |  | 2024-11-08 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 32.0°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13493 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9300 | MW
4 | Reserve(Generation end) |  |  |  | 1493 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 248.502 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8669 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8175 | MKWHr. | ii) HVDC Flow at Peak Time |  | 900 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.296 | MKWHr. | iii) Maximum HVDC Flow : |  | 901 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 100.1 |  | (b) Today: | 99.86 |  | (c) Rule Curve: |  | 108.3
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-11-07 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 8 | 0 | 132 | 40 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 12 | 0 | 24 | 0 | 0 | 0 | 310 | 0 | 0 | 190 | 50 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 42 | 0 | 56 | 31 | 0 | 208 | 0 | 0 | 0 | 280 | 13 | 5 | 0 | 0 | 0 | 0 | 96 | 0 | 47 | 0 | 50 | 85 | 23 | 372 | 57 | 17 | 0 | 0 | 52 | 35 | 0 | 0 | 47 | 12 | 346 | 0 | 0 | 90 | 35 | 0 | 17 | 0 | 22 | 18 | 395 | 0 | 0 | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 900 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 130 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244 | 220 | 0 | 137 | 0 | 0 | 35 | 0 | 0 | 364 | 0 | 0 | 719 | 0 | 0 | 0 | 0 | 0 |  | 5549 | 4783 | 10332 | 3522 | 900 | 1635 | 0 | 918 | 2362 | 172 | 0 | 48 | 56 | 719 | 0 | 0 | 0 | 100.15
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 8 | 0 | 131 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 12 | 0 | 37 | 0 | 0 | 0 | 310 | 0 | 0 | 190 | 50 | 43 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 33 | 0 | 0 | 56 | 31 | 0 | 208 | 0 | 0 | 0 | 280 | 13 | 5 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 50 | 51 | 13 | 372 | 57 | 17 | 0 | 0 | 68 | 35 | 0 | 0 | 29 | 0 | 346 | 0 | 0 | 54 | 0 | 0 | 17 | 0 | 17 | 18 | 395 | 0 | 0 | 562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 900 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 131 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244 | 220 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 726 | 0 | 0 | 0 | 0 | 0 |  | 5220 | 4706 | 9926 | 3446 | 900 | 1629 | 0 | 620 | 2366 | 171 | 0 | 16 | 52 | 726 | 0 | 0 | 0 | 100.14
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 8 | 0 | 130 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 8 | 0 | 39 | 0 | 0 | 0 | 310 | 0 | 0 | 190 | 50 | 43 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 30 | 0 | 0 | 56 | 83 | 0 | 209 | 0 | 0 | 0 | 285 | 13 | 5 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 17 | 0 | 372 | 45 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 0 | 0 | 562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 900 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 132 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 723 | 0 | 0 | 0 | 0 | 0 |  | 4900 | 4603 | 9503 | 3395 | 900 | 1694 | 0 | 243 | 2324 | 170 | 0 | 0 | 54 | 723 | 0 | 0 | 0 | 100.13
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 8 | 0 | 129 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 310 | 0 | 0 | 190 | 50 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 48 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 33 | 0 | 0 | 56 | 83 | 0 | 209 | 0 | 0 | 0 | 280 | 13 | 5 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 900 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 132 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 716 | 0 | 0 | 0 | 0 | 0 |  | 4698 | 4499 | 9197 | 3360 | 900 | 1696 | 0 | 170 | 2122 | 169 | 0 | 16 | 48 | 716 | 0 | 0 | 0 | 100.12
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 8 | 0 | 128 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 310 | 0 | 0 | 180 | 50 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 48 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 56 | 83 | 0 | 209 | 0 | 0 | 0 | 290 | 13 | 5 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 900 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 132 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 718 | 0 | 0 | 0 | 0 | 0 |  | 4480 | 4503 | 8983 | 3343 | 900 | 1674 | 0 | 137 | 1979 | 168 | 0 | 16 | 48 | 718 | 0 | 0 | 0 | 100.11
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 23 | 33 | 8 | 0 | 130 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 310 | 0 | 0 | 180 | 50 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 56 | 83 | 0 | 210 | 0 | 0 | 0 | 295 | 13 | 5 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 900 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 133 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 |  | 4458 | 4566 | 9024 | 3345 | 900 | 1722 | 0 | 134 | 1967 | 170 | 0 | 16 | 50 | 720 | 0 | 0 | 0 | 100.1
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 20 | 21 | 23 | 33 | 8 | 0 | 132 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 1 | 0 | 36 | 0 | 0 | 0 | 330 | 0 | 0 | 180 | 70 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 55 | 80 | 0 | 210 | 0 | 0 | 0 | 300 | 13 | 5 | 0 | 0 | 0 | 0 | 86 | 0 | 2 | 5 | 12 | 8 | 3 | 317 | 55 | 17 | 0 | 1 | 50 | 11 | 0 | 0 | 9 | 12 | 357 | 0 | 5 | 17 | 7 | 0 | 0 | 4 | 8 | 12 | 360 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 9 | 0 | 0 |  | 900 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 133 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 220 | 0 | 6 | 0 | 9 | 35 | 0 | 0 | 370 | 2 | 0 | 723 | 20 | 0 | 0 | 6 | 9 |  | 4739 | 4689 | 9428 | 3395 | 900 | 1723 | 0 | 368 | 2019 | 172 | 0 | 16 | 42 | 723 | 70 | 0 | 0 | 100.09
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 21 | 23 | 32 | 8 | 0 | 131 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 10 | 0 | 0 | 0 | 290 | 0 | 0 | 180 | 70 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 25 | 0 | 0 | 1 | 0 | 30 | 0 | 36 | 0 | 0 | 61 | 83 | 0 | 210 | 0 | 0 | 0 | 295 | 13 | 5 | 0 | 0 | 0 | 0 | 86 | 0 | 33 | 11 | 12 | 26 | 13 | 312 | 55 | 17 | 0 | 2 | 80 | 17 | 5 | 0 | 9 | 12 | 315 | 0 | 21 | 17 | 17 | 0 | 14 | 14 | 16 | 18 | 360 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 18 | 0 | 0 |  | 900 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 134 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1244 | 180 | 0 | 54 | 2 | 30 | 35 | 0 | 0 | 369 | 12 | 0 | 722 | 71 | 0 | 0 | 23 | 28 |  | 4917 | 4886 | 9803 | 3355 | 900 | 1647 | 0 | 573 | 2111 | 171 | 0 | 49 | 40 | 722 | 235 | 0 | 0 | 0
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 21 | 23 | 33 | 12 | 0 | 134 | 40 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 2 | 0 | 0 | 15 | 6 | 0 | 3 | 0 | 0 | 0 | 285 | 0 | 0 | 180 | 50 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 25 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 60 | 83 | 0 | 211 | 0 | 0 | 0 | 280 | 13 | 5 | 0 | 0 | 0 | 0 | 95 | 0 | 46 | 15 | 12 | 51 | 12 | 312 | 58 | 52 | 0 | 3 | 80 | 17 | 17 | 0 | 9 | 12 | 316 | 0 | 34 | 17 | 17 | 0 | 17 | 21 | 16 | 18 | 360 | 17 | 0 | 302 | 0 | 0 | 0 | 0 | 55 | 0 | 0 |  | 901 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 130 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1140 | 180 | 0 | 54 | 3 | 55 | 35 | 0 | 0 | 367 | 24 | 0 | 719 | 119 | 0 | 0 | 37 | 65 |  | 5042 | 4876 | 9918 | 3336 | 901 | 1556 | 0 | 691 | 2003 | 174 | 0 | 51 | 50 | 719 | 437 | 0 | 0 | 0
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 25 | 17 | 0 | 0 | 19 | 15 | 23 | 32 | 25 | 0 | 134 | 40 | 0 | 0 | 1 | 223 | 0 | 0 | 0 |  | 6 | 24 | 51 | 0 | 25 | 13 | 0 | 4 | 0 | 0 | 0 | 290 | 0 | 0 | 189 | 50 | 44 | 0 | 0 | 43 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 50 | 11 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 60 | 83 | 0 | 209 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 0 | 0 | 0 | 95 | 0 | 52 | 20 | 37 | 71 | 13 | 386 | 58 | 52 | 0 | 5 | 89 | 17 | 17 | 0 | 21 | 12 | 340 | 0 | 49 | 90 | 30 | 0 | 17 | 25 | 16 | 18 | 393 | 17 | 0 | 305 | 0 | 0 | 0 | 0 | 65 | 0 | 32 |  | 899 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 130 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 12 | 0 | 0 | 0 | 6 | 0 | 1120 | 180 | 0 | 54 | 5 | 70 | 35 | 0 | 0 | 366 | 35 | 0 | 721 | 183 | 0 | 0 | 53 | 99 |  | 5670 | 5018 | 10688 | 3499 | 899 | 1651 | 0 | 919 | 1986 | 174 | 0 | 172 | 50 | 721 | 617 | 0 | 0 | 0
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 25 | 17 | 0 | 0 | 19 | 15 | 23 | 32 | 25 | 0 | 134 | 40 | 0 | 0 | 1 | 223 | 0 | 0 | 0 |  | 6 | 24 | 51 | 0 | 25 | 13 | 0 | 4 | 0 | 0 | 0 | 290 | 0 | 0 | 189 | 50 | 44 | 0 | 0 | 43 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 50 | 11 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 60 | 83 | 0 | 209 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 0 | 0 | 0 | 95 | 0 | 52 | 20 | 37 | 71 | 13 | 386 | 58 | 52 | 0 | 5 | 89 | 17 | 17 | 0 | 21 | 12 | 340 | 0 | 49 | 90 | 30 | 0 | 17 | 25 | 16 | 18 | 393 | 17 | 0 | 305 | 0 | 0 | 0 | 0 | 65 | 0 | 32 |  | 899 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 130 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 12 | 0 | 0 | 0 | 6 | 0 | 1120 | 180 | 0 | 54 | 5 | 70 | 35 | 0 | 0 | 366 | 35 | 0 | 721 | 183 | 0 | 0 | 53 | 99 |  | 5670 | 5018 | 10688 | 3499 | 899 | 1651 | 0 | 919 | 1986 | 174 | 0 | 172 | 50 | 721 | 617 | 0 | 0 | 0
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 19 | 15 | 23 | 31 | 25 | 0 | 134 | 40 | 0 | 0 | 9 | 223 | 0 | 0 | 0 |  | 6 | 25 | 68 | 0 | 26 | 50 | 0 | 8 | 0 | 0 | 0 | 330 | 0 | 0 | 189 | 50 | 43 | 0 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 50 | 11 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 57 | 83 | 0 | 209 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 95 | 0 | 51 | 20 | 37 | 103 | 13 | 387 | 56 | 52 | 0 | 4 | 52 | 20 | 17 | 3 | 47 | 12 | 357 | 0 | 33 | 117 | 35 | 0 | 17 | 31 | 30 | 22 | 393 | 17 | 0 | 310 | 0 | 0 | 0 | 0 | 72 | 0 | 36 |  | 900 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 130 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 0 | 0 | 6 | 15 | 1160 | 220 | 0 | 54 | 2 | 84 | 48 | 0 | 0 | 366 | 26 | 0 | 721 | 143 | 0 | 0 | 54 | 75 |  | 5926 | 5169 | 11095 | 3590 | 900 | 1753 | 0 | 1125 | 2031 | 174 | 0 | 199 | 50 | 721 | 552 | 0 | 0 | 0
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 2 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 19 | 15 | 23 | 31 | 25 | 0 | 134 | 40 | 0 | 0 | 17 | 223 | 0 | 0 | 0 |  | 6 | 47 | 68 | 0 | 32 | 50 | 0 | 8 | 0 | 0 | 0 | 310 | 0 | 0 | 189 | 50 | 43 | 0 | 0 | 43 | 0 | 36 | 28 | 0 | 0 | 0 | 16 | 58 | 11 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 58 | 83 | 0 | 207 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 15 | 0 | 0 | 95 | 0 | 60 | 20 | 50 | 104 | 12 | 387 | 47 | 52 | 0 | 4 | 52 | 35 | 17 | 70 | 57 | 12 | 340 | 0 | 43 | 126 | 35 | 0 | 17 | 30 | 66 | 36 | 393 | 17 | 0 | 308 | 0 | 0 | 0 | 0 | 50 | 0 | 36 |  | 900 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 7 | 41 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 130 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 95 | 0 | 35 | 0 | 5 | 60 | 1244 | 220 | 0 | 54 | 5 | 26 | 94 | 0 | 0 | 366 | 30 | 0 | 719 | 120 | 0 | 0 | 51 | 42 |  | 6099 | 5332 | 11431 | 3453 | 900 | 1728 | 0 | 1543 | 2114 | 174 | 0 | 314 | 58 | 719 | 428 | 0 | 0 | 0
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 20 | 15 | 23 | 0 | 17 | 0 | 134 | 40 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 6 | 47 | 64 | 0 | 37 | 50 | 0 | 6 | 0 | 0 | 0 | 280 | 0 | 0 | 189 | 50 | 43 | 0 | 0 | 43 | 0 | 36 | 51 | 0 | 0 | 0 | 16 | 60 | 9 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 60 | 83 | 0 | 207 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 60 | 0 | 0 | 86 | 0 | 86 | 16 | 50 | 103 | 13 | 387 | 57 | 35 | 0 | 3 | 52 | 35 | 33 | 70 | 57 | 12 | 340 | 0 | 40 | 126 | 35 | 0 | 17 | 25 | 73 | 36 | 360 | 17 | 0 | 309 | 0 | 0 | 0 | 0 | 58 | 0 | 44 |  | 900 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 5 | 23 | 0 | 0 | 0 | 0 | 7 | 41 | 0 | 0 | 22 | 0 | 15 | 0 | 0 | 5 | 66 | 0 | 134 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 94 | 0 | 35 | 0 | 4 | 70 | 1120 | 180 | 0 | 54 | 4 | 52 | 115 | 0 | 0 | 367 | 30 | 0 | 725 | 102 | 0 | 0 | 43 | 80 |  | 6106 | 5169 | 11275 | 3273 | 900 | 1607 | 0 | 1740 | 1996 | 174 | 0 | 341 | 60 | 725 | 459 | 0 | 0 | 0
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 19 | 21 | 23 | 0 | 17 | 0 | 134 | 40 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 6 | 47 | 64 | 0 | 38 | 50 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 190 | 50 | 43 | 0 | 0 | 43 | 0 | 36 | 52 | 0 | 0 | 0 | 16 | 60 | 10 | 0 | 0 | 1 | 0 | 30 | 0 | 36 | 0 | 0 | 59 | 83 | 0 | 204 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 60 | 0 | 0 | 76 | 0 | 86 | 11 | 50 | 103 | 12 | 389 | 56 | 35 | 0 | 2 | 52 | 35 | 34 | 70 | 55 | 12 | 370 | 0 | 27 | 126 | 35 | 0 | 17 | 13 | 73 | 36 | 360 | 17 | 0 | 313 | 1 | 0 | 0 | 0 | 42 | 0 | 0 |  | 899 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 48 | 0 | 0 | 0 | 13 | 7 | 41 | 0 | 0 | 28 | 0 | 15 | 0 | 0 | 5 | 63 | 0 | 130 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 94 | 0 | 35 | 0 | 3 | 70 | 1080 | 220 | 0 | 54 | 3 | 42 | 115 | 0 | 0 | 366 | 17 | 0 | 727 | 55 | 0 | 0 | 30 | 53 |  | 6104 | 5143 | 11247 | 3371 | 899 | 1702 | 0 | 1762 | 1952 | 174 | 0 | 300 | 60 | 727 | 299 | 1 | 0 | 100.01
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 19 | 21 | 23 | 0 | 17 | 0 | 134 | 40 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 10 | 46 | 68 | 0 | 38 | 50 | 0 | 3 | 0 | 0 | 0 | 295 | 0 | 0 | 190 | 50 | 43 | 0 | 0 | 43 | 0 | 38 | 52 | 0 | 0 | 0 | 16 | 58 | 11 | 0 | 0 | 1 | 0 | 30 | 0 | 36 | 0 | 0 | 60 | 83 | 0 | 204 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 60 | 0 | 0 | 77 | 0 | 77 | 4 | 47 | 103 | 13 | 388 | 56 | 35 | 0 | 1 | 52 | 35 | 34 | 70 | 63 | 12 | 352 | 0 | 10 | 126 | 35 | 0 | 17 | 7 | 82 | 36 | 360 | 17 | 0 | 310 | 2 | 0 | 0 | 0 | 19 | 0 | 0 |  | 899 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 127 | 5 | 48 | 0 | 0 | 0 | 47 | 7 | 41 | 0 | 0 | 35 | 0 | 15 | 0 | 0 | 5 | 65 | 0 | 77 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 94 | 0 | 35 | 0 | 1 | 70 | 1080 | 220 | 0 | 54 | 1 | 20 | 115 | 0 | 0 | 367 | 9 | 0 | 721 | 42 | 0 | 0 | 9 | 23 |  | 6055 | 5023 | 11078 | 3368 | 899 | 1688 | 0 | 1773 | 1899 | 174 | 0 | 349 | 58 | 721 | 147 | 2 | 0 | 100
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 8 | 42 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 19 | 21 | 23 | 12 | 17 | 0 | 134 | 40 | 0 | 0 | 17 | 226 | 0 | 0 | 0 |  | 18 | 65 | 70 | 0 | 34 | 50 | 0 | 11 | 0 | 0 | 0 | 280 | 0 | 0 | 190 | 50 | 43 | 0 | 0 | 43 | 0 | 42 | 52 | 0 | 0 | 0 | 16 | 54 | 15 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 61 | 83 | 0 | 207 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 62 | 0 | 0 | 85 | 0 | 81 | 0 | 88 | 117 | 20 | 386 | 56 | 53 | 0 | 0 | 52 | 35 | 31 | 70 | 67 | 12 | 345 | 0 | 0 | 144 | 35 | 0 | 0 | 1 | 92 | 36 | 360 | 54 | 0 | 308 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 900 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 0 | 101 | 5 | 48 | 0 | 0 | 0 | 46 | 11 | 41 | 0 | 0 | 38 | 0 | 15 | 0 | 0 | 5 | 65 | 0 | 75 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 94 | 0 | 40 | 0 | 0 | 70 | 1040 | 180 | 0 | 54 | 0 | 2 | 115 | 0 | 0 | 522 | 1 | 0 | 722 | 4 | 0 | 0 | 0 | 3 |  | 6215 | 4972 | 11187 | 3316 | 900 | 1598 | 0 | 1927 | 2010 | 174 | 0 | 474 | 54 | 722 | 12 | 0 | 0 | 99.99
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 31 | 335 | 0 | 0 | 0 | 8 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 21 | 23 | 25 | 25 | 0 | 134 | 40 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 18 | 78 | 78 | 0 | 40 | 50 | 0 | 16 | 0 | 0 | 0 | 335 | 0 | 0 | 190 | 50 | 43 | 0 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 18 | 68 | 15 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 60 | 83 | 0 | 208 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 138 | 0 | 0 | 95 | 0 | 97 | 0 | 100 | 147 | 27 | 385 | 56 | 88 | 17 | 0 | 52 | 35 | 17 | 77 | 97 | 12 | 375 | 0 | 0 | 162 | 41 | 0 | 2 | 0 | 92 | 36 | 393 | 160 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 900 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 19 | 60 | 0 | 127 | 7 | 80 | 0 | 0 | 0 | 46 | 12 | 94 | 0 | 0 | 43 | 0 | 15 | 0 | 0 | 11 | 65 | 0 | 130 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 94 | 0 | 68 | 0 | 0 | 113 | 1060 | 220 | 0 | 137 | 0 | 0 | 115 | 0 | 0 | 627 | 0 | 0 | 713 | 0 | 0 | 0 | 0 | 0 |  | 6945 | 5685 | 12630 | 3622 | 900 | 1754 | 0 | 2425 | 2194 | 174 | 0 | 780 | 68 | 713 | 0 | 0 | 0 | 99.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 19 | 21 | 23 | 25 | 25 | 0 | 134 | 40 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 18 | 39 | 50 | 0 | 44 | 26 | 0 | 18 | 0 | 0 | 0 | 310 | 0 | 0 | 190 | 50 | 40 | 0 | 0 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 62 | 15 | 0 | 0 | 0 | 0 | 30 | 0 | 33 | 0 | 0 | 62 | 83 | 0 | 207 | 0 | 0 | 0 | 265 | 13 | 2 | 0 | 95 | 0 | 0 | 96 | 0 | 96 | 0 | 100 | 170 | 45 | 385 | 58 | 88 | 17 | 0 | 52 | 35 | 17 | 52 | 104 | 12 | 400 | 0 | 0 | 126 | 53 | 0 | 32 | 0 | 93 | 36 | 393 | 108 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 900 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 22 | 51 | 0 | 127 | 7 | 80 | 0 | 0 | 0 | 46 | 4 | 94 | 0 | 0 | 46 | 0 | 30 | 0 | 0 | 11 | 65 | 0 | 132 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 17 | 0 | 50 | 0 | 70 | 0 | 0 | 70 | 1220 | 220 | 0 | 137 | 0 | 0 | 74 | 0 | 0 | 620 | 0 | 0 | 722 | 0 | 0 | 0 | 0 | 0 |  | 6667 | 5726 | 12393 | 3635 | 900 | 1707 | 0 | 2203 | 2350 | 174 | 0 | 640 | 62 | 722 | 0 | 0 | 0 | 99.95
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 |  | 0 | 350 | 0 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 21 | 23 | 25 | 25 | 0 | 134 | 40 | 0 | 0 | 25 | 227 | 0 | 0 | 0 |  | 18 | 40 | 50 | 0 | 44 | 26 | 0 | 24 | 0 | 0 | 0 | 285 | 0 | 0 | 190 | 50 | 40 | 0 | 0 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 60 | 18 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 61 | 83 | 0 | 207 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 95 | 0 | 0 | 96 | 0 | 110 | 0 | 100 | 170 | 53 | 385 | 57 | 88 | 17 | 0 | 52 | 35 | 17 | 52 | 104 | 12 | 400 | 0 | 0 | 126 | 53 | 0 | 35 | 0 | 92 | 36 | 395 | 108 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 899 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 20 | 51 | 0 | 127 | 7 | 80 | 0 | 0 | 0 | 46 | 4 | 95 | 0 | 0 | 43 | 0 | 30 | 0 | 0 | 11 | 65 | 0 | 132 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 1244 | 180 | 0 | 137 | 0 | 0 | 74 | 0 | 0 | 619 | 0 | 0 | 720 | 0 | 0 | 0 | 0 | 0 |  | 6565 | 5580 | 12145 | 3567 | 899 | 1560 | 0 | 2155 | 2373 | 174 | 0 | 637 | 60 | 720 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 350 | 0 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 21 | 23 | 33 | 25 | 0 | 134 | 40 | 0 | 0 | 25 | 227 | 0 | 0 | 0 |  | 18 | 40 | 50 | 0 | 45 | 26 | 0 | 24 | 0 | 0 | 0 | 290 | 0 | 0 | 190 | 50 | 43 | 0 | 0 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 60 | 18 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 61 | 83 | 0 | 207 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 95 | 0 | 0 | 97 | 0 | 113 | 0 | 100 | 170 | 52 | 385 | 55 | 88 | 17 | 0 | 52 | 35 | 17 | 52 | 105 | 12 | 400 | 0 | 0 | 72 | 53 | 0 | 35 | 0 | 92 | 36 | 395 | 108 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 900 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 20 | 51 | 0 | 101 | 7 | 80 | 0 | 0 | 0 | 46 | 4 | 95 | 0 | 0 | 46 | 0 | 30 | 0 | 0 | 8 | 66 | 0 | 133 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 17 | 0 | 50 | 0 | 35 | 0 | 0 | 35 | 1244 | 180 | 0 | 137 | 0 | 0 | 74 | 0 | 0 | 622 | 0 | 0 | 718 | 0 | 0 | 0 | 0 | 0 |  | 6501 | 5525 | 12026 | 3547 | 900 | 1506 | 0 | 2105 | 2376 | 174 | 0 | 640 | 60 | 718 | 0 | 0 | 0 | 99.96
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 |  | 0 | 350 | 0 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 21 | 22 | 23 | 33 | 25 | 0 | 134 | 0 | 0 | 0 | 25 | 227 | 0 | 0 | 0 |  | 18 | 39 | 50 | 0 | 44 | 26 | 0 | 22 | 0 | 0 | 0 | 290 | 0 | 0 | 190 | 50 | 44 | 0 | 0 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 62 | 31 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 61 | 83 | 0 | 210 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 45 | 0 | 0 | 96 | 0 | 120 | 0 | 100 | 170 | 53 | 385 | 56 | 88 | 17 | 0 | 52 | 35 | 17 | 52 | 106 | 12 | 400 | 11 | 0 | 72 | 53 | 0 | 35 | 0 | 92 | 36 | 395 | 108 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 897 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 20 | 51 | 0 | 127 | 8 | 64 | 0 | 0 | 0 | 46 | 4 | 95 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 8 | 67 | 0 | 134 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 50 | 0 | 35 | 0 | 0 | 35 | 1244 | 220 | 0 | 137 | 0 | 0 | 74 | 0 | 0 | 622 | 0 | 0 | 594 | 0 | 0 | 0 | 0 | 0 |  | 6350 | 5435 | 11785 | 3570 | 897 | 1541 | 0 | 1978 | 2371 | 134 | 0 | 638 | 62 | 594 | 0 | 0 | 0 | 99.95
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 350 | 0 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 21 | 22 | 23 | 33 | 25 | 0 | 134 | 0 | 0 | 0 | 25 | 227 | 0 | 0 | 0 |  | 18 | 16 | 17 | 0 | 45 | 26 | 0 | 38 | 0 | 0 | 0 | 305 | 0 | 0 | 190 | 50 | 44 | 0 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 54 | 31 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 60 | 83 | 0 | 210 | 0 | 0 | 0 | 280 | 13 | 5 | 0 | 45 | 0 | 0 | 96 | 0 | 135 | 0 | 100 | 155 | 55 | 385 | 57 | 88 | 17 | 0 | 69 | 35 | 17 | 17 | 105 | 12 | 400 | 16 | 0 | 35 | 53 | 0 | 35 | 0 | 92 | 36 | 395 | 54 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 896 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 67 | 0 | 131 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 50 | 0 | 35 | 0 | 0 | 35 | 1244 | 220 | 0 | 137 | 0 | 0 | 74 | 0 | 0 | 623 | 0 | 0 | 518 | 0 | 0 | 0 | 0 | 0 |  | 6108 | 5120 | 11228 | 3571 | 896 | 1597 | 0 | 1846 | 2368 | 134 | 0 | 244 | 54 | 518 | 0 | 0 | 0 | 99.94
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 350 | 0 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 21 | 22 | 23 | 25 | 25 | 0 | 134 | 0 | 0 | 0 | 20 | 228 | 0 | 0 | 0 |  | 18 | 14 | 17 | 0 | 45 | 14 | 0 | 39 | 0 | 0 | 0 | 295 | 0 | 0 | 190 | 50 | 44 | 0 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 58 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 60 | 83 | 0 | 209 | 0 | 0 | 0 | 300 | 13 | 5 | 0 | 45 | 0 | 0 | 96 | 0 | 149 | 0 | 50 | 155 | 75 | 385 | 57 | 70 | 17 | 0 | 52 | 35 | 17 | 17 | 107 | 12 | 400 | 16 | 0 | 35 | 53 | 0 | 35 | 0 | 93 | 33 | 395 | 17 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 898 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 133 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 50 | 0 | 35 | 0 | 0 | 35 | 1244 | 220 | 0 | 137 | 0 | 0 | 74 | 0 | 0 | 623 | 0 | 0 | 517 | 0 | 0 | 0 | 0 | 0 |  | 6001 | 5120 | 11121 | 3544 | 898 | 1617 | 0 | 1778 | 2370 | 134 | 0 | 205 | 58 | 517 | 0 | 0 | 0 | 99.93
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 |  | 0 | 400 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 21 | 22 | 23 | 25 | 8 | 0 | 131 | 0 | 0 | 0 | 8 | 228 | 0 | 0 | 0 |  | 18 | 14 | 17 | 0 | 45 | 12 | 0 | 39 | 0 | 0 | 0 | 310 | 0 | 0 | 190 | 50 | 44 | 0 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 56 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 62 | 83 | 0 | 209 | 0 | 0 | 0 | 300 | 13 | 5 | 0 | 45 | 0 | 0 | 96 | 0 | 100 | 0 | 50 | 155 | 107 | 385 | 57 | 35 | 17 | 0 | 52 | 35 | 17 | 17 | 53 | 12 | 400 | 0 | 0 | 17 | 40 | 0 | 35 | 0 | 92 | 18 | 395 | 17 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 898 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 133 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 1244 | 220 | 0 | 137 | 0 | 0 | 74 | 0 | 0 | 372 | 0 | 0 | 517 | 0 | 0 | 0 | 0 | 0 |  | 5874 | 4931 | 10805 | 3603 | 898 | 1733 | 0 | 1577 | 2118 | 131 | 0 | 172 | 56 | 517 | 0 | 0 | 0 | 99.92
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8870400 | 0 |  | 0 | 10158800 | 0 | 0 | 0 | 266095 | 7200467 | 0 | 0 | 0 | 50400 | 1450560 | 0 | 0 | 0 | 0 | 521640 | 417247 | 391123 | 0 | 490200 | 480960 | 600700 | 618200 | 410880 | 0 | 3155433 | 832000 | 0 | 0 | 252633 | 5329429 | 0 | 0 | 0 |  | 251760 | 617520 | 727379 | 0 | 593280 | 565440 | 0 | 498240 | 0 | 0 | 0 | 7636700 | 0 | 0 | 4499636 | 1242240 | 1048752 | 0 | 0 | 959328 | 0 | 228976 | 515712 | 0 | 0 | 0 | 397590 | 1296000 | 525120 | 0 | 0 | 13050 | 0 | 696960 | 0 | 815688 | 109145 | 0 | 1398432 | 1863360 | 0 | 5202690 | 0 | 0 | 0 | 7136000 | 343440 | 85824 | 0 | 885709 | 0 | 0 | 2126400 | 0 | 1568160 | 138780 | 1123200 | 2200320 | 595490 | 9139000 | 1185600 | 1107840 | 117927 | 26641 | 1231964 | 645304 | 367998 | 665760 | 1249080 | 242880 | 8623700 | 39360 | 307440 | 1585440 | 715091 | 0 | 422640 | 192072 | 1201920 | 576720 | 9152800 | 759418 | 0 | 8399999 | 3360 | 0 | 0 | 0 | 415882 | 0 | 150000 |  | 21817454 | 0 | 7796736 | 0 | 0 | 0 | 0 | 0 | 100320 | 249856 | 0 | 3049000 | 148547 | 581184 | 0 | 0 | 0 | 312392 | 67129 | 756160 | 0 | 0 | 296793 | 0 | 168141 | 0 | 0 | 152406 | 1515490 | 0 | 3115000 | 0 | 0 | 4319818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8731636 | 49920 | 0 | 942432 | 0 | 483782 | 0 | 39673 | 758016 | 30059100 | 5324980 | 0 | 1706400 | 34080 | 478080 | 1406976 | 0 | 0 | 10560000 | 212493 | 0 | 16399373 | 1044720 | 0 | 3709 | 357752 | 579440 |  | 137929324 | 123618988 | 261548312 | 84401564 | 21817454 | 40245360 | 0 | 30019723 | 53649589 | 3987433 | 0 | 5884644 | 1296000 | 16399373 | 3843812 | 3360 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25546752 | 0 |  | 0 | 32304984 | 0 | 0 | 0 | 4688593.9 | 21961424.35 | 0 | 0 | 0 | 904680 | 28169875.2 | 0 | 0 | 0 | 0 | 9525146.4 | 6575812.72 | 7153639.67 | 0 | 367650 | 0 | 0 | 0 | 7358860.8 | 0 | 0 | 0 | 0 | 0 | 4784869.02 | 17000878.51 | 0 | 0 | 0 |  | 4428458.4 | 10874527.2 | 13027357.89 | 0 | 11610489.6 | 9307142.4 | 0 | 0 | 0 | 0 | 0 | 21306393 | 0 | 0 | 15073780.6 | 4012435.2 | 3534294.24 | 0 | 0 | 3846905.28 | 0 | 4100960.16 | 9313758.72 | 0 | 0 | 0 | 298192.5 | 8501760 | 1633123.2 | 0 | 0 | 0 | 0 | 2599660.8 | 0 | 3711380.4 | 373275.9 | 0 | 7761297.6 | 9726739.2 | 0 | 14515505.1 | 0 | 0 | 0 | 22050240 | 257580 | 65226.24 | 0 | 18068463.6 | 0 | 0 | 40848144 | 0 | 27615297.6 | 0 | 20004192 | 38175552 | 9873224.2 | 24218350 | 22597536 | 20783078.4 | 2115610.38 | 0 | 20142611.4 | 12544709.76 | 6601884.12 | 12722673.6 | 24244642.8 | 4325692.8 | 22939042 | 671875.2 | 0 | 28997697.6 | 11999226.98 | 0 | 7552576.8 | 0 | 21658598.4 | 9769636.8 | 27183816 | 10692605.44 | 0 | 58547993.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 61307045.74 | 0 | 23000371.2 | 0 | 0 | 0 | 0 | 0 | 1887019.2 | 4699791.36 | 0 | 9634840 | 704112.78 | 10019612.16 | 0 | 0 | 0 | 5594940.72 | 1231817.15 | 12711049.6 | 0 | 0 | 5315562.63 | 0 | 3011405.31 | 0 | 0 | 115371.342 | 16715854.7 | 0 | 26290600 | 0 | 0 | 14255399.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25496377.12 | 852633.6 | 0 | 18679002.24 | 0 | 9636937.44 | 0 | 0 | 15039037.44 | 194782968 | 16560687.8 | 0 | 33018840 | 0 | 0 | 24411033.6 | 0 | 0 | 77088000 | 0 | 0 | 108399855.53 | 0 | 0 | 0 | 0 | 0 |  | 853168381.11 | 720460166.062 | 1573628547.172 | 242207602.682 | 61307045.74 | 129848483.08 | 0 | 548621472.55 | 373425415.73 | 0 | 0 | 101316911.86 | 8501760 | 108399855.53 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 19 | 15 | 23 | 31 | 25 | 0 | 134 | 40 | 0 | 0 | 9 | 223 | 0 | 0 | 0 |  | 6 | 25 | 68 | 0 | 26 | 50 | 0 | 8 | 0 | 0 | 0 | 330 | 0 | 0 | 189 | 50 | 43 | 0 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 50 | 11 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 57 | 83 | 0 | 209 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 95 | 0 | 51 | 20 | 37 | 103 | 13 | 387 | 56 | 52 | 0 | 4 | 52 | 20 | 17 | 3 | 47 | 12 | 357 | 0 | 33 | 117 | 35 | 0 | 17 | 31 | 30 | 22 | 393 | 17 | 0 | 310 | 0 | 0 | 0 | 0 | 72 | 0 | 36 |  | 900 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 130 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 0 | 0 | 6 | 15 | 1160 | 220 | 0 | 54 | 2 | 84 | 48 | 0 | 0 | 366 | 26 | 0 | 721 | 143 | 0 | 0 | 54 | 75 |  | 11095 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 31 | 335 | 0 | 0 | 0 | 8 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 21 | 23 | 25 | 25 | 0 | 134 | 40 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 18 | 78 | 78 | 0 | 40 | 50 | 0 | 16 | 0 | 0 | 0 | 335 | 0 | 0 | 190 | 50 | 43 | 0 | 0 | 43 | 0 | 43 | 52 | 0 | 0 | 0 | 18 | 68 | 15 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 60 | 83 | 0 | 208 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 138 | 0 | 0 | 95 | 0 | 97 | 0 | 100 | 147 | 27 | 385 | 56 | 88 | 17 | 0 | 52 | 35 | 17 | 77 | 97 | 12 | 375 | 0 | 0 | 162 | 41 | 0 | 2 | 0 | 92 | 36 | 393 | 160 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 900 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 19 | 60 | 0 | 127 | 7 | 80 | 0 | 0 | 0 | 46 | 12 | 94 | 0 | 0 | 43 | 0 | 15 | 0 | 0 | 11 | 65 | 0 | 130 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 94 | 0 | 68 | 0 | 0 | 113 | 1060 | 220 | 0 | 137 | 0 | 0 | 115 | 0 | 0 | 627 | 0 | 0 | 713 | 0 | 0 | 0 | 0 | 0 |  | 12630 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 22 | 23 | 33 | 25 | 0 | 132 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 18 | 70 | 84 | 0 | 35 | 50 | 0 | 30 | 0 | 0 |  | 310 | 0 | 0 | 190 | 50 | 44 | 0 | 0 | 43 | 0 | 36 | 52 | 0 | 0 |  | 18 | 82 | 25 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 61 | 86 | 0 | 210 | 0 | 0 | 0 | 310 | 13 | 5 | 0 | 300 | 0 | 0 | 96 | 0 | 149 | 0 | 100 | 200 | 120 | 385 | 57 | 105 | 17 | 0 | 52 | 35 | 17 | 106 | 84 | 12 | 400 | 16 | 0 | 162 | 53 | 0 | 35 | 0 | 92 | 36 | 400 | 160 | 0 | 612 | 15 | 0 | 0 | 0 |  |  |  |  | 668 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 127 | 10 | 110 | 0 | 0 | 0 | 45 | 25 | 95 | 0 | 0 | 43 | 0 | 30 | 0 | 0 | 11 | 67 | 0 | 130 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 95 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 137 | 0 | 0 | 115 | 0 | 0 | 617 | 0 | 0 | 730 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 20 | 22 | 23 | 33 | 25 | 0 | 132 | 0 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 50 | 65 | 0 | 31 | 50 | 0 | 30 | 0 | 0 | 0 | 310 | 0 | 0 | 190 | 50 | 44 | 0 | 0 | 43 | 0 | 35 | 52 | 0 | 0 |  | 18 | 66 | 25 | 0 | 0 | 1.6 | 0 | 30 | 0 | 36 | 0 | 0 | 60 | 86 | 0 | 210 | 0 | 0 | 0 | 300 | 13 | 5 | 0 | 100 | 0 | 0 | 96 | 0 | 52 | 20 | 50 | 100 | 120 | 385 | 55 | 52 | 17 | 5 | 52 | 35 | 17 | 106 | 35 | 12 | 400 | 0 | 50 | 100 | 35 | 0 | 17 | 35 | 51 | 36 | 400 | 17 | 0 | 612 | 15 | 0 | 0 | 0 | 70 |  |  |  | 719 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 0 | 120 | 10 | 16 | 0 | 0 | 0 | 45 | 0 | 50 | 0 | 0 | 26 | 0 | 22 | 0 | 0 | 5 | 67 | 0 | 130 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 95 | 0 | 113 | 0 | 8 | 113 | 1244 | 220 |  | 51 | 6 | 100 | 54 | 0 | 0 | 375 | 30 | 0 | 730 | 170 | 0 |  | 29 | 47 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 17 | 33 | 8 | 0 | 132 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 290 | 0 | 0 | 190 | 50 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | 30 | 0 | 0 | 1 | 0 | 30 | 0 | 36 | 0 | 0 | 61 | 83 | 0 | 210 | 0 | 0 | 0 | 300 | 13 | 5 | 0 | 0 | 0 | 0 | 75 | 0 | 50 | 11 | 0 | 0 | 0 | 335 | 35 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 22 | 0 | 0 | 0 | 0 | 12 | 0 | 18 | 330 | 0 | 0 | 502 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 897 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 130 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 960 | 180 | 0 | 0 | 2 | 32 | 0 | 0 | 0 | 375 | 13 | 0 | 518 | 60 | 0 | 0 | 22 | 40 | 0 |  |  |  | 124646924 | 21817454 | 0 | 53649589 | 35904367 | 1296000 | 3843812 | 3360 | 3987433 |  |  |  | 245148939
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [10 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 124.6469 | 21.8175 | 0 | 53.6496 | 35.9044 | 1.296 | 3.8438 | 0.00336 | 3.9874
| Minimum Generation |  | 8983 | 5:00
| Highest Generation |  | 12630 | 18:00 | [129 empty] | 0 | [76 empty] | 245.1489
| Day Peak Generation |  | 11095 | 12:00
| Evening Peak Generation |  | 12630 | 18:00 | [206 empty] | 202699852
| HVDC Max Flow |  | 901 | 9:00 | [206 empty] | 202.6999
| HVDC EvPeak Flow |  | 900 | 18:00
| Load factor L.F |  | 86.29% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-11-08
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-11-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11095 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 8669
Evening Peak Generation : |  |  | 12630 | MW Hour : | 18:00 | Available Max Generation : |  | 13493
E.P. Demand (at gen end) : |  |  | 12630 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 12000
Maximum Generation : |  |  | 12630 | MW Hour : | 18:00 | Reserve(Generation end) |  | 1493
Total Gen. (MKWH) : |  |  | 261.5483 | System Load Factor : | 86.29% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 782 | MW at | 22:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-11-08
Actual : |  | 99.86 | Ft.(MSL) , | Rule curve : | 108.3 | Ft.( MSL )
Gas Consumed : |  | Total = | 881.39 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 372056085.762 | Adani : | 108399855.53
|  |  | Coal : | 373425415.73 | Oil: | 649938384.41 | Total: | 1503819741.432
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4533.8427 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1245.692 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1744.9061 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1516.5797 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1247.9061 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 928.0993 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 520.2585 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 433.5457 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 847.94 |  |  | 0 | 0%
Total |  | 0 |  | 13018.7703 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:08 | 17:30 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to Annual
Maintenance at 132/33kV TR-01.
08:09 | 17:28 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to Annual
Maintenance at 132/33kV TR-01.
08:15 | 18:01 | Natore-Rajshahi 132kV Ckt-1 Scheduled S/D from Natore
132/33kV end Due to Annual maintenance and from Rajshahi
132/33kV end Due to For Annual Maintenance work.
08:15 | 13:37 | Juldah 132/33kV S/S Julda power plant unit-1 Scheduled S/D
Due to scheduled shutdown.
08:23 | 17:55 | Bagerhat-Mongla 132 kV Ckt-2 Scheduled S/D from Mongla
132/33kV end Due to Annual maintenance and from Bagerhat
132/33kV end Due to Annual Shutdown work.
08:25 | 15:53 | Jaldhaka-Saidpur 132kV Ckt-2 Scheduled S/D from Jaldhaka
132/33kV end Due to Annual Maintenance work. and from
Saidpur 132/33kV end Due to For annual maintanance.
08:29 | 17:21 | Cumilla(N)-Meghnaghat 230 kV Ckt-2 Scheduled S/D from
Meghnaghat 230/132kV end Due to For Annual Maintenance
08:44 | 17:02 | Sreemongol 132/33kV S/S 132/33kv T-1AB LT Scheduled S/D Due to Annual Maintenance.
08:45 | 17:01 | Sreemongol 132/33kV S/S 132/33kv T-1AB HT Scheduled S/D Due to Annual Maintenance.
08:49 | 15:41 | Aminbazar 400/230/132kV S/S 230 kv Bus 02 Scheduled S/D Due to Annual maintenance
08:53 | 13:38 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from
Aminbazar 400/230/132kV end Due to Annual maintenance
08:55 | 19:55 | Sylhet (South) S/S Trafo-1 LT Project Work S/D Due to PDB Maintenance works.
08:56 | 19:55 | Sylhet (South) S/S Trafo-1 HT Project Work S/D Due to PDB Maintenance works.
08:57 | 16:18 | Ashuganj-Brahmanbaria 132kV Ckt-1 Scheduled S/D from
Brahmanbaria 132/33kV end.
08:59 | 12:24 | Sylhet 132/33kV S/S Sylhet-90MW P/S Project Work S/D Due to
Annual Maintenance Purpose.
09:01 |  | Bhulta-Rampura 230 kV Ckt-2 Scheduled S/D from Bhulta
400/230kV end Due to S/D taken by Rampura GSS. and from
Rampura 230/132kV end Due to Annual Maintenance 2024-25
09:02 | 15:31 | Rajbari 132/33kV S/S Bheramara-1 Scheduled Shut down.
09:02 | 15:32 | Rajbari 132/33kV S/S Bheramara-2 Scheduled Shut down.
09:03 | 15:31 | Bheramara P/S-Faridpur 132 kV Ckt-1 Scheduled S/D from
Bheramara 230/132kV end Due to A/M
09:03 | 15:32 | Bheramara P/S-Faridpur 132 kV Ckt-2 Scheduled S/D from
Bheramara 230/132kV end Due to A/M
09:11 | 16:01 | Bhaluka 132/33kV S/S Bus A Forced S/D Due to For Mymensingh
CKT-02 Anuual Maintenace purpose.
09:27 |  | Madaripur 132/33kV S/S Aux Tr-01 HT Scheduled S/D Due to Annual Maintenance.
09:27 |  | Madaripur 132/33kV S/S Aux Tr-01 LT Scheduled S/D Due to Annual Maintenance.
09:32 |  | BIPTC S/S 20DF31 Scheduled S/D Due to Shutdown is taken for
annual maintenance work
09:32 | 17:05 | BSRM-Cumilla(N) 230 kV Ckt-2 Scheduled S/D from BSRM
230/33kV end Due to Deadline checking
09:44 | 16:31 | Dohazari-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Dohazari
132/33kV end Due to Annual maintenance Bay and from
Shikalbaha 230/132kV end Due to Annual Maintenance
09:54 | 11:09 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi
230/132/33kV end.
10:10 | 17:48 | Jamalpur 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance.
10:10 | 17:48 | Jamalpur 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance.
10:20 | 16:00 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Annual Maintenance.
10:20 | 10:56 | Sherpur 132/33kV S/S Bus B Scheduled S/D Due to Annual Maintenance.
10:20 | 15:59 | Sherpur 132/33kV S/S Transformer- 01 HT Scheduled S/D Due Annual Maintenance.
10:32 | 12:51 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT
Scheduled S/D Due to Annual Maintenance
10:32 | 12:50 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) HT
Scheduled S/D Due to Annual Maintenance
11:10 | 17:02 | Sherpur 132/33kV S/S Bus A Scheduled S/D Due to Annual
Maintenance
11:16 | 13:16 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi
230/132/33kV end Due to Regular maintenance work by SPMD
| 12:29 | Chandpur 132/33kV S/S 402T HT is restored.
| 12:38 | Chandpur 132/33kV S/S 402T LT is restored.
13:23 | 15:17 | Tongi 230/132/33kV S/S Tongi-Uttara Ckt Scheduled S/D Due
to Regular maintenance work by SPMD
14:15 | 15:55 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from
Aminbazar 400/230/132kV end Due to Annual Maintenance
15:19 | 16:47 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D Due to Relay testing.
16:03 |  | Ghorashal GIS 230/33kV transformer was switched ON. (no load).
| 16:26 | Patuakhali 132/33kV S/S 415T (T-2) HT is restored.
| 16:27 | Patuakhali 132/33kV S/S 415T (T-2) LT is restored.
| 16:28 | Barguna 132/33kV S/S Transformer-1 HT is restored.
| 16:28 | Barguna 132/33kV S/S Transformer-1 LT is restored.
| 16:52 | Amnura 132/33kV S/S T-1 (406T) HT is restored.
| 16:57 | Barishal 132/33kV S/S Bus B is restored.
| 16:57 | Amnura 132/33kV S/S T-1 (406T) LT is restored.
| 17:40 | Jamalpur 132/33kV S/S Bus-A is restored.
18:58 |  | Sreepur BR PowerGen 132/11kV T-1 transformer was switched ON.
19:04 |  | Sreepur BR PowerGen 132/11kV T-2 transformer was switched ON.
06:14 |  | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Haripur
230/132kV end Due to OPGW Changing Work. and from
Meghnaghat 230/132kV end Due to As per request of NLDC
06:43 |  | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing 1.
86 2. LBB protection operated( RED670) relays Due to During this time Matuail line was also tripped.
06:43 |  | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing 1) Distance Trip: i. | [5 empty] | 54 MW load interrup in
06:43 |  | Zone-2 ii. Phase-Y iii. Distance-6.2 km 2) Lock out relays Due to Loop disconnect from line DS in Y phase. | [5 empty] | Siddhirganj 132/33 kV end.
06:55 |  | Bogura 132/33kV S/S Transformer-1 LT Scheduled S/D Due to maintenance work.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-11-07
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 411 | 8870400
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10158800
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 31 | 266095 | Low demand.
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7200467
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 50400 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 521640
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1450560 | Fuel shortage
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 417247
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 391123
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 40 | 971160 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 23 | 600700 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 618200 | Engine problem
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 410880 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 138 | 885709 | Low demand.
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 97 | 1568160 | Fuel shortage
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1107840 | Fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 39360 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1585440
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 192072
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 576720 | Fuel shortage
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 2165 | 37882973
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 252633
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 138780
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 565440
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 174 | 3987433
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5329429
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 117927 | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 78 | 617520 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 78 | 727379 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1123200
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 498240
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 40 | 593280 | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26641
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1231964 | Fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 645304 | Fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 367998 | Fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 242880 | Fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 41 | 715091 | Fuel shortage
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 160 | 759418
55 | SS Power I |  | IPP | 2*612 | 1224 | 312 | 8399999 | Coal shortage
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 3360
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 0 | 0 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1432 | 26343916
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 335 | 7636700 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 393 | 9152800
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 43 | 1048752 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 190 | 4499636
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 959328 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 27 | 595490 | Fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 228976 | Engine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1242240 | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 147 | 2200320 | High Voltage
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 68 | 1296000
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 515712
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 397590 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 77 | 665760 | High Voltage
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 97 | 1249080 | Engine problem
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 1201920 | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 415882
| Cumilla Area Total |  |  |  | 2917 | 1675 | 33306186
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 15 | 525120 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13050
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 95 | 2126400 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 56 | 1185600 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 307440
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 251760 | Fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 2 | 422640 | Fuel shortage
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 150000
| Mymensingh Area Total |  |  |  | 646 | 186 | 4982010
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Under maint.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 696960 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 109145
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 36 | 815688 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 85824 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1398432
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1863360
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 208 | 5202690
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 343440 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7136000 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 385 | 9139000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 375 | 8623700
| Sylhet Area Total |  |  |  | 2417 | 1487 | 35414239
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 900 | 21817454
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 19 | 100320 | Engine problem
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 60 | 249856 | Engine problem
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 321 | 7796736 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 49920 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 478080
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 627 | 10560000 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1944 | 41052366
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 581184 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 7 | 148547
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 127 | 3049000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 30059100 | FGMO
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5324980
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 137 | 1706400 | Fuel shortage
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Under maint.
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3709
| Barisal Area Total |  |  |  | 2236 | 1631 | 40872920
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 46 | 312392 | Engine problem
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 12 | 67129 | Machine problem.
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Lube Oil porblem
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 43 | 296793 | Engine problem
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 177 | 4319818 | Gas shortage
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 8731636
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 15 | 168141 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 152406
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 756160 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 942432 | Fuel shortage
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 758016
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34080
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 713 | 16399373
135 | Sirajganj 68 MW Solar Park |  | NWPGCL | 68 | 68 | 0 | 357752
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 579440
| Rajshahi Area Total |  |  |  | 3449 | 1732 | 33875568
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 65 | 1515490 | Machine problem.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 130 | 3115000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 68 | 483782 | Low demand.
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39673
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1406976
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 212493
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 1044720
| Rangpur Area Total |  |  |  | 950 | 378 | 7818134
| Total |  |  |  | 27086 | 12630 | 261548312
| Eastern Grid Total |  |  |  | 16752 | 6945 | 137929324
| Western Grid Total |  |  |  | 10334 | 5685 | 123618988
| National Grid Total |  |  |  | 27086 | 12630 | 261548312
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-11-07
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8635.21 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3803.1 | MW
i) Dhaka area |  |  | 4813.21 |  | MW | i) Khulna area |  |  |  | 1454 | MW
ii) Chattogram area |  |  | 1250 |  | MW | ii) Barishal area |  |  |  | 347.7 | MW
iii) Cumilla area |  |  | 1120 |  | MW | iii) Rajshahi area |  |  |  | 1199.4 | MW
iv) Mymensingh area |  |  | 975 |  | MW | iv) Rangpur area |  |  |  | 802 | MW
v) Sylhet area |  |  | 477 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12438.31 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jashore | 107 | 18:00 | 133 | Rajbari | 66 | 18:00
2 | AKSML | 105 | 03:00 | 68 | Jhenaidah | 110 | 18:00 | 134 | Rajendrapur | 90 | 18:30
3 | Aftabnagar | 54 | 12:00 | 69 | Joydebpur | 170 | 18:00 | 135 | Rajshahi | 96 | 18:30
4 | Agargaon | 103 | 13:00 | 70 | Joypurhat | 44 | 18:00 | 136 | Rajshahi-230 | 60 | 13:00
5 | Agrabad | 88 | 18:00 | 71 | Juldah | 14 | 18:00 | 137 | Ramganj | 96 | 18:00
6 | Amnura | 48 | 18:00 | 72 | KSRM | 26.5 | 14:00 | 138 | Rampur | 38 | 18:00
7 | Ashuganj | 82 | 00:00 | 73 | Kabirpur | 248 | 17:00 | 139 | Rangamati | 14 | 18:00
8 | BSRM | 66 | 02:00 | 74 | Kachua | 60 | 18:00 | 140 | Rangpur | 122 | 18:30
9 | Bagerhat | 77 | 18:00 | 75 | Kallyanpur | 93 | 18:00 | 141 | Ruppur | 6.8 | 15:00
10 | Bakulia | 90 | 13:00 | 76 | Kalurghat | 36 | 10:00 | 142 | SSM | 12 | 05:00
11 | Banani | 58.8 | 13:00 | 77 | Kamrangirchar | 61 | 13:00 | 143 | Saidpur | 90 | 18:00
12 | Bangabhaban | 18 | 10:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 109 | 18:00
13 | Barapukuria | 48 | 13:00 | 79 | Kazla | 93 | 13:00 | 145 | Satmasjid | 90 | 18:30
14 | Barguna | 16 | 18:30 | 80 | Keranigonj | 69 | 19:00 | 146 | Savar | 196 | 12:00
15 | Barishal | 92 | 21:00 | 81 | Khagrachori | 24 | 18:00 | 147 | SevenRings | 15.59 | 05:00
16 | Barishal-230 | 70 | 18:00 | 82 | Khulna | 74 | 18:30 | 148 | ShahCement | 10 | 15:00
17 | Baroaulia | 57 | 12:00 | 83 | Khulshi | 142 | 11:00 | 149 | Shahjadpur | 65 | 18:30
18 | Baroirhat | 48 | 18:00 | 84 | Kishoreganj | 128 | 18:30 | 150 | Shahjibazar | 107 | 21:00
19 | Bashundhara | 157 | 18:00 | 85 | Kodda | 294 | 18:00 | 151 | Shahmirpur | 50 | 15:00
20 | BashundharaCement | 11 | 00:00 | 86 | Kulaura | 36 | 18:00 | 152 | Shariatpur | 62 | 18:00
21 | Beanibazar | 54 | 18:00 | 87 | Kurigram | 49 | 18:00 | 153 | Sherpur | 118 | 18:00
22 | Benapole | 60 | 18:00 | 88 | Kushtia | 130 | 18:00 | 154 | Shikalbaha | 25 | 11:00
23 | Bhaluka | 122 | 18:00 | 89 | Lalbag | 76 | 19:00 | 155 | Shitalakhya | 75.6 | 12:00
24 | Bhandaria | 49 | 18:30 | 90 | Lalmonirhat | 46 | 18:00 | 156 | Sholosohor | 43 | 15:00
25 | Bhangura | 30 | 19:00 | 91 | MI_Cement | 15.1 | 16:00 | 157 | Shyampur | 152 | 11:00
26 | Bheramara(GK) | 47 | 18:30 | 92 | Madanganj | 31 | 19:00 | 158 | Siddhirganj | 104 | 17:00
27 | Bhulta | 280 | 19:00 | 93 | Madaripur | 76 | 21:00 | 159 | Sirajganj | 74 | 19:30
28 | Bog-Sherpur | 64 | 18:00 | 94 | Madartek | 74.48 | 19:00 | 160 | Sonargaon | 83 | 11:00
29 | Bogura | 128 | 19:00 | 95 | Madunaghat | 49 | 23:00 | 161 | Sreemongol | 61 | 18:00
30 | Borhanuddin | 59 | 21:00 | 96 | Magura | 52 | 18:30 | 162 | Sreepur | 66 | 18:00
31 | Brahmanbaria | 140 | 18:00 | 97 | Mahasthangarh | 56 | 18:00 | 163 | Srinagar | 37.88 | 13:00
32 | Cantonment | 106 | 13:00 | 98 | Manikganj | 111 | 18:00 | 164 | Sunamganj | 45 | 19:30
33 | Chandpur | 57 | 18:00 | 99 | Maniknagar | 60 | 12:00 | 165 | Sylhet | 54 | 22:00
34 | Chandraghona | 32 | 18:00 | 100 | Matarbari | 40 | 18:00 | 166 | Sylhet-132 | 114 | 18:00
35 | Chapai | 51 | 18:30 | 101 | Matuail | 60 | 17:00 | 167 | TK | 27.4 | 21:00
36 | Charsaidpur | 42 | 17:00 | 102 | Millgate | 115 | 15:00 | 168 | Tangail | 158 | 18:00
37 | Chauddagram | 55 | 18:00 | 103 | Mirpur | 123 | 18:00 | 169 | Thakurgaon | 75 | 18:30
38 | Chhatak | 25 | 18:30 | 104 | Mirsorai | 6 | 18:00 | 170 | Tongi | 124 | 11:00
39 | Chowmuhani | 172 | 19:30 | 105 | Mirzapur | 34 | 12:00 | 171 | Ullahpara | 33 | 20:00
40 | Chuadanga | 87 | 18:00 | 106 | Mithapukur | 46 | 18:00 | 172 | Ullon | 37 | 18:00
41 | Coxsbazar | 107 | 18:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 78 | 11:00
42 | Cumilla(N) | 143 | 20:00 | 108 | Mogbazar | 120.6 | 16:00 | 174 | UttaraNew | 60 | 09:00
43 | Cumilla(S) | 141 | 18:00 | 109 | Mongla | 43 | 13:00 | 175 | Zigatola | 78 | 19:00
44 | Daudkandi | 132 | 18:30 | 110 | Motijheel | 40 | 13:00
45 | Dhaka | 34 | 11:00 | 111 | Munshiganj | 86 | 19:30
46 | Dhamrai | 124 | 18:00 | 112 | Mymensingh | 204 | 18:00
47 | Dhanmondi | 126 | 13:00 | 113 | Naogaon | 98 | 18:00
48 | Dohazari | 85 | 19:00 | 114 | Narail | 48 | 18:00
49 | Faridpur | 128 | 18:00 | 115 | Narinda | 70 | 13:00
50 | Fatullah | 82 | 11:00 | 116 | Narshingdi | 164 | 18:00
51 | Fenchuganj | 33 | 18:00 | 117 | Natore | 117 | 18:00
52 | Feni | 94 | 18:00 | 118 | Nawabganj | 36 | 18:00
53 | GPH | 90 | 10:00 | 119 | Netrakona | 103 | 18:00
54 | Ghatail | 56 | 18:00 | 120 | New | 52.5 | 11:00
55 | Ghorashal | 51 | 18:00 | 121 | Niamatpur | 47 | 18:00
56 | Goalpara | 36 | 13:00 | 122 | Noapara | 35 | 18:30
57 | Gollamari | 62 | 13:00 | 123 | PHP | 3 | 09:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-11-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 389 | 04:00 | 377 | 12:00 | Kaliakoir | 378 | 21:00 | 362 | 12:00
| Ashuganj | 412 | 20:42 | 397 | 14:14 | Madunaghat | 399 | 00:00 | 390 | 12:00
| Bhulta | 404 | 20:00 | 389 | 12:00 | Meghnaghat | 384 | 04:00 | 373 | 12:00
| Bibiana | 394 | 19:00 | 385 | 12:00 | Payra | 410 | 06:00 | 405 | 12:00
| BIPTC | 401 | 03:00 | 393 | 18:00 | Rahanpur | 395 | 14:00 | 389 | 00:00
| Bogura | 388 | 14:00 | 38 | 15:00 | Rampal | 404 | 05:00 | 392 | 18:00
| Gopalganj | 400 | 04:00 | 389 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 233 | 01:00 | 224 | 12:00 | Haripur | 232 | 05:00 | 223 | 12:00
| AKSML | 239 | 20:00 | 227 | 02:00 | Hasnabad | 234 | 20:00 | 225 | 11:00
| Aminbazar | 233 | 01:00 | 225 | 10:00 | Hathazari | 238 | 18:00 | 232 | 12:00
| Ashuganj | 240 | 01:00 | 230 | 12:00 | Ishurdi | 237 | 04:00 | 231 | 12:00
| Ashuganj-400 | 240 | 1:00 | 230 | 12:00 | Jhenaidah | 232 | 06:00 | 222 | 18:00
| Baghabari | 232 | 05:00 | 227 | 12:00 | Kaliakoir | 235 | 22:00 | 224 | 12:00
| Barapukuria | 227 | 14:00 | 221 | 00:00 | Keranigonj | 233 | 05:00 | 224 | 12:00
| Barapukuria-230 | 227 | 14:00 | 221 | 0:00 | Khulna(S) | 232 | 05:00 | 224 | 12:00
| Barishal | 238 | 02:00 | 234 | 12:00 | Madunaghat | 237 | 20:00 | 231 | 04:00
| Bheramara | 234 | 03:00 | 228 | 12:00 | Maniknagar | 233 | 03:00 | 224 | 12:00
| Bhulta | 235 | 02:00 | 225 | 12:00 | Meghnaghat | 240 | 00:00 | 235 | 12:00
| Bibiana | 227 | 00:00 | 220 | 10:00 | Meghnaghat-400 | 235 | 20:00 | 232 | 04:00
| BIPTC | 237 | 05:00 | 229 | 12:00 | Mirsorai | 241 | 20:00 | 228 | 03:00
| Bogura | 238 | 14:00 | 231 | 00:00 | Rajshahi | 235 | 05:00 | 228 | 12:00
| Bogura-400 | 237 | 14:00 | 232 | 00:00 | Rampal | 231 | 04:00 | 222 | 18:00
| Borhanuddin | 243 | 06:00 | 238 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 240 | 21:00 | 230 | 05:00 | Rampura | 233 | 05:00 | 223 | 12:00
| Cumilla(N) | 233 | 19:30 | 223 | 10:00 | Shikalbaha | 238 | 17:00 | 229 | 04:00
| Faridpur | 236 | 03:00 | 230 | 12:00 | Shyampur | 234 | 21:00 | 225 | 12:00
| Fenchuganj | 228 | 00:00 | 222 | 15:00 | Siddhirganj | 235 | 02:00 | 226 | 11:00
| Ghorashal | 238 | 01:00 | 230 | 13:00 | Sirajgonj | 242 | 05:00 | 237 | 12:00
| Ghorashal-230 | 233 | 04:00 | 224 | 12:00 | Sreepur | 236 | 04:00 | 226 | 15:00
| Gopalganj | 237 | 05:00 | 230 | 13:00 | Tongi | 233 | 23:00 | 223 | 11:00
| GPH | 238 | 21:00 | 230 | 02:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 137 | 03:00 | 129 | 12:00 | Kushtia | 137 | 05:00 | 133 | 21:00
| Agargaon | 138 | 02:00 | 131 | 12:00 | Lalbag | 138 | 04:00 | 132 | 10:00
| Agrabad | 137 | 21:00 | 131 | 10:00 | Lalmonirhat | 133 | 13:00 | 125 | 07:00
| AKS | 135 | 21:00 | 130 | 05:00 | Madanganj | 129 | 07:00 | 124 | 12:00
| Aminbazar | 140 | 01:00 | 132 | 01:00 | Madaripur | 133 | 04:00 | 130 | 12:00
| Amnura | 140 | 21:00 | 127 | 07:00 | Madartek | 136 | 00:00 | 129 | 12:00
| Ashuganj | 140 | 08:00 | 135 | 15:00 | Madunaghat | 138 | 19:00 | 133 | 05:00
| Bagerhat | 137 | 06:00 | 126 | 18:00 | Magura | 137 | 06:00 | 128 | 18:00
| Bakulia | 136 | 17:00 | 132 | 10:00 | Mahasthangarh | 138 | 16:00 | 133 | 00:00
| Banani | 137 | 05:00 | 128 | 12:00 | Manikganj | 130 | 20:00 | 120 | 11:00
| Bangabhaban | 132 | 00:00 | 125 | 11:00 | Maniknagar | 132 | 00:00 | 125 | 12:00
| Barapukuria | 139 | 14:00 | 134 | 00:00 | Matarbari | 125 | 17:00 | 120 | 02:00
| Barguna | 139 | 18:00 | 133 | 04:00 | Matuail | 131.3 | 07:00 | 126.2 | 12:00
| Barishal | 133 | 20:00 | 128 | 00:00 | Millgate | 136 | 04:00 | 128 | 12:00
| Barishal-230 | 133 | 03:00 | 129 | 12:00 | Mirpur | 139 | 00:00 | 133 | 09:00
| Baroaulia | 137 | 19:00 | 132 | 06:00 | Mirzapur | 131 | 22:00 | 121 | 18:00
| Baroirhat | 133 | 17:00 | 123 | 10:00 | Mithapukur | 136 | 13:00 | 130 | 00:00
| Bashundhara | 137 | 02:00 | 128 | 12:00 | MI_Cement | 137 | 07:00 | 129 | 12:00
| BashundharaCement | 129 | 07:00 | 124 | 12:00 | Modern | 137 | 21:00 | 132 | 04:00
| Beanibazar | 128 | 00:00 | 126 | 11:00 | Mogbazar | 137 | 02:00 | 129 | 12:00
| Benapole | 137 | 05:00 | 127 | 18:00 | Mongla | 135 | 06:00 | 126 | 10:00
| Bhaluka | 132 | 06:00 | 127 | 16:00 | Motijheel | 132 | 00:00 | 125 | 11:00
| Bhandaria | 130 | 06:00 | 125 | 12:00 | Munshiganj | 129 | 00:00 | 125 | 10:00
| Bhangura | 139 | 09:00 | 136 | 00:00 | Mymensingh | 136 | 23:00 | 121 | 15:00
| Bheramara | 137 | 02:00 | 134 | 12:00 | Naogaon | 138 | 17:00 | 131 | 00:00
| Bheramara(GK) | 137 | 03:00 | 134 | 12:00 | Narail | 137 | 06:00 | 128 | 18:00
| Bhulta | 124 | 19:30 | 116 | 12:00 | Narinda | 132 | 7:00 | 124 | 15:00
| Bog-Sherpur | 138 | 13:00 | 135 | 00:00 | Narshingdi | 123 | 06:00 | 116 | 12:00
| Bogura | 140 | 13:00 | 134 | 00:00 | Natore | 137 | 04:00 | 133 | 11:00
| Bogura-230 | 140 | 14:00 | 134 | 00:00 | Nawabganj | 138 | 04:00 | 132 | 12:00
| Brahmanbaria | 134 | 07:00 | 129 | 12:00 | Netrakona | 135 | 21:00 | 123 | 18:00
| Cantonment | 138 | 03:00 | 131 | 12:00 | New | 136 | 20:00 | 129 | 12:00
| Chandpur | 139 | 17:00 | 128 | 04:00 | Niamatpur | 132 | 04:00 | 130 | 00:00
| Chandraghona | 138 | 19:00 | 133 | 03:00 | Noapara | 138 | 04:00 | 130 | 18:00
| Chapai | 131 | 17:00 | 128 | 00:00 | Pabna | 138 | 05:00 | 133 | 12:00
| Charsaidpur | 130 | 05:00 | 125 | 10:00 | Palashbari | 136 | 17:00 | 129 | 07:00
| Chauddagram | 135 | 17:00 | 125 | 10:00 | Panchagarh | 137 | 14:00 | 127 | 07:00
| Chhatak | 128 | 05:00 | 124 | 10:00 | Patuakhali | 140 | 18:30 | 134 | 05:00
| Chowmuhani | 135 | 17:00 | 120 | 07:00 | Payra | 137 | 01:00 | 134 | 03:00
| Chuadanga | 134 | 06:00 | 124 | 18:00 | PHP | 135 | 18:30 | 124 | 10:00
| Coxsbazar | 124 | 08:00 | 119 | 03:00 | Postogola | 138 | 02:00 | 132 | 12:00
| Cumilla(N) | 136 | 17:00 | 128 | 10:00 | Purbachal | 137 | 00:00 | 128 | 12:00
| Cumilla(S) | 135 | 18:30 | 128 | 10:00 | Purbasadipur | 135 | 13:00 | 127 | 07:00
| Daudkandi | 130 | 17:00 | 123 | 10:00 | Rahanpur | 134 | 17:00 | 130 | 02:00
| Dhaka | 137 | 01:00 | 129 | 12:00 | Rahim | 130 | 05:00 | 125 | 11:00
| Dhamrai | 134 | 05:00 | 126 | 12:00 | Rajbari | 131 | 03:00 | 127 | 13:00
| Dhanmondi | 137 | 00:00 | 130 | 11:00 | Rajendrapur | 134 | 22:00 | 118 | 12:00
| Dohazari | 133 | 17:00 | 126 | 10:00 | Rajshahi | 136 | 04:00 | 132 | 12:00
| Faridpur | 132 | 02:00 | 130 | 00:00 | Rajshahi-230 | 137 | 17:00 | 122 | 12:00
| Fatullah | 137 | 20:00 | 130 | 12:00 | Ramganj | 134 | 17:00 | 120 | 05:00
| Fenchuganj | 136 | 22:00 | 131 | 01:00 | Rampur | 136 | 18:30 | 132 | 03:00
| Feni | 135 | 18:00 | 125 | 05:00 | Rampura | 137 | 05:00 | 129 | 12:00
| Ghatail | 132 | 00:00 | 121 | 18:00 | Rangamati | 137 | 18:30 | 133 | 03:00
| Ghorashal | 139 | 01:00 | 133 | 16:00 | Rangpur | 136 | 14:00 | 130 | 07:00
| Goalpara | 139 | 05:00 | 131 | 18:00 | Ruppur | 139 | 04:00 | 135 | 18:00
| Gollamari | 138 | 04:00 | 132 | 18:00 | Saidpur | 135 | 13:00 | 128 | 07:00
| Gopalganj | 135 | 04:00 | 130 | 12:00 | Satkhira | 136 | 06:00 | 127 | 18:00
| Gopalganj-400 | 134 | 08:00 | 130 | 12:00 | Satmasjid | 138 | 02:00 | 131 | 12:00
| Gulshan | 136 | 01:00 | 128 | 12:00 | Savar | 140 | 20:00 | 130 | 10:00
| Halishahar | 137 | 19:00 | 131 | 10:00 | SevenRings | 141 | 22:00 | 133 | 15:00
| Haripur | 130 | 00:00 | 126 | 12:00 | ShahCement | 130 | 05:00 | 125 | 10:00
| HaripurSBU | 130 | 00:00 | 126 | 13:00 | Shahjadpur | 140 | 00:00 | 138 | 10:00
| Hasnabad | 138 | 03:00 | 132 | 10:00 | Shahjibazar | 135 | 07:00 | 130 | 00:00
| Hathazari | 139 | 18:30 | 135 | 10:00 | Shahmirpur | 137 | 18:00 | 131 | 10:00
| Ishurdi | 139 | 03:00 | 135 | 12:00 | Shariatpur | 133 | 04:00 | 128 | 18:00
| Jaldhaka | 133 | 13:00 | 125 | 07:00 | Sherpur | 137 | 09:00 | 120 | 18:00
| Jamalpur | 139 | 13:00 | 124 | 18:00 | Shikalbaha | 126 | 19:00 | 120 | 04:00
| Jashore | 136 | 04:00 | 129 | 18:00 | Shikalbaha-230 | 138 | 20:00 | 132 | 04:00
| Jhenaidah | 138 | 06:00 | 131 | 13:00 | Shitalakhya | 137 | 07:00 | 129 | 12:00
| Jhenaidah-230 | 139 | 06:00 | 132 | 18:00 | Sholosohor | 137 | 19:00 | 131 | 10:00
| Joydebpur | 140 | 19:30 | 128 | 12:00 | Shyampur | 135 | 20:00 | 129 | 12:00
| Joypurhat | 136 | 14:00 | 132 | 00:00 | Shyampur-230 | 136 | 04:00 | 130 | 11:00
| Juldah | 137 | 20:00 | 133 | 07:00 | Siddhirganj | 132 | 07:00 | 126 | 11:00
| Kabirpur | 134 | 21:00 | 121 | 12:00 | Sirajganj | 138 | 13:00 | 134 | 12:00
| Kachua | 137 | 19:00 | 126 | 02:00 | Sonargaon | 130 | 21:00 | 124 | 10:00
| Kaliakoir | 136 | 21:00 | 124 | 15:00 | Sreemongol | 133 | 08:00 | 129 | 15:00
| Kallyanpur | 133 | 04:00 | 128 | 10:00 | Sreepur | 135 | 05:00 | 128 | 15:00
| Kalurghat | 137 | 17:00 | 132 | 05:00 | Srinagar | 138 | 06:00 | 132 | 11:00
| Kamrangirchar | 138 | 04:00 | 126 | 12:00 | SSM | 140 | 07:00 | 138 | 01:00
| Kaptai | 139 | 20:00 | 136 | 5:00 | Sunamganj | 126 | 04:00 | 123 | 18:00
| Kazla | 132 | 02:00 | 125 | 11:00 | Sylhet | 130 | 08:00 | 126 | 11:00
| Keranigonj | 138 | 03:00 | 132 | 12:00 | Sylhet-132 | 129 | 07:00 | 126 | 12:00
| Khagrachori | 137 | 19:00 | 131 | 10:00 | Tangail | 130 | 23:00 | 119 | 18:00
| Khulna | 138 | 06:00 | 133 | 12:00 | Thakurgaon | 139 | 14:00 | 128 | 02:00
| Khulna(S) | 139 | 05:00 | 132 | 18:00 | TK | 137 | 18:30 | 132 | 08:00
| Khulshi | 136 | 21:00 | 131 | 05:00 | Tongi | 137 | 04:00 | 131 | 11:00
| Kishoreganj | 133 | 02:00 | 127 | 12:00 | Ullahpara | 139 | 17:00 | 136 | 00:00
| Kodda | 136 | 22:00 | 119 | 11:00 | Ullon | 136 | 00:00 | 129 | 12:00
| KSRM | 137 | 18:30 | 132 | 10:00 | Uttara | 139 | 01:00 | 132 | 09:00
| Kulaura | 133 | 09:00 | 130 | 15:00 | UttaraNew | 140 | 01:00 | 130 | 03:00
| Kurigram | 134 | 14:00 | 125 | 18:00 | Zigatola | 138 | 05:00 | 132 | 12:00

## L-Curve
Date | 2024-11-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 882 | 5874 | 4931 | 10805 |  |  |  | QF-LDC-11
0:30 | 870 | 5711.5 | 4857 | 10568.5 | Date: | 2024-11-07
1:00 | 858 | 5549 | 4783 | 10332
1:30 | 857 | 5384.5 | 4744.5 | 10129
2:00 | 856 | 5220 | 4706 | 9926
2:30 | 905 | 5060 | 4654.5 | 9714.5 | [5 empty] | Gen. at Eve. Peak | 12630 | 12630 MW (18:00 )
3:00 | 954 | 4900 | 4603 | 9503 | [6 empty] | 18:00
3:30 | 1026 | 4799 | 4551 | 9350 | [5 empty] | Gen. at Day Peak | 11095 | 11095 MW (12:00 )
4:00 | 1098 | 4698 | 4499 | 9197 | [6 empty] | 12:00
4:30 | 1136 | 4589 | 4501 | 9090 | [5 empty] | Highest Generation | 12630
5:00 | 1174 | 4480 | 4503 | 8983 | [6 empty] | 18:00
5:30 | 1198 | 4469 | 4534.5 | 9003.5
6:00 | 1222 | 4458 | 4566 | 9024
6:30 | 1123 | 4598.5 | 4627.5 | 9226
7:00 | 1024 | 4739 | 4689 | 9428
7:30 | 1048 | 4828 | 4787.5 | 9615.5
8:00 | 1072 | 4917 | 4886 | 9803
8:30 | 1172 | 4979.5 | 4881 | 9860.5
9:00 | 1272 | 5042 | 4876 | 9918
9:30 | 1377 | 5356 | 4947 | 10303
10:00 | 1482 | 5670 | 5018 | 10688
10:30 | 1440 | 5670 | 5018 | 10688
11:00 | 1398 | 5670 | 5018 | 10688
11:30 | 1439 | 5798 | 5093.5 | 10891.5
12:00 | 1480 | 5926 | 5169 | 11095
12:30 | 1406 | 6012.5 | 5250.5 | 11263
13:00 | 1332 | 6099 | 5332 | 11431
13:30 | 1302 | 6102.5 | 5250.5 | 11353
14:00 | 1272 | 6106 | 5169 | 11275
14:30 | 1339 | 6105 | 5156 | 11261
15:00 | 1406 | 6104 | 5143 | 11247
15:30 | 1365 | 6079.5 | 5083 | 11162.5
16:00 | 1324 | 6055 | 5023 | 11078
16:30 | 1324 | 6135 | 4997.5 | 11132.5
17:00 | 1324 | 6215 | 4972 | 11187
17:30 | 1077 | 6580 | 5328.5 | 11908.5
18:00 | 830 | 6945 | 5685 | 12630
18:30 | 823 | 6806 | 5705.5 | 12511.5
19:00 | 816 | 6667 | 5726 | 12393
19:30 | 820 | 6565 | 5580 | 12145
20:00 | 788 | 6501 | 5525 | 12026 |  |  |  | Executive Engineer
20:30 | 797 | 6425.5 | 5480 | 11905.5 |  |  |  | Network Operation Division
21:00 | 806 | 6350 | 5435 | 11785
21:30 | 794 | 6229 | 5277.5 | 11506.5
22:00 | 782 | 6108 | 5120 | 11228 |  |  |  |  | Page 6 of 7
22:30 | 828 | 6054.5 | 5120 | 11174.5
23:00 | 874 | 6001 | 5120 | 11121
23:30 | 878 | 5937.5 | 5025.5 | 10963
24:00 | 882 | 5874 | 4931 | 10805
12630 MW (18:00 )
11095 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-11-07 |  | Energy |  | 261548312
[16 empty] | 2024-11-07 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3603 | 898 | 1733 | 0 | 1577 | 2118 | 131 | 0 | 172 | 56 | 517 | 0 | 0 | 0
0:30 | 3562.5 | 899 | 1684 | 0 | 1247.5 | 2240 | 151.5 | 0 | 110 | 56 | 618 | 0 | 0 | 0 |  |  | Date: | 44141
1:00 | 3522 | 900 | 1635 | 0 | 918 | 2362 | 172 | 0 | 48 | 56 | 719 | 0 | 0 | 0
1:30 | 3484 | 900 | 1632 | 0 | 769 | 2364 | 171.5 | 0 | 32 | 54 | 722.5 | 0 | 0 | 0 | [8 empty] | Total Energy | 261.5483 | 261.5483 | Total Energy Gen 261.548 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 261.548 MKWHr
2:00 | 3446 | 900 | 1629 | 0 | 620 | 2366 | 171 | 0 | 16 | 52 | 726 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 3420.5 | 900 | 1661.5 | 0 | 431.5 | 2345 | 170.5 | 0 | 8 | 53 | 724.5 | 0 | 0 | 0 | [8 empty] | Energy Requirement | 261.5483 | 261.5483
3:00 | 3395 | 900 | 1694 | 0 | 243 | 2324 | 170 | 0 | 0 | 54 | 723 | 0 | 0 | 0
3:30 | 3377.5 | 900 | 1695 | 0 | 206.5 | 2223 | 169.5 | 0 | 8 | 51 | 719.5 | 0 | 0 | 0 | [7 empty] | Shortage
4:00 | 3360 | 900 | 1696 | 0 | 170 | 2122 | 169 | 0 | 16 | 48 | 716 | 0 | 0 | 0
4:30 | 3351.5 | 900 | 1685 | 0 | 153.5 | 2050.5 | 168.5 | 0 | 16 | 48 | 717 | 0 | 0 | 0
5:00 | 3343 | 900 | 1674 | 0 | 137 | 1979 | 168 | 0 | 16 | 48 | 718 | 0 | 0 | 0
5:30 | 3344 | 900 | 1698 | 0 | 135.5 | 1973 | 169 | 0 | 16 | 49 | 719 | 0 | 0 | 0
6:00 | 3345 | 900 | 1722 | 0 | 134 | 1967 | 170 | 0 | 16 | 50 | 720 | 0 | 0 | 0
6:30 | 3370 | 900 | 1722.5 | 0 | 251 | 1993 | 171 | 0 | 16 | 46 | 721.5 | 35 | 0 | 0 | [6 empty] | Coal
7:00 | 3395 | 900 | 1723 | 0 | 368 | 2019 | 172 | 0 | 16 | 42 | 723 | 70 | 0 | 0
7:30 | 3375 | 900 | 1685 | 0 | 470.5 | 2065 | 171.5 | 0 | 32.5 | 41 | 722.5 | 152.5 | 0 | 0 | [5 empty] | Oil
8:00 | 3355 | 900 | 1647 | 0 | 573 | 2111 | 171 | 0 | 49 | 40 | 722 | 235 | 0 | 0
8:30 | 3345.5 | 900.5 | 1601.5 | 0 | 632 | 2057 | 172.5 | 0 | 50 | 45 | 720.5 | 336 | 0 | 0
9:00 | 3336 | 901 | 1556 | 0 | 691 | 2003 | 174 | 0 | 51 | 50 | 719 | 437 | 0 | 0
9:30 | 3417.5 | 900 | 1603.5 | 0 | 805 | 1994.5 | 174 | 0 | 111.5 | 50 | 720 | 527 | 0 | 0
10:00 | 3499 | 899 | 1651 | 0 | 919 | 1986 | 174 | 0 | 172 | 50 | 721 | 617 | 0 | 0
10:30 | 3499 | 899 | 1651 | 0 | 919 | 1986 | 174 | 0 | 172 | 50 | 721 | 617 | 0 | 0
11:00 | 3499 | 899 | 1651 | 0 | 919 | 1986 | 174 | 0 | 172 | 50 | 721 | 617 | 0 | 0
11:30 | 3544.5 | 899.5 | 1702 | 0 | 1022 | 2008.5 | 174 | 0 | 185.5 | 50 | 721 | 584.5 | 0 | 0
12:00 | 3590 | 900 | 1753 | 0 | 1125 | 2031 | 174 | 0 | 199 | 50 | 721 | 552 | 0 | 0
12:30 | 3521.5 | 900 | 1740.5 | 0 | 1334 | 2072.5 | 174 | 0 | 256.5 | 54 | 720 | 490 | 0 | 0
13:00 | 3453 | 900 | 1728 | 0 | 1543 | 2114 | 174 | 0 | 314 | 58 | 719 | 428 | 0 | 0
13:30 | 3453 | 900 | 1728 | 0 | 1543 | 2114 | 174 | 0 | 314 | 58 | 719 | 428 | 0 | 0
14:00 | 3453 | 900 | 1728 | 0 | 1543 | 2114 | 174 | 0 | 314 | 58 | 719 | 428 | 0 | 0
14:30 | 3412 | 899.5 | 1715 | 0 | 1652.5 | 2033 | 174 | 0 | 307 | 59 | 723 | 363.5 | 0.5 | 0
15:00 | 3371 | 899 | 1702 | 0 | 1762 | 1952 | 174 | 0 | 300 | 60 | 727 | 299 | 1 | 0
15:30 | 3369.5 | 899 | 1695 | 0 | 1767.5 | 1925.5 | 174 | 0 | 324.5 | 59 | 724 | 223 | 1.5 | 0
16:00 | 3368 | 899 | 1688 | 0 | 1773 | 1899 | 174 | 0 | 349 | 58 | 721 | 147 | 2 | 0
16:30 | 3342 | 899.5 | 1643 | 0 | 1850 | 1954.5 | 174 | 0 | 411.5 | 56 | 721.5 | 79.5 | 1 | 0
17:00 | 3316 | 900 | 1598 | 0 | 1927 | 2010 | 174 | 0 | 474 | 54 | 722 | 12 | 0 | 0
17:30 | 3469 | 900 | 1676 | 0 | 2176 | 2102 | 174 | 0 | 627 | 61 | 717.5 | 6 | 0 | 0
18:00 | 3622 | 900 | 1754 | 0 | 2425 | 2194 | 174 | 0 | 780 | 68 | 713 | 0 | 0 | 0
18:30 | 3628.5 | 900 | 1730.5 | 0 | 2314 | 2272 | 174 | 0 | 710 | 65 | 717.5 | 0 | 0 | 0
19:00 | 3635 | 900 | 1707 | 0 | 2203 | 2350 | 174 | 0 | 640 | 62 | 722 | 0 | 0 | 0
19:30 | 3567 | 899 | 1560 | 0 | 2155 | 2373 | 174 | 0 | 637 | 60 | 720 | 0 | 0 | 0
20:00 | 3547 | 900 | 1506 | 0 | 2105 | 2376 | 174 | 0 | 640 | 60 | 718 | 0 | 0 | 0
20:30 | 3558.5 | 898.5 | 1523.5 | 0 | 2041.5 | 2373.5 | 154 | 0 | 639 | 61 | 656 | 0 | 0 | 0
21:00 | 3570 | 897 | 1541 | 0 | 1978 | 2371 | 134 | 0 | 638 | 62 | 594 | 0 | 0 | 0
21:30 | 3570.5 | 896.5 | 1569 | 0 | 1912 | 2369.5 | 134 | 0 | 441 | 58 | 556 | 0 | 0 | 0
22:00 | 3571 | 896 | 1597 | 0 | 1846 | 2368 | 134 | 0 | 244 | 54 | 518 | 0 | 0 | 0
22:30 | 3557.5 | 897 | 1607 | 0 | 1812 | 2369 | 134 | 0 | 224.5 | 56 | 517.5 | 0 | 0 | 0
23:00 | 3544 | 898 | 1617 | 0 | 1778 | 2370 | 134 | 0 | 205 | 58 | 517 | 0 | 0 | 0
23:30 | 3573.5 | 898 | 1675 | 0 | 1677.5 | 2244 | 132.5 | 0 | 188.5 | 57 | 517 | 0 | 0 | 0 |  |  | Max Temp. in Dhaka |  | 32.0°C
24:00 | 3603 | 898 | 1733 | 0 | 1577 | 2118 | 131 | 0 | 172 | 56 | 517 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 261.548 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 261.548 MKWHr
Note on X13: Author:

## Generation
2024-11-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 132 | 131 | 130 | 129 | 128 | 130 | 132 | 131 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 |  | 134 | 134 | 134 | 134 | 134 | 134 | 131 | 3155433
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 0 |  |  |  | 832000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [9 empty] | 1 | 1 | 9 | 17 | 17 | 17 | 17 | 17 | 25 |  | 25 | 25 | 25 | 25 | 25 | 20 | 8 | 252633
| Teknaf 20MW PP (Solartech) | [6 empty] | 5 | 11 | 15 | 20 | 20 | 20 | 20 | 16 | 11 | 4 | 0 | [9 empty] | 138780
6 | Sikalbaha 225MW CCPP (Gas) | 228 | 227 | 227 | 227 | 227 | 227 | 227 | 227 | 228 | 223 | 223 | 223 | 223 | 222 | 222 | 222 | 226 | 225 |  | 225 | 227 | 227 | 227 | 227 | 228 | 228 | 5329429
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [9 empty] | 51 | 51 | 68 | 68 | 64 | 64 | 68 | 70 | 78 |  | 50 | 50 | 50 | 50 | 17 | 17 | 17 | 727379
12 | Hathazari 100 MW peaking PP | [8 empty] | 2 | 24 | 24 | 25 | 47 | 47 | 47 | 46 | 65 | 78 |  | 39 | 40 | 40 | 39 | 16 | 14 | 14 | 617520
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 117927
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [12 empty] | 36 | 36 | 36 | 38 | 42 | 43 | [8 empty] | 228976
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 260 | 260 | 260 | 260 | 260 | 260 | 335 | 335 | 335 | 335 | 335 | 280 | 280 | 280 | 280 | 280 | 335 |  | 335 | 280 | 280 | 280 | 280 | 280 | 335 | 7200467
18 | Kodda 300 MW PP Unit-2 (Summit) | [12 empty] | 15 | 60 | 60 | 60 | 62 | 138 |  | 95 | 95 | 95 | 45 | 45 | 45 | 45 | 885709
19 | Ashuganj 195 MW PP (APSCL-United) | 190 | 190 | 190 | 190 | 180 | 180 | 180 | 180 | 180 | 189 | 189 | 189 | 189 | 189 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4499636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 561 | 562 | 562 | 455 | 313 | 303 | 304 | 300 | 302 | 305 | 305 | 310 | 308 | 309 | 313 | 310 | 308 | 312 |  | 313 | 313 | 311 | 304 | 303 | 304 | 303 | 8399999
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 40 | 40 | 43 | 44 | 44 | 44 | 44 | 1048752
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 310 | 330 | 290 | 285 | 290 | 290 | 330 | 310 | 280 | 310 | 295 | 280 | 335 |  | 310 | 285 | 290 | 290 | 305 | 295 | 310 | 7636700
| Ashuganj 420 MW CCPP(East) | 395 | 395 | 350 | 350 | 350 | 350 | 360 | 360 | 360 | 393 | 393 | 393 | 393 | 360 | 360 | 360 | 360 | 393 |  | 393 | 395 | 395 | 395 | 395 | 395 | 395 | 9152800
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1242240
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 361 | 352 | 340 | 335 | 327 | 308 | 306 | 300 | 341 | 408 | 408 | 409 | 403 | 370 | 378 | 407 | 411 | 411 |  | 411 | 416 | 409 | 386 | 360 | 350 | 340 | 8870400
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 380 | 420 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 350 | 350 | 350 | 350 | 350 | 400 | 10158800
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 11 | 11 | 11 | 11 | 9 | 10 | 11 | 15 | 15 |  | 15 | 18 | 18 | 31 | 31 | 33 | 33 | 525120
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 5 | 21 | 34 | 49 | 49 | 33 | 43 | 40 | 27 | 10 | 0 | [9 empty] | 307440
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 696960
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 61 | 60 | 60 | 60 | 57 | 58 | 60 | 59 | 60 | 61 | 60 |  | 62 | 61 | 61 | 61 | 60 | 60 | 62 | 1398432
48 | Shahjibazar 86 MW PP (Shahjibazar) | 31 | 31 | 83 | 83 | 83 | 83 | 80 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 1863360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 208 | 208 | 209 | 209 | 209 | 210 | 210 | 210 | 211 | 209 | 209 | 209 | 207 | 207 | 204 | 204 | 207 | 208 |  | 207 | 207 | 207 | 210 | 210 | 209 | 209 | 5202690
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 85824
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 343440
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 285 | 280 | 290 | 295 | 300 | 295 | 280 | 315 | 315 | 305 | 290 | 280 | 315 | 310 | 285 | 295 |  | 265 | 300 | 280 | 275 | 280 | 300 | 300 | 7136000
| Bibiyana South 400 MW | 346 | 346 | 346 | 346 | 346 | 346 | 357 | 315 | 316 | 340 | 340 | 357 | 340 | 340 | 370 | 352 | 345 | 375 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8623700
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 17 | 35 | 35 | 35 | 55 | 55 |  | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 391123
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 251760
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 56 | 52 | 54 | 48 | 48 | 50 | 42 | 40 | 50 | 50 | 50 | 50 | 58 | 60 | 60 | 58 | 54 | 68 |  | 62 | 60 | 60 | 62 | 54 | 58 | 56 | 1296000
64 | Malancha, Ctg. EPZ (United) | 24 | 37 | 39 | 39 | 23 | 36 | 36 | 10 | 3 | 4 | 4 | 8 | 8 | 6 | 2 | 3 | 11 | 16 |  | 18 | 24 | 24 | 22 | 38 | 39 | 39 | 498240
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 16 | 16 | 12 | 12 | 12 | 16 | 16 | 16 | 16 | 16 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 397590
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 20 | 19 | 19 | 19 | 19 |  | 19 | 20 | 20 | 21 | 21 | 21 | 21 | 490200
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 15 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 480960
71 | Maona 33 MW PP(Summit) | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 600700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 33 | 32 | 32 | 31 | 31 | 0 | 0 | 0 | 12 | 25 |  | 25 | 25 | 33 | 33 | 33 | 25 | 25 | 618200
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [11 empty] | 3 | 70 | 70 | 70 | 70 | 70 | 77 |  | 52 | 52 | 52 | 52 | 17 | 17 | 17 | 665760
| Chowmuhani 113 MW | 47 | 29 | 29 | 29 | 12 | 9 | 9 | 9 | 9 | 21 | 21 | 47 | 57 | 57 | 55 | 63 | 67 | 97 |  | 104 | 104 | 105 | 106 | 105 | 107 | 53 | 1249080
| Manikgonj 162MW PP(MPGL) | 90 | 54 |  |  |  |  | 17 | 17 | 17 | 90 | 90 | 117 | 126 | 126 | 126 | 126 | 144 | 162 |  | 126 | 126 | 72 | 72 | 35 | 35 | 17 | 1585440
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 25 | 25 | 25 | 25 | 17 | 17 | 17 | 17 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 410880
79 | Kodda 150 MW PP | 48 | 16 |  | 16 | 16 | 16 | 16 | 32 | 32 | 48 | 48 | 48 | 48 | 48 | 32 | 32 | 42 | 132 |  | 150 | 150 | 150 | 150 | 115 | 115 | 82 | 1450560
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [9 empty] | 1 | 1 | 8 | 28 | 51 | 52 | 52 | 52 | 52 |  | 43 | 43 | 43 | 43 | 25 | 25 | 25 | 515712
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 35 | 35 | 35 | 53 | 88 |  | 88 | 88 | 88 | 88 | 88 | 70 | 35 | 1107840
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 5 | 5 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 26641
| Jodiac Power | 35 | 35 |  |  |  |  | 11 | 17 | 17 | 17 | 17 | 20 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 645304
| Karnaphuli Power Ltd. | [7 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 33 | 34 | 34 | 31 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 367998
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [22 empty] | 11 | 16 | 16 |  | 39360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 5 | 33 | 30 | 33 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 33 | 36 | 36 | 36 | 36 | 36 | 36 | 815688
93 | Ashuganj 51 MW PP (Midland) | 43 | 34 | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 959328
94 | Gagnagar 102 MW PP (Digital Power) | [14 empty] | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 |  |  |  |  | 50400
95 | Patenga 50MW PP (Baraka) | 12 | 12 | 8 |  |  |  | 1 | 6 | 6 | 13 | 13 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 26 | 26 | 26 | 26 | 26 | 14 | 12 | 565440
96 | Chattogram 108 MW PP (ECPV) | [8 empty] | 15 | 25 | 25 | 26 | 32 | 37 | 38 | 38 | 34 | 40 |  | 44 | 44 | 45 | 44 | 45 | 45 | 45 | 593280
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 2 | 30 | 30 | 30 | 30 | 31 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 266095
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 417247
101 | Kushiara 163 MW CCPP (KP) | 42 | [25 empty] | 109145
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13050
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [5 empty] | 3 | 17 | 17 | 25 | 25 | 35 | 35 | 35 | 35 | 35 | 54 | 54 |  | 54 | 54 | 54 | 17 |  |  |  | 521640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 96 | 96 | 96 | 86 | 86 | 86 | 86 | 86 | 95 | 95 | 95 | 95 | 95 | 86 | 76 | 77 | 85 | 95 |  | 96 | 96 | 97 | 96 | 96 | 96 | 96 | 2126400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 47 | [5 empty] | 2 | 33 | 46 | 52 | 52 | 51 | 60 | 86 | 86 | 77 | 81 | 97 |  | 96 | 110 | 113 | 120 | 135 | 149 | 100 | 1568160
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 |  |  |  |  | 12 | 12 | 12 | 37 | 37 | 37 | 50 | 50 | 50 | 47 | 88 | 100 |  | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 1123200
116 | Chandpur 200 MW (Desh energy) | 85 | 51 | 17 |  |  |  | 8 | 26 | 51 | 71 | 71 | 103 | 104 | 103 | 103 | 103 | 117 | 147 |  | 170 | 170 | 170 | 170 | 155 | 155 | 155 | 2200320
117 | Ashuganj 150 MW PP (Midland) | 23 | 13 |  |  |  |  | 3 | 13 | 12 | 13 | 13 | 13 | 12 | 13 | 12 | 13 | 20 | 27 |  | 45 | 53 | 52 | 53 | 55 | 75 | 107 | 595490
118 | Bibiyana-III 400 MW CCPP | 372 | 372 | 372 | 339 | 318 | 307 | 317 | 312 | 312 | 386 | 386 | 387 | 387 | 387 | 389 | 388 | 386 | 385 |  | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 9139000
| Jamalpur 115 MW PP (United) | 57 | 57 | 45 | 24 | 8 | 8 | 55 | 55 | 58 | 58 | 58 | 56 | 47 | 57 | 56 | 56 | 56 | 56 |  | 58 | 57 | 55 | 56 | 57 | 57 | 57 | 1185600
| Anwara 300 MW PP (United) | 52 | 68 |  |  |  |  | 50 | 80 | 80 | 89 | 89 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 69 | 52 | 52 | 1231964
| Juldah unit-2 (Acorn) | 12 | [5 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 242880
| Anlima Energy Ltd. | 35 | [5 empty] | 7 | 17 | 17 | 30 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 41 |  | 53 | 53 | 53 | 53 | 53 | 53 | 40 | 715091
| Bhairob 54.5 MW | 17 | 17 | [5 empty] | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 2 |  | 32 | 35 | 35 | 35 | 35 | 35 | 35 | 422640
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 14 | 21 | 25 | 25 | 31 | 30 | 25 | 13 | 7 | 1 | [9 empty] | 192072
| Chandpur 115(Doreen) | 22 | 17 | 17 |  |  |  | 8 | 16 | 16 | 16 | 16 | 30 | 66 | 73 | 73 | 82 | 92 | 92 |  | 93 | 92 | 92 | 92 | 92 | 93 | 92 | 1201920
| Kanchan Purbachal Power Generation Ltd. | 18 | 18 |  |  |  |  | 12 | 18 | 18 | 18 | 18 | 22 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 33 | 18 | 576720
| Mirsharai 150 MW (Oil) | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 160 |  | 108 | 108 | 108 | 108 | 54 | 17 | 17 | 759418
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3360
| Sonagazi 75 MW Solar Plant | [6 empty] | 9 | 18 | 55 | 65 | 65 | 72 | 50 | 58 | 42 | 19 | 1 | [9 empty] | 415882
Matarbari 2*600 MW (CPGCL)
Meghnaghat (Reliance) 718MW CCPP
| Sreepur 150 MW | [9 empty] | 32 | 32 | 36 | 36 | 44 | [12 empty] | 150000
120
121 | Eastern Zone Total | 5549 | 5220 | 4900 | 4698 | 4480 | 4458 | 4739 | 4917 | 5042 | 5670 | 5670 | 5926 | 6099 | 6106 | 6104 | 6055 | 6215 | 6945 |  | 6667 | 6565 | 6501 | 6350 | 6108 | 6001 | 5874 | 137929324
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | [16 empty] | 18 | 19 |  | 22 | 20 | 20 | 20 |  |  |  | 100320
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  |  | 49920
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 9 | 30 | 55 | 70 | 70 | 84 | 26 | 52 | 42 | 20 | 2 | [9 empty] | 478080
132 | Rampal 1320 MW (BIFPCL) | 364 | 365 | 366 | 371 | 370 | 369 | 370 | 369 | 367 | 366 | 366 | 366 | 366 | 367 | 366 | 367 | 522 | 627 |  | 620 | 619 | 622 | 622 | 623 | 623 | 372 | 10560000
133 | United Payra Power Ltd. | 137 | 72 |  |  |  |  | 6 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 137 |  | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 1706400
| Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 220 | 220 | 180 | 220 | 220 | 180 | 220 |  | 220 | 180 | 180 | 220 | 220 | 220 | 220 | 5324980
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [13 empty] | 23 | 48 | 48 | 48 | 80 |  | 80 | 80 | 80 | 64 | 32 | 32 | 32 | 581184
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3709
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 127 | 129 | 129 | 127 | 127 | 127 | 127 | 101 | 101 | 101 | 101 | 124 | 127 | 101 | 127 | 127 | 101 | 127 |  | 127 | 127 | 101 | 127 | 127 | 127 | 127 | 3049000
141 | Bhola 33 MW PP (Venture) | 7 | 7 | 6 | 6 | 6 | 6 | 5 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 |  | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 148547
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP | [15 empty] | 3 | 32 | 60 |  | 51 | 51 | 51 | 51 |  |  |  | 249856
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
147 | Bheramara HVDC | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 900 | 901 | 899 | 899 | 900 | 900 | 900 | 899 | 899 | 900 | 900 |  | 900 | 899 | 900 | 897 | 896 | 898 | 898 | 21817454
148 | Bheramara 410 MW CCPP | 308 | 315 | 320 | 325 | 337 | 370 | 347 | 347 | 342 | 338 | 338 | 339 | 280 | 280 | 280 | 280 | 250 | 321 |  | 328 | 328 | 328 | 328 | 338 | 339 | 336 | 7796736
149 | Payra 1320 MW | 1244 | 1244 | 1200 | 1100 | 1100 | 1100 | 1150 | 1244 | 1140 | 1120 | 1120 | 1160 | 1244 | 1120 | 1080 | 1080 | 1040 | 1060 |  | 1220 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 30059100
150
151 | Barapukuria TPP Unit-1 | 63 | 64 | 64 | 64 | 64 | 62 | 62 | 64 | 64 | 65 | 65 | 65 | 66 | 66 | 63 | 65 | 65 | 65 |  | 65 | 65 | 66 | 67 | 67 | 66 | 66 | 1515490
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 130 | 131 | 132 | 132 | 132 | 133 | 133 | 134 | 130 | 130 | 130 | 130 | 130 | 134 | 130 | 77 | 75 | 130 |  | 132 | 132 | 133 | 134 | 131 | 133 | 133 | 3115000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [14 empty] | 13 | 47 | 46 | 46 |  | 46 | 46 | 46 | 46 |  |  |  | 312392
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 5 | 5 | 2 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 34080
157 | Sirajganj 68 MW Solar Park | [6 empty] | 6 | 23 | 37 | 53 | 53 | 54 | 51 | 43 | 30 | 9 | 0 | [9 empty] | 357752
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 181 | 181 | 181 | 181 | 181 | 181 | 187 | 193 | 160 | 160 | 160 | 173 | 187 | 160 | 160 | 160 | 160 | 177 |  | 185 | 185 | 185 | 186 | 186 | 187 | 187 | 4319818
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 343 | 347 | 357 | 352 | 343 | 373 | 373 | 366 | 367 | 376 | 376 | 414 | 404 | 335 | 358 | 348 | 315 | 414 |  | 398 | 347 | 313 | 314 | 349 | 348 | 414 | 8731636
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | [11 empty] | 5 | 7 | 7 | 7 | 7 | 11 | 12 |  | 4 | 4 | 4 | 4 |  |  |  | 67129
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 8 | 8 | 8 | 5 | 5 | 152406
166 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | [12 empty] | 14 | 22 | 28 | 35 | 38 | 43 |  | 46 | 43 | 46 | 45 |  |  |  | 296793
169 | Santahar 50 MW Peaking PP | [13 empty] | 15 | 15 | 15 | 15 | 15 |  | 30 | 30 | 30 | 30 |  |  |  | 168141
170 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
171 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 41 | 41 | 41 | 41 | 41 | 94 |  | 94 | 95 | 95 | 95 | 42 | 42 | 42 | 756160
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [9 empty] | 12 | 12 | 35 | 95 | 94 | 94 | 94 | 94 | 94 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 942432
173 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 15 | 60 | 70 | 70 | 70 | 70 | 113 |  | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 758016
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [12 empty] | 35 | 35 | 35 | 35 | 40 | 68 |  | 70 | 34 | 35 | 35 | 35 | 35 | 34 | 483782
178 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 2 | 4 | 6 | 6 | 6 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 39673
| Energypac Power Venture Thakurgaon Ltd. | 35 | [5 empty] | 35 | 35 | 35 | 35 | 35 | 48 | 94 | 115 | 115 | 115 | 115 | 115 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1406976
| Intraco Solar 30 MW | [6 empty] | 2 | 12 | 24 | 35 | 35 | 26 | 30 | 30 | 17 | 9 | 1 | [9 empty] | 212493
178 | Adani Power Jharkhanda Ltd | 719 | 726 | 723 | 716 | 718 | 720 | 723 | 722 | 719 | 721 | 721 | 721 | 719 | 725 | 727 | 721 | 722 | 713 |  | 722 | 720 | 718 | 594 | 518 | 517 | 517 | 16399373
| Teesta Solar Limited | [6 empty] | 20 | 71 | 119 | 183 | 183 | 143 | 120 | 102 | 55 | 42 | 4 | [9 empty] | 1044720