## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-11-10 | Sunday
|  | Date (day): | 2024-11-10 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12094.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12812 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-11-09 | 2024-11-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint. |  | 2024-11-17
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 0 | 0 |  | 75 | Under maint.
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 0 | 8 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 19 | 54 | 35 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 132 | 149 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 35 | 55 | 0
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55 | 0
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 44 | 45 | 45 |  | 35 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 23 | 23 | 23 |  | 10 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 24 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 18 | 25 | 25 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 195 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 39 | 112 | 149 | 149
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 53 | 105 | 52 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 0 | 16 | 88 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 18 | 36 | 36 | 36 |  | 19 | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 120 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1162 | 1995 | 1982 | 2055 | 2504 | 1299
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 33 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 134 | 134 | 134 | 134 | 96 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 225 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 68 | 51 | 68 | 37 |  | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 79 | 50 | 70 |  | 28 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 34 | 65 | 84 |  | 18 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 76 | 50 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 8 | 2 | 10 | 10
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 45 | 45 | 45 | 63 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 48 | 52 | 52 | 52 | 248 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 24 | 35 | 35 | 35 | 19 |  | Fuel shortage
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 54 | 56 | 110 | 0 |  | Fuel shortage
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 12 | 12 | 88 |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 21 | 53 | 35 | 53 | 63 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 160 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 600 | 555 | 612 | 612 |  | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 0 | 15 | 15 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 0 | 0 | 0 | 0 | 1150 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1118 | 1642 | 1547 | 1860 | 1944 | 988
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 310 | 310 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 395 | 350 | 400 | 400
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 44 | 44 | 44 | 44
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 187 | 199 | 190 | 190
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 13 | 127 | 120 | 130 | 20 |  | Fuel shortage
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 35 | 36 |  | 16 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 70 | 70 | 93 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 40 | 162 | 140 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 52 | 58 | 66 | 82
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 70 | 106 | 106 |  | 8
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 31 | 27 | 55 | 58 |  | Fuel shortage
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 20 | 92 | 92 | 92 | 23 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 72 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1260 | 1635 | 1775 | 1820 | 249 | 628
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 29 | 33 | 44 | 35 | 167 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 86 | 96 | 96 | 104 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 56 | 55 | 57 | 58 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 50 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 18 | 6 | 24
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 19 | 17 | 35 | 19 |  | Fuel shortage
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 0 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 224 | 212 | 269.6 | 247 | 167 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 70 | 100 |  | 163
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract Expired
90 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 36 | 35 | 36 | 36 | 14 |  | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 |  | 6 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 62 | 60 | 61
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86
94 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 206 | 207 | 210 | 210 |  | 21 | Machine problem
96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 13 | 13 | 13 |  | 12 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 300 | 310 |  |  | FGMO
99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 382 | 385 | 385 |  |  | FGMO
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 346 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1454 | 1443 | 1595 | 1636 | 34 | 662
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 895 | 895 | 908 | 908
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 20 | 35 |  | 19 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 49 | 30 | 60 |  | 49 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 368 | 350 | 360 | 50 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 0 | 17 | 88 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 367 | 624 | 375 | 617 | 617 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1696 | 1993 | 1783 | 1997 | 1001 | 68
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 16 | 110
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 5 | 7 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 125 | 123 | 127 | 127 |  | 67 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1232 | 1060 | 622 | 622 |  |  | Unit-2 S/D.
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 60 | 135 | 51 | 137 |  | 13 | Engine problem
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  | 307 | Under maint
118 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1642 | 1609 | 1046 | 1226 | 0 | 387
119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 0 | 40 |  | 12 | Engine problem
121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 17 | 0 | 25 |  | 46 | Engine problem
122 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 26 | 43 |  | 7 | Engine problem
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 184 | 160 | 210 | 180 | 30 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 404 | 318 | 414 | 414 |  |  | FGMO
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 5 | 11
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 50 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 95 | 95 |  | 18 | Engine problem
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 512 | 517 | 500 | 500
135 | Sirajganj 68 MW Solar Park |  | Solar | NWPGCL | 68 | 68 | 68 | 54 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 110 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1271 | 1336 | 1525 | 1546 | 693 | 112
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 67 | 66 | 67 | 67 |  | 18 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 132 | 135 | 130 | 130 |  | 144 | Machine problem
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 89 | 113 | 113
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 54 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 189 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 466 | 405 | 572 | 425 | 40 | 247
| Total |  |  |  |  | 27791 | 27086 | 10293 | 12270 | 12094.6 | 12812 | 6632 | 4391
A. |  | 2024-11-09 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 12270 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 8390 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12270 | MW
3 | Day peak Generation : |  |  | 10293 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11765.44 | MW
4 | Evening peak Generation : |  |  | 12270 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 245.5941 | MKWHr | By Solar | 4.3395 | MKWHr
| By Gas : | 118.273 | MKWHr |  | By Oil: | 29.3696 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 55.5924 | MKWHr |  | By Hydro: | 3.1702 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 11.9073 | MKWHr |  | By Wind: | 0.01104 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6632 | MW | Dhaka | 4616.74 | 4616.74 |  | 0 |  | 18:00 |  | 61
|  |  | For Plants S/D or M/C prob = |  |  | 4391 | MW | Chittagong | 1119 | 1119 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 11023 | MW | Khulna | 1333 | 1333 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 852.67 | MMCFD | **Import Adani: | Taka | 78707074.53 | Rajshahi | 1127.6 | 1127.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 350704080.34 | ii) Oil : | Taka | 530827816.67 | Comilla | 1137 | 1137 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 389118627.41 | Total | Taka | 1349357598.95 | Mymensingh | 942 | 942 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 10484.1 | MKWHr. | Sylhet | 462 | 462 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 824 | MW (W to E) at | 19:00 | hrs | Barisal | 354.1 | 354.1 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 824 | MW at | 19:00 | hrs | Rangpur | 674 | 674 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.2°C |  |  | Total | 11765.44 | 11765.44 |  | 0
B. |  | 2024-11-10 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 32.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 265 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12812 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 260.2057 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8759 | MW at | 5:00 | 60 | 23 | 41 | 44 | 32 | 28 | 11 | 0 | 26
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6611 | MKWHr. | ii) HVDC Flow at Peak Time |  | 895 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.2701 | MKWHr. | iii) Maximum HVDC Flow : |  | 897 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.62 |  | (b) Today: | 99.43 |  | (c) Rule Curve: |  | 108.1
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-11-09 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 11 | 17 | 33 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 0 | 199 | 50 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 58 | 64 | 0 | 0 | 0 | 0 | 30 | 0 | 33 | 0 | 0 | 61 | 83 | 0 | 209 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 17 | 0 | 0 | 51 | 0 | 383 | 27 | 0 | 0 | 0 | 68 | 17 | 0 | 0 | 37 | 0 | 350 | 14 | 0 | 0 | 17 | 0 | 17 | 0 | 16 | 18 | 330 | 0 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 896 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 135 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 519 | 0 | 0 | 0 | 0 | 0 |  | 5182 | 4445 | 9627 | 3528 | 896 | 1703 | 0 | 436 | 2340 | 131 | 0 | 16 | 58 | 519 | 0 | 0 | 0 | 99.67
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 17 | 33 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 0 | 199 | 50 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 64 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 62 | 83 | 0 | 209 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 17 | 0 | 383 | 24 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 44 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 330 | 0 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 896 | 0 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 136 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 517 | 0 | 0 | 0 | 0 | 0 |  | 4956 | 4301 | 9257 | 3515 | 896 | 1675 | 0 | 212 | 2241 | 131 | 0 | 16 | 54 | 517 | 0 | 0 | 0 | 99.66
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 17 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 0 | 199 | 50 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 65 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 62 | 56 | 0 | 209 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 17 | 0 | 383 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 896 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 132 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 515 | 0 | 0 | 0 | 0 | 0 |  | 4683 | 4160 | 8843 | 3463 | 896 | 1651 | 0 | 114 | 2017 | 131 | 0 | 0 | 56 | 515 | 0 | 0 | 0 | 99.65
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 17 | 16 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 0 | 0 | 180 | 50 | 41 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | 67 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 62 | 22 | 0 | 209 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 17 | 0 | 372 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 895 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 133 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 515 | 0 | 0 | 0 | 0 | 0 |  | 4497 | 4003 | 8500 | 3355 | 895 | 1457 | 0 | 114 | 1981 | 131 | 0 | 0 | 52 | 515 | 0 | 0 | 0 | 99.64
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 17 | 25 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 295 | 0 | 0 | 180 | 70 | 41 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 56 | 65 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 40 | 22 | 0 | 209 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 17 | 0 | 383 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 897 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 135 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 513 | 0 | 0 | 0 | 0 | 0 |  | 4466 | 3949 | 8415 | 3345 | 897 | 1454 | 0 | 105 | 1914 | 131 | 0 | 0 | 56 | 513 | 0 | 0 | 0 | 99.63
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 17 | 25 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 295 | 0 | 0 | 180 | 70 | 41 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | 68 | 0 | 0 | 0 | 0 | 30 | 0 | 33 | 0 | 0 | 40 | 22 | 0 | 211 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 17 | 0 | 381 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 896 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 134 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 515 | 0 | 0 | 0 | 0 | 0 |  | 4456 | 3934 | 8390 | 3333 | 896 | 1451 | 0 | 105 | 1912 | 134 | 0 | 0 | 44 | 515 | 0 | 0 | 0 | 99.62
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 17 | 25 | 4 | 0 | 134 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 305 | 0 | 0 | 180 | 80 | 44 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 64 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 40 | 22 | 0 | 213 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 66 | 0 | 1 | 5 | 2 | 17 | 0 | 381 | 13 | 0 | 0 | 1 | 30 | 1 | 0 | 0 | 29 | 0 | 316 | 0 | 6 | 0 | 0 | 0 | 0 | 5 | 0 | 2 | 395 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 16 | 0 | 0 |  | 896 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 131 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 180 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 372 | 3 | 0 | 522 | 20 | 0 | 0 | 5 | 11 |  | 4607 | 4118 | 8725 | 3397 | 896 | 1538 | 0 | 171 | 1930 | 134 | 0 | 16 | 40 | 522 | 81 | 0 | 0 | 99.61
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 17 | 15 | 17 | 0 | 8 | 0 | 131 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 3 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 0 | 180 | 50 | 44 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 38 | 64 | 0 | 0 | 1 | 0 | 30 | 0 | 36 | 0 | 0 | 40 | 22 | 0 | 214 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 68 | 0 | 17 | 11 | 0 | 17 | 12 | 344 | 45 | 0 | 0 | 2 | 48 | 17 | 0 | 0 | 29 | 0 | 316 | 0 | 24 | 35 | 26 | 0 | 0 | 15 | 7 | 18 | 400 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 40 | 0 | 0 |  | 896 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 130 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 920 | 180 | 0 | 10 | 2 | 34 | 0 | 0 | 0 | 371 | 13 | 0 | 521 | 79 | 0 | 0 | 25 | 41 |  | 4694 | 4214 | 8908 | 3257 | 896 | 1394 | 0 | 379 | 1987 | 131 | 0 | 16 | 38 | 521 | 289 | 0 | 0 | 99.6
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 15 | 17 | 16 | 15 | 0 | 132 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 12 | 0 | 6 | 0 | 0 | 0 | 285 | 0 | 0 | 175 | 50 | 44 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 46 | 30 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 40 | 83 | 0 | 212 | 0 | 0 | 0 | 275 | 0 | 2 | 0 | 0 | 0 | 0 | 77 | 0 | 17 | 0 | 0 | 17 | 12 | 347 | 37 | 17 | 0 | 3 | 15 | 17 | 0 | 0 | 29 | 0 | 316 | 7 | 36 | 17 | 17 | 0 | 0 | 23 | 16 | 18 | 300 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 56 | 0 | 0 |  | 895 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 130 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1020 | 180 | 0 | 17 | 4 | 59 | 0 | 0 | 0 | 370 | 25 | 0 | 517 | 131 | 0 | 0 | 39 | 70 |  | 4583 | 4407 | 8990 | 2982 | 895 | 1393 | 0 | 380 | 2147 | 132 | 0 | 48 | 46 | 517 | 450 | 0 | 0 | 99.59
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 23 | 15 | 17 | 16 | 16 | 0 | 133 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 350 | 0 | 0 | 128 | 50 | 44 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 31 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 40 | 83 | 0 | 207 | 0 | 0 | 0 | 300 | 8 | 2 | 0 | 0 | 0 | 0 | 68 | 0 | 34 | 17 | 0 | 17 | 0 | 360 | 45 | 34 | 0 | 4 | 0 | 0 | 0 | 0 | 13 | 0 | 370 | 0 | 46 | 0 | 0 | 0 | 0 | 29 | 0 | 18 | 300 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 66 | 0 | 0 |  | 896 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 130 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1020 | 180 | 0 | 0 | 5 | 74 | 0 | 0 | 0 | 368 | 32 | 0 | 517 | 169 | 0 | 0 | 49 | 91 |  | 4498 | 4543 | 9041 | 2956 | 896 | 1430 | 0 | 268 | 2154 | 133 | 0 | 48 | 50 | 517 | 589 | 0 | 0 | 99.59
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 23 | 15 | 17 | 16 | 16 | 0 | 133 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 285 | 0 | 0 | 185 | 50 | 44 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 50 | 29 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 58 | 83 | 0 | 206 | 0 | 0 | 0 | 325 | 8 | 2 | 0 | 0 | 0 | 0 | 67 | 0 | 34 | 20 | 0 | 17 | 2 | 386 | 45 | 34 | 0 | 4 | 15 | 0 | 0 | 0 | 9 | 0 | 370 | 0 | 50 | 0 | 0 | 0 | 0 | 33 | 0 | 18 | 393 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 69 | 0 | 0 |  | 895 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 132 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1140 | 220 | 0 | 17 | 5 | 83 | 0 | 0 | 0 | 366 | 36 | 0 | 520 | 186 | 0 | 0 | 53 | 91 |  | 4754 | 4807 | 9561 | 3020 | 895 | 1656 | 0 | 297 | 2304 | 133 | 0 | 48 | 50 | 520 | 638 | 0 | 0 | 99.58
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 23 | 15 | 17 | 16 | 18 | 0 | 134 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 34 | 0 | 0 | 6 | 0 | 8 | 0 | 0 | 0 | 310 | 0 | 0 | 187 | 50 | 44 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 52 | 29 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 58 | 86 | 0 | 206 | 0 | 0 | 0 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 75 | 0 | 39 | 0 | 0 | 40 | 13 | 386 | 45 | 53 | 0 | 4 | 48 | 24 | 0 | 17 | 9 | 0 | 350 | 0 | 50 | 54 | 21 | 0 | 17 | 33 | 20 | 18 | 395 | 17 | 0 | 600 | 0 | 0 | 0 | 0 | 72 | 0 | 0 |  | 895 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 132 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1232 | 220 | 0 | 60 | 5 | 84 | 35 | 0 | 0 | 367 | 37 | 0 | 512 | 189 | 0 | 0 | 54 | 110 |  | 5218 | 5075 | 10293 | 3165 | 895 | 1731 | 0 | 645 | 2398 | 134 | 0 | 115 | 52 | 512 | 646 | 0 | 0 | 99.58
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 2 | 0 | 0 | 23 | 6 | 23 | 16 | 25 | 0 | 134 | 0 | 0 | 0 | 1 | 223 | 0 | 0 | 0 |  | 6 | 32 | 34 | 0 | 13 | 18 | 0 | 8 | 0 | 0 | 0 | 310 | 0 | 0 | 187 | 50 | 43 | 0 | 0 | 35 | 0 | 25 | 1 | 0 | 0 | 0 | 16 | 54 | 29 | 0 | 0 | 2 | 0 | 30 | 0 | 35 | 0 | 0 | 59 | 86 | 0 | 206 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 84 | 0 | 52 | 0 | 0 | 97 | 37 | 386 | 45 | 53 | 0 | 4 | 150 | 35 | 14 | 17 | 9 | 10 | 350 | 0 | 48 | 108 | 35 | 0 | 17 | 31 | 50 | 31 | 395 | 17 | 0 | 600 | 0 | 0 | 0 | 0 | 68 | 0 | 0 |  | 895 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 5 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 133 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1244 | 180 | 0 | 100 | 5 | 79 | 35 | 0 | 0 | 368 | 34 | 0 | 515 | 177 | 0 | 0 | 51 | 106 |  | 5664 | 5086 | 10750 | 3199 | 895 | 1662 | 0 | 1088 | 2412 | 134 | 0 | 181 | 54 | 515 | 610 | 0 | 0 | 99.57
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 48 | 0 | 0 | 23 | 15 | 23 | 16 | 25 | 0 | 131 | 0 | 0 | 0 | 9 | 223 | 0 | 0 | 0 |  | 6 | 38 | 34 | 0 | 18 | 45 | 0 | 6 | 0 | 0 | 0 | 290 | 0 | 0 | 189 | 50 | 43 | 0 | 0 | 35 | 0 | 36 | 16 | 0 | 0 | 0 | 16 | 58 | 29 | 0 | 0 | 2 | 0 | 30 | 0 | 35 | 0 | 0 | 58 | 86 | 0 | 206 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 85 | 0 | 52 | 0 | 20 | 120 | 70 | 387 | 47 | 53 | 0 | 3 | 150 | 35 | 22 | 17 | 8 | 12 | 350 | 0 | 41 | 108 | 35 | 0 | 17 | 25 | 50 | 36 | 350 | 17 | 0 | 520 | 0 | 0 | 0 | 80 | 58 | 0 | 0 |  | 895 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 134 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1200 | 180 | 0 | 100 | 4 | 67 | 35 | 0 | 0 | 370 | 29 | 0 | 515 | 150 | 0 | 0 | 45 | 81 |  | 5734 | 4799 | 10533 | 3003 | 895 | 1644 | 0 | 1282 | 2291 | 131 | 0 | 205 | 58 | 515 | 509 | 0 | 0 | 99.58
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 0 | 23 | 18 | 23 | 16 | 16 | 0 | 131 | 0 | 0 | 0 | 17 | 218 | 0 | 0 | 0 |  | 6 | 38 | 34 | 0 | 20 | 45 | 0 | 4 | 0 | 0 | 0 | 325 | 0 | 0 | 199 | 50 | 43 | 0 | 0 | 35 | 0 | 36 | 16 | 0 | 0 | 0 | 16 | 58 | 29 | 0 | 0 | 1 | 0 | 30 | 0 | 35 | 0 | 0 | 57 | 86 | 0 | 204 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 86 | 0 | 35 | 6 | 25 | 120 | 97 | 387 | 56 | 53 | 0 | 2 | 156 | 35 | 31 | 17 | 9 | 12 | 365 | 0 | 29 | 108 | 35 | 0 | 17 | 18 | 50 | 36 | 350 | 17 | 0 | 505 | 7 | 0 | 0 | 65 | 43 | 0 | 0 |  | 895 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 4 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 133 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1200 | 180 | 0 | 100 | 3 | 48 | 35 | 0 | 0 | 368 | 18 | 0 | 513 | 105 | 0 | 0 | 33 | 50 |  | 5859 | 4849 | 10708 | 3148 | 895 | 1772 | 0 | 1347 | 2273 | 131 | 0 | 205 | 58 | 513 | 359 | 7 | 0 | 99.56
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 0 | 23 | 22 | 23 | 16 | 16 | 0 | 132 | 0 | 0 | 0 | 17 | 221 | 0 | 0 | 0 |  | 10 | 38 | 17 | 0 | 19 | 46 | 0 | 2 | 0 | 0 | 0 | 350 | 0 | 0 | 199 | 50 | 43 | 0 | 0 | 43 | 0 | 36 | 16 | 0 | 0 | 0 | 16 | 60 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 35 | 0 | 0 | 57 | 86 | 0 | 205 | 0 | 0 | 0 | 305 | 13 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 34 | 0 | 37 | 120 | 107 | 387 | 56 | 53 | 0 | 1 | 52 | 35 | 34 | 17 | 9 | 12 | 385 | 0 | 12 | 108 | 35 | 0 | 17 | 9 | 50 | 36 | 350 | 17 | 0 | 505 | 3 | 0 | 0 | 65 | 20 | 0 | 0 |  | 895 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 5 | 16 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 133 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1200 | 180 | 0 | 103 | 1 | 22 | 35 | 0 | 0 | 378 | 9 | 0 | 518 | 50 | 0 | 0 | 10 | 23 |  | 5770 | 4679 | 10449 | 3153 | 895 | 1784 | 0 | 1275 | 2283 | 132 | 0 | 188 | 60 | 518 | 158 | 3 | 0 | 99.56
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 330 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 23 | 22 | 23 | 24 | 16 | 0 | 131 | 0 | 0 | 0 | 17 | 219 | 0 | 0 | 0 |  | 18 | 38 | 34 | 0 | 19 | 46 | 0 | 7 | 0 | 0 | 0 | 310 | 0 | 0 | 199 | 50 | 43 | 0 | 0 | 35 | 0 | 36 | 25 | 0 | 0 | 0 | 16 | 52 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 35 | 0 | 0 | 59 | 86 | 0 | 206 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 86 | 0 | 36 | 0 | 76 | 120 | 119 | 320 | 56 | 53 | 28 | 0 | 52 | 35 | 34 | 25 | 27 | 12 | 346 | 2 | 0 | 150 | 35 | 0 | 17 | 1 | 50 | 36 | 393 | 17 | 0 | 540 | 0 | 0 | 0 | 120 | 1 | 0 | 0 |  | 894 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 123 | 5 | 16 | 0 | 0 | 0 | 25 | 4 | 25 | 0 | 0 | 3 | 0 | 12 | 0 | 0 | 5 | 67 | 0 | 134 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 17 | 0 | 15 | 0 | 35 | 0 | 0 | 25 | 1200 | 220 | 0 | 100 | 0 | 2 | 35 | 0 | 0 | 606 | 1 | 0 | 510 | 3 | 0 | 0 | 0 | 2 |  | 5805 | 4972 | 10777 | 3149 | 894 | 1651 | 0 | 1542 | 2547 | 131 | 0 | 291 | 52 | 510 | 10 | 0 | 0 | 99.55
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 20 | 335 | 0 | 0 | 0 | 0 | 149 | 8 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 23 | 22 | 23 | 24 | 25 | 0 | 131 | 0 | 0 | 0 | 25 | 219 | 0 | 0 | 0 |  | 18 | 79 | 34 | 0 | 24 | 50 | 0 | 7 | 0 | 0 | 0 | 330 | 0 | 0 | 199 | 50 | 43 | 0 | 0 | 35 | 0 | 36 | 52 | 0 | 0 | 0 | 16 | 64 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 35 | 0 | 0 | 60 | 86 | 0 | 204 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 80 | 0 | 0 | 86 | 0 | 72 | 0 | 76 | 133 | 122 | 386 | 56 | 105 | 51 | 0 | 52 | 35 | 46 | 106 | 30 | 12 | 360 | 16 | 0 | 162 | 41 | 0 | 17 | 0 | 74 | 36 | 393 | 54 | 0 | 542 | 0 | 0 | 0 | 120 | 0 | 0 | 0 |  | 895 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 27 | 60 | 0 | 123 | 7 | 16 | 0 | 0 | 0 | 48 | 5 | 95 | 0 | 0 | 15 | 0 | 30 | 0 | 0 | 11 | 66 | 0 | 135 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 77 | 0 | 65 | 0 | 0 | 95 | 1200 | 220 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 624 | 0 | 0 | 519 | 0 | 0 | 0 | 0 | 0 |  | 6653 | 5613 | 12266 | 3286 | 895 | 1883 | 0 | 2289 | 2567 | 131 | 0 | 632 | 64 | 519 | 0 | 0 | 61 | 99.55
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 132 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 22 | 22 | 23 | 24 | 25 | 0 | 134 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 18 | 79 | 34 | 0 | 45 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 199 | 50 | 44 | 0 | 0 | 35 | 0 | 37 | 52 | 0 | 0 | 0 | 18 | 58 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 35 | 0 | 0 | 62 | 86 | 0 | 207 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 195 | 0 | 0 | 86 | 0 | 112 | 0 | 76 | 162 | 127 | 382 | 56 | 105 | 68 | 0 | 52 | 35 | 54 | 70 | 31 | 12 | 346 | 0 | 0 | 162 | 53 | 0 | 19 | 0 | 92 | 36 | 350 | 160 | 0 | 555 | 0 | 0 | 0 | 120 | 0 | 0 | 0 |  | 895 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 40 | 49 | 0 | 123 | 7 | 64 | 0 | 0 | 0 | 48 | 17 | 95 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 11 | 66 | 0 | 135 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 17 | 0 | 50 | 0 | 89 | 0 | 0 | 50 | 1060 | 220 | 0 | 135 | 0 | 0 | 115 | 0 | 0 | 624 | 0 | 0 | 517 | 0 | 0 | 0 | 0 | 0 |  | 6927 | 5343 | 12270 | 3160 | 895 | 1752 | 0 | 2553 | 2440 | 134 | 0 | 761 | 58 | 517 | 0 | 0 | 0 | 99.52
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 132 | 13 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 22 | 22 | 23 | 24 | 25 | 0 | 134 | 0 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 18 | 79 | 34 | 0 | 51 | 33 | 0 | 8 | 0 | 0 | 0 | 357 | 0 | 0 | 199 | 50 | 44 | 0 | 0 | 35 | 0 | 37 | 25 | 0 | 0 | 0 | 18 | 62 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 35 | 0 | 0 | 60 | 86 | 0 | 207 | 0 | 0 | 0 | 325 | 13 | 2 | 0 | 95 | 0 | 0 | 86 | 0 | 100 | 0 | 76 | 162 | 127 | 385 | 56 | 70 | 68 | 0 | 52 | 35 | 51 | 34 | 38 | 12 | 390 | 0 | 0 | 162 | 53 | 0 | 35 | 0 | 50 | 36 | 350 | 108 | 0 | 562 | 0 | 0 | 0 | 140 | 0 | 0 | 0 |  | 895 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 35 | 49 | 0 | 123 | 7 | 32 | 0 | 0 | 0 | 45 | 23 | 95 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 8 | 67 | 0 | 132 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 17 | 0 | 50 | 0 | 49 | 0 | 0 | 50 | 1030 | 220 | 0 | 135 | 0 | 0 | 92 | 0 | 0 | 625 | 0 | 0 | 515 | 0 | 0 | 0 | 0 | 0 |  | 6686 | 5260 | 11946 | 3194 | 895 | 1871 | 0 | 2152 | 2416 | 134 | 0 | 707 | 62 | 515 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 132 | 13 | 0 | 0 | 0 | 35 | 17 | 55 | 0 | 22 | 22 | 23 | 33 | 25 | 0 | 133 | 0 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 18 | 79 | 34 | 0 | 51 | 33 | 0 | 16 | 0 | 0 | 0 | 320 | 0 | 0 | 199 | 50 | 44 | 0 | 0 | 35 | 0 | 37 | 25 | 0 | 0 | 0 | 18 | 62 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 0 | 0 | 61 | 86 | 0 | 207 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 95 | 0 | 0 | 86 | 0 | 99 | 0 | 76 | 162 | 124 | 384 | 56 | 70 | 68 | 0 | 52 | 35 | 51 | 34 | 38 | 12 | 346 | 0 | 0 | 162 | 53 | 0 | 35 | 0 | 50 | 36 | 350 | 108 | 0 | 567 | 0 | 0 | 0 | 130 | 0 | 0 | 0 |  | 895 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 36 | 49 | 0 | 123 | 7 | 32 | 0 | 0 | 0 | 48 | 22 | 95 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 8 | 67 | 0 | 133 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 50 | 990 | 220 | 0 | 142 | 0 | 0 | 54 | 0 | 0 | 624 | 0 | 0 | 515 | 0 | 0 | 0 | 0 | 0 |  | 6570 | 5163 | 11733 | 3123 | 895 | 1833 | 0 | 2081 | 2381 | 133 | 0 | 710 | 62 | 515 | 0 | 0 | 0 | 99.53
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 22 | 22 | 23 | 33 | 25 | 0 | 132 | 0 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 18 | 71 | 34 | 0 | 49 | 33 | 0 | 20 | 0 | 0 | 0 | 320 | 0 | 0 | 199 | 70 | 44 | 0 | 0 | 35 | 0 | 37 | 25 | 0 | 0 | 0 | 18 | 62 | 35 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 79 | 0 | 61 | 86 | 0 | 208 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 85 | 0 | 76 | 0 | 76 | 145 | 120 | 385 | 57 | 52 | 68 | 0 | 52 | 35 | 51 | 34 | 38 | 12 | 358 | 0 | 0 | 162 | 53 | 0 | 35 | 0 | 50 | 36 | 350 | 72 | 0 | 572 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 895 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 36 | 44 | 0 | 123 | 8 | 16 | 0 | 0 | 0 | 46 | 23 | 95 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 8 | 67 | 0 | 133 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 50 | 0 | 14 | 0 | 0 | 50 | 890 | 220 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 624 | 0 | 0 | 517 | 0 | 0 | 0 | 0 | 0 |  | 6445 | 5018 | 11463 | 3162 | 895 | 1962 | 0 | 1837 | 2286 | 132 | 0 | 610 | 62 | 517 | 0 | 0 | 0 | 99.52
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 24 | 22 | 23 | 33 | 25 | 0 | 132 | 0 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 18 | 71 | 34 | 0 | 50 | 33 | 0 | 27 | 0 | 0 | 0 | 320 | 0 | 0 | 199 | 70 | 44 | 0 | 0 | 35 | 0 | 38 | 25 | 0 | 0 | 0 | 18 | 58 | 35 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 62 | 0 | 60 | 31 | 0 | 208 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 86 | 0 | 70 | 0 | 76 | 145 | 124 | 374 | 57 | 52 | 59 | 0 | 52 | 35 | 51 | 34 | 39 | 12 | 356 | 0 | 0 | 108 | 53 | 0 | 35 | 0 | 50 | 36 | 393 | 54 | 0 | 577 | 0 | 0 | 0 | 90 | 0 | 0 | 0 |  | 895 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 37 | 43 | 0 | 127 | 7 | 16 | 0 | 0 | 0 | 46 | 23 | 95 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 8 | 67 | 0 | 132 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 50 | 880 | 220 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 626 | 0 | 0 | 517 | 0 | 0 | 0 | 0 | 0 |  | 6200 | 5008 | 11208 | 3200 | 895 | 1796 | 0 | 1735 | 2282 | 132 | 0 | 593 | 58 | 517 | 0 | 0 | 0 | 99.51
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 22 | 22 | 17 | 33 | 16 | 0 | 132 | 0 | 0 | 0 | 8 | 228 | 0 | 0 | 0 |  | 18 | 71 | 34 | 0 | 51 | 30 | 0 | 23 | 0 | 0 | 0 | 310 | 0 | 0 | 199 | 70 | 44 | 0 | 0 | 35 | 0 | 38 | 25 | 0 | 0 | 0 | 18 | 58 | 35 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 25 | 0 | 59 | 31 | 0 | 207 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 86 | 0 | 70 | 0 | 50 | 145 | 123 | 373 | 57 | 52 | 51 | 0 | 52 | 35 | 51 | 34 | 39 | 12 | 346 | 0 | 0 | 108 | 53 | 0 | 35 | 0 | 50 | 36 | 393 | 54 | 0 | 612 | 0 | 0 | 0 | 60 | 0 | 0 | 0 |  | 895 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 37 | 43 | 0 | 127 | 7 | 16 | 0 | 0 | 0 | 46 | 23 | 98 | 0 | 0 | 38 | 0 | 30 | 0 | 0 | 5 | 67 | 0 | 133 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 860 | 220 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 628 | 0 | 0 | 515 | 0 | 0 | 0 | 0 | 0 |  | 6069 | 4932 | 11001 | 3166 | 895 | 1682 | 0 | 1659 | 2300 | 132 | 0 | 594 | 58 | 515 | 0 | 0 | 0 | 99.5
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 19 | 22 | 17 | 33 | 8 | 0 | 132 | 0 | 0 | 0 | 8 | 227 | 0 | 0 | 0 |  | 18 | 71 | 34 | 0 | 51 | 19 | 0 | 30 | 0 | 0 | 0 | 310 | 0 | 0 | 199 | 50 | 44 | 0 | 0 | 35 | 0 | 38 | 34 | 0 | 0 | 0 | 18 | 60 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 20 | 0 | 59 | 31 | 0 | 207 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 1 | 0 | 0 | 86 | 0 | 67 | 0 | 50 | 145 | 120 | 371 | 58 | 35 | 61 | 0 | 52 | 35 | 51 | 56 | 14 | 12 | 341 | 0 | 0 | 35 | 37 | 0 | 20 | 0 | 60 | 36 | 393 | 17 | 0 | 612 | 0 | 0 | 0 | 60 | 0 | 0 | 0 |  | 895 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 37 | 43 | 0 | 127 | 8 | 44 | 0 | 0 | 0 | 46 | 13 | 98 | 0 | 0 | 38 | 0 | 15 | 0 | 0 | 5 | 67 | 0 | 135 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 40 | 0 | 33 | 0 | 0 | 70 | 680 | 220 | 0 | 150 | 0 | 0 | 67 | 0 | 0 | 386 | 0 | 0 | 516 | 0 | 0 | 0 | 0 | 0 |  | 5982 | 4680 | 10662 | 3215 | 895 | 1742 | 0 | 1690 | 1880 | 132 | 0 | 532 | 60 | 516 | 0 | 0 | 0 | 99.49
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2372400 | 0 |  | 0 | 9918500 | 0 | 0 | 0 | 243666 | 7654194 | 0 | 0 | 0 | 50832 | 1301280 | 31000 | 0 | 0 | 0 | 529920 | 429977 | 234334 | 0 | 503400 | 398160 | 486720 | 522000 | 329760 | 0 | 3170225 | 0 | 0 | 0 | 156267 | 5272101 | 0 | 0 | 0 |  | 252000 | 640800 | 406839 | 0 | 418560 | 466080 | 0 | 485760 | 0 | 0 | 0 | 7874700 | 0 | 0 | 4533091 | 1361960 | 1042344 | 0 | 0 | 728164 | 0 | 94738 | 299054 | 0 | 0 | 0 | 394150 | 1270080 | 983040 | 0 | 0 | 14750 | 0 | 714600 | 0 | 750888 | 199473 | 0 | 1308768 | 1547520 | 0 | 4195350 | 0 | 0 | 0 | 7163000 | 298944 | 54096 | 0 | 539455 | 0 | 0 | 1819200 | 0 | 954720 | 49545 | 635520 | 1910400 | 1366618 | 9424000 | 999600 | 875520 | 463345 | 27480 | 1221927 | 565457 | 508506 | 470820 | 615720 | 135360 | 8319500 | 41280 | 349780 | 1581120 | 668673 | 0 | 340920 | 220928 | 799680 | 554040 | 8767800 | 605527 | 0 | 13369089 | 11040 | 0 | 0 | 1047759 | 498264 | 0 | 0 |  | 21661090 | 0 | 8337600 | 0 | 0 | 0 | 0 | 0 | 207840 | 307328 | 0 | 2823000 | 144594 | 232320 | 0 | 0 | 0 | 392057 | 108970 | 651408 | 0 | 0 | 196347 | 0 | 177847 | 0 | 0 | 131940 | 1555636 | 0 | 3281000 | 0 | 0 | 4585364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8709891 | 56640 | 0 | 448992 | 0 | 243638 | 0 | 39488 | 460800 | 26630300 | 5218260 | 0 | 1608000 | 37620 | 569520 | 718848 | 0 | 0 | 10756360 | 240110 | 0 | 11907273 | 1259310 | 0 | 3918 | 372752 | 655994 |  | 130862078 | 114732055 | 245594133 | 77826131 | 21661090 | 40446900 | 0 | 24278569 | 55592385 | 3170225 | 0 | 5090981 | 1270080 | 11907273 | 4339459 | 11040 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6832512 | 0 |  | 0 | 31540830 | 0 | 0 | 0 | 4293394.92 | 23345291.7 | 0 | 0 | 0 | 912434.4 | 25270857.6 | 578150 | 0 | 0 | 0 | 9676339.2 | 6776437.52 | 4285968.86 | 0 | 377550 | 0 | 0 | 0 | 5906001.6 | 0 | 0 | 0 | 0 | 0 | 2959696.98 | 16818002.19 | 0 | 0 | 0 |  | 4432680 | 11284488 | 7286486.49 | 0 | 8191219.2 | 7671676.8 | 0 | 0 | 0 | 0 | 0 | 21970413 | 0 | 0 | 15185854.85 | 4399130.8 | 3512699.28 | 0 | 0 | 2919937.64 | 0 | 1696757.58 | 5400915.24 | 0 | 0 | 0 | 295612.5 | 8331724.8 | 3057254.4 | 0 | 0 | 0 | 0 | 2665458 | 0 | 3416540.4 | 682197.66 | 0 | 7263662.4 | 8078054.4 | 0 | 11705026.5 | 0 | 0 | 0 | 22133670 | 224208 | 41112.96 | 0 | 11004882 | 0 | 0 | 34946832 | 0 | 16812619.2 | 0 | 11318611.2 | 33145440 | 22658526.44 | 24973600 | 19052376 | 16424755.2 | 8312409.3 | 0 | 19978506.45 | 10992484.08 | 9122597.64 | 8997370.2 | 11951125.2 | 2410761.6 | 22129870 | 704649.6 | 0 | 28918684.8 | 11220332.94 | 0 | 6092240.4 | 0 | 14410233.6 | 9385437.6 | 26040366 | 8525820.16 | 0 | 93182550.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60867662.9 | 0 | 24595920 | 0 | 0 | 0 | 0 | 0 | 3909470.4 | 5780839.68 | 0 | 8920680 | 685375.56 | 4005196.8 | 0 | 0 | 0 | 7021740.87 | 1999599.5 | 10950168.48 | 0 | 0 | 3516574.77 | 0 | 3185239.77 | 0 | 0 | 99878.58 | 17158665.08 | 0 | 27691640 | 0 | 0 | 15131701.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25432881.72 | 967411.2 | 0 | 8899021.44 | 0 | 4853268.96 | 0 | 0 | 9142272 | 172564344 | 16228788.6 | 0 | 31114800 | 0 | 0 | 12472012.8 | 0 | 0 | 78521428 | 0 | 0 | 78707074.53 | 0 | 0 | 0 | 0 | 0 |  | 784133329.81 | 634423656.84 | 1418556986.65 | 224399949.51 | 60867662.9 | 126304130.83 | 0 | 440399773.37 | 389118627.41 | 0 | 0 | 90428043.3 | 8331724.8 | 78707074.53 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 23 | 15 | 17 | 16 | 18 | 0 | 134 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 34 | 0 | 0 | 6 | 0 | 8 | 0 | 0 | 0 | 310 | 0 | 0 | 187 | 50 | 44 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 52 | 29 | 0 | 0 | 2 | 0 | 30 | 0 | 36 | 0 | 0 | 58 | 86 | 0 | 206 | 0 | 0 | 0 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 75 | 0 | 39 | 0 | 0 | 40 | 13 | 386 | 45 | 53 | 0 | 4 | 48 | 24 | 0 | 17 | 9 | 0 | 350 | 0 | 50 | 54 | 21 | 0 | 17 | 33 | 20 | 18 | 395 | 17 | 0 | 600 | 0 | 0 | 0 | 0 | 72 | 0 | 0 |  | 895 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 132 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1232 | 220 | 0 | 60 | 5 | 84 | 35 | 0 | 0 | 367 | 37 | 0 | 512 | 189 | 0 | 0 | 54 | 110 |  | 10293 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 132 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 22 | 22 | 23 | 24 | 25 | 0 | 134 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 18 | 79 | 34 | 0 | 45 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 0 | 199 | 50 | 44 | 0 | 0 | 35 | 0 | 37 | 52 | 0 | 0 | 0 | 18 | 58 | 33 | 0 | 0 | 0 | 0 | 30 | 0 | 35 | 0 | 0 | 62 | 86 | 0 | 207 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 195 | 0 | 0 | 86 | 0 | 112 | 0 | 76 | 162 | 127 | 382 | 56 | 105 | 68 | 0 | 52 | 35 | 54 | 70 | 31 | 12 | 346 | 0 | 0 | 162 | 53 | 0 | 19 | 0 | 92 | 36 | 350 | 160 | 0 | 555 | 0 | 0 | 0 | 120 | 0 | 0 | 0 |  | 895 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 40 | 49 | 0 | 123 | 7 | 64 | 0 | 0 | 0 | 48 | 17 | 95 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 11 | 66 | 0 | 135 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 17 | 0 | 50 | 0 | 89 | 0 | 0 | 50 | 1060 | 220 | 0 | 135 | 0 | 0 | 115 | 0 | 0 | 624 | 0 | 0 | 517 | 0 | 0 | 0 | 0 | 0 |  | 12270 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 23 | 22 | 23 | 33 | 25 | 0 | 134 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 24 | 70 | 84 | 0 | 45 | 50 | 0 | 10 | 0 | 0 |  | 310 | 0 | 0 | 190 | 70 | 44 | 0 | 0 | 35 | 0 | 36 | 52 | 0 | 0 |  | 18 | 82 | 35 | 0 | 0 | 0 | 0 | 30 | 0 | 36 | 100 | 0 | 61 | 86 | 0 | 210 | 0 | 0 | 0 | 310 | 13 | 5 | 0 | 300 | 0 | 0 | 96 | 0 | 149 | 0 | 100 | 200 | 130 | 385 | 57 | 105 | 68 | 0 | 52 | 35 | 110 | 106 | 55 | 12 | 400 | 16 | 0 | 162 | 53 | 0 | 35 | 0 | 92 | 36 | 400 | 160 | 0 | 612 | 15 | 0 | 0 | 0 |  |  |  |  | 908 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 127 | 10 | 110 | 0 | 0 | 0 | 40 | 25 | 95 | 0 | 0 | 43 | 0 | 30 | 0 | 0 | 11 | 67 | 0 | 130 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 95 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 137 | 0 | 0 | 115 | 0 | 0 | 617 | 0 | 0 | 500 | 0 | 0 |  |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 23 | 22 | 23 | 33 | 25 | 0 | 134 | 0 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 50 | 65 | 0 | 45 | 50 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 0 | 190 | 70 | 44 | 0 | 0 | 35 | 0 | 35 | 52 | 0 | 0 |  | 18 | 66 | 44 | 0 | 0 | 1.6 | 0 | 30 | 0 | 36 | 70 | 0 | 60 | 86 | 0 | 210 | 0 | 0 | 0 | 300 | 13 | 5 | 0 | 300 | 0 | 0 | 96 | 0 | 149 | 20 | 50 | 140 | 120 | 385 | 55 | 52 | 51 | 5 | 52 | 35 | 56 | 106 | 27 | 12 | 400 | 0 | 50 | 162 | 35 | 0 | 17 | 35 | 92 | 36 | 400 | 17 | 0 | 612 | 15 | 0 | 0 | 0 | 70 |  |  |  | 908 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 0 | 127 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 26 | 0 | 30 | 0 | 0 | 5 | 67 | 0 | 130 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 95 | 0 | 113 | 0 | 8 | 113 | 622 | 220 |  | 51 | 6 | 100 | 54 | 0 | 0 | 375 | 30 | 0 | 500 | 170 | 0 |  | 29 | 47 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 2 | 250 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 23 | 22 | 17 | 33 | 8 | 0 | 134 | 0 | 0 | 0 | 8 | 229 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 45 | 19 | 0 | 10 | 0 | 0 | 0 | 280 | 0 | 0 | 199 | 70 | 40 | 0 | 0 | 35 | 0 | 0 | 52 | 0 | 0 | 0 | 16 | 46 | 44 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 15 | 0 | 61 | 30 | 0 | 210 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 5 | 0 | 0 | 68 | 0 | 19 | 3 | 50 | 138 | 120 | 332 | 55 | 17 | 51 | 1 | 68 | 35 | 56 | 70 | 9 | 12 | 326 | 0 | 23 | 17 | 35 | 0 | 17 | 15 | 36 | 18 | 395 | 17 | 0 | 612 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 890 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 134 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 50 | 0 | 33 | 0 | 2 | 70 | 622 | 220 | 0 | 17 | 2 | 33 | 115 | 0 | 0 | 370 | 13 | 0 | 518 | 76 | 0 | 0 | 23 | 43 | 0 |  |  |  | 118273031 | 21661090 | 0 | 55592385 | 29369550 | 1270080 | 4339459 | 11040 | 3170225 |  |  |  | 233686860
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [10 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [10 empty] | 118.273 | 21.6611 | 0 | 55.5924 | 29.3696 | 1.2701 | 4.3395 | 0.01104 | 3.1702
| Minimum Generation |  | 8390 | 6:00
| Highest Generation |  | 12270 | 19:00 | [129 empty] | 0 | [76 empty] | 233.6869
| Day Peak Generation |  | 10293 | 12:00
| Evening Peak Generation |  | 12270 | 19:00 | [206 empty] | 202699852
| HVDC Max Flow |  | 897 | 5:00 | [206 empty] | 202.6999
| HVDC EvPeak Flow |  | 895 | 19:00
| Load factor L.F |  | 83.4% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-11-10
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-11-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10293 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 8759
Evening Peak Generation : |  |  | 12270 | MW Hour : | 19:00 | Available Max Generation : |  | 12812
E.P. Demand (at gen end) : |  |  | 12270 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13000
Maximum Generation : |  |  | 12270 | MW Hour : | 19:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 245.5941 | System Load Factor : | 83.4% | Load Shed : |  | 265
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 824 | MW at | 19:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-11-10
Actual : |  | 99.43 | Ft.(MSL) , | Rule curve : | 108.1 | Ft.( MSL )
Gas Consumed : |  | Total = | 852.67 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 350704080.34 | Adani : | 78707074.53
|  |  | Coal : | 389118627.41 | Oil: | 530827816.67 | Total: | 1349357598.95
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4533.8427 |  |  | 60 | 0%
Chittagong Area |  | 0 | 0:00 | 1245.692 |  |  | 23 | 0%
Khulna Area |  | 0 | 0:00 | 1744.9061 |  |  | 41 | 0%
Rajshahi Area |  | 0 | 0:00 | 1516.5797 |  |  | 44 | 0%
Cumilla Area |  | 0 | 0:00 | 1247.9061 |  |  | 32 | 0%
Mymensingh Area |  | 0 | 0:00 | 928.0993 |  |  | 28 | 0%
Sylhet Area |  | 0 | 0:00 | 520.2585 |  |  | 11 | 0%
Barisal Area |  | 0 | 0:00 | 433.5457 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 847.94 |  |  | 26 | 0%
Total |  | 0 |  | 13018.7703 |  |  | 265
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:01 |  | Barguna 132/33kV S/S Transformer-1 LT Tripped showing REF615 relays Due to T1A 33KV |  |  |  |  | About 10 MW p[ower interrupt.
Incomer Trip Due to WZPDCL Feeder-1 Fault.
08:07 | 16:23 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Scheduled S/D from Bog-Sherpur 132/33kV end. and
from Bogura 230/132kV end Due to Annual Maintenance
08:09 | 16:25 | Benapole 132/33kV S/S Transformer-1(406T) LT Scheduled S/D Due to Annual maintenance of Transformer 1
08:11 | 15:43 | Gollamari 132/33kV S/S Tr-1 LT Scheduled S/D Due to Annual Maintenance
08:11 | 16:30 | Keraniganj-Nawabganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Annual maintenance at Keraniganj end. and from Nawabganj 132/33kV end Due to Annual
08:12 | 15:42 | Gollamari 132/33kV S/S Tr-1 HT Scheduled S/D Due to Annual Maintenance
08:16 | 16:58 | Natore-Rajshahi 132kV Ckt-2 Scheduled S/D from Rajshahi 132/33kV end Due to Annual
maintenance work and from Natore 132/33kV end Due to Yearly maintenance
08:20 | 16:25 | Amnura 132/33kV S/S T-2 (416T) HT Scheduled S/D Due to Annual maintenance
| 08:21 | Rampura 230/132kV S/S 132 kV Busbar-2 is restored.
| 08:21 | Rampura 230/132kV S/S Auto Transformer - 02 LT is restored.
| 08:21 | Rampura 230/132kV S/S Auto Transformer - 02 HT is restored.
08:22 | 21:51 | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to From Other
End. and from Bhulta 400/230kV end Due to Due to Annual Maintenance Works.
08:30 | 16:32 | Ishwardi-Rooppur 132kV Ckt-1 Scheduled S/D from Ruppur 132/11kV end Due to Annual
Maintenance of 132kv Rp-Ish Line-01 and from Ishurdi 132/33kV end Due to Annual Maintenance
| 08:32 | Hasnabad-Sitalakhya 132kV Ckt-1 is restored.
08:40 | 16:41 | Gopalganj 400/132kV S/S ATR-03 HT Scheduled S/D
08:40 |  | Sreemongol 132/33kV S/S 132/33kv T-2 LT Scheduled S/D Due to Annual Maintenance.
08:40 |  | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to Annual Maintenance.
08:40 | 16:42 | Gopalganj 400/132kV S/S ATR-03 LT Scheduled S/D
08:42 |  | Sreemongol 132/33kV S/S 132/33kv T-2 HT Scheduled S/D Due to Annual Maintenance.
08:42 |  | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to Annual Maintenance.
08:47 | 16:13 | BSRM-Cumilla(N) 230 kV Ckt-2 S/D from Cumilla(N) end Due to Annual Maintenance Work
08:49 |  | Haripur 412 MW CCPP ST was shut down due to diverter damper maint.
08:52 |  | Barguna 132/33kV S/S Transformer-1 HT Forced S/D Due to T1A 33KV Incomer Trip Due to |  |  |  |  | About 10 MW p[ower interrupt.
WZPDCL Feeder-1 Fault.
08:52 | 15:00 | Rajbari 132/33kV S/S Bheramara-1 Scheduled S/D Due to Annual Maintenance
08:53 | 15:54 | Jhenaidah-Khulna 230kV Ckt-1 Scheduled S/D from Jhenaidah 230/132kV end Due to annual
maintenance and from Khulna(S) 230/132kV end Due to Annual Maintenance Work.
09:00 | 12:25 | Rampura 230/132kV S/S 132 kV Busbar-1 Project Work S/D
09:02 |  | Haripur 412 MW CCPP GT was shut down due to diverter damper maint.
09:09 |  | Ashuganj-Brahmanbaria 132kV Ckt-2 Scheduled S/D from Ashuganj 230/132/33kV end. and from
Brahmanbaria 132/33kVend.
09:10 | 16:36 | Fenchuganj -Sylhet 132kV Ckt-1 S/D from Beanibazar 132/33kV end Due to Maintenance work
09:30 | 16:54 | Jamalpur-Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to Annual
Maintenance Works and from Jamalpur 132/33kV end Due to Annual Maintenance
09:53 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Fenchuganj
230/132/33kV end Due to Annual maintenance
| 09:53 | Chandpur 132/33kV S/S 422T HT is restored.
09:55 |  | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D Due to Ordered by
NLDC due to load management purpose.
09:56 | 14:22 | New Tongi-Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
Maintenance Work
10:03 | 16:32 | Dohazari-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance Line and from Shikalbaha 230/132kV end Due to Annual Maintenance
| 10:35 | Barguna 132/33kV S/S Transformer-2 HT is restored.
10:40 | 16:16 | BIPTC S/S 20DF32 Scheduled S/D Due to For annual maintenance
10:47 | 12:33 | Noapara 132/33kV S/S T-2 LT Scheduled S/D |  |  |  |  | About 10 MW p[ower interrupt.
11:37 | 12:31 | Aminbazar-Keraniganj 230kV Ckt-1 Forced S/D from Keranigonj 230/132/33kV end Due to
Emergency shutdown for Bird nest remove from Aminbazar end. and from Aminbazar
400/230/132kV end Due to To remove bird nest from tower no 43
| 12:25 | Juldah 132/33kV S/S Julda power plant unit-2 & 3 is restored.
13:22 |  | Meghnaghat Summit U-2 GT was synch.
14:17 | 20:55 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Project Work S/D
| 15:34 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT is restored.
| 15:41 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT is restored.
16:07 |  | Summit Meghnaghat-2 589 MW PP ST was synchronized.
| 16:31 | Patuakhali 132/33kV S/S 425T (T-3) HT is restored.
| 17:15 | Shyampur 230/132kV S/S Auto TR-1 HT is restored.
| 17:18 | Shyampur 230/132kV S/S LV AC-1 is restored.
17:42 |  | Jhenaidah-Khulna 230kV Ckt-1 Forced S/D from Jhenaidah 230/132kV end Due to Flashing Y
phase of B-Bus D/S in finger point.
19:37 |  | Kushiara 163MW CCPP ST was sync.
20:51 |  | Summit Meghnaghat-2 589 MW PP ST tripped.
| 21:52 | Goalpara 132/33kV S/S T-6 HT is restored.
23:34 |  | Payra 400kV S/S GSUT-02 HT Scheduled S/D Due to overhaul inspection |  |  |  |  | About 622 MW power reduce
23:34 |  | Payra U-2 SD due to major inspection work
01:53 |  | Summit meghnaghat-2 589 MW PP (Gas) was forced shutdown hrs due to DP sensor problem of ST.
06:21 |  | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to For Annual
Bay Maintenance and from Halishahar 132/33kV end Due to For 132kv julda bay A/M.
06:58 |  | Haripur-Sonargaon 132kV Ckt-1 Forced S/D from Sonargaon 132/33kV end Due to According
to order of NLDC
06:59 |  | Haripur-Sonargaon 132kV Ckt-2 Forced S/D from Sonargaon 132/33kV end Due to According
to order of NLDC
07:24 |  | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D Due to Annual maintenance
07:31 |  | Keraniganj-Nawabganj 132kV Ckt-1 Scheduled S/D from Nawabganj 132/33kV end Due to Annual
Maintenance and from Keranigonj 230/132/33kV end Due to Yearly Maintenance at Nawabganj end
07:45 |  | Kabirpur -Kodda 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Annual
Maintenance Work.
07:51 |  | Amnura 132/33kV S/S T-2 (416T) LT Scheduled S/D Due to Annual maintenance
07:56 |  | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to
Annual Maintenance and from Bog-Sherpur 132/33kVend.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-11-09
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 0 | 2372400 | Machine problem.
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9918500
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 243666
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 31000
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7654194
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 50832 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 529920
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1301280 | Low demand.
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 429977
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 234334
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 44 | 901560 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 23 | 486720 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 522000 | Engine problem
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 329760 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 539455 | Low demand.
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 112 | 954720 | Low demand.
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 875520
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 41280 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1581120
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 220928
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 554040 | Fuel shortage
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 120 | 1047759 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 1995 | 30820965
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 156267
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 49545
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 466080 | Low demand.
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 134 | 3170225
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5272101
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 68 | 463345 | Engine problem
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 79 | 640800 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 406839 | Low demand.
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 635520 | Fuel shortage
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 485760
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 45 | 418560 | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27480
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1221927 | Fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 565457 | Fuel shortage
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 508506 | Fuel shortage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 135360 | Fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 668673 | Fuel shortage
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 160 | 605527
55 | SS Power I |  | IPP | 2*612 | 1224 | 555 | 13369089 | Coal shortage
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 11040
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 0 | 0 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1642 | 29278101
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7874700 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 350 | 8767800 | frequency control
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 44 | 1042344
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 199 | 4533091
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 728164 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 127 | 1366618 | Fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 94738 | Engine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1361960 | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 162 | 1910400 | Fuel shortage
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 58 | 1270080
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 299054
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 394150 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 470820 | Low demand.
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 31 | 615720 | Low demand.
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 799680 | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 498264
| Cumilla Area Total |  |  |  | 2917 | 1635 | 32027583
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 33 | 983040 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14750
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 86 | 1819200 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 56 | 999600 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 349780
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 252000 | Fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 19 | 340920 | Fuel shortage
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 646 | 212 | 4759290
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Under maint.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 714600 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 199473 | Under maint.
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 35 | 750888 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 54096 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1308768
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1547520
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 207 | 4195350 | Machine problem.
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 298944 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7163000 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 382 | 9424000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 346 | 8319500 | FGMO
| Sylhet Area Total |  |  |  | 2417 | 1443 | 33976139
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 895 | 21661090
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 207840 | Engine problem
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 49 | 307328 | Engine problem
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 368 | 8337600 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 56640 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 569520
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 624 | 10756360 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1993 | 41896378
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 232320 | Low demand.
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 7 | 144594 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 123 | 2823000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 26630300
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5218260
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 135 | 1608000 | Fuel shortage
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Under maint.
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3918
| Barisal Area Total |  |  |  | 2236 | 1609 | 36660392
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 392057 | Engine problem
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 17 | 108970 | Engine problem
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 196347 | Engine problem
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 160 | 4585364 | frequency control
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 318 | 8709891 | FGMO
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 177847 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 131940
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 651408 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 448992 | Low demand.
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 460800 | Low demand.
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37620
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 517 | 11907273
135 | Sirajganj 68 MW Solar Park |  | NWPGCL | 68 | 68 | 0 | 372752
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 655994
| Rajshahi Area Total |  |  |  | 3449 | 1336 | 28837255
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 66 | 1555636 | Machine problem.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 135 | 3281000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 89 | 243638 | Fuel shortage
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39488
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 718848
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 240110
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 1259310
| Rangpur Area Total |  |  |  | 950 | 405 | 7338030
| Total |  |  |  | 27086 | 12270 | 245594133
| Eastern Grid Total |  |  |  | 16752 | 6927 | 130862078
| Western Grid Total |  |  |  | 10334 | 5343 | 114732055
| National Grid Total |  |  |  | 27086 | 12270 | 245594133
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-11-09
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7285.68 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3408.1 | MW
i) Dhaka area |  |  | 3809.58 |  | MW | i) Khulna area |  |  |  | 1342 | MW
ii) Chattogram area |  |  | 1032.1 |  | MW | ii) Barishal area |  |  |  | 330.5 | MW
iii) Cumilla area |  |  | 1043 |  | MW | iii) Rajshahi area |  |  |  | 1053.6 | MW
iv) Mymensingh area |  |  | 968 |  | MW | iv) Rangpur area |  |  |  | 682 | MW
v) Sylhet area |  |  | 433 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10693.78 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 23:00 | 67 | Jashore | 114 | 18:30 | 133 | Rajbari | 64 | 18:00
2 | AKSML | 114.2 | 01:00 | 68 | Jhenaidah | 106 | 18:00 | 134 | Rajendrapur | 90 | 18:30
3 | Aftabnagar | 46 | 12:00 | 69 | Joydebpur | 161 | 18:00 | 135 | Rajshahi | 95 | 18:00
4 | Agargaon | 95 | 18:00 | 70 | Joypurhat | 42 | 18:00 | 136 | Rajshahi-230 | 62 | 20:00
5 | Agrabad | 88 | 19:00 | 71 | Juldah | 14 | 23:00 | 137 | Ramganj | 104 | 18:00
6 | Amnura | 48 | 18:00 | 72 | KSRM | 30 | 13:00 | 138 | Rampur | 39 | 18:30
7 | Ashuganj | 81 | 23:00 | 73 | Kabirpur | 258 | 18:00 | 139 | Rangamati | 15 | 18:00
8 | BSRM | 67 | 05:00 | 74 | Kachua | 57 | 18:00 | 140 | Rangpur | 117 | 18:00
9 | Bagerhat | 74 | 18:00 | 75 | Kallyanpur | 96 | 18:00 | 141 | Ruppur | 4.6 | 10:00
10 | Bakulia | 91 | 18:30 | 76 | Kalurghat | 35 | 12:00 | 142 | SSM | 8 | 23:00
11 | Banani | 37.2 | 14:00 | 77 | Kamrangirchar | 57.2 | 13:00 | 143 | Saidpur | 96 | 18:00
12 | Bangabhaban | 4 | 09:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 97 | 21:00
13 | Barapukuria | 47 | 18:00 | 79 | Kazla | 103 | 13:00 | 145 | Satmasjid | 85 | 18:00
14 | Barguna | 16 | 21:00 | 80 | Keranigonj | 68 | 19:00 | 146 | Savar | 189 | 17:00
15 | Barishal | 93 | 18:00 | 81 | Khagrachori | 28 | 18:00 | 147 | SevenRings | 3 | 22:00
16 | Barishal-230 | 66 | 18:00 | 82 | Khulna | 79 | 18:00 | 148 | ShahCement | 10 | 23:00
17 | Baroaulia | 58 | 13:00 | 83 | Khulshi | 151 | 15:00 | 149 | Shahjadpur | 64 | 18:00
18 | Baroirhat | 45 | 19:30 | 84 | Kishoreganj | 122 | 19:00 | 150 | Shahjibazar | 101 | 18:00
19 | Bashundhara | 150 | 18:00 | 85 | Kodda | 308 | 18:00 | 151 | Shahmirpur | 53 | 17:00
20 | BashundharaCement | 7 | 09:00 | 86 | Kulaura | 36 | 18:00 | 152 | Shariatpur | 59 | 18:00
21 | Beanibazar | 50 | 18:00 | 87 | Kurigram | 48 | 18:00 | 153 | Sherpur | 106 | 18:00
22 | Benapole | 52 | 18:00 | 88 | Kushtia | 120 | 18:30 | 154 | Shikalbaha | 19 | 18:00
23 | Bhaluka | 130 | 18:00 | 89 | Lalbag | 67 | 18:00 | 155 | Shitalakhya | 71.8 | 13:00
24 | Bhandaria | 49 | 20:00 | 90 | Lalmonirhat | 47 | 18:00 | 156 | Sholosohor | 42 | 18:00
25 | Bhangura | 28 | 18:00 | 91 | MI_Cement | 15.1 | 13:00 | 157 | Shyampur | 170 | 12:00
26 | Bheramara(GK) | 50 | 18:00 | 92 | Madanganj | 27 | 13:00 | 158 | Siddhirganj | 144 | 18:00
27 | Bhulta | 216 | 18:00 | 93 | Madaripur | 74 | 19:00 | 159 | Sirajganj | 72 | 19:00
28 | Bog-Sherpur | 60 | 18:00 | 94 | Madartek | 60 | 22:00 | 160 | Sonargaon | 75 | 18:30
29 | Bogura | 133 | 19:00 | 95 | Madunaghat | 47 | 18:00 | 161 | Sreemongol | 63 | 18:00
30 | Borhanuddin | 59 | 20:00 | 96 | Magura | 51 | 18:00 | 162 | Sreepur | 67 | 18:00
31 | Brahmanbaria | 149 | 18:30 | 97 | Mahasthangarh | 56 | 18:00 | 163 | Srinagar | 34.2 | 20:00
32 | Cantonment | 110 | 13:00 | 98 | Manikganj | 103 | 18:00 | 164 | Sunamganj | 46 | 18:00
33 | Chandpur | 58 | 19:00 | 99 | Maniknagar | 56 | 13:00 | 165 | Sylhet | 38 | 18:00
34 | Chandraghona | 31 | 17:00 | 100 | Matarbari | 40 | 18:00 | 166 | Sylhet-132 | 111 | 12:00
35 | Chapai | 49 | 18:00 | 101 | Matuail | 65 | 15:00 | 167 | TK | 20 | 18:30
36 | Charsaidpur | 42 | 01:00 | 102 | Millgate | 108 | 15:00 | 168 | Tangail | 148 | 18:00
37 | Chauddagram | 55 | 18:00 | 103 | Mirpur | 122 | 18:00 | 169 | Thakurgaon | 76 | 18:00
38 | Chhatak | 27 | 18:00 | 104 | Mirsorai | 6 | 15:00 | 170 | Tongi | 107 | 17:00
39 | Chowmuhani | 174 | 19:00 | 105 | Mirzapur | 32 | 13:00 | 171 | Ullahpara | 33 | 18:00
40 | Chuadanga | 86 | 18:30 | 106 | Mithapukur | 46 | 18:00 | 172 | Ullon | 40 | 18:00
41 | Coxsbazar | 110 | 19:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 79 | 13:00
42 | Cumilla(N) | 147 | 19:30 | 108 | Mogbazar | 95.6 | 12:00 | 174 | UttaraNew | 45 | 18:00
43 | Cumilla(S) | 144 | 18:00 | 109 | Mongla | 28 | 12:00 | 175 | Zigatola | 87 | 18:30
44 | Daudkandi | 134 | 18:30 | 110 | Motijheel | 38 | 13:00
45 | Dhaka | 28 | 12:00 | 111 | Munshiganj | 86 | 20:00
46 | Dhamrai | 116 | 18:00 | 112 | Mymensingh | 193 | 18:30
47 | Dhanmondi | 126 | 13:00 | 113 | Naogaon | 97 | 18:30
48 | Dohazari | 88 | 21:00 | 114 | Narail | 47 | 18:00
49 | Faridpur | 123 | 18:00 | 115 | Narinda | 74 | 13:00
50 | Fatullah | 79 | 18:00 | 116 | Narshingdi | 169 | 19:00
51 | Fenchuganj | 31 | 18:00 | 117 | Natore | 118 | 19:00
52 | Feni | 96 | 18:30 | 118 | Nawabganj | 40.4 | 20:00
53 | GPH | 97 | 15:00 | 119 | Netrakona | 103 | 18:30
54 | Ghatail | 50 | 18:30 | 120 | New | 48.7 | 12:00
55 | Ghorashal | 59 | 18:00 | 121 | Niamatpur | 46 | 18:30
56 | Goalpara | 26 | 00:00 | 122 | Noapara | 36 | 18:00
57 | Gollamari | 100 | 12:00 | 123 | PHP | 2 | 03:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-11-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 393 | 05:00 | 371 | 04:00 | Kaliakoir | 378 | 19:00 | 360 | 11:00
| Ashuganj | 410 | 18:00 | 390 | 11:00 | Madunaghat | 402 | 21:00 | 386 | 11:00
| Bhulta | 404 | 00:00 | 389 | 11:00 | Meghnaghat | 388 | 22:00 | 369 | 11:00
| Bibiana | 394 | 05:00 | 385 | 15:00 | Payra | 414 | 05:00 | 404 | 11:00
| BIPTC | 401 | 04:00 | 393 | 18:00 | Rahanpur | 394 | 05:00 | 387 | 14:00
| Bogura | 387 | 06:00 | 379 | 13:00 | Rampal | 408 | 06:00 | 394 | 11:00
| Gopalganj | 404 | 05:00 | 388 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 235 | 05:00 | 223 | 11:00 | Haripur | 235 | 06:00 | 223 | 12:00
| AKSML | 240 | 19:00 | 226 | 10:00 | Hasnabad | 236 | 23:00 | 222 | 11:00
| Aminbazar | 234 | 08:00 | 223 | 11:00 | Hathazari | 240 | 18:30 | 227 | 11:00
| Ashuganj | 239 | 19:00 | 230 | 11:00 | Ishurdi | 238 | 06:00 | 230 | 12:00
| Ashuganj-400 | 238 | 18:00 | 232 | 11:00 | Jhenaidah | 233 | 05:00 | 224 | 12:00
| Baghabari | 233 | 23:00 | 226 | 11:00 | Kaliakoir | 237 | 03:00 | 223 | 11:00
| Barapukuria | 225 | 04:00 | 220 | 08:00 | Keranigonj | 235 | 06:00 | 222 | 12:00
| Barapukuria-230 | 225 | 6:00 | 218 | 19:00 | Khulna(S) | 234 | 05:00 | 225 | 12:00
| Barishal | 240 | 05:00 | 233 | 12:00 | Madunaghat | 240 | 21:00 | 228 | 11:00
| Bheramara | 235 | 06:00 | 227 | 12:00 | Maniknagar | 235 | 03:00 | 223 | 11:00
| Bhulta | 236 | 01:00 | 225 | 11:00 | Meghnaghat | 241 | 01:00 | 230 | 11:00
| Bibiana | 225 | 06:00 | 220 | 11:00 | Meghnaghat-400 | 237 | 05:00 | 225 | 11:00
| BIPTC | 238 | 05:00 | 228 | 12:00 | Mirsorai | 242 | 19:00 | 224 | 11:00
| Bogura | 236 | 03:00 | 231 | 16:00 | Rajshahi | 235 | 04:00 | 226 | 12:00
| Bogura-400 | 236 | 04:00 | 231 | 13:00 | Rampal | 234 | 06:00 | 224 | 11:00
| Borhanuddin | 243 | 04:00 | 239 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 240 | 19:00 | 225 | 11:00 | Rampura | 236 | 02:00 | 223 | 11:00
| Cumilla(N) | 233 | 22:00 | 222 | 11:00 | Shikalbaha | 239 | 19:00 | 225 | 11:00
| Faridpur | 239 | 06:00 | 230 | 11:00 | Shyampur | 235 | 03:00 | 223 | 12:00
| Fenchuganj | 230 | 05:00 | 222 | 11:00 | Siddhirganj | 236 | 00:00 | 225 | 11:00
| Ghorashal | 235 | 00:00 | 230 | 11:00 | Sirajgonj | 242 | 06:00 | 237 | 12:00
| Ghorashal-230 | 235 | 06:00 | 224 | 11:00 | Sreepur | 235 | 04:00 | 226 | 11:00
| Gopalganj | 238 | 04:00 | 230 | 11:00 | Tongi | 235 | 19:00 | 222 | 12:00
| GPH | 239 | 19:00 | 226 | 10:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 139 | 01:00 | 129 | 10:00 | Kushtia | 138 | 02:00 | 133 | 12:00
| Agargaon | 140 | 06:00 | 131 | 12:00 | Lalbag | 140 | 06:00 | 131 | 11:00
| Agrabad | 136 | 19:00 | 128 | 10:00 | Lalmonirhat | 132 | 04:00 | 125 | 14:00
| AKS | 135 | 18:30 | 127 | 10:00 | Madanganj | 130 | 00:00 | 122 | 11:00
| Aminbazar | 141 | 02:00 | 130 | 09:00 | Madaripur | 132 | 07:00 | 129 | 12:00
| Amnura | 141 | 22:00 | 124 | 22:00 | Madartek | 138 | 00:00 | 129 | 11:00
| Ashuganj | 140 | 00:00 | 136 | 16:00 | Madunaghat | 137 | 18:00 | 130 | 10:00
| Bagerhat | 138 | 06:00 | 130 | 18:00 | Magura | 138 | 06:00 | 131 | 13:00
| Bakulia | 137 | 19:00 | 129 | 11:00 | Mahasthangarh | 137 | 06:00 | 133 | 12:00
| Banani | 138 | 02:00 | 128 | 12:00 | Manikganj | 132 | 20:00 | 118 | 15:00
| Bangabhaban | 134 | 08:00 | 124 | 11:00 | Maniknagar | 134 | 06:00 | 124 | 11:00
| Barapukuria | 137 | 04:00 | 132 | 08:00 | Matarbari | 124 | 09:00 | 115 | 11:00
| Barguna | 140 | 18:00 | 132 | 11:00 | Matuail | 132 | 02:00 | 125 | 11:00
| Barishal | 132 | 04:00 | 128 | 12:00 | Millgate | 137 | 04:00 | 129 | 11:00
| Barishal-230 | 134 | 05:00 | 128 | 12:00 | Mirpur | 141 | 06:00 | 131 | 11:00
| Baroaulia | 138 | 19:00 | 129 | 11:00 | Mirzapur | 130 | 20:00 | 122 | 15:00
| Baroirhat | 132 | 19:00 | 122 | 12:00 | Mithapukur | 135 | 05:00 | 129 | 08:00
| Bashundhara | 139 | 01:00 | 127 | 11:00 | MI_Cement | 138 | 05:00 | 128 | 12:00
| BashundharaCement | 130 | 00:00 | 122 | 11:00 | Modern | 137 | 18:30 | 130 | 10:00
| Beanibazar | 130 | 05:00 | 126 | 11:00 | Mogbazar | 140 | 03:00 | 129 | 12:00
| Benapole | 138 | 05:00 | 129 | 18:00 | Mongla | 138 | 06:00 | 128 | 18:30
| Bhaluka | 133 | 00:00 | 126 | 15:00 | Motijheel | 134 | 08:00 | 124 | 11:00
| Bhandaria | 130 | 06:00 | 120 | 18:00 | Munshiganj | 131 | 08:00 | 123 | 11:00
| Bhangura | 140 | 05:00 | 135 | 11:00 | Mymensingh | 136 | 00:00 | 123 | 15:00
| Bheramara | 138 | 03:00 | 134 | 12:00 | Naogaon | 136 | 05:00 | 132 | 13:00
| Bheramara(GK) | 138 | 06:00 | 134 | 12:00 | Narail | 138 | 05:00 | 131 | 12:00
| Bhulta | 126 | 08:00 | 119 | 11:00 | Narinda | 134 | 6:00 | 124 | 11:00
| Bog-Sherpur | 138 | 06:00 | 135 | 00:00 | Narshingdi | 127 | 21:00 | 119 | 10:00
| Bogura | 140 | 00:00 | 135 | 16:00 | Natore | 137 | 04:00 | 133 | 12:00
| Bogura-230 | 139 | 19:00 | 135 | 16:00 | Nawabganj | 139 | 05:00 | 130 | 12:00
| Brahmanbaria | 135 | 08:00 | 129 | 22:00 | Netrakona | 133 | 00:00 | 126 | 18:30
| Cantonment | 139 | 05:00 | 131 | 11:00 | New | 138 | 04:00 | 129 | 12:00
| Chandpur | 137 | 18:30 | 121 | 11:00 | Niamatpur | 133 | 05:00 | 130 | 11:00
| Chandraghona | 138 | 19:00 | 130 | 11:00 | Noapara | 139 | 05:00 | 133 | 12:00
| Chapai | 131 | 06:00 | 126 | 19:30 | Pabna | 139 | 06:00 | 133 | 12:00
| Charsaidpur | 131 | 04:00 | 124 | 12:00 | Palashbari | 134 | 04:00 | 129 | 08:00
| Chauddagram | 133 | 19:00 | 122 | 10:00 | Panchagarh | 135 | 19:00 | 121 | 08:00
| Chhatak | 128 | 00:00 | 124 | 12:00 | Patuakhali | 138 | 00:00 | 132 | 10:00
| Chowmuhani | 129 | 19:00 | 120 | 10:00 | Payra | 137 | 19:00 | 133 | 11:00
| Chuadanga | 136 | 05:00 | 126 | 18:00 | PHP | 132 | 19:00 | 120 | 11:00
| Coxsbazar | 122 | 08:00 | 118 | 00:00 | Postogola | 140 | 04:00 | 130 | 12:00
| Cumilla(N) | 135 | 22:00 | 127 | 11:00 | Purbachal | 139 | 01:00 | 127 | 12:00
| Cumilla(S) | 134 | 19:00 | 125 | 11:00 | Purbasadipur | 134 | 19:00 | 122 | 08:00
| Daudkandi | 131 | 16:00 | 124 | 11:00 | Rahanpur | 134 | 05:00 | 131 | 11:00
| Dhaka | 138 | 05:00 | 129 | 11:00 | Rahim | 132 | 00:00 | 123 | 11:00
| Dhamrai | 135 | 05:00 | 128 | 16:00 | Rajbari | 133 | 06:00 | 127 | 13:00
| Dhanmondi | 139 | 00:00 | 129 | 11:00 | Rajendrapur | 130 | 19:30 | 116 | 16:00
| Dohazari | 132 | 18:00 | 122 | 11:00 | Rajshahi | 138 | 06:00 | 131 | 12:00
| Faridpur | 134 | 03:00 | 129 | 11:00 | Rajshahi-230 | 137 | 04:00 | 122 | 13:00
| Fatullah | 138 | 04:00 | 128 | 12:00 | Ramganj | 132 | 19:00 | 119 | 11:00
| Fenchuganj | 136 | 06:00 | 132 | 12:00 | Rampur | 137 | 21:00 | 129 | 11:00
| Feni | 131 | 19:00 | 124 | 11:00 | Rampura | 139 | 02:00 | 128 | 12:00
| Ghatail | 130 | 00:00 | 124 | 16:00 | Rangamati | 137 | 19:00 | 130 | 11:00
| Ghorashal | 140 | 21:00 | 134 | 00:00 | Rangpur | 134 | 04:00 | 126 | 08:00
| Goalpara | 140 | 07:00 | 131 | 12:00 | Ruppur | 138 | 01:00 | 135 | 14:00
| Gollamari | 139 | 03:00 | 133 | 13:00 | Saidpur | 133 | 19:00 | 125 | 08:00
| Gopalganj | 136 | 05:00 | 130 | 12:00 | Satkhira | 138 | 05:00 | 131 | 12:00
| Gopalganj-400 | 135 | 06:00 | 129 | 11:00 | Satmasjid | 139 | 05:00 | 130 | 12:00
| Gulshan | 137 | 00:00 | 128 | 11:00 | Savar | 141 | 19:00 | 129 | 11:00
| Halishahar | 137 | 19:00 | 128 | 10:00 | SevenRings | 141 | 03:00 | 134 | 13:00
| Haripur | 132 | 06:00 | 125 | 11:00 | ShahCement | 131 | 04:00 | 124 | 11:00
| HaripurSBU | 132 | 05:00 | 125 | 10:00 | Shahjadpur | 143 | 23:00 | 137 | 12:00
| Hasnabad | 139 | 23:00 | 131 | 11:00 | Shahjibazar | 134 | 08:00 | 123 | 07:00
| Hathazari | 140 | 19:30 | 130 | 11:00 | Shahmirpur | 138 | 21:00 | 130 | 11:00
| Ishurdi | 139 | 00:00 | 136 | 12:00 | Shariatpur | 133 | 05:00 | 128 | 11:00
| Jaldhaka | 132 | 03:00 | 124 | 08:00 | Sherpur | 136 | 00:00 | 121 | 18:30
| Jamalpur | 138 | 00:00 | 127 | 18:30 | Shikalbaha | 127 | 19:30 | 117 | 10:00
| Jashore | 139 | 06:00 | 131 | 18:00 | Shikalbaha-230 | 138 | 19:00 | 129 | 11:00
| Jhenaidah | 140 | 06:00 | 130 | 07:00 | Shitalakhya | 137.5 | 05:00 | 128 | 12:00
| Jhenaidah-230 | 140 | 06:00 | 133 | 18:00 | Sholosohor | 136 | 18:00 | 129 | 11:00
| Joydebpur | 140 | 00:00 | 129 | 15:00 | Shyampur | 135 | 00:00 | 127 | 12:00
| Joypurhat | 136 | 19:00 | 131 | 05:00 | Shyampur-230 | 137 | 05:00 | 127 | 12:00
| Juldah | 138 | 20:00 | 130 | 10:00 | Siddhirganj | 133 | 05:00 | 124 | 11:00
| Kabirpur | 136 | 03:00 | 120 | 11:00 | Sirajganj | 138 | 22:00 | 133 | 16:00
| Kachua | 135 | 19:00 | 123 | 11:00 | Sonargaon | 132 | 02:00 | 122 | 11:00
| Kaliakoir | 137 | 19:00 | 124 | 11:00 | Sreemongol | 132 | 00:00 | 130 | 14:00
| Kallyanpur | 133 | 05:00 | 127 | 11:00 | Sreepur | 133 | 00:00 | 128 | 11:00
| Kalurghat | 138 | 20:00 | 129 | 11:00 | Srinagar | 139 | 05:00 | 130 | 12:00
| Kamrangirchar | 139 | 05:00 | 125 | 11:00 | SSM | 141 | 22:00 | 131 | 12:00
| Kaptai | 138 | 5:00 | 134 | 12:00 | Sunamganj | 127 | 06:00 | 123 | 12:00
| Kazla | 133 | 03:00 | 131 | 09:00 | Sylhet | 130 | 02:00 | 125 | 12:00
| Keranigonj | 140 | 06:00 | 131 | 12:00 | Sylhet-132 | 129 | 04:00 | 126 | 12:00
| Khagrachori | 136 | 19:00 | 130 | 11:00 | Tangail | 128 | 00:00 | 122 | 14:00
| Khulna | 137 | 04:00 | 133 | 11:00 | Thakurgaon | 137 | 19:00 | 121 | 08:00
| Khulna(S) | 141 | 06:00 | 134 | 12:00 | TK | 137 | 21:00 | 130 | 11:00
| Khulshi | 136 | 19:00 | 127 | 11:00 | Tongi | 138 | 19:00 | 130 | 12:00
| Kishoreganj | 133 | 04:00 | 127 | 15:00 | Ullahpara | 140 | 03:00 | 134 | 13:00
| Kodda | 136 | 18:30 | 116 | 11:00 | Ullon | 139 | 01:00 | 128 | 12:00
| KSRM | 138 | 21:00 | 130 | 11:00 | Uttara | 141 | 05:00 | 131 | 11:00
| Kulaura | 133 | 05:00 | 130 | 18:00 | UttaraNew | 141 | 04:00 | 131 | 11:00
| Kurigram | 132 | 06:00 | 124 | 07:00 | Zigatola | 140 | 06:00 | 131 | 12:00

## L-Curve
Date | 2024-11-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1254 | 5982 | 4680 | 10662 |  |  |  | QF-LDC-11
0:30 | 1044 | 5582 | 4562.5 | 10144.5 | Date: | 2024-11-09
1:00 | 834 | 5182 | 4445 | 9627
1:30 | 898 | 5069 | 4373 | 9442
2:00 | 962 | 4956 | 4301 | 9257
2:30 | 987 | 4819.5 | 4230.5 | 9050 | [5 empty] | Gen. at Eve. Peak | 12270 | 12270 MW (19:00 )
3:00 | 1012 | 4683 | 4160 | 8843 | [6 empty] | 19:00
3:30 | 1023 | 4590 | 4081.5 | 8671.5 | [5 empty] | Gen. at Day Peak | 10293 | 10293 MW (12:00 )
4:00 | 1034 | 4497 | 4003 | 8500 | [6 empty] | 12:00
4:30 | 1047 | 4481.5 | 3976 | 8457.5 | [5 empty] | Highest Generation | 12270
5:00 | 1060 | 4466 | 3949 | 8415 | [6 empty] | 19:00
5:30 | 1042 | 4461 | 3941.5 | 8402.5
6:00 | 1024 | 4456 | 3934 | 8390
6:30 | 980 | 4531.5 | 4026 | 8557.5
7:00 | 936 | 4607 | 4118 | 8725
7:30 | 916 | 4650.5 | 4166 | 8816.5
8:00 | 896 | 4694 | 4214 | 8908
8:30 | 973 | 4638.5 | 4310.5 | 8949
9:00 | 1050 | 4583 | 4407 | 8990
9:30 | 1288 | 4540.5 | 4475 | 9015.5
10:00 | 1526 | 4498 | 4543 | 9041
10:30 | 1531 | 4626 | 4675 | 9301
11:00 | 1536 | 4754 | 4807 | 9561
11:30 | 1505 | 4986 | 4941 | 9927
12:00 | 1474 | 5218 | 5075 | 10293
12:30 | 1389 | 5441 | 5080.5 | 10521.5
13:00 | 1304 | 5664 | 5086 | 10750
13:30 | 1233 | 5699 | 4942.5 | 10641.5
14:00 | 1162 | 5734 | 4799 | 10533
14:30 | 1273 | 5796.5 | 4824 | 10620.5
15:00 | 1384 | 5859 | 4849 | 10708
15:30 | 1305 | 5814.5 | 4764 | 10578.5
16:00 | 1226 | 5770 | 4679 | 10449
16:30 | 1196 | 5787.5 | 4825.5 | 10613
17:00 | 1166 | 5805 | 4972 | 10777
17:30 | 1060 | 6229 | 5292.5 | 11521.5
18:00 | 954 | 6653 | 5613 | 12266
18:30 | 889 | 6790 | 5478 | 12268
19:00 | 824 | 6927 | 5343 | 12270
19:30 | 890 | 6686 | 5260 | 11946
20:00 | 916 | 6570 | 5163 | 11733 |  |  |  | Executive Engineer
20:30 | 913 | 6507.5 | 5090.5 | 11598 |  |  |  | Network Operation Division
21:00 | 910 | 6445 | 5018 | 11463
21:30 | 958 | 6322.5 | 5013 | 11335.5
22:00 | 1006 | 6200 | 5008 | 11208 |  |  |  |  | Page 6 of 7
22:30 | 1020 | 6134.5 | 4970 | 11104.5
23:00 | 1034 | 6069 | 4932 | 11001
23:30 | 1144 | 6025.5 | 4806 | 10831.5
24:00 | 1254 | 5982 | 4680 | 10662
12270 MW (19:00 )
10293 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-11-09 |  | Energy |  | 245594133
[16 empty] | 2024-11-09 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3215 | 895 | 1742 | 0 | 1690 | 1880 | 132 | 0 | 532 | 60 | 516 | 0 | 0 | 0
0:30 | 3371.5 | 895.5 | 1722.5 | 0 | 1063 | 2110 | 131.5 | 0 | 274 | 59 | 517.5 | 0 | 0 | 0 |  |  | Date: | 44143
1:00 | 3528 | 896 | 1703 | 0 | 436 | 2340 | 131 | 0 | 16 | 58 | 519 | 0 | 0 | 0
1:30 | 3521.5 | 896 | 1689 | 0 | 324 | 2290.5 | 131 | 0 | 16 | 56 | 518 | 0 | 0 | 0 | [8 empty] | Total Energy | 245.5941 | 245.5941 | Total Energy Gen 245.594 MKWHr Energy Not Served 0.059 MKWHr Energy Requirement 245.653 MKWHr
2:00 | 3515 | 896 | 1675 | 0 | 212 | 2241 | 131 | 0 | 16 | 54 | 517 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0.05856 | 0.05856
2:30 | 3489 | 896 | 1663 | 0 | 163 | 2129 | 131 | 0 | 8 | 55 | 516 | 0 | 0 | 0 | [8 empty] | Energy Requirement | 245.6527 | 245.6527
3:00 | 3463 | 896 | 1651 | 0 | 114 | 2017 | 131 | 0 | 0 | 56 | 515 | 0 | 0 | 0
3:30 | 3409 | 895.5 | 1554 | 0 | 114 | 1999 | 131 | 0 | 0 | 54 | 515 | 0 | 0 | 0 | [7 empty] | Shortage
4:00 | 3355 | 895 | 1457 | 0 | 114 | 1981 | 131 | 0 | 0 | 52 | 515 | 0 | 0 | 0
4:30 | 3350 | 896 | 1455.5 | 0 | 109.5 | 1947.5 | 131 | 0 | 0 | 54 | 514 | 0 | 0 | 0
5:00 | 3345 | 897 | 1454 | 0 | 105 | 1914 | 131 | 0 | 0 | 56 | 513 | 0 | 0 | 0
5:30 | 3339 | 896.5 | 1452.5 | 0 | 105 | 1913 | 132.5 | 0 | 0 | 50 | 514 | 0 | 0 | 0
6:00 | 3333 | 896 | 1451 | 0 | 105 | 1912 | 134 | 0 | 0 | 44 | 515 | 0 | 0 | 0
6:30 | 3365 | 896 | 1494.5 | 0 | 138 | 1921 | 134 | 0 | 8 | 42 | 518.5 | 40.5 | 0 | 0 | [6 empty] | Coal
7:00 | 3397 | 896 | 1538 | 0 | 171 | 1930 | 134 | 0 | 16 | 40 | 522 | 81 | 0 | 0
7:30 | 3327 | 896 | 1466 | 0 | 275 | 1958.5 | 132.5 | 0 | 16 | 39 | 521.5 | 185 | 0 | 0 | [5 empty] | Oil
8:00 | 3257 | 896 | 1394 | 0 | 379 | 1987 | 131 | 0 | 16 | 38 | 521 | 289 | 0 | 0
8:30 | 3119.5 | 895.5 | 1393.5 | 0 | 379.5 | 2067 | 131.5 | 0 | 32 | 42 | 519 | 369.5 | 0 | 0
9:00 | 2982 | 895 | 1393 | 0 | 380 | 2147 | 132 | 0 | 48 | 46 | 517 | 450 | 0 | 0
9:30 | 2969 | 895.5 | 1411.5 | 0 | 324 | 2150.5 | 132.5 | 0 | 48 | 48 | 517 | 519.5 | 0 | 0
10:00 | 2956 | 896 | 1430 | 0 | 268 | 2154 | 133 | 0 | 48 | 50 | 517 | 589 | 0 | 0
10:30 | 2988 | 895.5 | 1543 | 0 | 282.5 | 2229 | 133 | 0 | 48 | 50 | 518.5 | 613.5 | 0 | 0
11:00 | 3020 | 895 | 1656 | 0 | 297 | 2304 | 133 | 0 | 48 | 50 | 520 | 638 | 0 | 0
11:30 | 3092.5 | 895 | 1693.5 | 0 | 471 | 2351 | 133.5 | 0 | 81.5 | 51 | 516 | 642 | 0 | 0
12:00 | 3165 | 895 | 1731 | 0 | 645 | 2398 | 134 | 0 | 115 | 52 | 512 | 646 | 0 | 0
12:30 | 3182 | 895 | 1696.5 | 0 | 866.5 | 2405 | 134 | 0 | 148 | 53 | 513.5 | 628 | 0 | 0
13:00 | 3199 | 895 | 1662 | 0 | 1088 | 2412 | 134 | 0 | 181 | 54 | 515 | 610 | 0 | 0
13:30 | 3199 | 895 | 1662 | 0 | 1088 | 2412 | 134 | 0 | 181 | 54 | 515 | 610 | 0 | 0
14:00 | 3199 | 895 | 1662 | 0 | 1088 | 2412 | 134 | 0 | 181 | 54 | 515 | 610 | 0 | 0
14:30 | 3173.5 | 895 | 1717 | 0 | 1217.5 | 2342.5 | 132.5 | 0 | 193 | 56 | 514 | 484.5 | 3.5 | 0
15:00 | 3148 | 895 | 1772 | 0 | 1347 | 2273 | 131 | 0 | 205 | 58 | 513 | 359 | 7 | 0
15:30 | 3150.5 | 895 | 1778 | 0 | 1311 | 2278 | 131.5 | 0 | 196.5 | 59 | 515.5 | 258.5 | 5 | 0
16:00 | 3153 | 895 | 1784 | 0 | 1275 | 2283 | 132 | 0 | 188 | 60 | 518 | 158 | 3 | 0
16:30 | 3151 | 894.5 | 1717.5 | 0 | 1408.5 | 2415 | 131.5 | 0 | 239.5 | 56 | 514 | 84 | 1.5 | 0
17:00 | 3149 | 894 | 1651 | 0 | 1542 | 2547 | 131 | 0 | 291 | 52 | 510 | 10 | 0 | 0
17:30 | 3217.5 | 894.5 | 1767 | 0 | 1915.5 | 2557 | 131 | 0 | 461.5 | 58 | 514.5 | 5 | 0 | 30.5
18:00 | 3286 | 895 | 1883 | 0 | 2289 | 2567 | 131 | 0 | 632 | 64 | 519 | 0 | 0 | 61
18:30 | 3223 | 895 | 1817.5 | 0 | 2421 | 2503.5 | 132.5 | 0 | 696.5 | 61 | 518 | 0 | 0 | 30.5
19:00 | 3160 | 895 | 1752 | 0 | 2553 | 2440 | 134 | 0 | 761 | 58 | 517 | 0 | 0 | 0
19:30 | 3194 | 895 | 1871 | 0 | 2152 | 2416 | 134 | 0 | 707 | 62 | 515 | 0 | 0 | 0
20:00 | 3123 | 895 | 1833 | 0 | 2081 | 2381 | 133 | 0 | 710 | 62 | 515 | 0 | 0 | 0
20:30 | 3142.5 | 895 | 1897.5 | 0 | 1959 | 2333.5 | 132.5 | 0 | 660 | 62 | 516 | 0 | 0 | 0
21:00 | 3162 | 895 | 1962 | 0 | 1837 | 2286 | 132 | 0 | 610 | 62 | 517 | 0 | 0 | 0
21:30 | 3181 | 895 | 1879 | 0 | 1786 | 2284 | 132 | 0 | 601.5 | 60 | 517 | 0 | 0 | 0
22:00 | 3200 | 895 | 1796 | 0 | 1735 | 2282 | 132 | 0 | 593 | 58 | 517 | 0 | 0 | 0
22:30 | 3183 | 895 | 1739 | 0 | 1697 | 2291 | 132 | 0 | 593.5 | 58 | 516 | 0 | 0 | 0
23:00 | 3166 | 895 | 1682 | 0 | 1659 | 2300 | 132 | 0 | 594 | 58 | 515 | 0 | 0 | 0
23:30 | 3190.5 | 895 | 1712 | 0 | 1674.5 | 2090 | 132 | 0 | 563 | 59 | 515.5 | 0 | 0 | 0 |  |  | Max Temp. in Dhaka |  | 32.2°C
24:00 | 3215 | 895 | 1742 | 0 | 1690 | 1880 | 132 | 0 | 532 | 60 | 516 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 245.594 MKWHr Energy Not Served 0.059 MKWHr Energy Requirement 245.653 MKWHr
Note on X13: Author:

## Generation
2024-11-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 131 | 131 | 131 | 131 | 131 | 134 | 134 | 131 | 132 | 133 | 133 | 134 | 134 | 131 | 131 | 132 | 131 | 131 |  | 134 | 134 | 133 | 132 | 132 | 132 | 132 | 3170225
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [12 empty] | 1 | 9 | 17 | 17 | 17 | 25 |  | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 156267
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5 | 11 |  | 17 | 20 |  |  |  | 6 |  | 0 | [9 empty] | 49545
6 | Sikalbaha 225MW CCPP (Gas) | 229 | 229 | 229 | 229 | 228 | 229 | 229 | 228 | 228 | 224 | 223 | 222 | 223 | 223 | 218 | 221 | 219 | 219 |  | 225 | 223 | 224 | 223 | 226 | 228 | 227 | 5272101
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [11 empty] | 34 | 34 | 34 | 34 | 17 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 406839
12 | Hathazari 100 MW peaking PP | [12 empty] | 32 | 38 | 38 | 38 | 38 | 79 |  | 79 | 79 | 79 | 71 | 71 | 71 | 71 | 640800
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 28 | 51 |  | 68 | 68 | 68 | 68 | 59 | 51 | 61 | 463345
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [12 empty] | 25 | 36 | 36 | 36 | 36 | 36 |  | 37 | 37 | 37 | 37 | 38 | 38 | 38 | 94738
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 280 | 280 | 280 | 335 | 327 | 280 | 331 | 328 | 335 | 335 |  | 335 | 280 | 280 | 280 | 280 | 280 | 335 | 7654194
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 80 |  | 195 | 95 | 95 |  |  |  | 1 | 539455
19 | Ashuganj 195 MW PP (APSCL-United) | 199 | 199 | 199 | 180 | 180 | 180 | 180 | 180 | 175 | 128 | 185 | 187 | 187 | 189 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 4533091
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 612 | 522 | 501 | 500 | 501 | 500 | 500 | 560 | 570 | 600 | 600 | 600 | 520 | 505 | 505 | 540 | 542 |  | 555 | 562 | 567 | 572 | 577 | 612 | 612 | 13369089
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 44 | 41 | 41 | 41 | 41 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1042344
33 | Ashuganj 225 MW CCPP
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 285 | 295 | 295 | 305 | 310 | 285 | 350 | 285 | 310 | 310 | 290 | 325 | 350 | 310 | 330 |  | 310 | 357 | 320 | 320 | 320 | 310 | 310 | 7874700
| Ashuganj 420 MW CCPP(East) | 330 | 330 | 330 | 330 | 330 | 330 | 395 | 400 | 300 | 300 | 393 | 395 | 395 | 350 | 350 | 350 | 393 | 393 |  | 350 | 350 | 350 | 350 | 393 | 393 | 393 | 8767800
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 70 | 70 | 80 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 70 | 70 | 70 | 50 | 1361960
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 305 | 287 | 286 | 287 | 284 | 272 | 236 | 228 | 156 | [16 empty] | 0 | 2372400
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | [13 empty] | 80 | 65 | 65 | 120 | 120 |  | 120 | 140 | 130 | 220 | 90 | 60 | 60 | 1047759
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 380 | 380 | 380 | 350 | 320 | 320 | 320 | 360 | 450 | 450 | 450 | 450 | 450 | 330 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9918500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 64 | 64 | 65 | 67 | 65 | 68 | 64 | 64 | 30 | 31 | 29 | 29 | 29 | 29 | 29 | 32 | 33 | 33 |  | 33 | 33 | 33 | 35 | 35 | 35 | 34 | 983040
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 24 | 36 | 46 | 50 | 50 | 48 | 41 | 29 | 12 | 0 | [9 empty] | 349780
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 714600
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 62 | 62 | 62 | 40 | 40 | 40 | 40 | 40 | 40 | 58 | 58 | 59 | 58 | 57 | 57 | 59 | 60 |  | 62 | 60 | 61 | 61 | 60 | 59 | 59 | 1308768
48 | Shahjibazar 86 MW PP (Shahjibazar) | 83 | 83 | 56 | 22 | 22 | 22 | 22 | 22 | 83 | 83 | 83 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 31 | 31 | 31 | 1547520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 209 | 209 | 209 | 209 | 209 | 211 | 213 | 214 | 212 | 207 | 206 | 206 | 206 | 206 | 204 | 205 | 206 | 204 |  | 207 | 207 | 207 | 208 | 208 | 207 | 207 | 4195350
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 54096
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 8 | 8 |  | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 298944
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 275 | 285 | 275 | 285 | 300 | 285 | 275 | 300 | 325 | 300 | 290 | 275 | 300 | 305 | 295 | 310 |  | 280 | 325 | 300 | 290 | 310 | 290 | 295 | 7163000
| Bibiyana South 400 MW | 350 | 350 | 350 | 350 | 316 | 316 | 316 | 316 | 316 | 370 | 370 | 350 | 350 | 350 | 365 | 385 | 346 | 360 |  | 346 | 390 | 346 | 358 | 356 | 346 | 341 | 8319500
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 55 | 55 | 55 | 35 | 17 | 17 | 35 | 234334
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 252000
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 58 | 54 | 56 | 52 | 56 | 44 | 40 | 38 | 46 | 50 | 50 | 52 | 54 | 58 | 58 | 60 | 52 | 64 |  | 58 | 62 | 62 | 62 | 58 | 58 | 60 | 1270080
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 10 | 6 | 5 | 5 | 8 | 8 | 6 | 4 | 2 | 7 | 7 |  | 2 | 8 | 16 | 20 | 27 | 23 | 30 | 485760
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 16 | 16 | 17 | 17 | 16 | 16 | 12 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 394150
69 | Summit Ashulia | 17 | 17 | 14 | 16 | 15 | 14 | 17 | 17 | 25 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 22 | 22 | 22 | 22 | 24 | 22 | 19 | 503400
70 | Summit Madhabdi | 11 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 6 | 15 | 18 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 398160
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 17 | 17 | 486720
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 0 | 16 | 25 | 25 | 25 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 |  | 24 | 24 | 33 | 33 | 33 | 33 | 33 | 522000
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [11 empty] | 17 | 17 | 17 | 17 | 17 | 25 | 106 |  | 70 | 34 | 34 | 34 | 34 | 34 | 56 | 470820
| Chowmuhani 113 MW | 37 | 44 | 28 | 28 | 29 | 29 | 29 | 29 | 29 | 13 | 9 | 9 | 9 | 8 | 9 | 9 | 27 | 30 |  | 31 | 38 | 38 | 38 | 39 | 39 | 14 | 615720
| Manikgonj 162MW PP(MPGL) | [7 empty] | 35 | 17 |  |  | 54 | 108 | 108 | 108 | 108 | 150 | 162 |  | 162 | 162 | 162 | 162 | 108 | 108 | 35 | 1581120
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 4 | 8 | 15 | 16 | 16 | 18 | 25 | 25 | 16 | 16 | 16 | 25 |  | 25 | 25 | 25 | 25 | 25 | 16 | 8 | 329760
79 | Kodda 150 MW PP | 16 | 16 |  |  |  |  | 16 | 16 | 48 | 48 | 48 | 64 | 64 | 64 | 64 | 64 | 82 | 149 |  | 132 | 132 | 132 | 82 | 82 | 82 | 82 | 1301280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [12 empty] | 1 | 16 | 16 | 16 | 25 | 52 |  | 52 | 25 | 25 | 25 | 25 | 25 | 34 | 299054
| Gazipur 100 MW PP | [8 empty] | 17 | 34 | 34 | 53 | 53 | 53 | 53 | 53 | 53 | 105 |  | 105 | 70 | 70 | 52 | 52 | 52 | 35 | 875520
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 27480
| Jodiac Power | 17 | [5 empty] | 1 | 17 | 17 |  | 0 | 24 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 565457
| Karnaphuli Power Ltd. | [11 empty] | 0 | 14 | 22 | 31 | 34 | 34 | 46 |  | 54 | 51 | 51 | 51 | 51 | 51 | 51 | 508506
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 8 |  | 13 | 13 | 13 |  |  |  | 0 | 31000
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 14 | [7 empty] | 7 | [7 empty] | 2 | 16 | [7 empty] | 0 | 41280
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 33 | 36 | 36 | 36 | 36 | 33 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 36 | 5 | 5 | 5 | 5 | 750888
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 24 | 35 | 35 | 35 | 35 | 43 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 728164
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 8 | 8 | 8 | 8 | 8 | [6 empty] | 8 |  |  | 0 | 50832
95 | Patenga 50MW PP (Baraka) | [7 empty] | 3 | 12 |  |  | 6 | 18 | 45 | 45 | 46 | 46 | 50 |  | 33 | 33 | 33 | 33 | 33 | 30 | 19 | 466080
96 | Chattogram 108 MW PP (ECPV) | [12 empty] | 13 | 18 | 20 | 19 | 19 | 24 |  | 45 | 51 | 51 | 49 | 50 | 51 | 51 | 418560
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 20 |  | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 243666
100 | Manikganj 55 MW PP (Northern) | [12 empty] | 2 | 48 | 55 | 55 | 55 | 55 |  | 55 | 17 | 17 | 17 | 17 | 17 | 35 | 429977
101 | Kushiara 163 MW CCPP (KP) | [22 empty] | 79 | 62 | 25 | 20 | 199473
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 14750
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [6 empty] | 13 | 17 | 17 | 17 | 19 | 35 | 35 | 35 | 35 | 54 | 54 |  | 54 | 54 | 35 | 17 | 17 | 17 | 17 | 529920
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 75 | 55 | 55 | 45 | 45 | 66 | 68 | 77 | 68 | 67 | 75 | 84 | 85 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 85 | 86 | 86 | 86 | 1819200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | [5 empty] | 1 | 17 | 17 | 34 | 34 | 39 | 52 | 52 | 35 | 34 | 36 | 72 |  | 112 | 100 | 99 | 76 | 70 | 70 | 67 | 954720
115 | Juldah 100 MW PP Unit-3 (Acorn) | [6 empty] | 2 | [6 empty] | 20 | 25 | 37 | 76 | 76 |  | 76 | 76 | 76 | 76 | 76 | 50 | 50 | 635520
116 | Chandpur 200 MW (Desh energy) | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 97 | 120 | 120 | 120 | 120 | 133 |  | 162 | 162 | 162 | 145 | 145 | 145 | 145 | 1910400
117 | Ashuganj 150 MW PP (Midland) | [7 empty] | 12 | 12 |  | 2 | 13 | 37 | 70 | 97 | 107 | 119 | 122 |  | 127 | 127 | 124 | 120 | 124 | 123 | 120 | 1366618
118 | Bibiyana-III 400 MW CCPP | 383 | 383 | 383 | 372 | 383 | 381 | 381 | 344 | 347 | 360 | 386 | 386 | 386 | 387 | 387 | 387 | 320 | 386 |  | 382 | 385 | 384 | 385 | 374 | 373 | 371 | 9424000
| Jamalpur 115 MW PP (United) | 27 | 24 | 8 | 8 | 8 | 8 | 13 | 45 | 37 | 45 | 45 | 45 | 45 | 47 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 57 | 57 | 57 | 58 | 999600
| Anwara 300 MW PP (United) | 68 | 30 |  |  |  |  | 30 | 48 | 15 |  | 15 | 48 | 150 | 150 | 156 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1221927
| Juldah unit-2 (Acorn) | [12 empty] | 10 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 135360
| Anlima Energy Ltd. | 17 | [6 empty] | 26 | 17 |  |  | 21 | 35 | 35 | 35 | 35 | 35 | 41 |  | 53 | 53 | 53 | 53 | 53 | 53 | 37 | 668673
| Bhairob 54.5 MW | 17 | [9 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 19 | 35 | 35 | 35 | 35 | 35 | 20 | 340920
| Spectra Solar Plant Ltd. | [6 empty] | 5 | 15 | 23 | 29 | 33 | 33 | 31 | 25 | 18 | 9 | 1 | [9 empty] | 220928
| Chandpur 115(Doreen) | 16 | 16 | [5 empty] | 7 | 16 |  |  | 20 | 50 | 50 | 50 | 50 | 50 | 74 |  | 92 | 50 | 50 | 50 | 50 | 50 | 60 | 799680
| Kanchan Purbachal Power Generation Ltd. | 18 | [5 empty] | 2 | 18 | 18 | 18 | 18 | 18 | 31 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 554040
| Mirsharai 150 MW (Oil) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 160 | 108 | 108 | 72 | 54 | 54 | 17 | 605527
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 3 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11040
| Sonagazi 75 MW Solar Plant | [6 empty] | 16 | 40 | 56 | 66 | 69 | 72 | 68 | 58 | 43 | 20 | 1 | [9 empty] | 498264
Matarbari 2*600 MW (CPGCL)
Meghnaghat (Reliance) 718MW CCPP
| Sreepur 150 MW | [25 empty] | 0 | 0
120
121 | Eastern Zone Total | 5182 | 4956 | 4683 | 4497 | 4466 | 4456 | 4607 | 4694 | 4583 | 4498 | 4754 | 5218 | 5664 | 5734 | 5859 | 5770 | 5805 | 6653 |  | 6927 | 6686 | 6570 | 6445 | 6200 | 6069 | 5982 | 130862078
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | [17 empty] | 27 |  | 40 | 35 | 36 | 36 | 37 | 37 | 37 | 207840
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [15 empty] | 1 | 17 | 17 |  | 17 | 17 |  |  |  |  | 0 | 56640
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 9 | 34 | 59 | 74 | 83 | 84 | 79 | 67 | 48 | 22 | 2 | [9 empty] | 569520
132 | Rampal 1320 MW (BIFPCL) | 367 | 367 | 376 | 370 | 372 | 370 | 372 | 371 | 370 | 368 | 366 | 367 | 368 | 370 | 368 | 378 | 606 | 624 |  | 624 | 625 | 624 | 624 | 626 | 628 | 386 | 10756360
133 | United Payra Power Ltd. | 17 | [6 empty] | 10 | 17 |  | 17 | 60 | 100 | 100 | 100 | 103 | 100 | 150 |  | 135 | 135 | 142 | 150 | 150 | 150 | 150 | 1608000
| Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 180 | 180 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5218260
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [14 empty] | 16 | 16 | 16 | 16 |  | 64 | 32 | 32 | 16 | 16 | 16 | 44 | 232320
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3918
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 127 | 127 | 127 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 125 | 123 | 80 | 83 | 83 | 123 | 123 |  | 123 | 123 | 123 | 123 | 127 | 127 | 127 | 2823000
141 | Bhola 33 MW PP (Venture) | 7 | 7 | 6 | 6 | 6 | 5 | 5 | 5 | 4 | 4 | 4 | 5 | 5 | 5 | 4 | 5 | 5 | 7 |  | 7 | 7 | 7 | 8 | 7 | 7 | 8 | 144594
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP | [16 empty] | 15 | 60 |  | 49 | 49 | 49 | 44 | 43 | 43 | 43 | 307328
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
147 | Bheramara HVDC | 896 | 896 | 896 | 895 | 897 | 896 | 896 | 896 | 895 | 896 | 895 | 895 | 895 | 895 | 895 | 895 | 894 | 895 |  | 895 | 895 | 895 | 895 | 895 | 895 | 895 | 21661090
148 | Bheramara 410 MW CCPP | 371 | 371 | 358 | 335 | 340 | 337 | 350 | 300 | 300 | 300 | 300 | 350 | 350 | 300 | 350 | 300 | 340 | 372 |  | 368 | 370 | 370 | 374 | 374 | 372 | 368 | 8337600
149 | Payra 1320 MW | 1160 | 1060 | 920 | 910 | 840 | 840 | 860 | 920 | 1020 | 1020 | 1140 | 1232 | 1244 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1060 | 1030 | 990 | 890 | 880 | 860 | 680 | 26630300
150
151 | Barapukuria TPP Unit-1 | 66 | 66 | 67 | 67 | 67 | 67 | 67 | 66 | 67 | 66 | 66 | 67 | 67 | 67 | 67 | 67 | 67 | 66 |  | 66 | 67 | 67 | 67 | 67 | 67 | 67 | 1555636
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 135 | 136 | 132 | 133 | 135 | 134 | 131 | 130 | 130 | 130 | 132 | 132 | 133 | 134 | 133 | 133 | 134 | 135 |  | 135 | 132 | 133 | 133 | 132 | 133 | 135 | 3281000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 9 | 16 | 16 | 16 | 25 | 48 |  | 48 | 45 | 48 | 46 | 46 | 46 | 46 | 392057
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 4 | 5 | 5 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 37620
157 | Sirajganj 68 MW Solar Park | [6 empty] | 5 | 25 | 39 | 49 | 53 | 54 | 51 | 45 | 33 | 10 | 0 | [9 empty] | 372752
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 214 | 214 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 184 | 214 | 214 | 210 | 214 | 214 | 214 |  | 160 | 160 | 160 | 160 | 160 | 160 | 190 | 4585364
Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 341 | 315 | 324 | 316 | 323 | 314 | 414 | 346 | 304 | 364 | 414 | 404 | 386 | 303 | 414 | 414 | 319 | 414 |  | 318 | 366 | 354 | 350 | 360 | 337 | 389 | 8709891
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | [16 empty] | 4 | 5 |  | 17 | 23 | 22 | 23 | 23 | 23 | 13 | 108970
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 8 | 8 | 8 | 8 | 5 | 5 | 131940
166 | Amnura 50 MW PP(Sinha)
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | [16 empty] | 3 | 15 |  | 40 | 40 | 40 | 40 | 40 | 38 | 38 | 196347
169 | Santahar 50 MW Peaking PP | [16 empty] | 12 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 15 | 177847
170 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
171 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 25 | 95 |  | 95 | 95 | 95 | 95 | 95 | 98 | 98 | 651408
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [16 empty] | 15 | 77 |  | 50 | 50 | 50 | 50 | 50 | 35 | 40 | 448992
173 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 25 | 95 |  | 50 | 50 | 50 | 50 | 50 | 35 | 70 | 460800
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 65 |  | 89 | 49 | 49 | 14 |  |  | 33 | 243638
178 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 | 2 | 5 | 6 | 6 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 39488
| Energypac Power Venture Thakurgaon Ltd. | [11 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 113 |  | 115 | 92 | 54 | 55 | 55 | 55 | 67 | 718848
| Intraco Solar 30 MW | [6 empty] | 3 | 13 | 25 | 32 | 36 | 37 | 34 | 29 | 18 | 9 | 1 | [9 empty] | 240110
178 | Adani Power Jharkhanda Ltd | 519 | 517 | 515 | 515 | 513 | 515 | 522 | 521 | 517 | 517 | 520 | 512 | 515 | 515 | 513 | 518 | 510 | 519 |  | 517 | 515 | 515 | 517 | 517 | 515 | 516 | 11907273
| Teesta Solar Limited | [6 empty] | 20 | 79 | 131 | 169 | 186 | 189 | 177 | 150 | 105 | 50 | 3 | [9 empty] | 1259310