## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month: August 2024
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2024-08-01 |  | 2024-07-01 |  | 2023-08-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 14612 | 2024-08-31 | 15223 | 2024-07-28 | 14889 | 2023-08-30 | 16477 | 2024-04-30
|  |  | 19:30 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 9444 | 2024-08-03 | 10542 | 2024-07-23 | 8071 | 2023-08-01 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 14612 | 2024-08-31 | 15223 | 2024-07-28 | 14889 | 2023-08-30 | 16477 | 2024-04-30
|  |  | 19:30 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 13449 | 2024-08-15 | 13868 | 2024-07-28 | 13382 | 2023-08-29 | 14488 | 2024-05-16
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 15530 | 2024-08-31 | 16000 | 2024-07-30 | 14889 | 2023-08-30 | 17200 | 2024-04-29
|  |  | 19:30 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 13511.7742 |  | 14431 |  | 13968.6452 |  | - | -
7 | Average Generation (MW) at Day Peak | 12004.0645 |  | 12793.5806 |  | 12169.7097 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 927 | 2024-08-07 | 970 | 2024-07-06 | 936 | 2023-08-29 | 970 | 2024-07-06
|  |  | 13:00 |  | 14:30 |  | 4:30 |  | 14:30
9 | Maximum Power Import from Tripura, India (MW) | 108 | 2024-08-14 | 106 | 2024-07-18 | 170 | 2023-08-05 | 194 | 12/06/19
|  |  | 16:00 |  | 15:00 |  | 19:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1272 | 2024-08-15 | 1341 | 2024-07-10 | 634 | 2023-08-19 | 4395 | 04/10/2022
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14198 | 2024-08-15 | 14096 | 2024-07-10 | 14036 | 45157 | 14965 | 2024-05-16
|  |  | 21:00 | - | 21:00 | - | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2024-08-02 | 0 | 2024-07-05 | 0 | 45166 | - | -
|  |  | 21:00 |  | 21:00 |  | 19:30 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 11816 | 2024-08-02 | 13229 | 2024-07-05 | 13253 | 2023-08-08 | - | -
|  |  | 21:00 |  | 21:00 |  | 19:30 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 871 | 2024-08-14 | 1795 | 2024-07-11 | 1042 | 45155 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 13188 | 2024-08-14 | 12870 | 2024-07-11 | 12309 | 45155 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2024-08-02 | 0 | 2024-07-05 | 0 | 45146 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 10003 | 2024-08-02 | 11167 | 2024-07-05 | 10921 | 45146 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 26 |  | 29 |  | 26 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 22 |  | 17 |  | 22 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1248.1003 |  | 1553.74 |  | 2157.9023 |  | - | -
21 | Station Use of BPDB (MKWH) | 43.702 |  | 63.1342 |  | 186.3465 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1204.3983 |  | 1490.6058 |  | 1971.5558 |  | - | -
23 | Net Generation of IPP (MKWH) | 3344.5118 |  | 3471.59 |  | 2984.36 |  | - | -
23b | Net Generation by Generation Companies | 2761.3843 |  | 2904.26 |  | 2881.7466 |  | - | -
24 | Net Generation of REB (MKWH) | 80.6642 |  | 72.09 |  | 132.336 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 143.5199 |  | 224.06 |  | 273.6692 |  | - | -
25 | Total Net Generation (MKHWh) (Excluding Import) | 7534.4785 |  | 8162.6058 |  | 8243.6677 |  | - | -
26 | Energy Generation by Gas (MKWH) | 3620.1589 |  | 3966.4454 |  | 4451.0325 |  | - | -
27 | Energy Generation by Diesel (MKWH) | 21.9232 |  | 18.1087 |  | 171.571 |  | - | -
28 | Energy Generation by Furnace Oil (MKWH) | 1233.5983 |  | 1371.0357 |  | 1284.8303 |  | - | -
29 | Energy Generation by Hydro (MKWH) | 154.5809 |  | 138.7193 |  | 128.7252 |  | - | -
30 | Energy Generation by Solar (MKWH) | 83.4784 |  | 93.2904 |  | 59.1982 |  | - | -
30b | Energy Generation by Wind (MKWH) | 8.4058 |  | 16.4786 |  | 5.9338 |  | - | -
31 | Energy Generation by Coal (MKWH) | 2456.035 |  | 2621.6684 |  | 2328.2862 |  | - | -
32 | Enegry Import from India (MKWH) | 1377.1055 |  | 1606.12 |  | 758.441 |  | - | -
33 | Monthly Load Factor (%) | 82.3753 |  | 81.3292 |  | 81.9186 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: August 2024
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 14612 | 2024-08-31 | 19:30
Generation Period
| Dhaka | MW | 5117.85
| Chattogram | MW | 1278.7
| Cumilla | MW | 1222
| Mymensingh | MW | 982
| Sylhet | MW | 576
a) | Total supply in East zone | MW | 9176.55
| Khulna | MW | 1794.8
| Barisal | MW | 457
| Rajshahi | MW | 1555.8
| Rangpur | MW | 884
b) | Total supply in West zone | MW | 4691.6
c) | Total supply in both zone ( a+b) | MW | 13868.15
Ref: | 27.21.0000.603.16.087.20.855 | Date: 17/09/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:August 2024
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 108 | 2024-08-21 | 21:00
| b) Ishurdi end | MW | 348 | 2024-08-03 | 12:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 914 | 2024-08-04 | 10:00
| b) Ishurdi end | MW | 38 | 2024-08-21 | 21:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.096572
| b) Ishurdi end | MKWH | 123.2064
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 119.5102
| b) Ishurdi end | MKWH | 0.093759
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 350 | 2024-08-21 | 21:00
| b)Serajganj end | MW | 700 | 2024-08-04 | 10:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 280 | 2024-08-04 | 10:00
| b)Sirajganj end | MW | 26 | 2024-08-21 | 21:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.0248
| b)Sirajganj end | MKWH | 240.764
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 233.289
| b)Sirajganj end | MKWH | 0.0026
30 | Transmission loss of EWI /NO-2 | % | 3.10'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2690 | 2024-08-15 | 14:00
|  | MW | 1744
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2603 | 2024-08-15 | 14:00
|  | MW | 1705
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 36548 | 2024-08-15 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 36498 | 2024-08-15
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 853.385
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 851.324
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.241
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur 132/33kV Grid Sub-Station | Transformer- 03 HT | 2024-08-01 19:26 | 2024-08-01 21:02 | 1:36 | E/O | Due to emergency maint.work at 33 kV | 80 | 128 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-08-02 02:03 | 2024-08-02 02:09 | 0:06 | T | Tripped showing 86.1 & 86.2 Master relay | 45 | 4.5 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-08-02 10:22 | 2024-08-02 11:32 | 1:10 | E/O | Red hot maintenance at 33 kV | 40 | 46.6667 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 HT | 2024-08-02 10:22 | 2024-08-02 11:32 | 1:10 | E/O | Red hot maintenance at 33 kV | 40 | 46.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2024-08-03 05:23 | 2024-08-03 05:23 | 0:00 | T | Tripped showing O/C relays | 40 | 0 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr- 04 HT | 2024-08-03 23:10 | 2024-08-04 02:17 | 3:07 | E/O | Due to emergency maint.work at 33 kV | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr- 04 HT | 2024-08-04 23:10 | 2024-08-05 02:17 | 3:07 | E/O | Due to emergency maint.work at 33 kV | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-08-13 14:47 | 2024-08-13 14:54 | 0:07 | T | Tripped showing IDMT Relay | 71 | 8.2833 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-08-14 19:05 | 2024-08-14 19:12 | 0:07 | T | Tripped showing Master relay (Over current) relays. | 72 | 8.4 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | T-4 HT | 2024-08-16 18:05 | 2024-08-16 19:12 | 1:07 | T | Tripped showing No relays Due to T4 Transformer Bay CB Faulty | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | T-01 LT | 2024-08-19 18:25 | 2024-08-19 18:35 | 0:10 | T | Tripped showing Opened by NLDC relays | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | T-01 LT | 2024-08-22 22:38 | 2024-08-22 23:38 | 1:00 | E/O | Due to Red Hot remove. | 20 | 20 | Power interruption
New Tongi 132/33kV Grid Sub-Station | T-02 LT | 2024-08-26 07:50 | 2024-08-26 08:31 | 0:41 | T | Tripped showing micon, P122 relays Due to 33kv L-37(tongi-2 ckkt) over current, Earth foult. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2024-08-30 00:34 | 2024-08-30 00:34 | 0:00 | T | Tripped showing Differential 87T, B Phase relays | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer HT | 2024-08-30 08:16 | 2024-08-30 08:46 | 0:30 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2024-08-30 14:40 | 2024-08-30 15:02 | 0:22 | T | Tripped showing Over current relays Due to 33kV Shambuganj - 1 & 2 feeders fault | 182 | 66.7333 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer HT | 2024-08-31 08:16 | 2024-08-31 08:46 | 0:30 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2024-08-31 14:40 | 2024-08-31 15:02 | 0:22 | T | Tripped showing Over current relays Due to 33kV Shambuganj - 1 & 2 feeders fault | 182 | 66.7333 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2024-08-31 15:02 | 2024-08-31 15:02 | 0:00 | T | Tripped showing Over current relays Due to 33kV Shambuganj - 1 & 2 feeders fault | 0 | 0 | No interruption
|  |  | Total : | 15:12 |  | Unserved Energy: |  | 395.9833
Dhaka (South) Grid Circle :
Madanganj 132/33kV Grid Sub-Station | GT2 HT | 2024-08-05 15:53 | 2024-08-05 19:40 | 3:47 | T | Tripped showing Backup protection relays.at PBS feeder | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2024-08-06 15:58 | 2024-08-06 16:24 | 0:26 | T | Tripped showing o/c operated, 86.1 relay | 45 | 19.5 | Power interruption
Hasnabad 132/33kV Grid Sub-Station | 404 T-1 LT | 2024-08-09 02:12 | 2024-08-09 03:14 | 1:02 | T | Tripped showing Trip relay MVAJM relays at 33 kV side | 14 | 14.4667 | Power interruption
Hasnabad 132/33kV Grid Sub-Station | 424 T-5 LT | 2024-08-09 02:12 | 2024-08-09 03:14 | 1:02 | T | Tripped showing Trip relay MVAJM relays at 33 kV side | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | T-01 LT | 2024-08-14 09:35 | 2024-08-14 11:01 | 1:26 | E/O | Due to emergency maint.work | 40 | 57.3333 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | Tr-02 LT | 2024-08-15 01:03 | 2024-08-15 01:15 | 0:12 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Transformer-1 (405T1) LT | 2024-08-21 07:31 | 2024-08-21 07:31 | 0:00 | T | Due to Red hot in Red and Yellow Phase. | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Tr-02 LT | 2024-08-22 07:02 | 2024-08-22 10:02 | 3:00 | E/O | Due to Due to Red Hot 33 kv bus-2 | 42 | 126 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Tr-01 LT | 2024-08-22 07:02 | 2024-08-22 10:02 | 3:00 | E/O | Due to Due to Red Hot 33 kv bus-2 | 12 | 36 | Power interruption
Bhulta 132/33kV Grid Sub-Station | GT2 HT | 2024-08-24 23:45 | 2024-08-25 07:08 | 7:23 | E/O | Due to Due to Red Hot | 30 | 221.5 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-08-26 09:26 | 2024-08-26 15:52 | 6:26 | E/O | Due to Due to Red Hot | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-08-27 13:25 | 2024-08-27 14:03 | 0:38 | E/O | Due to Due to Red Hot | 0 | 0 | No interruption
Shyampur 132/33kV Grid Sub-Station | GT3 HT | 2024-08-28 05:59 | 2024-08-28 07:20 | 1:21 | E/O | Due to Due to Red Hot | 0 | 0 | No interruption
|  |  | Total : | 29:43 |  | Unserved Energy: |  | 474.8
Chattogram Grid Circle :
Dohazari 132/33kV Grid Sub-Station | T-02 LT | 2024-08-03 23:42 | 2024-08-04 00:41 | 0:59 | E/O | Due to emergency maint.work at 33 kV | 62 | 60.9667 | Power interruption
Dohazari 132/33kV Grid Sub-Station | T-02 LT | 2024-08-04 23:42 | 2024-08-05 00:41 | 0:59 | E/O | Due to emergency maint.work at 33 kV | 62 | 60.9667 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-08-11 06:53 | 2024-08-11 07:25 | 0:32 | T | Tripped showing REF-615,REF-670 relays Due to PDB | 13 | 6.9333 | Power interruption
Hathazari 230/132kV Grid Sub-Station | T-01 HT | 2024-08-12 16:10 | 2024-08-12 20:45 | 4:35 | E/O | Due to emergency maint.work at 33 kV | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) HT | 2024-08-13 09:02 | 2024-08-13 14:11 | 5:09 | E/O | Due to emergency maint.work at 33 kV | 0 | 0 | No interruption
Hathazari 230/132kV Grid Sub-Station | T-01 LT | 2024-08-13 15:00 | 2024-08-13 17:50 | 2:50 | E/O | Due to cable termination | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | T-02 LT | 2024-08-17 13:12 | 2024-08-17 13:25 | 0:13 | T | Tripped showing O/C & Lockout Relay | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | T-02 LT | 2024-08-18 07:05 | 2024-08-18 09:24 | 2:19 | T | Tripped showing Differential relay | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2024-08-19 16:33 | 2024-08-19 17:39 | 1:06 | E/O | Due to emergency maint.work at 33 kV | 5 | 5.5 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | 415T-T2 HT | 2024-08-20 06:40 | 2024-08-20 12:26 | 5:46 | E/O | Due to Buchloz relay maintenance | 35 | 201.8333 | Power interruption
Hathazari 230/132kV Grid Sub-Station | T-01 HT | 2024-08-21 01:00 | 2024-08-21 01:58 | 0:58 | T | Tripped showing MiCOM relays. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | T-02 LT | 2024-08-21 08:23 | 2024-08-21 08:52 | 0:29 | T | Tripped showing Lockout relays Due to Lohagara PBS 33 kV Feeder Fault(O/C,E/F) | 50 | 24.1667 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) LT | 2024-08-22 15:54 | 2024-08-22 16:36 | 0:42 | E/O | Tripped showing Over current relays Due to 33 kv auxiliary transformer bus fault. | 25 | 17.5 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) LT | 2024-08-22 19:09 | 2024-08-22 19:30 | 0:21 | E/O | Tripped showing Over current relays Due to 33 kv auxiliary transformer bus fault. | 15 | 5.25 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) LT | 2024-08-24 22:43 | 2024-08-24 23:35 | 0:52 | E/O | Due to for bus coupler maintenance by BPDB. | 20 | 17.3333 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) LT | 2024-08-24 22:45 | 2024-08-24 23:25 | 0:40 | E/O | Due to for bus coupler maintenance by BPDB. | 10 | 6.6667 | Power interruption
Dohazari 132/33kV Grid Sub-Station | T-02 LT | 2024-08-25 04:54 | 2024-08-25 05:31 | 0:37 | T | Tripped showing 50/51 OC ,B &C Phase relays Due to Due to 33 kV | 50 | 30.8333 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) LT | 2024-08-29 11:34 | 2024-08-29 13:29 | 1:55 | E/O | Due to Oil leakage maintenance. | 0 | 0 | No interruption
|  |  | Total : | 31:02 |  | Unserved Energy: |  | 437.95
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2024-08-01 17:48 | 2024-08-01 18:48 | 1:00 | E/O | Maintenance work by BPDB | 20 | 20 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | 132/33kv T-2 HT | 2024-08-01 20:55 | 2024-08-01 22:41 | 1:46 | E/O | 33 KV T-3 Bus red hot maintenance. | 30 | 53 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2024-08-02 07:58 | 2024-08-02 08:55 | 0:57 | E/O | Due to emergency maint.work of PBS | 23 | 21.85 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-08-08 20:02 | 2024-08-08 21:41 | 1:39 | T | Tripped showing RET 670 ,RET650 relays | 6 | 9.9 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 LT | 2024-08-08 20:02 | 2024-08-08 20:12 | 0:10 | T | Tripped showing REF630 relays | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | T-2 LT | 2024-08-13 04:47 | 2024-08-13 04:58 | 0:11 | T | Tripped showing ABB REF 630 relays | 27 | 4.95 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-08-13 23:17 | 2024-08-13 23:22 | 0:05 | T | Tripped showing OC/EF, abc Inst. fault relays at 33kV | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-08-13 23:36 | 2024-08-13 23:37 | 0:01 | T | Tripped showing OC/EF, abc Inst. fault relays at 33kV | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T LT | 2024-08-19 13:04 | 2024-08-19 13:04 | 0:00 | T | Tripped showing 33 KV TCS & Lockout relay | 18 | 0 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 402T LT | 2024-08-19 13:04 | 2024-08-19 13:24 | 0:20 | T | Tripped showing O/C and E/F relays | 18 | 6 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-08-19 17:28 | 2024-08-19 17:30 | 0:02 | T | Tripped showing OC/EF, abc inst. fault relays | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | TR-02 HT | 2024-08-20 00:45 | 2024-08-20 00:45 | 0:00 | T | Tripped showing REC650 and RET670 relays | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | TR-02 HT | 2024-08-29 04:51 | 2024-08-29 11:20 | 6:29 | T | Tripped showing REC 650 relays. | 19 | 123.1833 | Power interruption
Cumilla(N) 230/132kV Grid Sub-Station | 230KV ATR-03 LT | 2024-08-30 03:15 | 2024-08-30 05:54 | 2:39 | T | Tripped showing General Trip | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2024-08-31 06:52 | 2024-08-31 07:27 | 0:35 | T | Tripped showing O/C relay | 20 | 11.6667 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T2 LT | 2024-08-30 06:52 | 2024-08-30 06:56 | 0:04 | T | Tripped showing O/C relay | 31 | 2.0667 | Power interruption
|  |  | Total : | 15:58 |  | Unserved Energy: |  | 252.6167
Khulna Grid Circle :
Barguna 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) LT | 2024-08-13 20:27 | 2024-08-13 20:39 | 0:12 | T | Tripped showing Over current relay | 14 | 2.8 | Power interruption
Mongla 132/33kV Grid Sub-Station | T1 LT | 2024-08-19 10:17 | 2024-08-19 10:50 | 0:33 | T | Tripped showing O/C relay | 12 | 6.6 | Power interruption
Mongla 132/33kV Grid Sub-Station | T1 LT | 2024-08-19 13:00 | 2024-08-19 15:24 | 2:24 | E/O | Due to 33 KV Bus Section loop breakdown due to thundering. | 0.5 | 1.2 | Power interruption
Mongla 132/33kV Grid Sub-Station | T1 LT | 2024-08-26 09:44 | 2024-08-26 10:42 | 0:58 | T | Tripped showing Ins. Over current phase A relay at 33kV | 6 | 5.8 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) HT | 2024-08-27 16:35 | 2024-08-27 22:39 | 6:04 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2024-08-27 21:16 | 2024-08-28 13:58 | 16:42 | E/O | Due to Red hot at 33 kV bust section DS that's why shutdown by PBS | 0 | 0 | No interruption
|  |  | Total : | 26:53 |  | Unserved Energy: |  | 16.4
HVDC Grid Circle :
Jhenaidah 132/33kV Grid Sub-Station | T-1 LT | 2024-08-03 10:55 | 2024-08-03 11:08 | 0:13 | T | Tripped showing Over current, ABC trip relays Due to WZPDCL | 65 | 14.0833 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | T-1 LT | 2024-08-04 10:55 | 2024-08-04 11:08 | 0:13 | T | Tripped showing Over current, ABC trip relays Due to WZPDCL | 65 | 14.0833 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-3 LT | 2024-08-04 11:17 | 2024-08-04 11:36 | 0:19 | T | Due to 33 kV feeder fault | 38 | 12.0333 | Power interruption
BIPTC | 10CF15 | 2024-08-10 09:56 | 2024-08-10 11:09 | 1:13 | T | Tripped showing 60/61 relays | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-08-12 08:51 | 2024-08-12 09:07 | 0:16 | T | Due to 33 kV feeder fault | 16 | 4.2667 | Power interruption
BIPTC | 20D10A 20MVA HT | 2024-08-15 16:59 | 2024-08-15 19:12 | 2:13 | T | Due to To work on tap changer motor. | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | T-3 LT | 2024-08-18 06:10 | 2024-08-18 06:51 | 0:41 | T | Tripped showing 50N/51N OC, C-Phase. Relays at 33 kV | 48 | 32.8 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-2 LT | 2024-08-18 07:30 | 2024-08-18 10:50 | 3:20 | T | Tripped showing O/C DMT-1 relays at 33 kV | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-2 LT | 2024-08-18 08:39 | 2024-08-18 10:49 | 2:10 | E/O | Due to T-2 33kv R phase DS fingur burn | 40 | 86.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-2 LT | 2024-08-18 11:09 | 2024-08-18 11:52 | 0:43 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-3 HT | 2024-08-20 21:34 | 2024-08-20 23:54 | 2:20 | T | Tripped showing SIEMENS relays Due to Rain,Thunders | 24 | 56 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2024-08-26 04:50 | 2024-08-26 11:27 | 6:37 | T | Tripped showing under frequency. relays | 10 | 66.1667 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-2 HT | 2024-08-26 12:37 | 2024-08-26 17:34 | 4:57 | T | Tripped showing 51N,50/51 Trip(87T2) relays | 35 | 173.25 | Power interruption
Ishurdi 230/132kV Grid Sub-Station | T-01 HT | 2024-08-28 12:56 | 2024-08-28 13:29 | 0:33 | T | Tripped showing earth fault stage 2 relays. | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | T-02 LT | 2024-08-28 12:56 | 2024-08-28 13:28 | 0:32 | T | Tripped showing earth fault stage 2 relays. | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | T-03 LT | 2024-08-28 12:56 | 2024-08-28 13:33 | 0:37 | T | Tripped showing earth fault stage 2 relays. | 0 | 0 | No interruption
BIPTC | 20DF24 | 2024-08-28 13:01 | 2024-08-28 17:28 | 4:27 | T | Due to Tripped by Impedence 21R | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | T-2 LT | 2024-08-29 21:39 | 2024-08-29 22:27 | 0:48 | E/O | Due to fired on 33 kv incomer CT. | 40 | 32 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | T-1 LT | 2024-08-29 21:39 | 2024-08-29 21:39 | 0:00 | T | Tripped showing siemens 7UT86 relays. | 42 | 0 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | T-2 HT | 2024-08-29 21:45 | 2024-08-29 22:27 | 0:42 | E/O | Due to 33 kV incmer ct fired. | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | T-1 HT | 2024-08-29 22:27 | 2024-08-30 21:54 | 23:27 | T | Tripped showing siemens 7UT85 relays. | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-08-30 07:02 | 2024-08-30 10:13 | 3:11 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 59:32 |  | Unserved Energy: |  | 491.35
Bogura Grid Circle:
Kurigram 230/132/33kV Grid Sub-Station | Capacitor Bank | 2024-08-01 12:58 | 2024-08-01 19:19 | 6:21 | T | Tripped showing Micom p-127 relays Due to Overvaltage | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | T-1 LT | 2024-08-01 15:15 | 2024-08-01 15:29 | 0:14 | T | Tripped showing Micon P142 relays | 0 | 0 | No interruption
Barapukuria 230/132/kV Grid Sub-Station | T-06, 723T LT | 2024-08-02 07:50 | 2024-08-02 09:51 | 2:01 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2024-08-12 16:39 | 2024-08-12 17:23 | 0:44 | T | Tripped showing Inst. E/F relays Due to NESCO 33kv feeder | 0 | 0 | No interruption
Bhangura 132/33kV Grid Sub-Station | T-1 LT | 2024-08-13 07:05 | 2024-08-13 07:05 | 0:00 | T | Due to 33kV feeder fault. | 26 | 0 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2024-08-13 08:20 | 2024-08-13 09:44 | 1:24 | T | Due to 33kV feeder fault. | 16 | 22.4 | Power interruption
Bhangura 132/33kV Grid Sub-Station | 403 Tr-1 HT | 2024-08-13 08:20 | 2024-08-13 09:11 | 0:51 | E/O | Due to emergency maint.work | 26 | 22.1 | Power interruption
Barapukuria 230/132/kV Grid Sub-Station | T-3 LT | 2024-08-14 23:27 | 2024-08-14 23:27 | 0:00 | T | Tripped showing RET 521 relays. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Bus coupler | 2024-08-17 01:45 | 2024-08-17 02:45 | 1:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Bus -B | 2024-08-17 01:50 | 2024-08-17 01:50 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | T-1 LT | 2024-08-17 07:40 | 2024-08-17 09:08 | 1:28 | E/O | 33kv Bus1Red Hot | 48 | 70.4 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | T-2 LT | 2024-08-17 07:41 | 2024-08-17 09:09 | 1:28 | E/O | 33kv Bus1Red Hot | 48 | 70.4 | Power interruption
Bhangura 132/33kV Grid Sub-Station | 403 Tr-1 HT | 2024-08-17 21:20 | 2024-08-17 22:04 | 0:44 | E/O | Due 33KV Red Hot maint.work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-3 HT | 2024-08-17 21:54 | 2024-08-17 23:37 | 1:43 | E/O | Due 33KV Red Hot maint.work | 0 | 0 | No interruption
Barapukuria 230/132/kV Grid Sub-Station | T-4 LT | 2024-08-18 16:42 | 2024-08-18 18:05 | 1:23 | E/O | Due 33KV Red Hot maint.work | 40 | 55.3333 | Power interruption
Palshabari 132/33kV Grid Sub-Station | TR2-404T LT | 2024-08-19 21:30 | 2024-08-19 23:20 | 1:50 | E/O | Due to 33 kV BUS RED HOT | 72 | 132 | Power interruption
Barapukuria 230/132/kV Grid Sub-Station | T-4 LT | 2024-08-20 12:50 | 2024-08-20 13:14 | 0:24 | T | Tripped showing Over Current relay | 37 | 14.8 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2024-08-22 07:39 | 2024-08-22 09:55 | 2:16 | T | Due to Red hot maintenance of T-3 33kv CT B-phase | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | T-2 LT | 2024-08-22 12:24 | 2024-08-22 14:45 | 2:21 | E/O | Due to emergency maint.work at 33kV | 25 | 58.75 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | T-4 HT | 2024-08-22 13:41 | 2024-08-22 16:39 | 2:58 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 HT | 2024-08-25 20:05 | 2024-08-25 21:26 | 1:21 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Barapukuria 230/132/kV Grid Sub-Station | T-5, 424T LT | 2024-08-25 21:02 | 2024-08-25 21:55 | 0:53 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-2 HT | 2024-08-26 19:02 | 2024-08-26 20:31 | 1:29 | E/O | Due to emergency maint.work at 33kV | 12 | 17.8 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2024-08-26 23:10 | 2024-08-27 01:25 | 2:15 | E/O | Due to Red hot maintenance of T-1 33KV CB R-phase. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2024-08-27 01:35 | 2024-08-27 02:41 | 1:06 | E/O | Due to Red hot maintenance of T-3 33KV CB R-phase. | 0 | 0 | No interruption
Barapukuria 230/132/kV Grid Sub-Station | T-4, 444T LT | 2024-08-27 09:17 | 2024-08-27 11:13 | 1:56 | E/O | Due to emergency maint.work at 33kV | 45 | 87 | Power interruption
Bogura 132/33kV Grid Sub-Station | T-3 LT | 2024-08-29 07:55 | 2024-08-29 09:46 | 1:51 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2024-08-29 09:08 | 2024-08-29 09:20 | 0:12 | E/O | Due to PT Connection Test by NESCO. | 15 | 3 | Power interruption
Palshbari 132/33kV Grid Sub-Station | TR2-404T HT | 2024-08-30 01:33 | 2024-08-30 02:07 | 0:34 | E/O | Due to 33 KV Bus Coupler red hot. | 65 | 36.8333 | Power interruption
Palshbari 132/33kV Grid Sub-Station | TR2-404T HT | 2024-08-30 15:55 | 2024-08-30 17:32 | 1:37 | E/O | Due to 33 KV Bus Coupler red hot. | 35 | 56.5833 | Power interruption
Palshbari 132/33kV Grid Sub-Station | TR2-404T LT | 2024-08-31 15:55 | 2024-08-31 17:32 | 1:37 | E/O | Due to 33 KV Bus Coupler red hot. | 35 | 56.5833 | Power interruption
|  |  | Total : | 44:01 |  | Unserved Energy: |  | 703.9833
Others :Nil
[7 empty] | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 222:21 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: August 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur 132/33kV Grid Sub-Station | Tongi-2 | 2024-08-08 10:27 | 2024-08-08 11:06 | 0:39 | T | Tripped showing Distance relay | 150 | 97.5 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 2024-08-08 10:27 | 2024-08-08 10:40 | 0:13 | T | Tripped showing OC, R,Y,B-Phase relays | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2024-08-15 18:54 | 2024-08-15 18:54 | 0:00 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2024-08-16 02:35 | 2024-08-16 02:48 | 0:13 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2024-08-16 03:10 | 2024-08-16 03:48 | 0:38 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | 230 kV Tongi-Tongi 80 MW PS | 2024-08-17 12:24 | 2024-08-17 15:33 | 3:09 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2024-08-18 13:08 | 2024-08-18 14:06 | 0:58 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Kallyanpur132/33kV Grid Sub-Station | Lalbagh 132 kV circuit-1 | 2024-08-20 06:30 | 2024-08-20 06:35 | 0:05 | T | Tripped showing operating 86B relay. | 0 | 0 | No interruption
Aminbazar 400/230kV Grid Sub-Station | Meghnaghat 400kV Ckt-2 | 2024-08-21 00:59 | 2024-08-21 01:32 | 0:33 | T | Tripped showing RED 670 & Siprotec relays | 14 | 7.7 | Power interruption
Aminbazar 400/230kV Grid Sub-Station | Meghnaghat 400kV Ckt-1 | 2024-08-21 00:59 | 2024-08-21 01:39 | 0:40 | T | Tripped showing RED 670 & Siprotec relays | 14 | 9.3333 | Power interruption
Ashuganj 230/132kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2024-08-21 09:23 | 2024-08-21 10:27 | 1:04 | T | Tripped showing no relays Due to Rain | 0 | 0 | No interruption
Ashuganj 230/132kV Sub-Station | Ghorasal 132kV Ckt-1 | 2024-08-21 09:23 | 2024-08-21 10:57 | 1:34 | T | Tripped showing no relays Due to Rain | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2024-08-24 10:55 | 2024-08-24 12:21 | 1:26 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ashuganj 230/132kV Sub-Station | Sreepur-2 | 2024-08-24 18:58 | 2024-08-24 19:35 | 0:37 | T | Tripped showing Main-1 REL316*4 Main-2 REL 521 relays | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sirajganj Ckt-2 | 2024-08-24 18:59 | 2024-08-24 19:35 | 0:36 | T | Tripped showing Distance Prot. relay relays. | 0 | 0 | No interruption
kodda 132/33kV Grid Sub-Station | RPCL 100 MW PS | 2024-08-24 23:49 | 2024-08-25 00:02 | 0:13 | T | Tripped showing Over current relay | 0 | 0 | No interruption
Motijheel 132/33kV Grid Sub-Station | Bangabhaban 132kV Ckt-2 | 2024-08-25 19:16 | 2024-08-26 01:22 | 6:06 | T | Tripped showing E/F. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2024-08-30 00:14 | 2024-08-30 00:32 | 0:18 | T | Tripped showing Over Current relay | 0 | 0 | No interruption
Ashuganj 230/132kV Sub-Station | Kishoreganj 132kV Ckt-1 | 2024-08-30 00:14 | 2024-08-30 02:13 | 1:59 | T | Tripped showing Distance, Y-Phase, Zone-2 relays | 120 | 238 | Power interruption
|  |  | Total : | 21:01 |  | Unserved Energy: |  | 352.5333
Dhaka (South) Grid Circle :
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 2 | 2024-08-01 10:46 | 2024-08-01 13:06 | 2:20 | T | Tripped showing REL670 relay | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Reliance PP 400KV Ckt-2 | 2024-08-01 10:46 | 2024-08-01 16:05 | 5:19 | T | Tripped showing siprotec 5 and 3 relays | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Reliance PP 400KV Ckt-2 | 2024-08-01 16:40 | 2024-08-01 16:40 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Shitalakhya Ckt | 2024-08-03 11:07 | 2024-08-03 11:07 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Shitalakhya Ckt | 2024-08-04 11:07 | 2024-08-04 11:07 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ghorashal 132/33kV Grid Sub-Station | Joydevpur-2 | 2024-08-10 11:37 | 2024-08-10 11:47 | 0:10 | T | Tripped showing Distance relay zone 2 Blue phase at Ghorashal end | 300 | 50 | Power interruption
Ghorashal 132/33kV Grid Sub-Station | Joydevpur-1 | 2024-08-10 11:37 | 2024-08-10 12:22 | 0:45 | T | Tripped showing Distance relay zone 2 Blue phase at Ghorashal end | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | 230 kV Ckt Cumilla(N)-2 | 2024-08-15 09:42 | 2024-08-15 14:25 | 4:43 | E/O | Due to As per request of NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Madunaghat-2 | 2024-08-17 09:46 | 2024-08-17 10:28 | 0:42 | T | Tripped showing Differential relay | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Madunaghat-2 | 2024-08-17 10:29 | 2024-08-17 14:11 | 3:42 | T | Tripped showing Differential relay | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Madunaghat-2 | 2024-08-17 14:14 | 2024-08-17 15:47 | 1:33 | T | Tripped showing Differential relay | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 2 | 2024-08-17 14:14 | 2024-08-17 15:58 | 1:44 | T | Tripped showing rel670 relay | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-1 | 2024-08-21 07:05 | 2024-08-21 08:45 | 1:40 | T | Tripped showing DIR O/C & E/F Relay General Trip, | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Munsiganj 132 kV Ckt-2 | 2024-08-22 05:11 | 2024-08-22 06:55 | 1:44 | T | Tripped showing Diff. Trip (R Phase) relays. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 55 MW 132 kv Ckt | 2024-08-22 05:11 | 2024-08-22 06:06 | 0:55 | T | Tripped showing E/F Relay(R,Y&B) relays. | 0 | 0 | No interruption
Bhulta 132/33kV Grid Sub-Station | Haripur 132 kV Ckt-1 | 2024-08-24 23:40 | 2024-08-24 23:58 | 0:18 | T | Tripped showing Trip Circuit Supervision Relay. | 80 | 24 | Power interruption
Meghnaghat 400/230kV Grid Sub-Station | Madunaghat-1 | 2024-08-25 15:38 | 2024-08-25 16:33 | 0:55 | T | Tripped showing 67,67N,51,51N relays. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddirganj 230kV Ckt-2 | 2024-08-25 22:45 | 2024-08-26 01:38 | 2:53 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 29:23 |  | Unserved Energy: |  | 74
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | Hathazari 132 kV Ckt-2 | 2024-08-07 22:17 | 2024-08-07 23:12 | 0:55 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Kaptai-2 | 2024-08-11 12:46 | 2024-08-11 13:36 | 0:50 | E/O | Tripped showing REL670 relays. | 0 | 0 | No interruption
Sikalbaha 132/33kV Grid Sub-Station | TKCL 132kV Ckt-1 | 2024-08-11 12:47 | 2024-08-11 15:23 | 2:36 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | 230 kV GPH-1 | 2024-08-18 09:22 | 2024-08-18 13:21 | 3:59 | T | Tripped showing Distance relay | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | 230 kV GPH-2 | 2024-08-18 09:47 | 2024-08-18 13:20 | 3:33 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-3 | 2024-08-20 10:08 | 2024-08-20 12:03 | 1:55 | T | Tripped showing Main 1 Protection-FN1 (REL670) relays | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hathazari 132 kV Ckt-2 | 2024-08-21 00:59 | 2024-08-21 00:59 | 0:00 | T | Trippedshowing Distance relay relays | 0 | 0 | No interruption
Madunaghat 400/230kV Grid Sub-Station | Meghnaghat-1 | 2024-08-21 00:59 | 2024-08-21 01:39 | 0:40 | E/O | .Blackout occurred at Chattogram zone | 411 | 274 | Power interruption
Madunaghat 400/230kV Grid Sub-Station | Meghnaghat-2 | 2024-08-21 00:59 | 2024-08-21 01:31 | 0:32 | E/O | .Blackout occurred at Chattogram zone | 408 | 217.6 | Power interruption
Hathazari 230/132kV Grid Sub-Station | 230 kV GPH-1 | 2024-08-21 01:00 | 2024-08-21 01:15 | 0:15 | T | Tripped showing ABB relays. | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Kaptai 132 kV Ckt-2 | 2024-08-27 14:44 | 2024-08-27 15:19 | 0:35 | T | Tripped showing REL670 relays. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | AKSML Ckt | 2024-08-29 13:35 | 2024-08-29 14:16 | 0:41 | T | Tripped showing Distance protection relay | 0 | 0 | No interruption
Hathazari 230/132kV Grid Sub-Station | Kaptai 132kV Ckt-1 & 2 | 2024-08-29 21:42 | 2024-08-29 22:05 | 0:23 | T | Tripped showing Main relays Due to Trip | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Juldah-1 | 2024-08-30 06:22 | 2024-08-30 09:18 | 2:56 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 19:50 |  | Unserved Energy: |  | 491.6
Cumilla Grid Circle :
Cumilla(N) 230/132kV Grid Sub-Station | Daudkandi-01 | 2024-08-01 08:36 | 2024-08-01 14:40 | 6:04 | T | showing Distance Relay relays. | 0 | 0 | No interruption
Chaddagram 132/33kV Grid Sub-Station | Feni-1 | 2024-08-05 10:42 | 2024-08-05 11:39 | 0:57 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Desh Energy Ckt-01 | 2024-08-14 08:44 | 2024-08-14 11:44 | 3:00 | E/O | Due to emergency maintenance work | 30 | 90 | Power interruption | 0.125
Chattak 132/33kV Grid Sub-Station | Sylhet-1 | 2024-08-15 23:16 | 2024-08-15 23:22 | 0:06 | T | Tripped showing Distance Relay relays. | 20 | 2 | Power interruption | 0
Chattak 132/33kV Grid Sub-Station | Sunamganj-1 | 2024-08-16 00:16 | 2024-08-16 00:46 | 0:30 | T | Tripped showing REL670 relays. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Daudkandi-01 | 2024-08-19 14:10 | 2024-08-19 14:50 | 0:40 | T | showing Distance Relay relays. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Ashuganj-1 | 2024-08-19 14:10 | 2024-08-19 14:55 | 0:45 | T | showing Distance Relay relays. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | BSRM-2 | 2024-08-20 23:29 | 2024-08-21 00:13 | 0:44 | T | Tripped showing Earth fault protection operated | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Narsinghdi-2 | 2024-08-21 00:16 | 2024-08-21 00:16 | 0:00 | T | Tripped showing Main protection relay. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Narsinghdi-2 | 2024-08-21 01:51 | 2024-08-21 12:05 | 10:14 | T | Tripped showing Main protection relay. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | 132 kV HFPL line | 2024-08-21 14:36 | 2024-08-21 15:32 | 0:56 | T | Tripped showing GR-A, GR-B relay relay. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni 132 kV Ckt-1 | 2024-08-21 14:36 | 2024-08-21 18:19 | 3:43 | T | Tripped showing Directional E/F relay. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni 132 kV Ckt-2 | 2024-08-21 14:46 | 2024-08-21 17:01 | 2:15 | T | Tripped showing Distance relay-A, B, C | 0 | 0 | No interruption
Chaddagram 132/33kV Grid Sub-Station | Feni-2 & 1 | 2024-08-21 21:39 | 2024-08-21 22:00 | 0:21 | T | Tripped showing Distance Relay(Quadramho) relays. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon 132 kV Ckt-1 | 2024-08-28 09:42 | 2024-08-28 10:11 | 0:29 | T | Tripped showing Distance Relay (P442) relay | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni 132 kV Ckt-2 | 2024-08-29 13:25 | 2024-08-29 13:43 | 0:18 | T | showing Distance Relay relay | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Narsinghdi-2 | 2024-08-30 00:46 | 2024-08-30 00:46 | 0:00 | T | showing 21 relays Due to E/F.relay | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Kachua 132 kV Ckt-1 | 2024-08-30 01:46 | 2024-08-30 02:01 | 0:15 | T | Tripped showing Distance Protection relay | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Meghnaghat 230 kV Ckt-1 | 2024-08-30 03:15 | 2024-08-30 04:00 | 0:45 | T | Tripped showing Distance Relay. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Meghnaghat 230 kV Ckt-2 | 2024-08-30 03:17 | 2024-08-30 04:03 | 0:46 | T | Tripped showing Directional overcurrent | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Meghnaghat 230 kV Ckt-2 | 2024-08-30 03:37 | 2024-08-30 04:00 | 0:23 | T | Tripped showing Distance Relay. | 26 | 9.9667 | Power interruption
Cumilla(N) 230/132kV Grid Sub-Station | Meghnaghat 230 kV Ckt-1 | 2024-08-30 14:39 | 2024-08-30 15:36 | 0:57 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Meghnaghat 230 kV Ckt-1 | 2024-08-31 14:39 | 2024-08-31 15:36 | 0:57 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
|  |  | Total : | 35:05 |  | Unserved Energy: |  | 101.9667
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Labanchura CKT-2 | 2024-08-05 03:28 | 2024-08-05 03:28 | 0:00 | T | Tripped showing No relay shows relays | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Bhandaria-1 | 2024-08-13 13:53 | 2024-08-13 14:21 | 0:28 | T | Tripped showing E/F relays. | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | 100MW ERBL Solar PS | 2024-08-14 21:48 | 2024-08-14 22:06 | 0:18 | E/O | Due to Ordered by ALDC. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | KPCL-2 | 2024-08-15 06:31 | 2024-08-15 08:22 | 1:51 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | 230 kV Ckt-Bhola-1 | 2024-08-19 16:16 | 2024-08-19 17:10 | 0:54 | T | Tripped showing Distance Relay relays. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-1 | 2024-08-22 10:25 | 2024-08-22 12:30 | 2:05 | E/O | Due to emergency work. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Labanchura 132kV Ckt-2 | 2024-08-23 03:20 | 2024-08-23 03:40 | 0:20 | T | showing distance zone 1 trip relays | 29 | 9.6667 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | Rupsha800 CKT-2 | 2024-08-24 11:55 | 2024-08-24 13:53 | 1:58 | T | showing differential relay. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Magura-Narail 132kV Ckt-2 | 2024-08-26 20:55 | 2024-08-26 22:27 | 1:32 | E/O | Due to emergency work. | 0 | 0 | No interruption
|  |  | Total : | 9:26 |  | Unserved Energy: |  | 9.6667
HVDC Grid Circle :
Ishurdi 132/33kV Grid Sub-Station | Natore-2 | 2024-08-12 12:27 | 2024-08-12 13:13 | 0:46 | T | Distance Zone-1 trip | 0 | 0 | No interruption
BIPTC | Baharampur-2 | 2024-08-23 14:23 | 2024-08-23 18:22 | 3:59 | T | Tripped showing 10C01.A relays. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | Pabna-1 | 2024-08-25 19:07 | 2024-08-25 19:07 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-1(L2) | 2024-08-26 18:31 | 2024-08-26 19:24 | 0:53 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2024-08-26 18:41 | 2024-08-26 19:25 | 0:44 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
BIPTC | Baharampur-1 | 2024-08-27 10:28 | 2024-08-27 19:36 | 9:08 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Baghabari P/S | Bangura 132 kV Ckt-1 | 2024-08-28 08:35 | 2024-08-28 15:14 | 6:39 | E/O | Due to emergency maintenance work | 15 | 99.75 | Power interruption
ishurdi 132/33kV Grid Sub-Station | Pabna 132kV Ckt | 2024-08-28 12:56 | 2024-08-28 16:50 | 3:54 | T | Trippedshowing earth fault, s phase, zone 2 and zone 3 relays. | 0 | 0 | No interruption
Baghabari P/S | Kustia 132 kV Ckt-2 | 2024-08-30 09:47 | 2024-08-30 10:23 | 0:36 | T | Tripped showing Alstom relay | 0 | 0 | No interruption
Baghabari P/S | Kustia 132 kV Ckt-2 | 2024-08-31 09:47 | 2024-08-31 10:23 | 0:36 | T | Tripped showing Alstom relay | 0 | 0 | No interruption
|  |  | Total : | 27:15 |  | Unserved Energy: |  | 99.75
Bogura Grid Circle:
Barapukuria 132/33kV Grid Sub-Station | 132 kV CKt Rangpur-1 | 2024-08-01 13:37 | 2024-08-01 13:59 | 0:22 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Barapukuria 132/33kV Grid Sub-Station | 132 kV CKt Rangpur-2 | 2024-08-01 13:51 | 2024-08-01 13:59 | 0:08 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Palashbari 132kV Ckt-1 | 2024-08-17 14:45 | 2024-08-17 17:40 | 2:55 | T | Due to Earth Fault relay | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Palashbari 132kV Ckt-1 | 2024-08-17 16:15 | 2024-08-17 17:40 | 1:25 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Rajshahi- 50 MW RPP | 2024-08-22 | 2024-08-22 | 0:00 | E/O | Due to emergency work | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Patnitola Ckt.-1 | 2024-08-23 10:22 | 2024-08-23 12:26 | 2:04 | E/O | Due to DS,PT,LA short looping | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Patnitola Ckt.-2 | 2024-08-23 10:23 | 2024-08-23 12:28 | 2:05 | E/O | Due to DS,PT,LA short looping | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullahpara 132KV Ckt-2 & 1 | 2024-08-25 20:37 | 2024-08-25 20:37 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mithapukur Ckt.-1 | 2024-08-30 15:50 | 2024-08-30 17:25 | 1:35 | E/O | Due to Metering ct cor problem | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mithapukur Ckt.-1 | 2024-08-31 15:50 | 2024-08-31 17:25 | 1:35 | E/O | Due to Metering ct cor problem | 0 | 0 | No interruption
|  |  | Total : | 12:09 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 154:09 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: August 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kodda 132/33kV Grid Sub-Station | Transformer- 05 LT | 2024-08-03 11:03 | 2024-08-03 13:59 | 2:56 | S/O | Due to Annunciator Replace | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Transformer- 05 LT | 2024-08-04 11:03 | 2024-08-04 13:59 | 2:56 | S/O | Due to Annunciator Replace | 40 | 117.3333 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-08-13 10:37 | 2024-08-13 13:05 | 2:28 | S/O | Due to Tan Delta test | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-08-15 11:14 | 2024-08-15 11:30 | 0:16 | S/O | Due to OLTC OIL Sample Collection | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-08-15 11:33 | 2024-08-15 12:00 | 0:27 | S/O | Due to OLTC OIL Sample Collection | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-08-16 06:32 | 2024-08-16 15:19 | 8:47 | S/O | Maintenance work | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-1 HT | 2024-08-26 13:08 | 2024-08-26 16:46 | 3:38 | S/O | Maintenance work | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-2 HT | 2024-08-31 07:33 | 2024-08-31 07:33 | 0:00 | S/O | Due to PRV upgradation work. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Transformer-2 ( 715T2) LT | 2024-08-31 07:34 | 2024-08-31 07:34 | 0:00 | S/O | Due to PRV upgradation work. | 0 | 0 | No interruption
|  |  | Total : | 21:28 |  | Unserved Energy: |  | 117.3333
Dhaka (South) Grid Circle : | [9 empty] | 39.3333
Srinagar 132/33kV Grid Sub-Station | Tr-01 HT | 2024-08-03 10:58 | 2024-08-03 13:30 | 2:32 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 HT | 2024-08-04 10:58 | 2024-08-04 13:30 | 2:32 | S/O | Red hot Maintenance | 10 | 25.3333 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-02 HT | 2024-08-05 09:10 | 2024-08-05 17:18 | 8:08 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | 424 TR-5 LT | 2024-08-09 12:55 | 2024-08-09 13:12 | 0:17 | S/O | Red hot Maintenance at 33kV side | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | 424 T-5 LT | 2024-08-09 15:20 | 2024-08-09 16:55 | 1:35 | S/O | Red hot Maintenance at 33kV side | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | 404 T-1 LT | 2024-08-09 15:30 | 2024-08-09 18:20 | 2:50 | S/O | Maintenance work at 33 kV side | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bus-1 | 2024-08-11 10:43 | 2024-08-11 17:12 | 6:29 | S/O | Due to Work on HPL-1 Bus DS | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | 404 T-1 HT | 2024-08-12 08:38 | 2024-08-12 21:10 | 12:32 | S/O | Maintenance work at PBS | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Auto Transformer - 01 HT | 2024-08-18 10:41 | 2024-08-19 14:28 | 27:47 | S/O | Due to 132kv busbar protection. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | 424 T-5 LT | 2024-08-20 08:52 | 2024-08-20 21:48 | 12:56 | S/O | Due to Modification of 132 kv busbar protection work | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-08-20 12:09 | 2024-08-20 21:59 | 9:50 | S/O | Due to Bus-2 Maintanences | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Reserve Bus | 2024-08-24 11:19 | 2024-08-24 18:26 | 7:07 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-08-24 11:46 | 2024-08-24 16:11 | 4:25 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | 414 T-2 HT | 2024-08-27 09:25 | 2024-08-27 18:38 | 9:13 | S/O | Due to Modification of 132kv bus bar protection work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bus-1 | 2024-08-27 09:54 | 2024-08-27 17:24 | 7:30 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Auto Transformer - 01 HT | 2024-08-28 09:45 | 2024-08-28 15:56 | 6:11 | S/O | Due to Project work. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | 404 T-1 LT | 2024-08-29 11:09 | 2024-08-29 21:46 | 10:37 | S/O | Due to Busbar protection. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-08-29 15:50 | 2024-08-29 16:22 | 0:32 | S/O | Maintenance work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2024-08-30 06:20 | 2024-08-30 06:20 | 0:00 | S/O | Due to R phase HT bushing loop change. | 0 | 0 | No interruption
|  |  | Total : | 133:03 |  | Unserved Energy: |  | 25.3333
Chattogram Grid Circle :
BSRM 230/33kV Grid Sub-Station | T-3 LT | 2024-08-10 11:43 | 2024-08-10 11:43 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | T-1 LT | 2024-08-10 11:45 | 2024-08-10 11:45 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-08-11 16:19 | 2024-08-11 17:41 | 1:22 | S/O | Due to red hot maintenance by BPDB. | 0 | 0 | No interruption
Marbari 132/33kV Grid Sub-Station | T-1 | 2024-08-12 08:09 | 2024-08-12 09:31 | 1:22 | S/O | Due to PBS work. | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | T-02 HT | 2024-08-15 09:10 | 2024-08-15 15:31 | 6:21 | S/O | Due to cleaning and checking . | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | T-03 HT | 2024-08-15 09:12 | 2024-08-15 15:34 | 6:22 | S/O | Due to cleaning and checking . | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | T-01 HT | 2024-08-15 16:10 | 2024-08-15 17:38 | 1:28 | S/O | Due to cleaning and checking. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) HT | 2024-08-16 07:18 | 2024-08-16 19:01 | 11:43 | S/O | Due to project work | 0 | 0 | No interruption
Hathazari 230/132kV Grid Sub-Station | T-01 LT | 2024-08-17 08:30 | 2024-08-17 13:59 | 5:29 | S/O | Due to 33 kV BUS repair By PBS | 0 | 0 | No interruption
Rampur 230/33kV Grid Sub-Station | TR-01 HT | 2024-08-25 11:18 | 2024-08-25 12:04 | 0:46 | S/O | Due to High Temparature maintenance. | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | TR-01 HT | 2024-08-29 10:32 | 2024-08-29 13:28 | 2:56 | S/O | Due to due to cse cleaning titghtness cheack. | 0 | 0 | No interruption
|  |  | Total : | 37:49 |  |  |  | 0
Cumilla Grid Circle :
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2024-08-03 07:32 | 2024-08-03 08:50 | 1:18 | S/O | Due to Shutdown taken by BPDB | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | 132 KV Bus-B | 2024-08-08 09:50 | 2024-08-08 14:30 | 4:40 | S/O | Red hot maintanance | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | T-01 LT | 2024-08-10 10:36 | 2024-08-10 12:06 | 1:30 | S/O | Red hot maintanance | 20 | 30 | Power interruption
Ramganj 132/33kV Grid Sub-Station | T-02 LT | 2024-08-10 12:08 | 2024-08-10 13:10 | 1:02 | S/O | Red hot maintanance | 20 | 20.6667 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 132 KV Bus-B | 2024-08-11 07:10 | 2024-08-11 14:58 | 7:48 | S/O | Red hot maintanance | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | 132 KV Bus-A | 2024-08-14 08:33 | 2024-08-14 11:42 | 3:09 | S/O | Red hot maintanance | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | T-02 LT | 2024-08-16 08:25 | 2024-08-16 10:38 | 2:13 | S/O | Due to 33kV breaker motor replacement. | 20 | 44.3333 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | T-01 HT | 2024-08-17 08:52 | 2024-08-17 17:26 | 8:34 | S/O | Due to Substation Work | 0 | 0 | No interruption
Sreemongal 132/33kV Grid Sub-Station | T-03 LT | 2024-08-17 11:07 | 2024-08-17 11:38 | 0:31 | S/O | Due to33 kV GCB SF6 Gas refilling | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T HT | 2024-08-19 06:41 | 2024-08-19 09:15 | 2:34 | S/O | Red hot maintanance at 33 kV | 50 | 128.3333 | Power interruption
Ramganj 132/33kV Grid Sub-Station | T-01 LT | 2024-08-20 08:11 | 2024-08-20 10:00 | 1:49 | S/O | Due to B phase Bushing clamp maintenance work | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2024-08-20 13:55 | 2024-08-20 19:13 | 5:18 | S/O | Maintenance work | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | T-03 LT | 2024-08-23 14:44 | 2024-08-23 16:31 | 1:47 | S/O | Maintenance work at 33 kV side | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2024-08-24 08:51 | 2024-08-24 11:30 | 2:39 | S/O | Due to for maintenance work by BPDB. | 15 | 39.75 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-4 HT | 2024-08-24 16:18 | 2024-08-24 17:28 | 1:10 | S/O | Maintenance work | 5 | 5.8333 | Power interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) LT | 2024-08-28 13:53 | 2024-08-28 15:26 | 1:33 | S/O | Due to flooded Condition | 0 | 0 | No interruption
|  |  | Total : | 47:35 |  | Unserved Energy: |  | 268.9167
Khulna Grid Circle :
Barishal 230/132kV Grid Sub-Station | Transformer-4 LT | 2024-08-03 07:22 | 2024-08-03 14:14 | 6:52 | S/O | Due to Project work for 33 kV feeder | 0 | 0 | No interruption
Faridpur 230/132kV Grid Sub-Station | ATR-1 | 2024-08-07 09:08 | 2024-08-07 12:17 | 3:09 | S/O | Maintenance work | 0 | 0 | No interruption
Faridpur 230/132kV Grid Sub-Station | ATR-2 | 2024-08-06 12:29 | 2024-08-06 14:17 | 1:48 | S/O | Maintenance work | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T1 LT | 2024-08-08 12:07 | 2024-08-08 14:29 | 2:22 | S/O | Maintenance work | 10 | 23.6667 | Power interruption
Barishal 230/132kV Grid Sub-Station | Transformer-4 LT | 2024-08-11 06:55 | 2024-08-11 09:17 | 2:22 | S/O | Maintenance work at 33 kV side | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Transformer-5 HT | 2024-08-11 10:32 | 2024-08-11 11:38 | 1:06 | S/O | Red hot maintenance work | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | T3 HT | 2024-08-12 14:46 | 2024-08-12 17:29 | 2:43 | S/O | Hot spot maintenance work | 0 | 0 | No interruption
Bhandaria 132/33 kV Grid Sub-Station | T1 LT | 2024-08-13 07:29 | 2024-08-13 07:29 | 0:00 | S/O | Maintenance work of PBS | 35 | 0 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | Main Bus-2 | 2024-08-14 10:20 | 2024-08-14 13:15 | 2:55 | S/O | Maintenance work | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | T3 LT | 2024-08-14 13:15 | 2024-08-14 19:05 | 5:50 | S/O | Maintenance work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | Bus-A | 2024-08-15 10:55 | 2024-08-15 10:55 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T2 LT | 2024-08-16 06:56 | 2024-08-16 08:39 | 1:43 | S/O | Maintenance work | 10 | 17.1667 | Power interruption
Noapara 132/33kV Grid Sub-Station | Bus-2 | 2024-08-16 07:06 | 2024-08-16 09:55 | 2:49 | S/O | Due to high temperature maintenance. | 10 | 28.1667 | Power interruption
Noapara 132/33kV Grid Sub-Station | T1 LT | 2024-08-16 09:03 | 2024-08-16 11:38 | 2:35 | S/O | Due to high temperature maintenance. | 20 | 51.6667 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-08-20 08:19 | 2024-08-20 10:19 | 2:00 | S/O | Due to Gas leakage maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2024-08-21 08:21 | 2024-08-21 14:14 | 5:53 | S/O | Due to South circuit 1 Main Bus DS Red Hot maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | T2 LT | 2024-08-21 08:24 | 2024-08-21 14:31 | 6:07 | S/O | Due to 33 kv bus section 2 shut down due to wzpdcl DS replace work | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132 kV Main Bus Section-1 | 2024-08-21 08:45 | 2024-08-21 13:55 | 5:10 | S/O | Red Hot maintenance | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2024-08-22 08:50 | 2024-08-22 10:25 | 1:35 | S/O | Due to PDB maint.work | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-08-22 09:07 | 2024-08-22 10:27 | 1:20 | S/O | Due to PDB maint.work | 10 | 13.3333 | Power interruption
Rajbari 132/33kV Grid Sub-Station | T2 LT | 2024-08-23 05:51 | 2024-08-23 18:11 | 12:20 | S/O | Project Work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Main Bus-2 | 2024-08-23 08:23 | 2024-08-23 14:34 | 6:11 | S/O | Maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | T2 LT | 2024-08-24 05:57 | 2024-08-24 17:57 | 12:00 | S/O | Project Work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400 kV Bus-1 | 2024-08-27 10:58 | 2024-08-27 13:35 | 2:37 | S/O | Due to Relay Change | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bay-1 | 2024-08-27 12:07 | 2024-08-27 12:07 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj 400132kV Grid Sub-Station | ATR-05 LT | 2024-08-27 12:08 | 2024-08-27 15:33 | 3:25 | S/O | Project Work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bay-2 | 2024-08-27 12:08 | 2024-08-27 12:08 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj 400132kV Grid Sub-Station | ATR-05 HT | 2024-08-27 12:09 | 2024-08-27 15:32 | 3:23 | S/O | Project Work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bus-1 | 2024-08-28 05:54 | 2024-08-28 17:41 | 11:47 | S/O | Project Work | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | T1 LT | 2024-08-28 06:38 | 2024-08-28 07:27 | 0:49 | S/O | Maintenance work | 19 | 15.5167 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-08-28 11:10 | 2024-08-28 12:09 | 0:59 | S/O | Due to Clamp temperature high | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bus-1 | 2024-08-29 05:52 | 2024-08-29 18:01 | 12:09 | S/O | Project Work | 0 | 0 | No interruption
Gopalganj 400132kV Grid Sub-Station | Bus-2 | 2024-08-29 08:48 | 2024-08-29 15:28 | 6:40 | S/O | Project Work | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | T3 HT | 2024-08-29 10:18 | 2024-08-29 12:12 | 1:54 | S/O | Due to Hot spot maintenance. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bus-1 | 2024-08-30 06:57 | 2024-08-30 17:20 | 10:23 | S/O | Project Work | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-08-30 08:05 | 2024-08-30 12:15 | 4:10 | S/O | Due to 33 KV bUS Shutdown | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 HT | 2024-08-30 08:07 | 2024-08-30 12:10 | 4:03 | S/O | Due to 33 KV bUS Shutdown | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-08-31 08:05 | 2024-08-31 12:15 | 4:10 | S/O | Due to 33 KV bUS Shutdown | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2024-08-31 08:05 | 2024-08-31 12:10 | 4:05 | S/O | Due to 33 KV bUS Shutdown | 0 | 0 | No interruption
|  |  | Total : | 159:24 |  | Unserved Energy : |  | 149.5167
HVDC Grid Circle
Jashore 132/33kV Grid Sub-Station | TR-1HT | 2024-08-02 07:35 | 2024-08-02 19:57 | 12:22 | S/O | 33 kV changing work | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | 132kV Tr.2 HT | 2024-08-03 08:55 | 2024-08-03 14:45 | 5:50 | S/O | Project work | 47 | 274.1667 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | T-2 HT | 2024-08-04 08:55 | 2024-08-04 14:46 | 5:51 | S/O | Project work | 17 | 99.45 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr-3 LT | 2024-08-11 08:50 | 2024-08-11 10:32 | 1:42 | S/O | Red hot maintanance | 0 | 0 | No interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr-3 LT | 2024-08-17 09:25 | 2024-08-17 13:26 | 4:01 | S/O | Project Work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2024-08-19 08:30 | 2024-08-19 16:51 | 8:21 | S/O | Project Work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-2 | 2024-08-20 08:32 | 2024-08-20 16:05 | 7:33 | S/O | Project Work | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-1 LT | 2024-08-21 14:34 | 2024-08-21 15:40 | 1:06 | S/O | Project Work | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-2 HT | 2024-08-21 16:19 | 2024-08-21 16:36 | 0:17 | S/O | Project Work | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | T-2 LT | 2024-08-24 07:34 | 2024-08-24 11:58 | 4:24 | S/O | Maintenance work | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-08-24 07:40 | 2024-08-24 09:09 | 1:29 | S/O | Maintenance work | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-2 LT | 2024-08-24 11:33 | 2024-08-24 13:37 | 2:04 | S/O | Maintenance work | 25 | 51.6667 | Power interruption
Baghabari 230/132kV Grid Sub-Station | T-1 LT | 2024-08-28 07:40 | 2024-08-28 15:21 | 7:41 | S/O | Due to S/D Taken by BPDB | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | T-2 LT | 2024-08-28 07:56 | 2024-08-28 15:07 | 7:11 | S/O | Due to S/D Taken by BPDB | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-3 LT | 2024-08-28 08:25 | 2024-08-28 10:03 | 1:38 | S/O | Project Work | 35 | 57.1667 | Power interruption
BIPTC | 20DF24 | 2024-08-28 15:42 | 2024-08-28 17:28 | 1:46 | S/O | Maintenance work | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | T-2 LT | 2024-08-29 07:20 | 2024-08-29 09:11 | 1:51 | S/O | Due to 33 kv isolator hook up with BUS conductor. | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | T-1 HT | 2024-08-30 07:00 | 2024-08-30 17:04 | 10:04 | S/O | Project Work | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | T-1 HT | 2024-08-31 06:18 | 2024-08-31 17:04 | 10:46 | S/O | Project Work | 0 | 0 | No interruption
|  |  | Total : | 95:57 |  | Unserved Energy : |  | 482.45
Bogura Grid Circle:
Purbasadipur 132/33kV Grid Sub-Station | T-1 LT | 2024-08-03 09:05 | 2024-08-03 09:45 | 0:40 | S/O | Due to TRTUD work | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 LT | 2024-08-04 09:05 | 2024-08-04 15:45 | 6:40 | S/O | Project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2024-08-14 10:13 | 2024-08-14 12:56 | 2:43 | S/O | Due to Protection-related work | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | T-1 LT | 2024-08-14 10:51 | 2024-08-14 12:52 | 2:01 | S/O | Red hot maintanance | 4 | 8.0667 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2024-08-14 13:13 | 2024-08-14 15:28 | 2:15 | S/O | Due to Protection-related work by SPMD | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | T-1 HT | 2024-08-18 07:15 | 2024-08-18 09:06 | 1:51 | S/O | Red hot maintanance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Main Bus- 1 | 2024-08-18 07:40 | 2024-08-18 17:30 | 9:50 | S/O | Project work | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Main Bus- 1 | 2024-08-19 07:36 | 2024-08-19 17:23 | 9:47 | S/O | Project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-4 HT | 2024-08-20 10:42 | 2024-08-20 17:25 | 6:43 | S/O | Project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Main Bus- 2 | 2024-08-20 10:44 | 2024-08-20 17:23 | 6:39 | S/O | Project work | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-4 LT | 2024-08-26 09:35 | 2024-08-26 10:41 | 1:06 | S/O | Due to PBS Maintenance works | 30 | 33 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-4 LT | 2024-08-26 12:54 | 2024-08-26 13:39 | 0:45 | S/O | Due to PBS Maintenance works | 12 | 9 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-2 (415 T) LT | 2024-08-27 09:01 | 2024-08-27 09:01 | 0:00 | S/O | Due to Transformer upgradation | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-4 (435 T) HT | 2024-08-27 09:02 | 2024-08-27 09:02 | 0:00 | S/O | Due to Transformer upgradation | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230 kV Bay | 2024-08-27 12:07 | 2024-08-27 12:07 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-08-29 08:37 | 2024-08-29 14:29 | 5:52 | S/O | Due to LT bushing hot clamp maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Main Bus- 2 | 2024-08-29 09:57 | 2024-08-29 14:15 | 4:18 | S/O | Project work | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-2 (415 T) HT | 2024-08-30 07:29 | 2024-08-30 09:08 | 1:39 | S/O | Due to Red hot maintenance. | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 HT | 2024-08-31 07:36 | 2024-08-31 07:36 | 0:00 | S/O | Due to T-1 33 kv bus Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 62:49 |  | Unserved Energy : |  | 50.0667
Others :
Ashuganj 230/132/33kV Grid Sub-Station | TR-OAT-12 LT | 2024-08-02 06:35 | 2024-08-02 06:35 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Grid Sub-Station | TR-4 | 2024-08-02 08:08 | 2024-08-02 08:08 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Grid Sub-Station | TR-OAT-11 LT | 2024-08-30 06:20 | 2024-08-30 06:20 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 558:05 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:August 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-08-01 10:21 | 2024-08-01 18:54 | 8:33 | S/O | New tower erection work | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-08-01 11:19 | 2024-08-01 13:35 | 2:16 | D/W | Project Work | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2024-08-02 08:21 | 2024-08-02 08:21 | 0:00 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-08-02 10:25 | 2024-08-02 17:13 | 6:48 | S/O | Tower Errection work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Shahjibazar 132kV Ckt-1 | 2024-08-02 12:45 | 2024-08-02 12:45 | 0:00 | S/O | Maintenance | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Brahmanbaria-2 | 2024-08-03 08:42 | 2024-08-03 11:48 | 3:06 | S/O | Due to NLDC | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-08-03 08:54 | 2024-08-03 18:31 | 9:37 | S/O | Due to Tower erection work | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Brahmanbaria-1 | 2024-08-03 11:49 | 2024-08-03 13:57 | 2:08 | S/O | Project Work | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Brahmanbaria-2 | 2024-08-04 08:42 | 2024-08-04 11:48 | 3:06 | S/O | Due to NLDC | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-08-04 08:54 | 2024-08-04 18:31 | 9:37 | S/O | Due to Tower erection work | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Brahmanbaria-1 | 2024-08-04 11:49 | 2024-08-04 13:57 | 2:08 | S/O | Project Work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kV Ckt Kaliakoir-01 | 2024-08-09 10:16 | 2024-08-09 19:31 | 9:15 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kV Ckt Kaliakoir-01 | 2024-08-10 09:41 | 2024-08-10 13:16 | 3:35 | S/O | Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | 230 kV Tongi-Tongi 80 MW PS | 2024-08-09 11:45 | 2024-08-09 16:25 | 4:40 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-08-14 10:49 | 2024-08-14 10:49 | 0:00 | S/O | NLDC. | 0 | 0 | No interruption
Ashuganj (S)230/132kV Sub-Station | 230 kV Ckt-1 Ghorashal-2 | 2024-08-14 13:06 | 2024-08-14 21:57 | 8:51 | S/O | Redhot maintenance | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Kishoreganj 132 kV Ckt-1 | 2024-08-16 06:25 | 2024-08-16 06:25 | 0:00 | S/O | Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2024-08-16 10:34 | 2024-08-16 10:34 | 0:00 | S/O | Maintenance | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2024-08-17 06:36 | 2024-08-17 21:32 | 14:56 | S/O | Project Work | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2024-08-18 05:53 | 2024-08-18 17:35 | 11:42 | S/O | Project Work | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2024-08-19 08:28 | 2024-08-19 17:28 | 9:00 | S/O | Project Work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | 230 kV Tongi-Tongi 80 MW PS | 2024-08-20 13:17 | 2024-08-20 13:17 | 0:00 | S/O | Maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV Sub-Station | Manikganj 132 Ckt-1 | 2024-08-23 08:32 | 2024-08-23 13:38 | 5:06 | S/O | Due to High temperature maintenance purpose. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2 | 2024-08-23 09:59 | 2024-08-23 21:10 | 11:11 | S/O | Due to Busbar Protection Work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-08-24 08:44 | 2024-08-24 16:30 | 7:46 | S/O | Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2024-08-24 10:58 | 2024-08-24 12:21 | 1:23 | S/O | Maintenance | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2024-08-26 06:10 | 2024-08-26 17:51 | 11:41 | S/O | Project Work | 0 | 0 | No interruption
Ashuganj 230/132kV Sub-Station | Sreepur 230 kV Ckt-2 | 2024-08-26 11:37 | 2024-08-26 16:23 | 4:46 | S/O | Maintenance | 0 | 0 | No interruption
Ashuganj 132/33kV Sub-Station | Kishoreganj 132 kV Ckt-1 | 2024-08-27 06:59 | 2024-08-27 13:02 | 6:03 | S/O | Project Work | 0 | 0 | No interruption
|  |  | Total : | 157:14 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Madanganj 132/33kV Grid Sub-Station | Munsiganj-01 | 2024-08-13 06:59 | 2024-08-16 17:20 | 82:21 | S/O | Due to Tower erection work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-02 | 2024-08-15 08:25 | 2024-08-15 13:33 | 5:08 | S/O | Due to Loop Red hot Maintenance | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | 230 kV Rampura Ckt-02 | 2024-08-15 08:58 | 2024-08-15 13:33 | 4:35 | S/O | Due to Disk cleaning by Haripur team. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-01 | 2024-08-15 13:34 | 2024-08-15 16:53 | 3:19 | S/O | Maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | 230 kV Rampura Ckt-01 | 2024-08-15 13:49 | 2024-08-15 16:52 | 3:03 | S/O | Maintenance work | 0 | 0 | No interruption
Moghbazar132/33kV Grid Sub-Station | Rampura-2 | 2024-08-16 06:14 | 2024-08-16 07:49 | 1:35 | S/O | Due to Red Hot at Rampura Ckt-02 Line | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-1 | 2024-08-18 10:43 | 2024-08-18 10:43 | 0:00 | S/O | Due to As the direction of NLDC. | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Madunaghat-1 | 2024-08-18 16:14 | 2024-08-18 16:26 | 0:12 | S/O | Project work, | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-08-20 08:30 | 2024-08-20 22:24 | 13:54 | S/O | Maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad- | 2024-08-21 09:07 | 2024-08-21 22:45 | 13:38 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Keranigonj-1 | 2024-08-22 09:35 | 2024-08-22 18:07 | 8:32 | S/O | Due to Busbar protection work at Sub-station . | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad- | 2024-08-22 09:35 | 2024-08-22 18:07 | 8:32 | S/O | Due to Busbar protection work at Sub-station . | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad- | 2024-08-24 08:38 | 2024-08-24 22:19 | 13:41 | S/O | Due to protection work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Keraniganj-1 (Pre- Lalbag) | 2024-08-24 08:46 | 2024-08-24 08:46 | 0:00 | S/O | Due to Modification of 132 kv bus bar protection work | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | Hasnabad- | 2024-08-24 08:52 | 2024-08-24 22:27 | 13:35 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Fatulla (Pre-Brahmongaon) | 2024-08-24 08:57 | 2024-08-24 22:27 | 13:30 | S/O | Due to Modification of 132kv bus bar Protection | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar-2 | 2024-08-24 09:35 | 2024-08-24 14:08 | 4:33 | S/O | Due to Relay change work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-1 | 2024-08-25 09:05 | 2024-08-25 18:05 | 9:00 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Keraniganj-1 (Pre- Lalbag) | 2024-08-25 09:12 | 2024-08-25 18:05 | 8:53 | S/O | Due to Modification of 132kv bus bar protection work. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Sitalakhya 132kV Ckt-1 | 2024-08-25 09:21 | 2024-08-25 18:08 | 8:47 | S/O | Due to Modification of 132kv bus bar protection work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddirganj 132kV Ckt-2 | 2024-08-25 22:45 | 2024-08-26 01:40 | 2:55 | S/O | Maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | 230 kV Hasnabad-1 | 2024-08-26 09:04 | 2024-08-26 20:34 | 11:30 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Keraniganj-1 (Pre- Lalbag) | 2024-08-26 09:04 | 2024-08-26 20:35 | 11:31 | S/O | Due to protection work. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Keraniganj-2 (Pre- Lalbag) | 2024-08-26 09:06 | 2024-08-26 20:37 | 11:31 | S/O | Due to protection work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko-1 | 2024-08-26 09:07 | 2024-08-26 20:35 | 11:28 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Keraniganj-2 (Pre- Lalbag) | 2024-08-27 09:13 | 2024-08-27 17:31 | 8:18 | S/O | Due to Modification of 132kv bus bar protection work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-08-27 09:17 | 2024-08-27 17:37 | 8:20 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | 230 kV Keraniganj-1 | 2024-08-28 09:22 | 2024-08-28 21:52 | 12:30 | S/O | Maintenance work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Summit 102 MW 132 kv Ckt | 2024-08-29 10:49 | 2024-08-29 10:49 | 0:00 | S/O | Due to Y phase cable pot head change. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132 kV Ckt Narsingdi -1 | 2024-08-30 09:18 | 2024-08-30 19:19 | 10:01 | S/O | Maintenance work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132 kV Ckt Narsingdi -1 | 2024-08-31 09:18 | 2024-08-31 19:19 | 10:01 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 314:53 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ramganj 132/33kV Grid Sub-Station | Desh Energy Ckt-01 | 2024-08-08 09:25 | 2024-08-08 12:13 | 2:48 | S/O | Maintenance work | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Desh Energy Ckt-02 | 2024-08-08 12:50 | 2024-08-08 14:27 | 1:37 | S/O | Maintenance work | 20 | 32.3333 | Power interruption
Cumilla(N) 132/33kV Grid Sub-Station | Cumilla(S)-1 | 2024-08-13 11:43 | 2024-08-13 11:43 | 0:00 | S/O | Due to TCS Relay Check Cum(N) | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | 230 kV Ckt Meghnaghat-1 | 2024-08-15 10:50 | 2024-08-15 12:32 | 1:42 | S/O | Maintenance work | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | PHP 132kV Ckt-1 | 2024-08-25 11:11 | 2024-08-25 12:08 | 0:57 | S/O | Due to For testing purpose | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Desh Energy Ckt-02 | 2024-08-28 09:02 | 2024-08-28 14:21 | 5:19 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 12:23 |  | Unserved Energy: |  | 32.3333
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria Ckt-1 | 2024-10-08 07:30 | 2024-10-08 09:12 | 1:42 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-1 | 2024-08-14 10:14 | 2024-08-14 10:18 | 0:04 | S/O | Maintenance work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-1 | 2024-08-14 13:29 | 2024-08-14 13:31 | 0:02 | S/O | Maintenance work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kV Ckt Barishal(N)-1 | 2024-08-14 15:11 | 2024-08-14 17:46 | 2:35 | S/O | Maintenance work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kV Ckt Barishal(N)-1 | 2024-08-15 11:57 | 2024-08-15 12:51 | 0:54 | S/O | Maintenance work | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Khulna (C) S/S North-WestCkt-1 | 2024-08-21 08:20 | 2024-08-21 14:07 | 5:47 | S/O | Due to South circuit 1 Main Bus DS Red Hot maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Khulna (C) S/S North-WestCkt-1 | 2024-08-21 08:20 | 2024-08-21 14:06 | 5:46 | S/O | Due to South circuit 1 Main Bus DS Red Hot maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Khulna(C )-Khulna (S) 132kV Ckt-1 | 2024-08-21 08:23 | 2024-08-21 14:02 | 5:39 | S/O | Maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-08-22 10:24 | 2024-08-22 12:29 | 2:05 | S/O | Due to kite move. | 0 | 0 | No interruption
Gopalganj 400/230/132/33kV Grid Sub-Station | 230 kV Faridpur Ckt-1 | 2024-08-22 10:28 | 2024-08-22 17:01 | 6:33 | S/O | project work | 0 | 0 | No interruption
Gopalganj 400/230/132/33kV Grid Sub-Station | 230 kV Faridpur Ckt-2 | 2024-08-22 17:09 | 2024-08-22 18:50 | 1:41 | S/O | project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-1 | 2024-08-23 08:17 | 2024-08-23 08:21 | 0:04 | S/O | Maintenance work | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | Payra-2 | 2024-08-24 21:56 | 2024-08-25 21:56 | 24:00 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
|  |  | Total : | 56:52 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi 230/132kV Grid Sub-Station | Ghorashal-2 & 1 | 2024-08-02 07:14 | 2024-08-02 16:56 | 9:42 | S/O | Project Work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | Ghorashal- 2 | 2024-08-02 07:14 | 2024-08-02 17:27 | 10:13 | S/O | Project Work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | Pabna Ckt | 2024-08-02 07:30 | 2024-08-02 18:04 | 10:34 | S/O | Due to line stringging work . | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Ruppur 230 KV ckt-1 | 2024-08-18 14:45 | 2024-08-18 17:30 | 2:45 | S/O | Maintenance work | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Ruppur 230 KV ckt-2 | 2024-08-18 14:46 | 2024-08-18 17:40 | 2:54 | S/O | Maintenance work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | Ruppur 230 KV ckt-1 | 2024-08-19 08:21 | 2024-08-19 17:07 | 8:46 | S/O | Project Work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | Ruppur 230 KV ckt-2 | 2024-08-19 08:23 | 2024-08-19 17:06 | 8:43 | S/O | Project Work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | Ruppur 132 KV ckt-1 | 2024-08-20 08:24 | 2024-08-20 16:16 | 7:52 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Magura 132 kV Ckt-1 | 2024-08-21 11:22 | 2024-08-21 13:21 | 1:59 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | Baghabari P/S | 2024-08-28 07:29 | 2024-08-28 13:11 | 5:42 | S/O | Due to Baghabari Power Station Work. | 0 | 0 | No interruption
|  |  | Total : | 69:10 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Thakurgaon 132/33kV Grid Sub-Station | Thakurgaon-EPV 132kV Ckt-2 | 2024-08-02 07:30 | 2024-08-02 10:30 | 3:00 | S/O | Due to red hot maintenance | 0 | 0 | No interruption
Barapukuria 230/132/kV Grid Sub-Station | Rangpur-2 | 2024-08-15 10:13 | 2024-08-16 12:44 | 26:31 | S/O | Due to replacement work | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur -1 | 2024-08-16 08:29 | 2024-08-16 14:48 | 6:19 | S/O | Project Work | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur -1 | 2024-08-17 09:25 | 2024-08-17 16:21 | 6:56 | S/O | Project Work | 20 | 138.6667 | Power interruption
Purbasadipur132/33kV Grid Sub-Station | Saidpur 132kV Ckt-1 | 2024-08-21 06:40 | 2024-08-21 06:40 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Rajshahi- 50 MW RPP | 2024-08-21 11:59 | 2024-08-21 17:12 | 5:13 | S/O | Due to Contract with BPDB has expired | 0 | 0 | No interruption
Sreepur 230/132/kV Grid Sub-Station | Sreepur-Sirajganj Ckt-2 | 2024-08-26 12:04 | 2024-08-26 16:24 | 4:20 | S/O | Due to Right of way | 0 | 0 | No interruption
|  |  | Total : | 52:19 |  | Unserved Energy: |  | 138.6667
Others :Nil
No interruption
|  |  | Total : | 0:00 |  |  |  | 0:00
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 662:51 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:August 2024
| Area | Previous Month (July' 2024) |  |  |  | Current Month (August '2024)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 29 | 19 | 74 | 122 | 27 | 11 | 38 | 76
2 | Dhaka (South) Grid Circle. | 19 | 7 | 51 | 77 | 19 | 12 | 50 | 81
3 | Chattogram Grid Circle. | 15 | 19 | 15 | 49 | 14 | 18 | 11 | 43
4 | Cumilla Grid Circle. | 7 | 6 | 17 | 30 | 32 | 7 | 22 | 61
5 | Khulna Grid Circle. | 4 | 16 | 26 | 46 | 8 | 7 | 62 | 77
6 | HVDC Grid Circle | 17 | 11 | 20 | 48 | 22 | 10 | 29 | 61
7 | Bogura Grid Circle. | 7 | 19 | 33 | 59 | 9 | 32 | 26 | 67
8 | Others | - | - | - | - | - | - | 3 | 3
9 | Total | 98 | 97 | 236 | 431 | 131 | 97 | 241 | 469
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:August 2024
| Area | Previous Month (July' 2024) |  |  |  | Current Month (August '2024)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 746.75 | 948.01 | 2692.45 | 4387.21 | 507.18 | 241.33 | 117.33 | 865.84
2 | Dhaka (South) Grid Circle. | 1281.15 | 186.67 | 301.33 | 1769.15 | 107.97 | 440.83 | 25.33 | 574.13
3 | Chattogram Grid Circle. | 410.29 | 118.47 | 5.5 | 534.26 | 61.93 | 867.62 | 0 | 929.55
4 | Cumilla Grid Circle. | 708.36 | 220.58 | 33.6 | 962.54 | 169.74 | 163 | 301.25 | 633.99
5 | Khulna Grid Circle. | 31.55 | 461.17 | 371.85 | 864.57 | 24.87 | 1.2 | 149.52 | 175.59
6 | HVDC Grid Circle | 307.53 | 749 | 253 | 1309.53 | 372.69 | 218.42 | 482.45 | 1073.56
7 | Bogura Grid Circle. | 420.12 | 328.3 | 235.75 | 984.17 | 37.2 | 666.78 | 188.73 | 892.71
8 | Others | - | - | - | - | - | - | - | 0
9 | Total | 3905.75 | 3012.2 | 3893.48 | 10811.43 | 1281.58 | 2599.18 | 1264.61 | 5145.37
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:August 2024
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 9 | 1 | 10 | 5 | 1 | 4 | 513.31
2 | Dhaka (South) | 5031.6 | 6 | 1 | 7 | 1 | - | 6 | 500.13
3 | Chattogram | 2042 | 11 | - | 11 | 2 | 7 | 2 | 437.95
4 | Khulna | 2434 | 4 | 6 | 10 | 1 | 3 | 6 | 165.92 |  | 754.05
5 | HVDC | 5954.3 | 10 | 4 | 14 | 4 | 2 | 8 | 973.8
6 | Bogura | 3145.6 | 14 | 3 | 17 | 2 | 3 | 12 | 754.05
7 | Cumilla | 2981 | 8 | 6 | 14 | 2 | 3 | 9 | 499.69
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 3844.85
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.91%
4 | Khulna | 99.99%
5 | HVDC | 99.96% | [6 empty] | Executive Engineer
6 | Bogura | 99.94% | [6 empty] | Information Management Division
7 | Cumilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:August 2024
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 4 | - | 4 | 2 | 3 | 1 | 352.53
2 | Dhaka (South) | 990.29 | - | 2 | - | 2 | - | 2 | - | 74
3 | Chattogram | 917 | - | 2 | - | 2 | - | 2 | - | 491.6
4 | Khulna | 1238.4 | - | 1 |  | 1 | 1 | - | - | 9.67
5 | HVDC | 1325 | - | 1 | - | 1 | - | - | 1 | 99.75
6 | Bogura | 1803.3 | - | - | 1 | 1 | - | - | 1 | 138.67
7 | Cumilla | 1648.16 | - | 3 | 1 | 4 | 2 | - | 2 | 134.3
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 1300.52
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 100%
7 | Cumilla | 99.99%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:August 2024
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2024-08-01 | 16 | - | 3 | 3hr17 min | 3 | 9hr45 min | - | - | 1 | 0:32 | - | - | Chattogram zone blackout
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:August 2024
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Kabirpur 132/33kV Grid Sub-Station | 1 | 1:36 | 128
Sreepur 230/132/33kV Grid Sub-Station | 1 | 0:06 | 4.5
Tangail 132/33kV Grid Sub-Station | 2 | 2:20 | 93.33
Sreepur 230/132/33kV Grid Sub-Station | 3 | 1:14 | 36.68
Mymensingh 132/33kV Grid Sub-Station | 2 | 0:44 | 133.47
Kabirpur 132/33kV Grid Sub-Station | 1 | 0:39 | 97.5
Aminbazar 400/230kV Grid Sub-Station | 2 | 1:33 | 17.03
Ashuganj 230/132kV Sub-Station | 1 | 1:59 | 238
Kodda 132/33kV Grid Sub-Station | 1 | 2:56 | 117.3333
Keranigonj 230/132/33kV Grid Sub-Station | 1 | 0:26 | 19.5
Hasnabad 132/33kV Grid Sub-Station | 1 | 1:02 | 14.4667
Sonargaon 132/33kV Grid Sub-Station | 1 | 1:26 | 57.3333
Munshiganj 132/33kV Grid Sub-Station | 2 | 6:00 | 162
Bhulta 132/33kV Grid Sub-Station | 1 | 7:23 | 221.5
Ghorashal 132/33kV Grid Sub-Station | 1 | 0:10 | 50
Bhulta 132/33kV Grid Sub-Station | 1 | 0:18 | 24
Srinagar 132/33kV Grid Sub-Station | 1 | 2:32 | 25.3333
Dohazari 132/33kV Grid Sub-Station | 2 | 1:58 | 121.93
Madunaghat 132/33kV Grid Sub-Station | 1 | 0:32 | 6.9333
Dohazari 132/33kV Grid Sub-Station | 1 | 1:06 | 5.5
Coxsbazar 132/33kV Grid Sub-Station | 1 | 5:46 | 201.8333
Dohazari 132/33kV Grid Sub-Station | 1 | 0:29 | 24.1667
Halishahar 132/33kV Grid Sub-Station | 2 | 1:03 | 22.75
Kalurghat 132/33kV Grid Sub-Station | 2 | 1:32 | 24
Madunaghat 400/230kV Grid Sub-Station | 2 | 1:12 | 491.6
Dohazari 132/33kV Grid Sub-Station | 1 | 0:37 | 30.8333
Beanibazar 132/33kV Grid Sub-Station | 1 | 1:00 | 20
Chowmuhani 132/33kV Grid Sub-Station | 1 | 1:46 | 53
Sunamganj 132/33kV Grid Sub-Station | 1 | 1:39 | 9.9
Chauddagram 132/33kV Grid Sub-Station | 1 | 0:11 | 4.95
Chandpur 132/33kV Grid Sub-Station | 1 | 0:20 | 6
Fenchuganj 230/132kV Grid Sub-Station | 1 | 6:29 | 123.1833
Sylhet 132/33kV Grid Sub-Station | 2 | 0:39 | 13.73
Ramganj 132/33kV Grid Sub-Station | 1 | 3:00 | 90
Chattak 132/33kV Grid Sub-Station | 1 | 0:06 | 2
Cumilla(N) 230/132kV Grid Sub-Station | 1 | 0:23 | 9.9667
Ramganj 132/33kV Grid Sub-Station | 3 | 4:45 | 95
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 2:34 | 128.3333
Cumilla(S) 132/33kV Grid Sub-Station | 2 | 3:49 | 45.58
Ramganj 132/33kV Grid Sub-Station | 1 | 1:37 | 32.3333
Barguna 132/33kV Grid Sub-Station | 1 | 0:12 | 2.8
Mongla 132/33kV Grid Sub-Station | 3 | 3:55 | 13.6
Goalpara 132/33kV Grid Sub-Station | 1 | 0:20 | 9.6667
Shariatpur 132/33kV Grid Sub-Station | 1 | 2:22 | 23.6667
Noapara 132/33kV Grid Sub-Station | 3 | 7:07 | 97
Goalpara 132/33kV Grid Sub-Station | 1 | 1:20 | 13.3333
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:49 | 15.5167
Jhenaidah 132/33kV Grid Sub-Station | 2 | 0:26 | 28.17
Kushtia 132/33kV Grid Sub-Station | 1 | 0:19 | 12.0333
BIPTC | 1 | 1:13 | 0
Kushtia 132/33kV Grid Sub-Station | 1 | 0:16 | 4.2667
BIPTC | 1 | 2:13 | 0
Jhenaidah 132/33kV Grid Sub-Station | 1 | 0:41 | 32.8
Kushtia 132/33kV Grid Sub-Station | 1 | 2:10 | 86.6667
Shahjadpur 132/33kV Grid Sub-Station | 1 | 2:20 | 56
Jashore 132/33kV Grid Sub-Station | 2 | 11:34 | 239.42
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:48 | 32
Baghabari P/S | 1 | 6:39 | 99.75
Jhenaidah 230/132kV Grid Sub-Station | 2 | 11:41 | 373.62
Kushtia 132/33kV Grid Sub-Station | 1 | 2:04 | 51.6667
Kushtia 132/33kV Grid Sub-Station | 1 | 1:38 | 57.1667
Naogaon 132/33kV Grid Sub-Station | 1 | 1:24 | 22.4
Bhangura 132/33kV Grid Sub-Station | 1 | 0:51 | 22.1
Bog-Sherpur 132/33kV Grid Sub-Station | 2 | 2:56 | 140.8
Barapukuria 230/132/kV Grid Sub-Station | 1 | 1:23 | 55.3333
Palshabari 132/33kV Grid Sub-Station | 1 | 1:50 | 132
Barapukuria 230/132/kV Grid Sub-Station | 1 | 0:24 | 14.8
Bogura 132/33kV Grid Sub-Station | 1 | 2:21 | 58.75
Naogaon 132/33kV Grid Sub-Station | 1 | 1:29 | 17.8
Barapukuria 230/132/kV Grid Sub-Station | 1 | 1:56 | 87
Naogaon 132/33kV Grid Sub-Station | 1 | 0:12 | 3
Palshbari 132/33kV Grid Sub-Station | 3 | 3:48 | 150
Barguna 132/33kV Grid Sub-Station | 1 | 2:01 | 8.0667
Purbasadipur 132/33kV Grid Sub-Station | 3 | 8:47 | 180.67
Total Unserved energy : | 100 | 164:26 | 5145.3633
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: August 2024
Sl. No | Sub-station | Load (MW) | Date and Time
1 | AKS | 15 | 2024-08-18 12:00
2 | AKSML | 126 | 2024-08-30 09:00
3 | Aftabnagar | 36 | 2024-08-14 18:30
4 | Agargaon | 122 | 2024-08-29 13:00
5 | Agrabad | 100 | 2024-08-25 11:00
6 | Amnura | 88 | 2024-08-01 00:00
7 | Ashuganj | 99 | 2024-08-17 01:00
8 | BIPTC | N/A | N/A
9 | BSRM | 195 | 2024-08-09 22:00
10 | Bagerhat | 98 | 2024-08-31 19:30
11 | Bakulia | 99 | 2024-08-31 16:00
12 | Banani | 128.16 | 2024-08-24 04:00
13 | Bangabhaban | 24 | 2024-08-11 11:00
14 | Barapukuria | 65 | 2024-08-14 22:00
15 | Barguna | 23 | 2024-08-21 23:00
16 | Barishal | 121 | 2024-08-13 12:00
17 | Barishal-230 | 102 | 2024-08-14 21:00
18 | Baroaulia | 73 | 2024-08-21 11:00
19 | Baroirhat | 63 | 2024-08-14 21:00
20 | Bashundhara | 181 | 2024-08-15 13:00
21 | BashundharaCement | 17 | 2024-08-25 13:00
22 | Beanibazar | 84 | 2024-08-30 18:30
23 | Benapole | 76 | 2024-08-28 21:00
24 | Bhaluka | 138 | 2024-08-29 09:00
25 | Bhandaria | 57 | 2024-08-01 00:00
26 | Bhangura | 42 | 2024-08-29 22:00
27 | Bheramara(GK) | 78 | 2024-08-11 21:00
28 | Bhulta | 266 | 2024-08-20 17:00
29 | Bog-Sherpur | 70 | 2024-08-17 00:00
30 | Bogura | 185 | 2024-08-29 23:00
31 | Borhanuddin | 89 | 2024-08-03 22:00
32 | Brahmanbaria | 186 | 2024-08-31 20:00
33 | Cantonment | 125 | 2024-08-03 07:00
34 | Chandpur | 80 | 2024-08-30 22:00
35 | Chandraghona | 38 | 2024-08-14 20:00
36 | Chapai | 77 | 2024-08-16 22:00
37 | Charsaidpur | 40 | 2024-08-01 15:00
38 | Chauddagram | 69 | 2024-08-11 22:00
39 | Chhatak | 40 | 2024-08-30 22:00
40 | Chowmuhani | 217 | 2024-08-12 19:00
41 | Chuadanga | 119 | 2024-08-01 00:00
42 | Coxsbazar | 127 | 2024-08-10 19:00
43 | Cumilla(N) | 169 | 2024-08-16 21:00
44 | Cumilla(S) | 192 | 2024-08-14 14:00
45 | Daudkandi | 164 | 2024-08-29 21:00
46 | Dhaka | 58 | 2024-08-14 13:00
47 | Dhamrai | 138 | 2024-08-10 11:00
48 | Dhanmondi | 150 | 2024-08-14 13:00
49 | Dohazari | 107 | 2024-08-31 21:00
50 | Faridpur | 178 | 2024-08-15 00:00
51 | Fatullah | 93 | 2024-08-15 16:00
52 | Fenchuganj | 47 | 2024-08-29 18:30
53 | Feni | 110 | 2024-08-13 20:00
54 | GPH | 99 | 2024-08-13 14:00
55 | Ghatail | 76 | 2024-08-30 18:30
56 | Ghorashal | 62 | 2024-08-12 22:00
57 | Goalpara | 36 | 2024-08-04 13:00
58 | Gollamari | 84 | 2024-08-14 13:00
59 | Gopalganj | 114 | 2024-08-31 22:00
60 | Gulshan | 128 | 2024-08-14 13:00
61 | Halishahar | 70 | 2024-08-01 11:00
62 | HaripurSBU | 184 | 2024-08-01 15:00
63 | Hasnabad | 103 | 2024-08-29 23:00
64 | Hathazari | 77 | 2024-08-13 19:00
65 | Ishurdi | 83 | 2024-08-29 19:00
66 | Jaldhaka | 103 | 2024-08-16 23:00
67 | Jamalpur | 127 | 2024-08-05 00:00
68 | Jashore | 153 | 2024-08-29 19:00
69 | Jhenaidah | 184 | 2024-08-30 16:00
70 | Joydebpur | 207 | 2024-08-27 19:00
71 | Joypurhat | 76 | 2024-08-01 00:00
72 | Juldah | 23 | 2024-08-03 11:00
73 | KSRM | 36 | 2024-08-16 17:00
74 | Kabirpur | 321 | 2024-08-27 19:00
75 | Kachua | 86 | 2024-08-15 04:00
76 | Kallyanpur | 129 | 2024-08-30 23:00
77 | Kalurghat | 40 | 2024-08-28 13:00
78 | Kamrangirchar | 55.2 | 2024-08-28 13:00
79 | Kaptai | N/A | N/A
80 | Kazla | 115 | 2024-08-29 12:00
81 | Keranigonj | 88 | 2024-08-10 22:00
82 | Khagrachori | 36 | 2024-08-31 19:00
83 | Khulna | 81 | 2024-08-30 12:00
84 | Khulshi | 168 | 2024-08-13 14:00
85 | Kishoreganj | 164 | 2024-08-27 19:30
86 | Kodda | 299 | 2024-08-20 21:00
87 | Kulaura | 60 | 2024-08-30 20:00
88 | Kurigram | 72 | 2024-08-12 19:30
89 | Kushtia | 160 | 2024-08-31 19:30
90 | Lalbag | 88 | 2024-08-30 00:00
91 | Lalmonirhat | 66 | 2024-08-04 20:00
92 | MI_Cement | 18.3 | 2024-08-31 20:00
93 | Madanganj | 39 | 2024-08-01 00:00
94 | Madaripur | 116 | 2024-08-15 01:00
95 | Madartek | 98.28 | 2024-08-16 00:00
96 | Madunaghat | 58 | 2024-08-10 19:00
97 | Magura | 70 | 2024-08-24 19:30
98 | Mahasthangarh | 90 | 2024-08-01 00:00
99 | Manikganj | 137 | 2024-08-29 22:00
100 | Maniknagar | 67 | 2024-08-30 00:00
101 | Matarbari | 51 | 2024-08-12 22:00
102 | Matuail | 78 | 2024-08-13 10:00
103 | Millgate | 136 | 2024-08-03 12:00
104 | Mirpur | 150 | 2024-08-14 19:30
105 | Mirsorai | 9 | 2024-08-03 19:00
106 | Mirzapur | 61 | 2024-08-07 19:30
107 | Mithapukur | 72 | 2024-08-16 19:00
108 | Modern | 0 | 2024-08-01 00:00
109 | Mogbazar | 136.6 | 2024-08-15 14:00
110 | Mongla | 40 | 2024-08-08 12:00
111 | Motijheel | 43 | 2024-08-14 13:00
112 | Munshiganj | 117 | 2024-08-30 00:00
113 | Mymensingh | 249 | 2024-08-18 21:00
114 | Naogaon | 157 | 2024-08-01 00:00
115 | Narail | 63 | 2024-08-31 19:00
116 | Narinda | 79 | 2024-08-15 13:00
117 | Narshingdi | 180 | 2024-08-30 22:00
118 | Natore | 168 | 2024-08-13 19:00
119 | Nawabganj | 55.4 | 2024-08-14 19:30
120 | Netrakona | 139 | 2024-08-07 22:00
121 | New | 63 | 2024-08-14 11:00
122 | Niamatpur | 83 | 2024-08-10 21:00
123 | Noapara | 56 | 2024-08-28 19:00
124 | PHP | 10 | 2024-08-01 13:00
125 | Pabna | 132 | 2024-08-31 19:30
126 | Palashbari | 138 | 2024-08-31 23:00
127 | Panchagarh | 69 | 2024-08-25 19:00
128 | Patuakhali | 93.8 | 2024-08-07 01:00
129 | Payra | 58 | 2024-08-28 20:00
130 | Postogola | 58 | 2024-08-01 00:00
131 | Purbachal | 32 | 2024-08-29 15:00
132 | Purbasadipur | 140 | 2024-08-28 19:00
133 | Rahim | 45 | 2024-08-04 10:00
134 | Rajbari | 86 | 2024-08-29 22:00
135 | Rajendrapur | 116 | 2024-08-27 21:00
136 | Rajshahi | 145 | 2024-08-28 21:00
137 | Rajshahi-230 | 88 | 2024-08-20 11:00
138 | Ramganj | 120 | 2024-08-06 21:00
139 | Rampur | 40 | 2024-08-16 00:00
140 | Rangamati | 20 | 2024-08-15 19:00
141 | Rangpur | 152 | 2024-08-26 19:00
142 | Ruppur | 8.5 | 2024-08-11 18:30
143 | SSM | 16 | 2024-08-01 00:00
144 | Saidpur | 120 | 2024-08-28 19:00
145 | Satkhira | 130 | 2024-08-31 22:00
146 | Satmasjid | 117 | 2024-08-14 19:00
147 | Savar | 226 | 2024-08-24 12:00
148 | SevenRings | 17.58 | 2024-08-30 18:00
149 | ShahCement | 31 | 2024-08-28 18:00
150 | Shahjadpur | 90 | 2024-08-31 20:00
151 | Shahjibazar | 133 | 2024-08-11 21:00
152 | Shahmirpur | 59 | 2024-08-13 01:00
153 | Shariatpur | 92 | 2024-08-29 22:00
154 | Sherpur | 148 | 2024-08-24 00:00
155 | Shikalbaha | 32 | 2024-08-08 21:00
156 | Shikalbaha-230 | N/A | N/A
157 | Shitalakhya | 85.4 | 2024-08-29 16:00
158 | Sholosohor | 47 | 2024-08-14 15:00
159 | Shyampur | 178 | 2024-08-16 00:00
160 | Siddhirganj | 133 | 2024-08-28 11:00
161 | Sirajganj | 124 | 2024-08-29 21:00
162 | Sonargaon | 96 | 2024-08-01 00:00
163 | Sreemongol | 76 | 2024-08-01 00:00
164 | Sreepur | 117 | 2024-08-29 17:00
165 | Srinagar | 62.4 | 2024-08-05 11:00
166 | Sunamganj | 62 | 2024-08-17 23:00
167 | Sylhet | 54 | 2024-08-03 06:00
168 | Sylhet-132 | 151 | 2024-08-29 16:00
169 | TK | 60 | 2024-08-25 17:00
170 | Tangail | 200 | 2024-08-07 20:00
171 | Thakurgaon | 116 | 2024-08-18 19:30
172 | Tongi | 164 | 2024-08-31 11:00
173 | Ullahpara | 30 | 2024-08-06 19:00
174 | Ullon | 61 | 2024-08-15 00:00
175 | Uttara | 92 | 2024-08-14 13:00
176 | UttaraNew | 61 | 2024-08-14 23:00
177 | Zigatola | 96 | 2024-08-31 00:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: August 2024
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5209.47 | 2024-08-15 | 11:00
Chattogram | 1433.9 | 2024-08-13 | 14:00
Cumilla | 1344 | 2024-08-07 | 22:00
Mymensingh | 1210 | 2024-08-07 | 22:00
Sylhet | 619 | 2024-08-27 | 20:00
Khulna | 1813 | 2024-08-29 | 21:00
Barishal | 486 | 2024-08-14 | 22:00
Rajshahi | 1593.6 | 2024-08-01 | 0:00
Rangpu | 961 | 2024-08-21 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August 2024
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 400 | 2024-08-20 07:00 | 333 | 2024-08-25 06:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 406 | 2024-08-05 16:00 | 372 | 2024-08-31 15:00
4 | Bibiana | 400 | 401 | 2024-08-05 16:00 | 293 | 2024-08-05 22:00
5 | BIPTC | 400 | 408 | 2024-08-27 05:00 | 229 | 2024-08-31 20:00
6 | Bogura | 400 | 402 | 2024-08-13 17:00 | 353 | 2024-08-28 02:00
7 | Gopalganj | 400 | 405 | 2024-08-05 18:00 | 361 | 2024-08-09 02:00
8 | Kaliakoir | 400 | 383 | 2024-08-05 17:00 | 358 | 2024-08-26 12:00
9 | Madunaghat | 400 | 398 | 2024-08-30 19:00 | 380 | 2024-08-27 16:00
10 | Meghnaghat | 400 | 391 | 2024-08-05 17:00 | 376 | 2024-08-21 13:00
11 | Payra | 400 | 414 | 2024-08-02 08:00 | 340 | 2024-08-13 15:00
12 | Rahanpur | 400 | 410 | 2024-08-02 08:00 | 376 | 2024-08-28 01:00
13 | Rampal | 400 | 408 | 2024-08-02 05:00 | 328 | 2024-08-24 10:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 258 | 2024-08-03 23:00 | 215 | 2024-08-14 12:00
2 | AKSML | 230 | 242 | 2024-08-10 19:00 | 220 | 2024-08-20 14:00
3 | Aminbazar | 230 | 238 | 2024-08-31 02:00 | 233 | 2024-08-25 06:00
4 | Ashuganj | 230 | 239 | 2024-08-09 18:00 | 233 | 2024-08-25 06:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 234 | 2024-08-02 04:00 | 219 | 2024-08-08 23:00
7 | Barapukuria | 230 | 222 | 2024-08-13 17:00 | 289 | 2024-08-18 04:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 260 | 2024-08-04 05:00 | 224 | 2024-08-06 23:00
10 | Bheramara | 230 | 235 | 2024-08-02 06:00 | 231 | 2024-08-16 18:30
11 | Bhulta | 230 | 238 | 2024-08-05 16:00 | 219 | 2024-08-04 10:00
12 | Bibiana | 230 | 230 | 2024-08-05 09:00 | 218 | 2024-08-27 11:00
13 | BIPTC | 230 | 238 | 2024-08-02 06:00 | 221 | 2024-08-04 23:00
14 | Bogura | 230 | 231 | 2024-08-13 17:00 | 222 | 2024-08-29 07:00
15 | Bogura-400 | 230 | 232 | 2024-08-13 17:00 | 205 | 2024-08-28 02:00
16 | Borhanuddin | 230 | 244 | 2024-08-26 07:00 | 236 | 2024-08-11 13:00
17 | BSRM | 230 | 239 | 2024-08-14 20:00 | 221 | 2024-08-07 13:00
18 | Cumilla(N) | 230 | 234 | 2024-08-09 18:00 | 217 | 2024-08-27 11:00
19 | Faridpur | 230 | 239 | 2024-08-26 06:00 | 217 | 2024-08-06 21:00
20 | Fenchuganj | 230 | 255 | 2024-08-30 16:00 | 220 | 2024-08-25 04:00
21 | Ghorashal | 230 | 238 | 2024-08-02 01:00 | 223 | 2024-08-25 14:00
22 | Ghorashal-230 | 230 | 236 | 2024-08-05 16:00 | 217 | 2024-08-04 10:00
23 | Gopalganj | 230 | 239 | 2024-08-02 08:00 | 225 | 2024-08-29 23:00
24 | GPH | 230 | 255 | 2024-08-08 01:00 | 223 | 2024-08-27 21:00
25 | Haripur | 230 | 236 | 2024-08-05 17:00 | 217 | 2024-08-04 10:00
26 | Hasnabad | 230 | 236 | 2024-08-05 18:00 | 222 | 2024-08-29 02:00
27 | Hathazari | 230 | 241 | 2024-08-11 19:00 | 220 | 2024-08-28 00:00
28 | Ishurdi | 230 | 237 | 2024-08-02 17:00 | 223 | 2024-08-28 13:00
29 | Jhenaidah | 230 | 238 | 2024-08-26 10:00 | 213 | 2024-08-08 00:00
30 | Kaliakoir | 230 | 239 | 2024-08-05 18:00 | 225 | 2024-08-19 00:00
31 | Keranigonj | 230 | 235 | 2024-08-05 18:00 | 215 | 2024-08-27 11:00
32 | Khulna(S) | 230 | 236 | 2024-08-02 06:00 | 215 | 2024-08-31 19:00
33 | Madunaghat | 230 | 237 | 2024-08-25 20:00 | 222 | 2024-08-25 09:00
34 | Maniknagar | 230 | 237 | 2024-08-05 18:00 | 217 | 2024-08-04 10:00
35 | Meghnaghat | 230 | 244 | 2024-08-09 18:00 | 226 | 2024-08-20 13:00
36 | Meghnaghat-400 | 230 | 239 | 2024-08-05 17:00 | 221 | 2024-08-04 10:00
37 | Mirsorai | 230 | 239 | 2024-08-10 19:30 | 226 | 2024-08-27 04:00
38 | Rajshahi | 230 | 238 | 2024-08-13 17:00 | 220 | 2024-08-05 22:00
39 | Rampal | 230 | 234 | 2024-08-02 05:00 | 224 | 2024-08-21 15:00
40 | Rampur | 230 | N/A | N/A | N/A | N/A
41 | Rampura | 230 | 236 | 2024-08-02 08:00 | 230 | 2024-08-23 19:30
42 | Shikalbaha | 230 | 242 | 2024-08-11 19:00 | 220 | 2024-08-21 02:00
43 | Shyampur | 230 | 236 | 2024-08-05 18:00 | 217 | 2024-08-27 11:00
44 | Siddhirganj | 230 | 237 | 2024-08-09 18:00 | 220 | 2024-08-04 10:00
45 | Sirajgonj | 230 | 239 | 2024-08-02 18:00 | 226 | 2024-08-28 01:00
46 | Sreepur | 230 | 234 | 2024-08-02 08:00 | 216 | 2024-08-04 11:00
47 | Tongi | 230 | 237 | 2024-08-05 15:00 | 228 | 2024-08-21 01:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 138 | 2024-08-03 06:00 | 122 | 2024-08-14 12:00
2 | Agargaon | 132 | 140 | 2024-08-05 16:00 | 123 | 2024-08-14 12:00
3 | Agrabad | 132 | 138 | 2024-08-21 07:00 | 113 | 2024-08-10 12:00
4 | AKS | 132 | 136 | 2024-08-21 02:00 | 116 | 2024-08-10 06:00
5 | Aminbazar | 132 | 141 | 2024-08-05 16:00 | 137 | 2024-08-23 02:00
6 | Amnura | 132 | 140 | 2024-08-13 17:00 | 113 | 2024-08-10 11:00
7 | Ashuganj | 132 | 140 | 2024-08-02 18:30 | 130 | 2024-08-31 15:00
8 | Bagerhat | 132 | 139 | 2024-08-23 18:00 | 118 | 2024-08-07 22:00
9 | Bakulia | 132 | 139 | 2024-08-21 02:00 | 112 | 2024-08-27 09:00
10 | Banani | 132 | 138 | 2024-08-05 11:00 | 121 | 2024-08-15 15:00
11 | Bangabhaban | 132 | 139 | 2024-08-09 01:00 | 116 | 2024-08-01 11:00
12 | Barapukuria | 132 | 138 | 2024-08-13 17:00 | 112 | 2024-08-10 02:00
13 | Barguna | 132 | 140 | 2024-08-01 18:30 | 127 | 2024-08-12 22:00
14 | Barishal | 132 | 141 | 2024-08-01 07:00 | 128 | 2024-08-19 23:00
15 | Barishal-230 | 132 | 143 | 2024-08-02 06:00 | 127 | 2024-08-19 21:00
16 | Baroaulia | 132 | 139 | 2024-08-16 23:00 | 128 | 2024-08-03 12:00
17 | Baroirhat | 132 | 155 | 2024-08-07 10:00 | 113 | 2024-08-07 15:00
18 | Bashundhara | 132 | 140 | 2024-08-05 16:00 | 121 | 2024-08-04 10:00
19 | BashundharaCement | 132 | 135 | 2024-08-05 18:30 | 122 | 2024-08-04 09:00
20 | Beanibazar | 132 | 130 | 2024-08-15 23:00 | 111 | 2024-08-31 18:30
21 | Benapole | 132 | 138 | 2024-08-04 18:00 | 120 | 2024-08-07 23:00
22 | Bhaluka | 132 | 131 | 2024-08-03 01:00 | 125 | 2024-08-09 05:00
23 | Bhandaria | 132 | 140 | 2024-08-02 07:00 | 120 | 2024-08-28 22:00
24 | Bhangura | 132 | 139 | 2024-08-02 06:00 | 126 | 2024-08-27 15:00
25 | Bheramara | 132 | 137 | 2024-08-02 05:00 | 129 | 2024-08-27 23:00
26 | Bheramara(GK) | 132 | 138 | 2024-08-02 06:00 | 130 | 2024-08-08 23:00
27 | Bhulta | 132 | 129 | 2024-08-05 16:00 | 114 | 2024-08-04 10:00
28 | Bog-Sherpur | 132 | 137 | 2024-08-13 17:00 | 116 | 2024-08-28 01:00
29 | Bogura | 132 | 139 | 2024-08-21 02:00 | 122 | 2024-08-26 22:00
30 | Bogura-230 | 132 | 140 | 2024-08-13 17:00 | 123 | 2024-08-26 21:00
31 | Brahmanbaria | 132 | 135 | 2024-08-02 08:00 | 113 | 2024-08-19 09:00
32 | Cantonment | 132 | 167 | 2024-08-05 14:00 | 123 | 2024-08-14 12:00
33 | Chandpur | 132 | 141 | 2024-08-21 11:00 | 117 | 2024-08-08 00:00
34 | Chandraghona | 132 | 139 | 2024-08-04 21:00 | 130 | 2024-08-03 12:00
35 | Chapai | 132 | 137 | 2024-08-02 09:00 | 119 | 2024-08-31 19:00
36 | Charsaidpur | 132 | 136 | 2024-08-05 18:00 | 124 | 2024-08-03 12:00
37 | Chauddagram | 132 | 137 | 2024-08-21 14:00 | 118 | 2024-08-06 21:00
38 | Chhatak | 132 | 130 | 2024-08-16 00:00 | 115 | 2024-08-12 15:00
39 | Chowmuhani | 132 | 140 | 2024-08-21 13:00 | 113 | 2024-08-14 20:00
40 | Chuadanga | 132 | 140 | 2024-08-26 06:00 | 113 | 2024-08-31 19:00
41 | Coxsbazar | 132 | 132 | 2024-08-01 02:00 | 114 | 2024-08-06 23:00
42 | Cumilla(N) | 132 | 143 | 2024-08-30 22:00 | 124 | 2024-08-20 14:00
43 | Cumilla(S) | 132 | 137 | 2024-08-21 18:00 | 120 | 2024-08-26 12:00
44 | Daudkandi | 132 | 138 | 2024-08-28 23:00 | 113 | 2024-08-11 12:00
45 | Dhaka | 132 | 138 | 2024-08-02 06:00 | 122 | 2024-08-15 15:00
46 | Dhamrai | 132 | 137 | 2024-08-05 17:00 | 121 | 2024-08-20 12:00
47 | Dhanmondi | 132 | 138 | 2024-08-10 02:00 | 123 | 2024-08-14 12:00
48 | Dohazari | 132 | 136 | 2024-08-11 13:00 | 116 | 2024-08-17 12:00
49 | Faridpur | 132 | 135 | 2024-08-02 08:00 | 126 | 2024-08-07 23:00
50 | Fatullah | 132 | 137 | 2024-08-05 17:00 | 124 | 2024-08-27 11:00
51 | Fenchuganj | 132 | 134 | 2024-08-05 17:00 | 125 | 2024-08-31 18:30
52 | Feni | 132 | 137 | 2024-08-21 15:00 | 115 | 2024-08-04 15:00
53 | Ghatail | 132 | 132 | 2024-08-01 09:00 | 113 | 2024-08-16 15:00
54 | Ghorashal | 132 | 140 | 2024-08-02 18:30 | 130 | 2024-08-04 10:00
55 | Goalpara | 132 | 141 | 2024-08-23 18:00 | 135 | 2024-08-03 10:00
56 | Gollamari | 132 | 139 | 2024-08-02 05:00 | 126 | 2024-08-31 19:00
57 | Gopalganj | 132 | 136 | 2024-08-02 06:00 | 124 | 2024-08-09 23:00
58 | Gopalganj-400 | 132 | 136 | 2024-08-02 06:00 | 126 | 2024-08-29 23:00
59 | Gulshan | 132 | 137 | 2024-08-02 06:00 | 122 | 2024-08-14 12:00
60 | Halishahar | 132 | 140 | 2024-08-21 04:00 | 126 | 2024-08-31 14:00
61 | Haripur | 132 | 134 | 2024-08-05 16:00 | 122 | 2024-08-04 10:00
62 | HaripurSBU | 132 | 130 | 2024-08-26 09:00 | 122 | 2024-08-04 10:00
63 | Hasnabad | 132 | 138 | 2024-08-05 16:00 | 127 | 2024-08-04 10:00
64 | Hathazari | 132 | 141 | 2024-08-16 07:00 | 116 | 2024-08-14 04:00
65 | Ishurdi | 132 | 139 | 2024-08-02 06:00 | 113 | 2024-08-24 01:00
66 | Jaldhaka | 132 | 134 | 2024-08-13 17:00 | 108 | 2024-08-17 05:00
67 | Jamalpur | 132 | 140 | 2024-08-01 13:00 | 111 | 2024-08-11 22:00
68 | Jashore | 132 | 140 | 2024-08-02 06:00 | 118 | 2024-08-21 05:00
69 | Jhenaidah | 132 | 142 | 2024-08-26 06:00 | 124 | 2024-08-31 19:00
70 | Jhenaidah-230 | 132 | 143 | 2024-08-02 06:00 | 131 | 2024-08-22 01:00
71 | Joydebpur | 132 | 140 | 2024-08-04 18:00 | 123 | 2024-08-04 10:00
72 | Joypurhat | 132 | 134 | 2024-08-05 18:00 | 111 | 2024-08-14 08:00
73 | Juldah | 132 | 140 | 2024-08-21 03:00 | 127 | 2024-08-27 15:00
74 | Kabirpur | 132 | 140 | 2024-08-07 20:00 | 118 | 2024-08-20 12:00
75 | Kachua | 132 | 140 | 2024-08-19 13:00 | 119 | 2024-08-08 00:00
76 | Kaliakoir | 132 | 165 | 2024-08-09 08:00 | 156 | 2024-08-17 04:00
77 | Kallyanpur | 132 | 157 | 2024-08-20 19:00 | 129 | 2024-08-24 10:00
78 | Kalurghat | 132 | 140 | 2024-08-14 20:00 | 128 | 2024-08-03 12:00
79 | Kamrangirchar | 132 | 138 | 2024-08-05 18:00 | 122 | 2024-08-31 15:00
80 | Kaptai | 132 | N/A | N/A | N/A | N/A
81 | Kazla | 132 | 138 | 2024-08-24 00:00 | 120 | 2024-08-01 12:00
82 | Keranigonj | 132 | 139 | 2024-08-06 05:00 | 125 | 2024-08-27 11:00
83 | Khagrachori | 132 | 138 | 2024-08-14 20:00 | 113 | 2024-08-16 09:00
84 | Khulna | 132 | 140 | 2024-08-23 18:00 | 124 | 2024-08-08 00:00
85 | Khulna(S) | 132 | 141 | 2024-08-02 06:00 | 126 | 2024-08-31 19:00
86 | Khulshi | 132 | 138 | 2024-08-21 04:00 | 125 | 2024-08-31 14:00
87 | Kishoreganj | 132 | 132 | 2024-08-01 07:00 | 119 | 2024-08-31 15:00
88 | Kodda | 132 | 138 | 2024-08-08 10:00 | 115 | 2024-08-20 12:00
89 | KSRM | 132 | 139 | 2024-08-14 19:30 | 128 | 2024-08-07 14:00
90 | Kulaura | 132 | 133 | 2024-08-12 09:00 | 123 | 2024-08-29 00:00
91 | Kurigram | 132 | 134 | 2024-08-01 14:00 | 110 | 2024-08-12 19:00
92 | Kushtia | 132 | 139 | 2024-08-26 06:00 | 126 | 2024-08-29 19:00
93 | Lalbag | 132 | 137 | 2024-08-05 16:00 | 113 | 2024-08-07 23:00
94 | Lalmonirhat | 132 | 137 | 2024-08-01 14:00 | 108 | 2024-08-28 01:00
95 | Madanganj | 132 | 135 | 2024-08-05 18:00 | 113 | 2024-08-21 23:00
96 | Madaripur | 132 | 138 | 2024-08-08 05:00 | 125 | 2024-08-11 01:00
97 | Madartek | 132 | 138 | 2024-08-02 06:00 | 121 | 2024-08-15 15:00
98 | Madunaghat | 132 | 139 | 2024-08-11 19:30 | 128 | 2024-08-03 12:00
99 | Magura | 132 | 140 | 2024-08-02 18:00 | 121 | 2024-08-31 19:00
100 | Mahasthangarh | 132 | 137 | 2024-08-13 17:00 | 117 | 2024-08-28 01:00
101 | Manikganj | 132 | 134 | 2024-08-05 17:00 | 123 | 2024-08-08 23:00
102 | Maniknagar | 132 | 135 | 2024-08-05 16:00 | 110 | 2024-08-05 01:00
103 | Matarbari | 132 | 137 | 2024-08-21 02:00 | 113 | 2024-08-06 23:00
104 | Matuail | 132 | 136 | 2024-08-05 18:00 | 123 | 2024-08-27 11:00
105 | Millgate | 132 | 164 | 2024-08-09 02:00 | 113 | 2024-08-06 04:00
106 | Mirpur | 132 | 140 | 2024-08-05 18:00 | 125 | 2024-08-14 12:00
107 | Mirzapur | 132 | 131 | 2024-08-04 01:00 | 114 | 2024-08-04 08:00
108 | Mithapukur | 132 | 136 | 2024-08-13 17:00 | 115 | 2024-08-28 01:00
109 | MI_Cement | 132 | 137 | 2024-08-03 20:00 | 123 | 2024-08-27 11:00
110 | Modern | 132 | 139 | 2024-08-21 02:00 | 126 | 2024-08-03 12:00
111 | Mogbazar | 132 | 140 | 2024-08-02 08:00 | 111 | 2024-08-15 22:00
112 | Mongla | 132 | 138 | 2024-08-23 18:00 | 118 | 2024-08-08 00:00
113 | Motijheel | 132 | 135 | 2024-08-05 18:00 | 113 | 2024-08-26 08:00
114 | Munshiganj | 132 | 135 | 2024-08-05 16:00 | 129 | 2024-08-02 01:00
115 | Mymensingh | 132 | 136 | 2024-08-08 11:00 | 111 | 2024-08-28 19:30
116 | Naogaon | 132 | 135 | 2024-08-05 16:00 | 113 | 2024-08-28 01:00
117 | Narail | 132 | 141 | 2024-08-26 06:00 | 117 | 2024-08-17 00:00
118 | Narinda | 132 | 0 | 2024-08-01 00:00 | N/A | N/A
119 | Narshingdi | 132 | 129 | 2024-08-05 17:00 | 111 | 2024-08-30 10:00
120 | Natore | 132 | 160 | 2024-08-10 05:00 | 118 | 2024-08-18 08:00
121 | Nawabganj | 132 | 162 | 2024-08-10 06:00 | 124 | 2024-08-27 11:00
122 | Netrakona | 132 | 137 | 2024-08-11 13:00 | 114 | 2024-08-16 15:00
123 | New | 132 | 140 | 2024-08-05 18:00 | 123 | 2024-08-04 10:00
124 | Niamatpur | 132 | 138 | 2024-08-02 03:00 | 123 | 2024-08-31 21:00
125 | Noapara | 132 | 139 | 2024-08-04 18:00 | 119 | 2024-08-05 19:30
126 | Pabna | 132 | 138 | 2024-08-02 06:00 | 119 | 2024-08-28 15:00
127 | Palashbari | 132 | 135 | 2024-08-01 14:00 | 112 | 2024-08-27 16:00
128 | Panchagarh | 132 | 141 | 2024-08-13 17:00 | 108 | 2024-08-27 05:00
129 | Patuakhali | 132 | 138 | 2024-08-19 20:00 | 128 | 2024-08-06 22:00
130 | Payra | 132 | 139 | 2024-08-22 08:00 | 113 | 2024-08-06 00:00
131 | PHP | 132 | 137 | 2024-08-21 14:00 | 112 | 2024-08-07 12:00
132 | Postogola | 132 | 139 | 2024-08-05 18:00 | 126 | 2024-08-27 11:00
133 | Purbachal | 132 | 139 | 2024-08-05 18:00 | 121 | 2024-08-15 15:00
134 | Purbasadipur | 132 | 136 | 2024-08-13 17:00 | 107 | 2024-08-27 05:00
135 | Rahanpur | 132 | 139 | 2024-08-02 04:00 | 126 | 2024-08-31 21:00
136 | Rahim | 132 | 132 | 2024-08-05 03:00 | 122 | 2024-08-04 10:00
137 | Rajbari | 132 | 135 | 2024-08-02 06:00 | 125 | 2024-08-06 23:00
138 | Rajendrapur | 132 | 138 | 2024-08-09 19:00 | 116 | 2024-08-20 12:00
139 | Rajshahi | 132 | 136 | 2024-08-02 06:00 | 126 | 2024-08-06 21:00
140 | Rajshahi-230 | 132 | 150 | 2024-08-17 11:00 | 114 | 2024-08-30 00:00
141 | Ramganj | 132 | 139 | 2024-08-22 12:00 | 110 | 2024-08-23 00:00
142 | Rampur | 132 | 138 | 2024-08-21 04:00 | 126 | 2024-08-27 14:00
143 | Rampura | 132 | 138 | 2024-08-02 08:00 | 122 | 2024-08-15 12:00
144 | Rangamati | 132 | 139 | 2024-08-21 04:00 | 128 | 2024-08-27 15:00
145 | Rangpur | 132 | 140 | 2024-08-01 14:00 | 112 | 2024-08-06 10:00
146 | Ruppur | 132 | 139 | 2024-08-02 06:00 | 113 | 2024-08-13 14:00
147 | Saidpur | 132 | 155 | 2024-08-02 10:00 | 110 | 2024-08-27 05:00
148 | Satkhira | 132 | 138 | 2024-08-02 05:00 | 112 | 2024-08-27 14:00
149 | Satmasjid | 132 | 140 | 2024-08-05 16:00 | 122 | 2024-08-31 12:00
150 | Savar | 132 | 139 | 2024-08-03 20:00 | 123 | 2024-08-27 11:00
151 | SevenRings | 132 | 141 | 2024-08-05 16:00 | 128 | 2024-08-04 10:00
152 | ShahCement | 132 | 136 | 2024-08-05 18:00 | 124 | 2024-08-03 12:00
153 | Shahjadpur | 132 | 141 | 2024-08-21 04:00 | 120 | 2024-08-28 13:00
154 | Shahjibazar | 132 | 133 | 2024-08-08 09:00 | 119 | 2024-08-29 00:00
155 | Shahmirpur | 132 | 139 | 2024-08-11 19:00 | 128 | 2024-08-03 11:00
156 | Shariatpur | 132 | 136 | 2024-08-01 18:30 | 123 | 2024-08-29 23:00
157 | Sherpur | 132 | 138 | 2024-08-01 14:00 | 112 | 2024-08-16 10:00
158 | Shikalbaha | 132 | 128 | 2024-08-21 19:30 | 116 | 2024-08-27 14:00
159 | Shikalbaha-230 | 132 | 140 | 2024-08-21 03:00 | 108 | 2024-08-10 06:00
160 | Shitalakhya | 132 | 137 | 2024-08-03 20:00 | 123 | 2024-08-27 11:00
161 | Sholosohor | 132 | 143 | 2024-08-21 01:00 | 135 | 2024-08-17 07:00
162 | Shyampur | 132 | 137 | 2024-08-05 17:00 | 130 | 2024-08-09 02:00
163 | Shyampur-230 | 132 | 138 | 2024-08-06 07:00 | 123 | 2024-08-14 12:00
164 | Siddhirganj | 132 | 135 | 2024-08-05 18:00 | 124 | 2024-08-04 10:00
165 | Sirajganj | 132 | 137 | 2024-08-23 18:00 | 113 | 2024-08-26 22:00
166 | Sonargaon | 132 | 134 | 2024-08-16 17:00 | 112 | 2024-08-02 01:00
167 | Sreemongol | 132 | 132 | 2024-08-21 06:00 | 120 | 2024-08-27 23:00
168 | Sreepur | 132 | 133 | 2024-08-05 16:00 | 120 | 2024-08-31 15:00
169 | Srinagar | 132 | 137 | 2024-08-09 18:00 | 125 | 2024-08-04 12:00
170 | SSM | 132 | 147 | 2024-08-16 21:00 | 129 | 2024-08-03 16:00
171 | Sunamganj | 132 | 133 | 2024-08-30 20:00 | 111 | 2024-08-31 18:30
172 | Sylhet | 132 | 131 | 2024-08-16 00:00 | 115 | 2024-08-31 18:30
173 | Sylhet-132 | 132 | 129 | 2024-08-12 08:00 | 115 | 2024-08-31 18:30
174 | Tangail | 132 | 130 | 2024-08-01 19:00 | 112 | 2024-08-12 23:00
175 | Thakurgaon | 132 | 140 | 2024-08-13 17:00 | 104 | 2024-08-27 05:00
176 | TK | 132 | 138 | 2024-08-14 19:00 | 113 | 2024-08-06 19:30
177 | Tongi | 132 | 140 | 2024-08-05 15:00 | 124 | 2024-08-03 09:00
178 | Ullahpara | 132 | 139 | 2024-08-23 18:00 | 116 | 2024-08-28 08:00
179 | Ullon | 132 | 138 | 2024-08-02 08:00 | 122 | 2024-08-15 13:00
180 | Uttara | 132 | 141 | 2024-08-05 15:00 | 125 | 2024-08-14 12:00
181 | UttaraNew | 132 | 140 | 2024-08-05 16:00 | 125 | 2024-08-14 12:00
182 | Zigatola | 132 | 138 | 2024-08-05 17:00 | 113 | 2024-08-04 00:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: August 2024
Substation | transformer | voltage_level | Date | Hour | MW(LT) | MVAR(LT)
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 25-08-2024 | 07:00 | 479 | 234
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 25-08-2024 | 07:00 | 479 | 234
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 31-08-2024 | 12:00 | 180 | 82
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 04-08-2024 | 07:00 | -244 | -97
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 04-08-2024 | 07:00 | -244 | -97
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 04-08-2024 | 23:00 | -197 | -15
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 04-08-2024 | 23:00 | -197 | -15
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 12-08-2024 | 18:00 | 444 | 13
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 28-08-2024 | 07:00 | 589 | 62
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 12-08-2024 | 18:00 | 444 | 13
Gopalganj 400/132kV Grid Sub-Station | ATR-04 | 400/230 | 19-08-2024 | 19:00 | -183 | -30
Gopalganj 400/132kV Grid Sub-Station | ATR-05 | 400/230 | 19-08-2024 | 19:00 | -183 | -30
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 30-08-2024 | 21:00 | -141 | -14
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 30-08-2024 | 21:00 | -141 | -14
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 30-08-2024 | 21:00 | -141 | -14
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 06-08-2024 | 08:00 | 190 | 92
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 06-08-2024 | 08:00 | 190 | 92
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 04-08-2024 | 06:00 | 297 | 38
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 04-08-2024 | 06:00 | 297 | 38
Meghnaghat 400/230kV Grid Sub-Station | ATR - 2 | 400/230 | 28-08-2024 | 08:00 | -465 | -233
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 28-08-2024 | 08:00 | -465 | -233
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 17-08-2024 | 21:00 | -392.18 | -53.65
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 29-08-2024 | 19:00 | -552 | -50
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 12-08-2024 | 22:00 | -64 | -25
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 12-08-2024 | 22:00 | -64 | -25
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 01-08-2024 | 00:00 | 165 | 65
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 01-08-2024 | 00:00 | 165 | 65
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Date | Hour | MW(LT) | MVAR(LT)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 31-08-2024 | 12:00 | 259 | 104
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 26-08-2024 | 14:00 | 222 | 48
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 07-08-2024 | 11:00 | 138 | 46
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 07-08-2024 | 11:00 | 138 | 46
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 14-08-2024 | 11:00 | 138 | 38
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 30-08-2024 | 18:00 | 270 | 140
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 31-08-2024 | 15:00 | 220 | 65
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 04-08-2024 | 23:00 | -197 | -15
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 02-08-2024 | 07:00 | -112 | 5
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 16-08-2024 | 20:00 | 198 | 24
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 16-08-2024 | 20:00 | 176 | 58
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 16-08-2024 | 20:00 | 229 | 46
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 13-08-2024 | 20:00 | 133 | 66
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 13-08-2024 | 20:00 | 133 | 66
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 03-08-2024 | 13:00 | 134 | -29
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 03-08-2024 | 13:00 | 82 | -29
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 28-08-2024 | 04:00 | 154 | 43
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 28-08-2024 | 04:00 | 154 | 43
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 28-08-2024 | 04:00 | 209 | 50
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 28-08-2024 | 04:00 | 209 | 50
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 04-08-2024 | 23:00 | 168 | 68
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 14-08-2024 | 04:00 | 167 | 71
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 04-08-2024 | 23:00 | 182 | 74
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 30-08-2024 | 22:00 | 173 | 74
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 30-08-2024 | 22:00 | 205 | 94
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 08-08-2024 | 03:00 | 103 | 0
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 08-08-2024 | 03:00 | 103 | 0
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 04-08-2024 | 06:00 | 100 | 15
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 04-08-2024 | 04:00 | 120 | 20
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 04-08-2024 | 04:00 | 110 | 15
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 31-08-2024 | 10:00 | 78 | 65
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 01-08-2024 | 00:00 | 72 | 52
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 31-08-2024 | 10:00 | 78 | 65
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 29-08-2024 | 14:00 | 109 | 39
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 29-08-2024 | 14:00 | 109 | 39
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 29-08-2024 | 14:00 | 109 | 39
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 29-08-2024 | 14:00 | 109 | 39
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 25-08-2024 | 19:00 | 83 | 42
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 25-08-2024 | 19:00 | 83 | 42
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 25-08-2024 | 19:00 | 83 | 42
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 07-08-2024 | 21:00 | 181 | -95
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 12-08-2024 | 19:30 | -199 | -84
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 09-08-2024 | 17:00 | 171 | 21
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 30-08-2024 | 00:00 | 108 | 31
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 30-08-2024 | 00:00 | 108 | 31
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 30-08-2024 | 00:00 | 108 | 31
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 17-08-2024 | 19:30 | -143 | -29
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 17-08-2024 | 19:30 | -143 | -29
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 17-08-2024 | 19:30 | -184 | -31
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 01-08-2024 | 11:00 | 274 | 160
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 18-08-2024 | 21:00 | 226 | 38
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 01-08-2024 | 09:00 | -76 | -9
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 01-08-2024 | 09:00 | -76 | -9
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 28-08-2024 | 13:00 | -123 | -21
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 01-08-2024 | 08:00 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 01-08-2024 | 01:00 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 15-08-2024 | 13:00 | 381 | 67
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 | 230/132 | 15-08-2024 | 13:00 | 381 | 67
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 14-08-2024 | 18:30 | 18 | 5
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 14-08-2024 | 18:30 | 18 | 5
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 15-08-2024 | 19:30 | 215 | 136
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 15-08-2024 | 19:30 | 215 | 136
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 11-08-2024 | 07:00 | 138 | 140
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 11-08-2024 | 07:00 | 138 | 140
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 12-08-2024 | 18:30 | 194 | 62
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 28-08-2024 | 18:30 | 193 | 68
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 12-08-2024 | 18:30 | 194 | 62
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 28-08-2024 | 18:30 | 193 | 68
Executive Engineer
Information Management Division
|  |  |  | LDC, PGCB, Dhaka. |  |  | 270

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: August 2024 | [5 empty] | (For Evening Peak) | [8 empty] | Month: August 2024 | [5 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2024-08-01 | 12374 | 12374 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-08-01 | 12249 | 12650 | 383 | 12:00 | 160 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 157 | -
2024-08-02 | 11816 | 11816 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-08-02 | 10003 | 10003 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-03 | 13370 | 13370 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-08-03 | 11437 | 11489 | 50 | 12:00 | 40 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | -
2024-08-04 | 12949 | 13090 | 135 | 21:00 | 80 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 28 | - | 2024-08-04 | 12542 | 12620 | 79 | 12:00 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-05 | 12059 | 12059 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-08-05 | 10439 | 10439 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-06 | 13064 | 13064 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-08-06 | 11098 | 11098 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-07 | 13790 | 13740 | 48 | 21:00 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-08-07 | 12249 | 12450 | 192 | 12:00 | 105 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | -
2024-08-08 | 13746 | 13790 | 157 | 21:00 | 130 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | - | 2024-08-08 | 12555 | 12800 | 234 | 12:00 | 200 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | -
2024-08-09 | 13251 | 13380 | 123 | 21:00 | 30 | 0 | 0 | 0 | 15 | 40 | 0 | 0 | 38 | - | 2024-08-09 | 11034 | 11100 | 63 | 12:00 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-10 | 13972 | 14130 | 151 | 21:00 | 71 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | - | 2024-08-10 | 11950 | 12270 | 306 | 12:00 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-11 | 14167 | 14500 | 318 | 21:00 | 118 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | - | 2024-08-11 | 12782 | 12930 | 141 | 12:00 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-12 | 14219 | 14550 | 316 | 20:00 | 40 | 0 | 0 | 0 | 20 | 205 | 0 | 0 | 51 | - | 2024-08-12 | 12880 | 13210 | 315 | 12:00 | 220 | 0 | 0 | 0 | 33 | 62 | 0 | 0 | 0 | -
2024-08-13 | 13982 | 15000 | 972 | 19:30 | 320 | 0 | 0 | 105 | 165 | 187 | 90 | 0 | 105 | - | 2024-08-13 | 12802 | 13550 | 557 | 12:00 | 320 | 0 | 0 | 0 | 142 | 55 | 40 | 0 | 0 | -
2024-08-14 | 14389 | 15450 | 1013 | 21:00 | 130 | 0 | 160 | 163 | 180 | 180 | 80 | 0 | 120 | - | 2024-08-14 | 13188 | 14100 | 871 | 12:00 | 391 | 0 | 0 | 70 | 150 | 110 | 75 | 0 | 75 | -
2024-08-15 | 14198 | 15530 | 1272 | 21:00 | 380 | 0 | 180 | 134 | 137 | 224 | 105 | 0 | 112 | - | 2024-08-15 | 13449 | 14200 | 715 | 12:00 | 290 | 0 | 0 | 76 | 86 | 176 | 46 | 0 | 41 | -
2024-08-16 | 13570 | 13725 | 148 | 21:00 | 20 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 20 | - | 2024-08-16 | 12075 | 12075 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-17 | 13635 | 14060 | 406 | 21:00 | 95 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 90 | - | 2024-08-17 | 11882 | 12100 | 208 | 12:00 | 53 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 65 | -
2024-08-18 | 13903 | 14250 | 331 | 20:00 | 111 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 95 | - | 2024-08-18 | 12471 | 12630 | 152 | 12:00 | 105 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | -
2024-08-19 | 13322 | 13450 | 122 | 21:00 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 87 | - | 2024-08-19 | 12123 | 12200 | 74 | 12:00 | 60 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | -
2024-08-20 | 13890 | 13800 | 45 | 21:00 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-08-20 | 11860 | 11920 | 57 | 12:00 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-21 | 13497 | 13576 | 75 | 19:30 | 60 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | - | 2024-08-21 | 11898 | 11970 | 69 | 12:00 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-22 | 13009 | 13040 | 30 | 19:30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-08-22 | 11704 | 11704 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-23 | 12512 | 12545 | 32 | 21:00 | 0 | 0 | 0 | 0 | 5 | 27 | 0 | 0 | 0 | - | 2024-08-23 | 10406 | 10406 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-24 | 13710 | 14100 | 372 | 19:30 | 100 | 0 | 0 | 0 | 30 | 125 | 0 | 0 | 117 | - | 2024-08-24 | 11729 | 11760 | 30 | 12:00 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-25 | 12861 | 11902 | 371 | 19:00 | 160 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 111 | - | 2024-08-25 | 11902 | 11980 | 74 | 12:00 | 40 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | -
2024-08-26 | 13033 | 13225 | 183 | 20:00 | 60 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 43 | - | 2024-08-26 | 11031 | 11090 | 56 | 12:00 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-08-27 | 13827 | 14220 | 375 | 19:30 | 111 | 0 | 0 | 0 | 12 | 120 | 7 | 0 | 125 | - | 2024-08-27 | 11888 | 12600 | 78 | 12:00 | 53 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | -
2024-08-28 | 13957 | 14470 | 490 | 21:00 | 130 | 0 | 0 | 0 | 20 | 190 | 20 | 0 | 130 | - | 2024-08-28 | 12799 | 13020 | 211 | 12:00 | 95 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 26 | -
2024-08-29 | 14388 | 15000 | 584 | 20:00 | 154 | 0 | 0 | 0 | 20 | 190 | 90 | 0 | 130 |  | 2024-08-29 | 12673 | 11825 | 742 | 12:00 | 382 | 0 | 0 | 50 | 0 | 180 | 75 | 0 | 55
2024-08-30 | 13793 | 14150 | 341 | 21:00 | 25 | 0 | 0 | 0 | 25 | 130 | 25 | 0 | 136 |  | 2024-08-30 | 12219 | 12450 | 221 | 12:00 | 115 | 0 | 0 | 0 | 16 | 90 | 0 | 0 | 0
2024-08-31 | 14612 | 15300 | 657 | 19:30 | 155 | 0 | 0 | 0 | 10 | 245 | 127 | 0 | 120 |  | 2024-08-31 | 12809 | 13250 | 421 | 12:00 | 260 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: August 2024
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | [11 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
9 | Meghnaghat CCPP(Summit) | IPP | 335
10 | Ashuganj 225 MW CCPP | APSCL | 221 |  |  |  |  | √ | √ | √ | √
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361 |  |  | √ | √ | √
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360 |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400 | [9 empty] | √ | √ | √
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: August 2024
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 14612 | 2024-08-31 | 19:30
2 | Maximum Day Peak Genaration | MW | 13449 | 2024-08-15 | 12:00
3 | Maximum Evening Peak Demand | MW | 15530 | 2024-08-31 | 19:30
4 | Minimum Generation | MW | 9444 | 2024-08-03 | 6:00
5 | Average of the daily evening peak Genaration | MW | 13511.7742 | - | -
6 | Average of the daily day peak Genaration | MW | 12004.0645 | - | -
7 | Maximum load shed (Evening Peak) | MW | 1272 | 2024-08-15 | 21:00
8 | Minimum load shed | MW | 0 | 2024-08-02 | 21:00
9 | Total nos. of load shed days | Day | 26 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 292.4839 | - | -
11 | Total Generation | MkWh | 9177.3 | - | -
12 | Total Generation by BPDB | MkWh | 1275.7689 | % of total Gen. | 13.9%
13 | Total Generation by IPP | MkWh | 3277.01 | '' | 35.71%
14 | A) Total Generation by Generation Companies | MkWh | 3001.2757 | '' | 32.7%
| B) Total Generation by REB | MkWh | 76.5989 | " | 0.8347%
| C) Total Generation by RENTAL | MkWh | 115.2578 | " | 1.256%
| D) Total Imported from India (BIPTC) | MkWh | 660.085 | " | 7.193%
| E) Total Imported from Tripura, India (A.C) | MkWh | 49.0589 | " | 0.5346%
| F) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 722.2414 |  | 7.87%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3879.5447 | % of total Gen. | 42.27%
| B) Oil | MkWh | 1199.8066 | '' | 13.07%
| C) Hydro | MkWh | 155.7384 | '' | 1.697%
| D) Solar | MkWh | 80.6135 | '' | 0.8784%
| E) Coal | MkWh | 2415.8978 | '' | 26.32%
| F) BIPTC (Import from India) | MkWh | 660.085 | '' | 7.193%
| G) A.C (Import from Tripura, India) | MkWh | 49.0589 | '' | 0.5346%
| H) Adani (Import from India) | MkWh | 722.2414 | '' | 7.87%
| I) Wind | MkWh | 14.3154 | '' | 0.156%
16 | Maximun of the daily total Generation . | MkWh | 324.9324 | 2024-08-15
17 | Monthly Load factor | % | 82.4411 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 5686.5499 | - | -
| A) Gas | M.Taka | 555.94 | - | -
| B) Liquid fuel | M.Taka | 1251.2744 | - | -
| C) Coal | M.Taka | 761.3389 | - | -
| D) BIPTC (Import from India) | M.Taka | 2693.1467 | - | -
| E) Tripura(Import from India) | M.Taka | 424.8499 | - | -
| F) Adani (Import from India) | M.Taka | 5113.4692 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2313.4058 | 2024-08-08
| A) Gas | M.Taka | 555.94 | 2024-08-01
| B) Liquid fuel | M.Taka | 1251.2744 | 2024-08-08
| C) Coal | M.Taka | 761.3389 | 2024-08-22
| D) BIPTC (Import from India) | M.Taka | 95.0299 | 2024-08-03
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 0.61963
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 0.63703
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 98.67 | 31/08/2024 | 06:00
b) | Actual | FT (MSL) | 108.79 | 31/08/2024 | 06:00
22 | Peak Genaration of August 2023 | MW | 14889 | 2023-08-30 | 21:00
23 | Peak Demand of August 2023 | MW | 14889 | 2023-08-30 | 21:00
24 | Maximum peak Generation recorded upto 31/08/2024 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 31/08/2024 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/08/2024 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable | [5 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable | [5 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable |  |  |  | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable |  |  |  | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable |  |  |  | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant