## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-11-19 | Tuesday
|  | Date (day): | 2024-11-19 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12768.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13158 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-11-18 | 2024-11-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint. |  | 2024-11-17
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 288 | 220 | 220 |  |  | GT-1 Under S/D
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 13 |  | 62 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 8 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 36 | 35 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 115 | 149 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 17 | 35 | 20 |  | Fuel shortage
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 22 | 42 | 47 | 47 |  | 33 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 17 | 25 | 25 |  | 8 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 25 | 25 | 27 |  | Fuel shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 36 | 62 | 96 | 53 |  | Fuel shortage
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 52 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 13 | 0 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 144 | 162 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 18 | 36 | 36 | 36 |  | 19 | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 240 | 240 | 235 | 235 | 349 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 150 | 150 | 433 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1527 | 1879 | 2464 | 2605 | 1856 | 1282
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 10 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 1 | 25 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 95 | 80 | 96 | 96 | 134 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 224 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 46 | 85 | 85 | 20 |  | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 8 | 70 | 70 |  | 28 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 65 | 84 |  | 18 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 75 | 12 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 2 | 5 | 15
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 19 | 38 | 44 | 64 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 87 | 50 | 50 | 250 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 35 | 35 | 19 |  | Fuel shortage
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 48 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 50 | 25 | 50 | 50 |  | Fuel shortage
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 3 | 32 | 35 | 35 | 81 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 160 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 575 | 612 | 612 | 612 |  | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 5 | 15 | 15 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 0 | 0 | 0 | 0 | 1150 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 950 | 1571 | 1578 | 1861 | 1948 | 988
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 181 | 200 | 220 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 310 | 330 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  |  | Under maint.
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 36 | 44 | 44
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 185 | 185 | 195 | 195
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 80 | 90 | 120 | 30 |  | Fuel shortage
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 30 | 44 |  | 8 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 218 | 100 | 200 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 56 | 60 | 66 | 82
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 12 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 106 | 106 |  | 8 | Engine problem
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 92 | 100 | 100 |  | 13 | Engine problem
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 47 | 92 | 92 |  | 23 | Engine problem
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 72 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1166 | 1268 | 1674 | 1704 | 198 | 419
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 26 | 29 | 30 | 30 | 172 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 96 | 96 | 96 | 104 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 12 | 54 | 54 | 57 | 58 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 24 | 6 | 24
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 28 | 17 | 35 | 19 |  | Fuel shortage
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 9 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 149 | 231 | 254.6 | 242 | 172 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 27 | 27 | 28 | 28 |  | 42 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 29 | 30 | 30 |  | 60 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint. |  | 2024-11-20
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract Expired
90 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 33 | 30 | 33 | 35 | 15 |  | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 2 | 5 | 5 |  | 6 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 61 | 60 | 62
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86
94 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
95 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 133 | 131 | 130 | 130 |  | 101 | Partial Shutdown due to maintenance
96 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
97 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 13 | 13 |  | 12 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 310 | 310 |  |  | FGMO
99 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 385 | 385 | 385 |  |  | FGMO
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
100 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 346 | 345 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1422 | 1419 | 1480 | 1484 | 35 | 714
101 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 909 | 898 | 914 | 914
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 35 |  | 19 | Engine problem
103 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 60 |  | 49 | Engine problem
105 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 324 | 290 | 320 | 350 | 60 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
107 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 75 | 0 | 100 | 0
109 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
110 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 370 | 370 | 370 | 370 | 864 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
** | Nepal |  | 0 | Imported power | 40 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1678 | 1558 | 1754 | 1729 | 1275 | 68
111 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 16 | 94 |  | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 4 | 6 | 10 | 10
113 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 127 | 123 | 127 | 127 |  | 67 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 570 | 590 | 622 | 622 |  | 622 | Unit-2 S/D.
115 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
116 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 7 | 150 | 54 | 150
117 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  | 307 | Under maint
118 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 928 | 1089 | 1033 | 1145 | 94 | 996
119 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 40 |  | 12 | Engine problem
121 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 28 |  | 43 | Engine problem
122 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 26 | 30 |  | 20 | Engine problem
124 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 176 | 162 | 175 | 175 | 35 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 172 | 170 | 170 | 50 |  | Gas shortage
126 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 362 | 414 | 414 | 414 |  |  | FGMO
128 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 11
130 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 60 | 50 | 96 |  | 8 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113
133 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
134 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 616 | 715 | 765 | 765
135 | Sirajganj 68 MW Solar Park |  | Solar | NWPGCL | 68 | 68 | 68 | 53 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 94 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1467 | 1617 | 1943 | 1985 | 528 | 103
136 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 64 | 67 | 65 | 65 |  | 20 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
137 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 111 | 103 | 110 | 110 |  | 164 | Machine problem
138 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
140 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 39 | 90 | 113
141 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
142 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 93 | 115 | 115
143 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 30 | 0
144 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 178 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 417 | 302 | 588 | 403 | 40 | 269
| Total |  |  |  |  | 27791 | 27086 | 9704 | 10934 | 12768.6 | 13158 | 6146 | 4839
A. |  | 2024-11-18 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 10934 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7425 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10934 | MW
3 | Day peak Generation : |  |  | 9704 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10759.01 | MW
4 | Evening peak Generation : |  |  | 10934 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 223.3826 | MKWHr | By Solar | 3.7197 | MKWHr
| By Gas : | 123.9435 | MKWHr |  | By Oil: | 15.7567 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 39.8435 | MKWHr |  | By Hydro: | 2.1103 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 14.8909 | MKWHr |  | By Wind: | 0.07056 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6146 | MW | Dhaka | 4262.71 | 4262.71 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4839 | MW | Chittagong | 1096.5 | 1096.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10985 | MW | Khulna | 1144.4 | 1144.4 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 907.34 | MMCFD | **Import Adani: | Taka | 98428908.49 | Rajshahi | 962.4 | 962.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : |  | 361379198.242 | ii) Oil : | Taka | 280413457.81 | Comilla | 955 | 955 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 284505342.13 | Total | Taka | 1024726906.672 | Mymensingh | 890 | 890 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 12264.45 | MKWHr. | Sylhet | 426 | 426 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1076 | MW (W to E) at | 18:00 | hrs | Barisal | 293 | 293 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 1028 | MW at | 18:30 | hrs | Rangpur | 729 | 729 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.1°C |  |  | Total | 10759.01 | 10759.01 |  | 0
B. |  | 2024-11-19 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 30.1°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13158 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
4 | Reserve(Generation end) |  |  |  | 2058 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 226.774 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7562 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector(India) : |  |  |  |  | i) Energy | 21.8349 | MKWHr. | ii) HVDC Flow at Peak Time |  | 898 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.2125 | MKWHr. | iii) Maximum HVDC Flow : |  | 911 | MW at | 11:00 | hrs.
* Import Through HVDC C/B Interconnector(Nepal) : |  |  |  |  | i) Energy | 0 | MKWHr.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 98.02 |  | (b) Today: | 97.87 |  | (c) Rule Curve: |  | 107.2
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-11-18 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | Nepal | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Nepal | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 311 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 17 | 33 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 290 | 0 | 182 | 199 | 70 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 54 | 35 | 0 | 0 | 0 | 27 | 30 | 0 | 21 | 0 | 0 | 61 | 86 | 0 | 136 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535 | 2 | 0 | 235 | 0 | 0 | 0 | 0 |  | 907 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 69 | 0 | 132 | 0 | 0 | 174 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 611 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4590 | 3905 | 8495 | 2925 | 907 | 0 | 2213 | 0 | 40 | 1653 | 90 | 0 | 0 | 54 | 611 | 0 | 2 | 0 | 98.04
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 312 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 17 | 33 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 300 | 0 | 190 | 199 | 72 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 48 | 45 | 0 | 0 | 0 | 27 | 30 | 0 | 33 | 0 | 0 | 61 | 86 | 0 | 137 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 239 | 0 | 0 | 0 | 0 |  | 908 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 69 | 0 | 135 | 0 | 0 | 175 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4431 | 3602 | 8033 | 2961 | 908 | 0 | 2187 | 0 | 0 | 1412 | 89 | 0 | 0 | 48 | 428 | 0 | 0 | 0 | 98.04
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 297 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 33 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 290 | 0 | 181 | 199 | 70 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 67 | 0 | 0 | 0 | 27 | 30 | 0 | 34 | 0 | 0 | 61 | 86 | 0 | 137 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 240 | 0 | 0 | 0 | 0 |  | 907 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 69 | 0 | 134 | 0 | 0 | 176 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4385 | 3483 | 7868 | 2955 | 907 | 0 | 2147 | 0 | 0 | 1303 | 88 | 0 | 0 | 50 | 418 | 0 | 0 | 0 | 98.03
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 350 | 270 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 33 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 295 | 0 | 186 | 108 | 70 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 44 | 67 | 0 | 0 | 0 | 27 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 137 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 226 | 0 | 0 | 0 | 0 |  | 908 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 70 | 0 | 137 | 0 | 0 | 175 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4120 | 3417 | 7537 | 2804 | 908 | 0 | 1998 | 0 | 0 | 1277 | 86 | 0 | 0 | 44 | 420 | 0 | 0 | 0 | 98.03
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 350 | 273 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 33 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 300 | 0 | 188 | 108 | 80 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 48 | 67 | 0 | 0 | 0 | 27 | 30 | 0 | 5 | 0 | 0 | 62 | 41 | 0 | 137 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 226 | 0 | 0 | 0 | 0 |  | 907 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 70 | 0 | 136 | 0 | 0 | 175 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4011 | 3414 | 7425 | 2753 | 907 | 0 | 1934 | 0 | 0 | 1277 | 85 | 0 | 0 | 48 | 421 | 0 | 0 | 0 | 98.02
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 380 | 278 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 22 | 17 | 33 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 310 | 0 | 191 | 150 | 80 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 66 | 0 | 0 | 0 | 27 | 30 | 0 | 5 | 0 | 0 | 62 | 41 | 0 | 137 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 229 | 0 | 0 | 0 | 0 |  | 907 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 69 | 0 | 136 | 0 | 0 | 176 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4153 | 3571 | 7724 | 2917 | 907 | 0 | 2071 | 0 | 0 | 1276 | 85 | 0 | 0 | 48 | 420 | 0 | 0 | 0 | 98.02
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 420 | 287 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 17 | 33 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 345 | 0 | 205 | 185 | 90 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 46 | 66 | 0 | 0 | 0 | 27 | 30 | 0 | 15 | 0 | 0 | 62 | 86 | 0 | 138 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 3 | 0 | 64 | 0 | 225 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 224 | 0 | 8 | 0 | 0 |  | 907 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 69 | 0 | 136 | 0 | 0 | 175 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 220 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 371 | 2 | 0 | 511 | 9 | 0 | 0 | 3 | 7 | 0 |  | 4552 | 3824 | 8376 | 3089 | 907 | 0 | 2200 | 0 | 76 | 1406 | 85 | 0 | 12 | 46 | 511 | 44 | 0 | 0 | 98.01
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 360 | 253 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 280 | 0 | 182 | 185 | 90 | 44 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 36 | 32 | 0 | 0 | 1 | 27 | 30 | 0 | 33 | 0 | 0 | 40 | 86 | 0 | 138 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 41 | 0 | 7 | 10 | 0 | 211 | 0 | 225 | 35 | 0 | 0 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 16 | 0 | 0 | 0 | 0 | 9 | 0 | 2 | 0 | 0 | 0 | 500 | 0 | 0 | 228 | 0 | 28 | 0 | 0 |  | 906 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 0 | 132 | 0 | 0 | 176 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 540 | 220 | 0 | 0 | 1 | 24 | 0 | 0 | 0 | 370 | 10 | 0 | 611 | 50 | 0 | 0 | 15 | 30 | 0 |  | 4554 | 4050 | 8604 | 2763 | 906 | 0 | 2043 | 0 | 326 | 1610 | 96 | 0 | 16 | 36 | 611 | 197 | 0 | 0 | 98.01
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 320 | 283 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 22 | 0 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 280 | 0 | 182 | 185 | 90 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 40 | 29 | 0 | 0 | 1 | 27 | 30 | 0 | 33 | 0 | 0 | 40 | 86 | 0 | 137 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 15 | 0 | 218 | 0 | 296 | 8 | 0 | 0 | 3 | 15 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 30 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 0 | 0 | 0 | 500 | 0 | 0 | 230 | 0 | 49 | 0 | 0 |  | 907 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 69 | 0 | 130 | 0 | 0 | 177 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 540 | 180 | 0 | 0 | 2 | 45 | 35 | 0 | 0 | 370 | 18 | 0 | 610 | 108 | 0 | 0 | 33 | 56 | 0 |  | 4643 | 4092 | 8735 | 2711 | 907 | 0 | 1972 | 0 | 362 | 1609 | 96 | 0 | 48 | 40 | 610 | 380 | 0 | 0 | 98
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 320 | 284 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 22 | 23 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 280 | 0 | 183 | 148 | 50 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 46 | 26 | 0 | 0 | 2 | 27 | 30 | 0 | 33 | 0 | 0 | 40 | 41 | 0 | 135 | 0 | 0 | 0 | 295 | 13 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 16 | 19 | 0 | 218 | 0 | 375 | 8 | 0 | 0 | 4 | 15 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 40 | 0 | 0 | 0 | 0 | 23 | 0 | 18 | 0 | 0 | 0 | 450 | 0 | 0 | 240 | 0 | 64 | 0 | 0 |  | 910 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 92 | 0 | 0 | 177 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 500 | 180 | 0 | 0 | 3 | 62 | 35 | 0 | 0 | 370 | 27 | 0 | 613 | 144 | 0 | 0 | 47 | 72 | 0 |  | 4623 | 4105 | 8728 | 2746 | 910 | 0 | 1918 | 0 | 361 | 1479 | 96 | 0 | 48 | 46 | 613 | 511 | 0 | 0 | 98
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 22 | 23 | 33 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 335 | 0 | 199 | 148 | 50 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 56 | 26 | 0 | 0 | 2 | 27 | 30 | 0 | 33 | 0 | 0 | 60 | 41 | 0 | 135 | 0 | 0 | 0 | 310 | 13 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 20 | 0 | 218 | 0 | 385 | 8 | 0 | 0 | 4 | 15 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 500 | 0 | 0 | 240 | 0 | 69 | 0 | 18 |  | 911 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 94 | 0 | 0 | 176 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 510 | 180 | 0 | 0 | 4 | 72 | 35 | 0 | 0 | 371 | 32 | 0 | 614 | 166 | 0 | 0 | 55 | 86 | 0 |  | 5012 | 4201 | 9213 | 2967 | 911 | 0 | 2048 | 0 | 362 | 1542 | 95 | 0 | 66 | 56 | 614 | 552 | 0 | 0 | 97.99
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 33 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 50 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 26 | 0 | 0 | 2 | 27 | 30 | 0 | 33 | 0 | 0 | 58 | 86 | 0 | 133 | 0 | 0 | 0 | 310 | 13 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 20 | 0 | 218 | 0 | 386 | 12 | 0 | 0 | 4 | 15 | 0 | 0 | 0 | 0 | 10 | 346 | 0 | 49 | 17 | 3 | 0 | 0 | 27 | 0 | 18 | 0 | 0 | 0 | 575 | 0 | 0 | 240 | 0 | 72 | 0 | 9 |  | 909 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 111 | 0 | 0 | 176 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 570 | 220 | 0 | 7 | 4 | 75 | 35 | 0 | 0 | 370 | 24 | 0 | 616 | 178 | 0 | 0 | 53 | 94 | 0 |  | 5214 | 4490 | 9704 | 3037 | 909 | 0 | 2233 | 0 | 404 | 1690 | 95 | 0 | 57 | 56 | 616 | 607 | 0 | 0 | 97.99
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 290 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 22 | 33 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 11 | 0 | 13 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 50 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 25 | 0 | 0 | 2 | 27 | 30 | 0 | 33 | 0 | 0 | 59 | 86 | 0 | 133 | 0 | 0 | 0 | 300 | 13 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 19 | 16 | 218 | 15 | 382 | 24 | 0 | 0 | 4 | 100 | 25 | 0 | 0 | 0 | 12 | 346 | 0 | 35 | 54 | 17 | 0 | 0 | 26 | 0 | 17 | 0 | 0 | 0 | 612 | 0 | 0 | 240 | 0 | 64 | 0 | 13 |  | 910 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 99 | 0 | 0 | 172 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 622 | 220 | 0 | 54 | 4 | 68 | 35 | 0 | 0 | 370 | 31 | 0 | 646 | 163 | 0 | 0 | 46 | 81 | 0 |  | 5471 | 4574 | 10045 | 3084 | 910 | 0 | 2201 | 0 | 666 | 1768 | 95 | 0 | 77 | 50 | 646 | 548 | 0 | 0 | 97.98
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 370 | 315 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 22 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 12 | 0 | 4 | 0 | 0 | 0 | 280 | 0 | 183 | 185 | 50 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 23 | 0 | 0 | 2 | 27 | 28 | 0 | 30 | 0 | 0 | 59 | 86 | 0 | 133 | 0 | 0 | 0 | 280 | 13 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 16 | 16 | 25 | 218 | 50 | 343 | 24 | 17 | 0 | 3 | 100 | 35 | 0 | 0 | 0 | 12 | 353 | 0 | 39 | 54 | 17 | 0 | 0 | 20 | 0 | 18 | 0 | 0 | 0 | 612 | 0 | 0 | 240 | 0 | 55 | 0 | 18 |  | 910 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 105 | 0 | 0 | 140 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 622 | 180 | 0 | 54 | 3 | 55 | 35 | 0 | 0 | 370 | 25 | 0 | 708 | 82 | 0 | 0 | 43 | 66 | 0 |  | 5313 | 4336 | 9649 | 2808 | 910 | 0 | 2083 | 0 | 738 | 1776 | 93 | 0 | 66 | 54 | 708 | 413 | 0 | 0 | 97.99
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 420 | 292 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 22 | 33 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 0 | 0 | 0 | 290 | 0 | 182 | 185 | 70 | 36 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 52 | 25 | 0 | 0 | 1 | 27 | 28 | 0 | 30 | 0 | 0 | 59 | 86 | 0 | 131 | 0 | 0 | 0 | 295 | 13 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 16 | 12 | 25 | 100 | 50 | 386 | 8 | 17 | 0 | 2 | 106 | 35 | 0 | 0 | 0 | 12 | 345 | 0 | 28 | 54 | 17 | 0 | 0 | 12 | 0 | 18 | 0 | 0 | 0 | 612 | 1 | 0 | 240 | 0 | 39 | 0 | 18 |  | 909 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 102 | 0 | 0 | 140 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 54 | 2 | 37 | 35 | 0 | 0 | 370 | 6 | 0 | 710 | 81 | 0 | 0 | 28 | 43 | 0 |  | 5286 | 4307 | 9593 | 2921 | 909 | 0 | 2174 | 0 | 610 | 1773 | 86 | 0 | 66 | 52 | 710 | 291 | 1 | 0 | 97.97
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 420 | 319 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 22 | 33 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 12 | 0 | 5 | 0 | 0 | 0 | 315 | 0 | 196 | 185 | 50 | 36 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 48 | 27 | 0 | 0 | 0 | 27 | 28 | 0 | 30 | 0 | 0 | 60 | 86 | 0 | 131 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 0 | 25 | 68 | 50 | 387 | 8 | 17 | 0 | 1 | 87 | 35 | 0 | 0 | 0 | 25 | 360 | 4 | 11 | 54 | 17 | 0 | 0 | 5 | 0 | 18 | 0 | 0 | 0 | 552 | 7 | 0 | 240 | 0 | 18 | 0 | 8 |  | 910 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 104 | 0 | 0 | 140 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 622 | 220 | 0 | 54 | 0 | 16 | 35 | 0 | 0 | 370 | 8 | 0 | 711 | 31 | 0 | 0 | 10 | 18 | 0 |  | 5161 | 4217 | 9378 | 2957 | 910 | 0 | 2227 | 0 | 575 | 1715 | 85 | 0 | 24 | 48 | 711 | 119 | 7 | 0 | 97.97
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 269 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 8 | 2 | 17 | 0 | 20 | 22 | 18 | 33 | 0 | 0 | 80 | 0 | 0 | 0 | 1 | 226 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 1 | 14 | 0 | 10 | 0 | 0 | 0 | 290 | 0 | 183 | 185 | 50 | 36 | 0 | 0 | 43 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 56 | 29 | 0 | 0 | 0 | 27 | 28 | 0 | 30 | 0 | 0 | 40 | 86 | 0 | 131 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 48 | 68 | 53 | 365 | 19 | 20 | 5 | 0 | 87 | 54 | 4 | 17 | 36 | 25 | 345 | 12 | 0 | 90 | 17 | 0 | 8 | 0 | 5 | 18 | 0 | 54 | 0 | 570 | 8 | 0 | 240 | 0 | 1 | 0 | 0 |  | 898 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 10 | 0 | 22 | 0 | 0 | 2 | 67 | 0 | 102 | 0 | 0 | 152 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 10 | 0 | 34 | 0 | 0 | 0 | 590 | 180 | 0 | 150 | 0 | 2 | 35 | 0 | 0 | 370 | 0 | 0 | 713 | 2 | 0 | 0 | 0 | 0 | 0 |  | 5328 | 4324 | 9652 | 2891 | 898 | 0 | 2167 | 0 | 959 | 1699 | 80 | 0 | 176 | 56 | 713 | 5 | 8 | 0 | 97.96
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 288 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 115 | 0 | 0 | 0 | 0 | 36 | 17 | 17 | 0 | 20 | 22 | 17 | 33 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 224 | 0 | 0 | 0 |  | 24 | 8 | 34 | 0 | 19 | 25 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 50 | 36 | 0 | 0 | 43 | 0 | 37 | 12 | 0 | 0 | 0 | 18 | 60 | 29 | 0 | 0 | 0 | 27 | 29 | 0 | 30 | 0 | 0 | 61 | 86 | 0 | 131 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 96 | 0 | 36 | 0 | 75 | 100 | 80 | 385 | 54 | 52 | 46 | 0 | 87 | 54 | 48 | 17 | 92 | 50 | 345 | 13 | 0 | 144 | 32 | 0 | 28 | 0 | 47 | 36 | 0 | 160 | 0 | 612 | 5 | 0 | 240 | 0 | 0 | 0 | 0 |  | 898 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 30 | 0 | 0 | 5 | 67 | 0 | 103 | 0 | 0 | 162 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 39 | 0 | 0 | 0 | 590 | 220 | 0 | 150 | 0 | 0 | 93 | 0 | 0 | 370 | 0 | 0 | 715 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6368 | 4566 | 10934 | 3020 | 898 | 0 | 2274 | 0 | 1672 | 1742 | 80 | 0 | 468 | 60 | 715 | 0 | 5 | 0 | 97.96
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 276 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 51 | 17 | 0 | 0 | 21 | 22 | 17 | 33 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 24 | 34 | 34 | 0 | 44 | 32 | 0 | 17 | 0 | 0 | 0 | 290 | 0 | 181 | 190 | 70 | 43 | 0 | 0 | 43 | 0 | 45 | 0 | 0 | 0 | 0 | 18 | 58 | 31 | 0 | 0 | 0 | 27 | 29 | 0 | 30 | 0 | 0 | 62 | 86 | 0 | 134 | 0 | 0 | 0 | 270 | 13 | 2 | 0 | 0 | 0 | 0 | 75 | 0 | 76 | 0 | 100 | 100 | 117 | 384 | 45 | 17 | 17 | 0 | 87 | 54 | 17 | 0 | 93 | 50 | 320 | 0 | 0 | 108 | 53 | 0 | 35 | 0 | 51 | 36 | 0 | 108 | 0 | 612 | 14 | 0 | 240 | 0 | 0 | 0 | 0 |  | 896 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 5 | 68 | 0 | 103 | 0 | 0 | 164 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 220 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 369 | 0 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6233 | 4457 | 10690 | 3009 | 896 | 0 | 2181 | 0 | 1512 | 1752 | 81 | 0 | 435 | 58 | 752 | 0 | 14 | 0 | 97.94
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 300 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 21 | 22 | 17 | 33 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 24 | 34 | 0 | 0 | 25 | 33 | 0 | 20 | 0 | 0 | 0 | 315 | 0 | 193 | 192 | 70 | 43 | 0 | 0 | 43 | 0 | 45 | 0 | 0 | 0 | 0 | 18 | 58 | 33 | 0 | 0 | 0 | 27 | 30 | 0 | 30 | 0 | 0 | 61 | 86 | 0 | 134 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 0 | 0 | 0 | 75 | 0 | 50 | 0 | 100 | 51 | 122 | 384 | 45 | 17 | 17 | 0 | 51 | 54 | 17 | 0 | 95 | 50 | 335 | 0 | 0 | 54 | 53 | 0 | 35 | 0 | 51 | 36 | 0 | 54 | 0 | 612 | 8 | 0 | 240 | 0 | 0 | 0 | 0 |  | 897 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 5 | 68 | 0 | 102 | 0 | 0 | 164 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 220 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 369 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6041 | 4490 | 10531 | 3063 | 897 | 0 | 2286 | 0 | 1314 | 1751 | 87 | 0 | 311 | 58 | 756 | 0 | 8 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 292 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 21 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 24 | 34 | 0 | 0 | 24 | 27 | 0 | 27 | 0 | 0 | 0 | 290 | 0 | 182 | 194 | 70 | 44 | 0 | 0 | 43 | 0 | 45 | 0 | 0 | 0 | 0 | 18 | 58 | 33 | 0 | 0 | 0 | 27 | 30 | 0 | 31 | 0 | 0 | 60 | 86 | 0 | 134 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 75 | 0 | 44 | 0 | 100 | 51 | 124 | 385 | 45 | 17 | 17 | 0 | 51 | 54 | 17 | 0 | 94 | 50 | 320 | 0 | 0 | 54 | 53 | 0 | 35 | 0 | 51 | 36 | 0 | 54 | 0 | 612 | 9 | 0 | 240 | 0 | 0 | 0 | 0 |  | 897 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 5 | 67 | 0 | 103 | 0 | 0 | 164 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 220 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 369 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5943 | 4490 | 10433 | 3012 | 897 | 0 | 2272 | 0 | 1283 | 1751 | 96 | 0 | 297 | 58 | 758 | 0 | 9 | 0 | 97.95
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 283 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 24 | 34 | 0 | 0 | 25 | 28 | 0 | 29 | 0 | 0 | 0 | 290 | 0 | 181 | 197 | 70 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 34 | 0 | 0 | 0 | 27 | 30 | 0 | 33 | 0 | 0 | 62 | 86 | 0 | 134 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 75 | 0 | 16 | 0 | 70 | 51 | 80 | 383 | 45 | 0 | 0 | 0 | 51 | 54 | 0 | 0 | 92 | 50 | 320 | 0 | 0 | 54 | 53 | 0 | 35 | 0 | 51 | 36 | 0 | 54 | 0 | 612 | 0 | 0 | 240 | 0 | 0 | 0 | 0 |  | 897 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 103 | 0 | 0 | 165 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 220 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 370 | 0 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5714 | 4411 | 10125 | 3010 | 897 | 0 | 2261 | 0 | 1130 | 1762 | 96 | 0 | 162 | 54 | 753 | 0 | 0 | 0 | 97.94
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 258 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 26 | 0 | 29 | 0 | 0 | 0 | 290 | 0 | 181 | 197 | 70 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 34 | 0 | 0 | 0 | 27 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 134 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 50 | 51 | 50 | 370 | 45 | 0 | 0 | 0 | 51 | 54 | 0 | 0 | 55 | 50 | 320 | 0 | 0 | 54 | 53 | 0 | 35 | 0 | 51 | 36 | 0 | 0 | 0 | 612 | 6 | 0 | 240 | 0 | 0 | 0 | 0 |  | 898 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68 | 0 | 104 | 0 | 0 | 168 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5430 | 4257 | 9687 | 2969 | 898 | 0 | 2198 | 0 | 867 | 1776 | 96 | 0 | 66 | 56 | 755 | 0 | 6 | 0 | 97.94
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 296 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 13 | 0 | 40 | 0 | 0 | 0 | 290 | 0 | 180 | 199 | 70 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 34 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 135 | 0 | 0 | 0 | 270 | 13 | 2 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 17 | 20 | 371 | 45 | 0 | 0 | 0 | 51 | 17 | 0 | 0 | 26 | 12 | 320 | 0 | 0 | 17 | 20 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 612 | 15 | 0 | 240 | 0 | 0 | 0 | 0 |  | 898 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 102 | 0 | 0 | 170 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5071 | 4157 | 9228 | 2990 | 898 | 0 | 2222 | 0 | 422 | 1773 | 96 | 0 | 0 | 54 | 758 | 0 | 15 | 0 | 97.93
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 110 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 6 | 0 | 36 | 0 | 0 | 0 | 295 | 0 | 185 | 199 | 70 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 34 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 135 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 17 | 20 | 323 | 45 | 0 | 0 | 0 | 51 | 17 | 0 | 0 | 26 | 12 | 316 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 612 | 10 | 0 | 239 | 0 | 0 | 0 | 0 |  | 899 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 104 | 0 | 0 | 170 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 180 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4790 | 4127 | 8917 | 2896 | 899 | 0 | 2021 | 0 | 412 | 1774 | 96 | 0 | 0 | 54 | 755 | 0 | 10 | 0 | 97.93
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 9773500 | 7014080 | 0 | 0 | 0 | 7571394 | 0 | 0 | 0 | 28080 | 701280 | 0 | 0 | 0 | 0 | 260640 | 38318 | 42240 | 0 | 444000 | 494280 | 446760 | 810800 | 0 | 0 | 2110282 | 0 | 0 | 0 | 25396 | 5365309 | 0 | 0 | 0 |  | 279360 | 96624 | 56604 | 0 | 137280 | 230400 | 0 | 510240 | 0 | 0 | 0 | 7616200 | 0 | 4602000 | 4265455 | 1573650 | 941976 | 0 | 0 | 1040120 | 0 | 108160 | 33403 | 0 | 0 | 0 | 366960 | 1212480 | 847680 | 0 | 0 | 12050 | 642000 | 680280 | 0 | 717336 | 0 | 0 | 1375392 | 1868160 | 0 | 3268230 | 0 | 0 | 0 | 7259000 | 333072 | 42288 | 0 | 0 | 0 | 0 | 1077600 | 0 | 351360 | 138510 | 599040 | 2436960 | 801236 | 8471000 | 525600 | 182400 | 125454 | 27480 | 1008655 | 531898 | 121270 | 30780 | 582960 | 365760 | 8027800 | 33600 | 290840 | 777600 | 411491 | 0 | 191520 | 163397 | 291840 | 417240 | 0 | 424873 | 0 | 12730908 | 70560 | 0 | 5683181 | 0 | 467945 | 0 | 76800 |  | 21834909 | 0 | 6990624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2657000 | 134030 | 0 | 0 | 0 | 0 | 0 | 0 | 318048 | 0 | 0 | 82049 | 0 | 95011 | 0 | 0 | 82926 | 1575709 | 0 | 2842000 | 0 | 0 | 4066818 | 0 | 4202318 | 0 | 0 | 0 | 0 | 0 | 8561018 | 0 | 0 | 63648 | 0 | 68083 | 0 | 33499 | 0 | 13742200 | 5196590 | 0 | 1135200 | 29580 | 466560 | 590976 | 0 | 0 | 8952727 | 188153 | 0 | 14890909 | 992880 | 0 | 3284 | 340500 | 565070 | 0 |  | 122680317 | 100702319 | 223382636 | 71920757 | 21834909 | 0 | 52022710 | 0 | 13797288 | 39843544 | 2110282 | 0 | 1959449 | 1212480 | 14890909 | 3719748 | 70560 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 31079730 | 23988153.6 | 0 | 0 | 0 | 23092751.7 | 0 | 0 | 0 | 504036 | 13618857.6 | 0 | 0 | 0 | 0 | 4759286.4 | 603891.68 | 772569.6 | 0 | 333000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 481000.24 | 17115335.71 | 0 | 0 | 0 |  | 4913942.4 | 1701548.64 | 1013777.64 | 0 | 2686569.6 | 3792384 | 0 | 0 | 0 | 0 | 0 | 21249198 | 0 | 15278640 | 14289274.25 | 5082889.5 | 3174459.12 | 0 | 0 | 4170881.2 | 0 | 1937145.6 | 603258.18 | 0 | 0 | 0 | 275220 | 7953868.8 | 2636284.8 | 0 | 0 | 0 | 2503800 | 2537444.4 | 0 | 3263878.8 | 0 | 0 | 7633425.6 | 9751795.2 | 0 | 9118361.7 | 0 | 0 | 0 | 22430310 | 249804 | 32138.88 | 0 | 0 | 0 | 0 | 20700696 | 0 | 6187449.6 | 0 | 10668902.4 | 42281256 | 13284492.88 | 22448150 | 10017936 | 3421824 | 2250644.76 | 0 | 16491509.25 | 10340097.12 | 2175583.8 | 588205.8 | 11315253.6 | 6514185.6 | 21353948 | 573552 | 0 | 14222304 | 6904818.98 | 0 | 3422462.4 | 0 | 5258956.8 | 7068045.6 | 0 | 5982211.84 | 0 | 88734428.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 61356094.29 | 0 | 20622340.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8396120 | 635302.2 | 0 | 0 | 0 | 0 | 0 | 0 | 5346386.88 | 0 | 0 | 1469497.59 | 0 | 1701647.01 | 0 | 0 | 62774.982 | 17380070.27 | 0 | 23986480 | 0 | 0 | 13420499.4 | 0 | 13993718.94 | 0 | 0 | 0 | 0 | 0 | 24998172.56 | 0 | 0 | 1261503.36 | 0 | 1356213.36 | 0 | 0 | 0 | 89049456 | 16161394.9 | 0 | 21966120 | 0 | 0 | 10253433.6 | 0 | 0 | 65354907.1 | 0 | 0 | 98428908.49 | 0 | 0 | 0 | 0 | 0 | 0 |  | 596835828.03 | 497201041.732 | 1094036869.762 | 210610305.532 | 61356094.29 | 0 | 150768892.71 | 0 | 247642385.01 | 284505342.13 | 0 | 0 | 32771072.8 | 7953868.8 | 98428908.49 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 298 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 33 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 50 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 26 | 0 | 0 | 2 | 27 | 30 | 0 | 33 | 0 | 0 | 58 | 86 | 0 | 133 | 0 | 0 | 0 | 310 | 13 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 20 | 0 | 218 | 0 | 386 | 12 | 0 | 0 | 4 | 15 | 0 | 0 | 0 | 0 | 10 | 346 | 0 | 49 | 17 | 3 | 0 | 0 | 27 | 0 | 18 | 0 | 0 | 0 | 575 | 0 | 0 | 240 | 0 | 72 | 0 | 9 |  | 909 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 111 | 0 | 0 | 176 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 570 | 220 | 0 | 7 | 4 | 75 | 35 | 0 | 0 | 370 | 24 | 0 | 616 | 178 | 0 | 0 | 53 | 94 | 0 |  | 9704 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 288 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 115 | 0 | 0 | 0 | 0 | 36 | 17 | 17 | 0 | 20 | 22 | 17 | 33 | 0 | 0 | 80 | 0 | 0 | 0 | 10 | 224 | 0 | 0 | 0 | 0 | 24 | 8 | 34 | 0 | 19 | 25 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 50 | 36 | 0 | 0 | 43 | 0 | 37 | 12 | 0 | 0 | 0 | 18 | 60 | 29 | 0 | 0 | 0 | 27 | 29 | 0 | 30 | 0 | 0 | 61 | 86 | 0 | 131 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 96 | 0 | 36 | 0 | 75 | 100 | 80 | 385 | 54 | 52 | 46 | 0 | 87 | 54 | 48 | 17 | 92 | 50 | 345 | 13 | 0 | 144 | 32 | 0 | 28 | 0 | 47 | 36 | 0 | 160 | 0 | 612 | 5 | 0 | 240 | 0 | 0 | 0 | 0 |  | 898 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 30 | 0 | 0 | 5 | 67 | 0 | 103 | 0 | 0 | 162 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 39 | 0 | 0 | 0 | 590 | 220 | 0 | 150 | 0 | 0 | 93 | 0 | 0 | 370 | 0 | 0 | 715 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10934 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 220 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 22 | 25 | 33 | 25 | 0 | 96 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 24 | 70 | 84 | 0 | 44 | 50 | 0 | 15 | 0 | 0 |  | 330 | 0 | 220 | 195 | 50 | 44 | 0 | 0 | 51 | 0 | 44 | 52 | 0 | 0 |  | 18 | 82 | 30 | 0 | 0 | 0 | 28 | 30 | 0 | 35 | 0 | 0 | 62 | 86 | 0 | 130 | 0 | 0 | 0 | 310 | 13 | 5 | 0 | 300 | 0 | 0 | 96 | 0 | 96 | 0 | 100 | 200 | 120 | 385 | 57 | 105 | 85 | 0 | 50 | 35 | 110 | 106 | 100 | 50 | 400 | 17 | 0 | 162 | 35 | 0 | 35 | 0 | 92 | 36 | 0 | 160 | 0 | 612 | 15 | 0 | 235 | 150 |  |  |  |  | 914 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 127 | 10 | 16 | 0 | 0 | 0 | 40 | 28 | 96 | 0 | 0 | 30 | 0 | 30 | 0 | 0 | 11 | 65 | 0 | 110 | 0 | 0 | 175 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 370 | 0 | 0 | 765 | 0 | 0 |  |  |  | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 |  | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 220 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 25 | 22 | 25 | 33 | 25 | 0 | 96 | 0 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 70 | 65 | 0 | 38 | 50 | 0 | 5 | 0 | 0 | 0 | 310 | 0 | 200 | 195 | 50 | 44 | 0 | 0 | 51 | 0 | 30 | 52 | 0 | 0 |  | 18 | 66 | 30 | 0 | 0 | 1.6 | 28 | 30 | 0 | 33 | 0 | 0 | 60 | 86 | 0 | 130 | 0 | 0 | 0 | 310 | 13 | 5 | 0 | 300 | 0 | 0 | 96 | 0 | 62 | 20 | 12 | 200 | 90 | 385 | 54 | 50 | 85 | 5 | 50 | 35 | 110 | 106 | 100 | 25 | 400 | 0 | 50 | 162 | 35 | 0 | 17 | 35 | 92 | 36 | 0 | 17 | 0 | 612 | 15 | 0 | 235 | 150 | 70 |  |  |  | 914 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 0 | 127 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 26 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 110 | 0 | 0 | 175 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 90 | 0 | 8 | 113 | 622 | 220 |  | 54 | 6 | 100 | 115 | 0 | 0 | 370 | 30 | 0 | 765 | 170 | 0 |  | 29 | 47 | 0 |  |  |  |  | gas | hvdc |  | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 132 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 17 | 33 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 6 | 6 | 0 | 6 | 0 | 0 | 0 | 290 | 0 | 182 | 153 | 80 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 36 | 27 | 0 | 0 | 1 | 28 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 137 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 7 | 10 | 12 | 17 | 20 | 275 | 45 | 17 | 17 | 1 | 49 | 17 | 17 | 0 | 26 | 25 | 316 | 0 | 21 | 17 | 17 | 0 | 17 | 13 | 16 | 17 | 0 | 17 | 0 | 530 | 0 | 0 | 240 | 80 | 39 | 0 | 0 | 0 | 899 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 105 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 550 | 180 | 0 | 17 | 1 | 25 | 35 | 0 | 0 | 372 | 11 | 0 | 751 | 69 | 0 | 0 | 17 | 35 | 0 | 0 |  |  |  | 123943467 | 21834909 |  | 0 | 39843544 | 15756737 | 1212480 | 3719748 | 70560 | 2110282 |  |  |  | 208491727
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [10 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [11 empty] | 123.9435 | 21.8349 |  | 0 | 39.8435 | 15.7567 | 1.2125 | 3.7197 | 0.07056 | 2.1103
| Minimum Generation |  | 7425 | 5:00
| Highest Generation |  | 10934 | 18:00 | [129 empty] | 0 | [77 empty] | 208.4917
| Day Peak Generation |  | 9704 | 12:00
| Evening Peak Generation |  | 10934 | 18:00 | [207 empty] | 202699852
| HVDC Max Flow |  | 911 | 11:00 | [207 empty] | 202.6999
| HVDC EvPeak Flow |  | 898 | 18:00
| Load factor L.F |  | 85.13% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-11-19
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-11-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9704 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7562
Evening Peak Generation : |  |  | 10934 | MW Hour : | 18:00 | Available Max Generation : |  | 13158
E.P. Demand (at gen end) : |  |  | 10934 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 11100
Maximum Generation : |  |  | 10934 | MW Hour : | 18:00 | Reserve(Generation end) |  | 2058
Total Gen. (MKWH) : |  |  | 223.3826 | System Load Factor : | 85.13% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1028 | MW at | 18:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-11-19
Actual : |  | 97.87 | Ft.(MSL) , | Rule curve : | 107.2 | Ft.( MSL )
Gas Consumed : |  | Total = | 907.34 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 361379198.242 | Adani : | 98428908.49
|  |  | Coal : | 284505342.13 | Oil: | 280413457.81 | Total: | 1024726906.672
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3758.0485 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1027.7912 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1438.2562 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1248.7433 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1028.1895 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 763.9927 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 429.0126 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 356.8265 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 697.9062 |  |  | 0 | 0%
Total |  | 0 |  | 10748.7667 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
8:00 | 10:12 | Bhaluka 132/33kV S/S Bus Section- 01 Forced S/D Due to Red hot in bus section of shakhipur feeder
8:00 | 10:12 | Bhaluka 132/33kV S/S Bus Section- 03 Forced S/D Due to Red hot in bus section of shakhipur feeder
8:18 | 16:53 | Benapole 132/33kV S/S Bus-A Scheduled S/D Due to Annual maintenance
8:22 | 16:09 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Scheduled S/D Due to Annual Maintenance work.
8:23 | 16:03 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Scheduled S/D Due to Annual maintenance work.
8:23 | 16:01 | Bibiana 400/230kV S/S ICT-01 HT Scheduled S/D Due to AM
8:25 | 15:51 | Khulna (S)-Rampal Ckt-2 Scheduled S/D from Rampal 400/230kV end Due to Requested by Khulna ALDC. and
from Khulna(S) 230/132kV end Due to Annual Maintenance Work.
8:30 | 16:37 | Rajbari 132/33kV S/S Bheramara-1 Scheduled S/D Due to S/D by Bheramara SS.
8:31 | 13:08 | Ghatail 132/33kV S/S T-1 HT Scheduled S/D Due to 33kv T-1 Breaker source and load side Lux Installation by pbs |  |  |  |  | 25.0MW load interrup.
8:35 | 14:23 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Scheduled S/D from Bog-Sherpur 132/33kV end. and from
Sirajganj 132/33kV end Due to Annual Maintenance
8:38 | 16:05 | Chandraghona-Rangamati 132 kV Ckt-2 Scheduled S/D from Rangamati 132/33kV end Due to
Rangamati-Chandraghona Ckt-02 is shutdown due to annual maintenance.
8:40 | 15:40 | Purbasadipur-Saidpur 132kV Ckt-1 Scheduled S/D from Purbasadipur 132/33kV end Due to Annual Maintenance
and from Saidpur 132/33kV end Due to Annual maintenance
8:50 | 16:19 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end Due to Annual
Maintenance and from Fenchuganj 230/132/33kV end Due to Annual maintenance
8:53 | - | Niamatpur 132/33kV S/S 132 kV Naogaon ckt-2 Scheduled S/D Due to Earthing Boring (LA,PT)
8:57 | 17:12 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due to Annual maintenance.
8:57 | 16:50 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Annual Maintenance
8:58 | 15:28 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Annual Maintenance
8:59 | 16:28 | Sonargaon 132/33kV S/S BUS A Scheduled S/D Due to Annual maintenance work.
9:00 | 16:10 | Khulna(S) 230/132kV S/S 230 KV Main Bus 2 Scheduled S/D Due to Annual Maintenance Work.
9:07 | 16:57 | Rajshahi 230/132/33kV S/S 132 kV Main BUS-02 Scheduled S/D Due to None
9:19 | - | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Annual Maintenance
9:20 | - | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Annual Maintenance
9:22 | 14:34 | Kulaura 132/33kV S/S TR-2 HT Scheduled S/D Due to Annual maintenance.
9:22 | 18:36 | Shyampur-Shyampur(New) 132kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to Annual Maintenance
9:22 | 14:34 | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual maintenance.
9:25 | - | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Project Work S/D Due to payra power plant shedule shutdown
9:29 | 14:09 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Beanibazar 132/33kV end Due to Annual Maintenance
9:34 | 16:12 | Gopalganj 400/132kV S/S 400kV Payra Ckt-1 Project Work S/D
9:35 | 11:27 | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Scheduled S/D Due to Tan delta testing work by SPMD, Ishurdi.
9:35 | 11:24 | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Scheduled S/D Due to Tan delta testing work by SPMD, Ishurdi.
9:38 | 16:55 | Bhulta 400/230kV S/S ATR-01 HT Scheduled S/D Due to Annual Maintenance work.
9:43 | 14:41 | Gopalganj 400/132kV S/S 400kV Bus-01 Scheduled S/D
9:51 | 15:53 | BIPTC S/S 10CF23 Scheduled S/D Due to For annual maintenance
10:08 | 16:28 | Madanganj 132/33kV S/S Madanganj -Bashundhara 132 kv Ckt Forced S/D Due to Reserve Bus DS Y phase red hot maintenance
- | 10:17 | Bhaluka 132/33kV S/S Transformer- 01 LT is restored.
- | 10:18 | Bhaluka 132/33kV S/S Transformer- 01 HT is restored.
- | 10:31 | Brahmanbaria 132/33kV S/S 403T LT is restored.
- | 10:31 | Brahmanbaria 132/33kV S/S 403T HT is restored.
10:34 | 15:54 | Gopalganj 132/33kV S/S Gopalganj 100 MW PS Project Work S/D Due to Project work
10:59 | 16:33 | Baghabari-Sirajganj 230 kV Ckt-2 Tripped from Sirajgonj 230 end showing Rel321*4 / REL 521 relays Due to
OPGW to cut and from Baghabari 230/132kV end showing General trip Dist trip L1 Dist trip L2 Dist trip L3 67N
trip DTT trip A/R blocked Zone 1 SOTF CR CH 2 relays Due to Disconnected OPGW from cross arm.
11:37 | 14:03 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D Due to Tan Delta testing work by SPMD, Ishurdi.
11:37 | 14:03 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to Tan Delta testing work by SPMD, Ishurdi.
- | 12:25 | Chowmuhani-Ramganj 132 kV Ckt-1 is restored.
13:08 | 16:32 | Baghabari-Sirajganj 230 kV Ckt-2 Forced S/D from Sirajgonj 230 end Due to OPGW to cut & Trip this ckt.
Sutdown For Maintenance Work
- | 14:16 | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 is restored.
14:35 | 15:17 | Mahasthangar-Palashbari 132kV Ckt-2 Scheduled S/D from Mahasthangarh 132/33kV end Due to Polashbari
ckt 2 Energy meter change.
15:13 | 15:28 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Tripped showing Incommer-01 CB relays Due to PBS |  |  |  |  | 15.0MW load interrup.
Kumerjani Feeder Trip
15:13 | 15:28 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Tripped showing Kumerjani Feeder trip and Jamper cable are |  |  |  |  | 16.0MW load interrup.
torn. relays Due to Incomer CB
- | 15:59 | Brahmanbaria 132/33kV S/S 402T LT is restored.
- | 15:59 | Brahmanbaria 132/33kV S/S 402T HT is restored.
- | 16:10 | Shahjadpur 132/33kV S/S T-1(405T) HT is restored.
- | 16:11 | Shahjadpur 132/33kV S/S T-1(405T) LT is restored.
16:26 | 17:23 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Forced S/D Due to Due to PBS Kumerjani feeder Jumper |  |  |  |  | 17.0MW load interrup.
Maintenance work
16:26 | 17:22 | Mirzapur 132/33kV S/S Transformer-02(E07) HT Forced S/D Due to Due to PBS Kumerjani feeder Jumper |  |  |  |  | 17.0MW load interrup.
Maintenance Work
- | 16:48 | Barishal 132/33kV S/S 132 kv Summit power is restored.
- | 17:06 | Barguna 132/33kV S/S Transformer-2 HT is restored.
- | 17:07 | Barguna 132/33kV S/S Transformer-2 LT is restored.
- | 17:12 | Jamalpur-Mymensingh 132kV Ckt-2 is restored.
18:00 | - | Evening peak Generation is 10899 MW

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-11-18
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 0 | 0 | Gas shortage
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9773500
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 288 | 7014080 | FGMO
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7571394
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 28080 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 36 | 260640 | Fuel shortage
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 701280 | Low demand
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 38318 | Low demand
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 42240 | Low demand
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 938280 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 446760 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 810800
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | 33 kV feeder fault.
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 36 | 351360 | Low demand
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 182400 | Low demand
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 13 | 33600 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 777600
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 163397
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 417240 | Fuel shortage
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 240 | 5683181 | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 1879 | 35234150
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 10 | 25396 | Low demand
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 138510
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 230400 | Trandformer O/L
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 80 | 2110282 | Low water level
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 224 | 5365309
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 46 | 125454 | Low demand
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 96624 | Low demand
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 56604 | Low demand
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 75 | 599040 | High Voltage
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 510240
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 19 | 137280 | Low demand
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27480
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 87 | 1008655 | Fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 531898
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 48 | 121270 | High Voltage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 365760 | 33 kV feeder fault.
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 32 | 411491 | Fuel shortage
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 160 | 424873
55 | SS Power I |  | IPP | 2*612 | 1224 | 612 | 12730908 | Coal shortage
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 5 | 70560
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 0 | 0 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1571 | 25088034
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4602000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7616200 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 941976 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 185 | 4265455
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1040120 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 80 | 801236 | Fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 108160 | Engine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1573650 | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 2436960 | High Voltage
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 60 | 1212480
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 12 | 33403 | Low demand
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 366960 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 30780 | Low demand
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 92 | 582960 | Fuel shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 47 | 291840 | High Voltage
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 467945
| Cumilla Area Total |  |  |  | 2917 | 1268 | 26372125
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 29 | 847680 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12050
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 96 | 1077600 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 54 | 525600 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 290840
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 279360 | Fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 28 | 191520 | Fuel shortage
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 76800
| Mymensingh Area Total |  |  |  | 646 | 231 | 3301450
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 27 | 642000 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 680280 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Contact expired
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 30 | 717336 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 42288 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1375392
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1868160
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 131 | 3268230 | ST under Maint
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 333072 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7259000 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 385 | 8471000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 345 | 8027800 | FGMO
| Sylhet Area Total |  |  |  | 2417 | 1419 | 32684558
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 898 | 21834909
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 290 | 6990624 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 466560
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 370 | 8952727 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Nepal |  | Imported power | 40 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1558 | 38244820
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 6 | 134030 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 123 | 2657000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 590 | 13742200 | Unit-2 under overhauling
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5196590
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1135200
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Under maint.
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3284
| Barisal Area Total |  |  |  | 2236 | 1089 | 22868304
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 82049 | Fuel shortage
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 162 | 4066818 | Gas shortage
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 172 | 4202318
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 8561018
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 95011 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 82926 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 60 | 318048 | High Voltage
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 63648 | Low demand
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29580
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 715 | 14890909
135 | Sirajganj 68 MW Solar Park |  | NWPGCL | 68 | 68 | 0 | 340500
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 565070
| Rajshahi Area Total |  |  |  | 3449 | 1617 | 33297895
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 67 | 1575709
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 103 | 2842000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 39 | 68083 | Low demand
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33499
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 93 | 590976 | Fuel shortage
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 188153
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 992880
| Rangpur Area Total |  |  |  | 950 | 302 | 6291300
| Total |  |  |  | 27086 | 10934 | 223382636
| Eastern Grid Total |  |  |  | 16752 | 6368 | 122680317
| Western Grid Total |  |  |  | 10334 | 4566 | 100702319
| National Grid Total |  |  |  | 27086 | 10934 | 223382636
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-11-18
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7630.21 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3128.8 | MW
i) Dhaka area |  |  | 4262.71 |  | MW | i) Khulna area |  |  |  | 1144.4 | MW
ii) Chattogram area |  |  | 1096.5 |  | MW | ii) Barishal area |  |  |  | 293 | MW
iii) Cumilla area |  |  | 955 |  | MW | iii) Rajshahi area |  |  |  | 962.4 | MW
iv) Mymensingh area |  |  | 890 |  | MW | iv) Rangpur area |  |  |  | 729 | MW
v) Sylhet area |  |  | 426 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10759.01 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 06:00 | 67 | Jashore | 95 | 18:00 | 133 | Rajbari | 52 | 18:00
2 | AKSML | 103 | 04:00 | 68 | Jhenaidah | 80 | 18:30 | 134 | Rajendrapur | 96 | 18:00
3 | Aftabnagar | 28 | 13:00 | 69 | Joydebpur | 173 | 18:00 | 135 | Rajshahi | 71 | 18:00
4 | Agargaon | 86 | 13:00 | 70 | Joypurhat | 38 | 18:00 | 136 | Rajshahi-230 | 52 | 13:00
5 | Agrabad | 82 | 18:00 | 71 | Juldah | 12 | 23:00 | 137 | Ramganj | 78 | 19:30
6 | Amnura | 38 | 18:00 | 72 | KSRM | 50 | 15:00 | 138 | Rampur | 33 | 18:00
7 | Ashuganj | 64 | 23:00 | 73 | Kabirpur | 247 | 18:30 | 139 | Rangamati | 13 | 18:00
8 | BSRM | 83 | 01:00 | 74 | Kachua | 53 | 18:00 | 140 | Rangpur | 111 | 18:00
9 | Bagerhat | 67 | 18:00 | 75 | Kallyanpur | 75 | 13:00 | 141 | Ruppur | 5.6 | 15:00
10 | Bakulia | 81 | 17:00 | 76 | Kalurghat | 32 | 18:00 | 142 | SSM | 0 | 00:00
11 | Banani | 50 | 13:00 | 77 | Kamrangirchar | 58.1 | 18:30 | 143 | Saidpur | 88 | 18:00
12 | Bangabhaban | 12 | 10:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 81 | 18:00
13 | Barapukuria | 43 | 18:00 | 79 | Kazla | 97 | 13:00 | 145 | Satmasjid | 75 | 12:00
14 | Barguna | 18 | 21:00 | 80 | Keranigonj | 61 | 13:00 | 146 | Savar | 176 | 15:00
15 | Barishal | 83 | 13:00 | 81 | Khagrachori | 24 | 18:00 | 147 | SevenRings | 4.96 | 16:00
16 | Barishal-230 | 64 | 20:00 | 82 | Khulna | 52 | 18:00 | 148 | ShahCement | 22 | 08:00
17 | Baroaulia | 60 | 13:00 | 83 | Khulshi | 137 | 16:00 | 149 | Shahjadpur | 53 | 18:00
18 | Baroirhat | 47 | 18:00 | 84 | Kishoreganj | 106 | 18:00 | 150 | Shahjibazar | 81 | 18:30
19 | Bashundhara | 138 | 18:00 | 85 | Kodda | 157 | 15:00 | 151 | Shahmirpur | 43 | 16:00
20 | BashundharaCement | 12 | 00:00 | 86 | Kulaura | 34 | 18:00 | 152 | Shariatpur | 52 | 20:00
21 | Beanibazar | 46 | 18:00 | 87 | Kurigram | 46 | 18:00 | 153 | Sherpur | 100 | 18:00
22 | Benapole | 40 | 18:30 | 88 | Kushtia | 98 | 18:00 | 154 | Shikalbaha | 26 | 12:00
23 | Bhaluka | 112 | 18:00 | 89 | Lalbag | 69 | 18:00 | 155 | Shitalakhya | 69.4 | 13:00
24 | Bhandaria | 34.5 | 21:00 | 90 | Lalmonirhat | 41 | 18:00 | 156 | Sholosohor | 38 | 18:00
25 | Bhangura | 22 | 18:00 | 91 | MI_Cement | 13.2 | 00:00 | 157 | Shyampur | 144 | 02:00
26 | Bheramara(GK) | 38 | 18:00 | 92 | Madanganj | 30 | 19:00 | 158 | Siddhirganj | 106 | 12:00
27 | Bhulta | 225 | 12:00 | 93 | Madaripur | 64 | 19:00 | 159 | Sirajganj | 66 | 19:00
28 | Bog-Sherpur | 54 | 18:00 | 94 | Madartek | 52 | 18:00 | 160 | Sonargaon | 70 | 00:00
29 | Bogura | 116 | 18:30 | 95 | Madunaghat | 41 | 18:30 | 161 | Sreemongol | 52 | 18:00
30 | Borhanuddin | 51 | 21:00 | 96 | Magura | 42 | 16:00 | 162 | Sreepur | 72 | 18:00
31 | Brahmanbaria | 120 | 18:00 | 97 | Mahasthangarh | 44 | 18:00 | 163 | Srinagar | 29.8 | 21:00
32 | Cantonment | 90 | 13:00 | 98 | Manikganj | 90 | 18:00 | 164 | Sunamganj | 40 | 18:00
33 | Chandpur | 45 | 18:00 | 99 | Maniknagar | 56 | 12:00 | 165 | Sylhet | 32 | 18:00
34 | Chandraghona | 26 | 18:00 | 100 | Matarbari | 38 | 18:00 | 166 | Sylhet-132 | 92 | 18:00
35 | Chapai | 44 | 00:00 | 101 | Matuail | 60 | 12:00 | 167 | TK | 22 | 18:00
36 | Charsaidpur | 40 | 11:00 | 102 | Millgate | 101 | 12:00 | 168 | Tangail | 130 | 18:00
37 | Chauddagram | 44 | 13:00 | 103 | Mirpur | 111 | 18:00 | 169 | Thakurgaon | 73 | 18:00
38 | Chhatak | 23 | 18:00 | 104 | Mirsorai | 6 | 18:00 | 170 | Tongi | 114 | 15:00
39 | Chowmuhani | 140 | 18:00 | 105 | Mirzapur | 40 | 18:00 | 171 | Ullahpara | 28 | 20:00
40 | Chuadanga | 65 | 18:00 | 106 | Mithapukur | 42 | 18:00 | 172 | Ullon | 38 | 18:00
41 | Coxsbazar | 94 | 18:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 66 | 12:00
42 | Cumilla(N) | 112 | 18:30 | 108 | Mogbazar | 96.5 | 14:00 | 174 | UttaraNew | 38 | 13:00
43 | Cumilla(S) | 130 | 18:00 | 109 | Mongla | 28 | 12:00 | 175 | Zigatola | 81 | 18:00
44 | Daudkandi | 113 | 19:00 | 110 | Motijheel | 35 | 13:00
45 | Dhaka | 32 | 13:00 | 111 | Munshiganj | 76 | 13:00
46 | Dhamrai | 108 | 18:30 | 112 | Mymensingh | 177 | 18:00
47 | Dhanmondi | 114 | 13:00 | 113 | Naogaon | 80 | 20:00
48 | Dohazari | 73 | 18:00 | 114 | Narail | 34 | 18:00
49 | Faridpur | 107 | 18:00 | 115 | Narinda | 58 | 13:00
50 | Fatullah | 74 | 12:00 | 116 | Narshingdi | 150 | 21:00
51 | Fenchuganj | 27 | 18:00 | 117 | Natore | 102 | 18:00
52 | Feni | 72 | 18:00 | 118 | Nawabganj | 28.2 | 21:00
53 | GPH | 5 | 16:00 | 119 | Netrakona | 102 | 18:00
54 | Ghatail | 50 | 17:00 | 120 | New | 37.6 | 12:00
55 | Ghorashal | 49 | 18:00 | 121 | Niamatpur | 39 | 18:00
56 | Goalpara | 26 | 13:00 | 122 | Noapara | 29 | 18:30
57 | Gollamari | 64 | 13:00 | 123 | PHP | 10 | 12:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-11-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 402 | 03:00 | 386 | 11:00 | Kaliakoir | 381 | 03:00 | 366 | 12:00
| Ashuganj | 303 | 15:00 | 392 | 12:00 | Madunaghat | 405 | 08:00 | 396 | 12:00
| Bhulta | 409 | 03:00 | 394 | 12:00 | Meghnaghat | 396 | 05:00 | 380 | 12:00
| Bibiana | 396 | 00:00 | 387 | 12:00 | Payra | 417 | 04:00 | 408 | 11:00
| BIPTC | 403 | 03:00 | 394 | 17:00 | Rahanpur | 400 | 03:00 | 393 | 18:00
| Bogura | 394 | 03:00 | 384 | 13:00 | Rampal | 411 | 02:00 | 400 | 12:00
| Gopalganj | 410 | 03:00 | 395 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 241 | 03:00 | 231 | 12:00 | Haripur | 240 | 03:00 | 228 | 12:00
| AKSML | 239 | 19:30 | 230 | 11:00 | Hasnabad | 240 | 03:00 | 230 | 12:00
| Aminbazar | 239 | 03:00 | 230 | 12:00 | Hathazari | 244 | 19:00 | 234 | 12:00
| Ashuganj | 243 | 18:30 | 232 | 12:00 | Ishurdi | 242 | 03:00 | 231 | 12:00
| Ashuganj-400 | 242 | 21:00 | 231 | 12:00 | Jhenaidah | 236 | 04:00 | 225 | 13:00
| Baghabari | 236 | 04:00 | 227 | 12:00 | Kaliakoir | 240 | 03:00 | 229 | 12:00
| Barapukuria | 227 | 02:00 | 223 | 07:00 | Keranigonj | 241 | 05:00 | 230 | 12:00
| Barapukuria-230 | 227 | 02:00 | 223 | 07:00 | Khulna(S) | 238 | 03:00 | 226 | 12:00
| Barishal | 244 | 03:00 | 237 | 11:00 | Madunaghat | 239 | 08:00 | 233 | 12:00
| Bheramara | 239 | 03:00 | 228 | 12:00 | Maniknagar | 239 | 03:00 | 228 | 12:00
| Bhulta | 241 | 03:00 | 228 | 12:00 | Meghnaghat | 248 | 00:00 | 239 | 12:00
| Bibiana | 229 | 05:00 | 221 | 16:00 | Meghnaghat-400 | 243 | 03:00 | 233 | 12:00
| BIPTC | 241 | 03:00 | 229 | 12:00 | Mirsorai | 245 | 18:30 | 232 | 11:00
| Bogura | 241 | 06:00 | 235 | 12:00 | Rajshahi | 239 | 03:00 | 227 | 13:00
| Bogura-400 | 241 | 03:00 | 235 | 13:00 | Rampal | 235 | 03:00 | 226 | 12:00
| Borhanuddin | 246 | 01:00 | 240 | 19:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 243 | 18:30 | 232 | 12:00 | Rampura | 239 | 05:00 | 227 | 12:00
| Cumilla(N) | 238 | 18:30 | 228 | 11:00 | Shikalbaha | 242 | 18:30 | 230 | 11:00
| Faridpur | 242 | 01:00 | 233 | 12:00 | Shyampur | 241 | 03:00 | 231 | 12:00
| Fenchuganj | 230 | 03:00 | 224 | 12:00 | Siddhirganj | 242 | 05:00 | 230 | 12:00
| Ghorashal | 240 | 01:00 | 235 | 00:00 | Sirajgonj | 244 | 00:00 | 240 | 11:00
| Ghorashal-230 | 239 | 02:00 | 226 | 12:00 | Sreepur | 240 | 03:00 | 230 | 12:00
| Gopalganj | 242 | 03:00 | 233 | 12:00 | Tongi | 239 | 00:00 | 225 | 11:00
| GPH | 241 | 18:00 | 231 | 12:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 139 | 03:00 | 130 | 00:00 | Kushtia | 140 | 01:00 | 134 | 13:00
| Agargaon | 140 | 03:00 | 133 | 12:00 | Lalbag | 138 | 03:00 | 131 | 12:00
| Agrabad | 139 | 18:30 | 132 | 11:00 | Lalmonirhat | 130 | 05:00 | 120 | 18:30
| AKS | 136 | 18:30 | 131 | 11:00 | Madanganj | 133 | 08:00 | 125 | 12:00
| Aminbazar | 141 | 04:00 | 133 | 13:00 | Madaripur | 135 | 00:00 | 130 | 12:00
| Amnura | 134 | 03:00 | 130 | 07:00 | Madartek | 138 | 03:00 | 131 | 15:00
| Ashuganj | 141 | 05:00 | 136 | 12:00 | Madunaghat | 140 | 18:00 | 133 | 11:00
| Bagerhat | 140 | 01:00 | 131 | 13:00 | Magura | 140 | 01:00 | 132 | 13:00
| Bakulia | 138 | 18:00 | 131 | 12:00 | Mahasthangarh | 137 | 03:00 | 133 | 08:00
| Banani | 139 | 04:00 | 129 | 12:00 | Manikganj | 135 | 03:00 | 122 | 16:00
| Bangabhaban | 137 | 03:00 | 128 | 12:00 | Maniknagar | 137 | 08:00 | 128 | 12:00
| Barapukuria | 137 | 02:00 | 132 | 08:00 | Matarbari | 128 | 16:00 | 123 | 00:00
| Barguna | 141 | 18:00 | 133 | 11:00 | Matuail | 135.7 | 22:00 | 127.5 | 12:00
| Barishal | 135 | 01:00 | 129 | 12:00 | Millgate | 140 | 01:00 | 131 | 12:00
| Barishal-230 | 136 | 01:00 | 131 | 11:00 | Mirpur | 141 | 05:00 | 134 | 12:00
| Baroaulia | 140 | 18:00 | 133 | 12:00 | Mirzapur | 131 | 18:30 | 125 | 12:00
| Baroirhat | 137 | 19:00 | 131 | 11:00 | Mithapukur | 135 | 04:00 | 13 | 15:00
| Bashundhara | 140 | 01:00 | 129 | 12:00 | MI_Cement | 140 | 04:00 | 133 | 12:00
| BashundharaCement | 133 | 08:00 | 125 | 12:00 | Modern | 139 | 18:00 | 132 | 10:00
| Beanibazar | 132 | 07:00 | 127 | 11:00 | Mogbazar | 141 | 08:00 | 131 | 12:00
| Benapole | 138 | 03:00 | 131 | 12:00 | Mongla | 139 | 03:00 | 132 | 12:00
| Bhaluka | 134 | 04:00 | 128 | 12:00 | Motijheel | 137 | 03:00 | 128 | 12:00
| Bhandaria | 134 | 04:00 | 127 | 12:00 | Munshiganj | 134 | 04:00 | 126 | 12:00
| Bhangura | 141 | 04:00 | 136 | 12:00 | Mymensingh | 136 | 18:30 | 125 | 12:00
| Bheramara | 140 | 03:00 | 135 | 12:00 | Naogaon | 137 | 06:00 | 132 | 12:00
| Bheramara(GK) | 140 | 04:00 | 135 | 12:00 | Narail | 140 | 03:00 | 133 | 13:00
| Bhulta | 129 | 22:00 | 120 | 11:00 | Narinda | 137 | 08:00 | 128 | 12:00
| Bog-Sherpur | 138 | 03:00 | 135 | 07:00 | Narshingdi | 136 | 07:00 | 122 | 12:00
| Bogura | 139 | 05:00 | 135 | 08:00 | Natore | 139 | 03:00 | 133 | 12:00
| Bogura-230 | 139 | 06:00 | 135 | 07:00 | Nawabganj | 138 | 03:00 | 131 | 12:00
| Brahmanbaria | 138 | 08:00 | 131 | 12:00 | Netrakona | 133 | 00:00 | 121 | 16:00
| Cantonment | 139 | 03:00 | 132 | 12:00 | New | 141 | 04:00 | 132 | 12:00
| Chandpur | 140 | 08:00 | 130 | 23:00 | Niamatpur | 135 | 06:00 | 132 | 00:00
| Chandraghona | 139 | 18:00 | 133 | 11:00 | Noapara | 141 | 05:00 | 132 | 13:00
| Chapai | 133 | 02:00 | 130 | 00:00 | Pabna | 141 | 03:00 | 135 | 12:00
| Charsaidpur | 134 | 04:00 | 126 | 12:00 | Palashbari | 133 | 04:00 | 129 | 08:00
| Chauddagram | 139 | 18:00 | 130 | 11:00 | Panchagarh | 131 | 03:00 | 121 | 08:00
| Chhatak | 131 | 06:00 | 127 | 11:00 | Patuakhali | 140 | 18:30 | 131 | 11:00
| Chowmuhani | 135 | 18:00 | 128 | 00:00 | Payra | 139 | 18:30 | 134 | 11:00
| Chuadanga | 140 | 03:00 | 129 | 12:00 | PHP | 137 | 18:30 | 129 | 12:00
| Coxsbazar | 127 | 09:00 | 122 | 11:00 | Postogola | 141 | 03:00 | 13 | 16:00
| Cumilla(N) | 139 | 18:30 | 132 | 11:00 | Purbachal | 141 | 03:00 | 129 | 12:00
| Cumilla(S) | 138 | 18:00 | 129 | 17:00 | Purbasadipur | 130 | 18:30 | 121 | 08:00
| Daudkandi | 130 | 18:00 | 124 | 12:00 | Rahanpur | 136 | 03:00 | 134 | 00:00
| Dhaka | 139 | 02:00 | 130 | 12:00 | Rahim | 134 | 05:00 | 126 | 12:00
| Dhamrai | 138 | 03:00 | 131 | 11:00 | Rajbari | 136 | 03:00 | 129 | 13:00
| Dhanmondi | 139.5 | 05:00 | 129 | 16:00 | Rajendrapur | 134 | 18:30 | 121 | 16:00
| Dohazari | 135 | 18:00 | 129 | 11:00 | Rajshahi | 139 | 06:00 | 132 | 16:00
| Faridpur | 136 | 02:00 | 131 | 11:00 | Rajshahi-230 | 138 | 02:00 | 120 | 21:00
| Fatullah | 139 | 04:00 | 133 | 12:00 | Ramganj | 137 | 19:00 | 128 | 01:00
| Fenchuganj | 138 | 08:00 | 133 | 12:00 | Rampur | 139 | 18:00 | 131 | 12:00
| Feni | 136 | 18:30 | 128 | 16:00 | Rampura | 138 | 01:00 | 130 | 12:00
| Ghatail | 132 | 18:30 | 123 | 16:00 | Rangamati | 139 | 18:00 | 132 | 12:00
| Ghorashal | 142 | 06:00 | 137 | 15:00 | Rangpur | 134 | 03:00 | 130 | 07:00
| Goalpara | 143 | 03:00 | 133 | 12:00 | Ruppur | 142 | 02:00 | 136 | 11:00
| Gollamari | 142 | 06:00 | 135 | 11:00 | Saidpur | 134 | 03:00 | 124 | 08:00
| Gopalganj | 138 | 02:00 | 131 | 12:00 | Satkhira | 141 | 04:00 | 133 | 12:00
| Gopalganj-400 | 137 | 03:00 | 131 | 12:00 | Satmasjid | 140 | 03:00 | 132 | 12:00
| Gulshan | 138 | 01:00 | 130 | 12:00 | Savar | 141 | 18:00 | 130 | 12:00
| Halishahar | 139 | 18:30 | 131 | 12:00 | SevenRings | 142 | 00:00 | 134 | 12:00
| Haripur | 135 | 02:00 | 127 | 12:00 | ShahCement | 134 | 04:00 | 126 | 12:00
| HaripurSBU | 135 | 00:00 | 127 | 12:00 | Shahjadpur | 145 | 03:00 | 140 | 11:00
| Hasnabad | 142 | 04:00 | 134 | 12:00 | Shahjibazar | 138 | 08:00 | 131 | 15:00
| Hathazari | 142 | 19:00 | 135 | 12:00 | Shahmirpur | 139 | 18:30 | 132 | 12:00
| Ishurdi | 142 | 03:00 | 136 | 12:00 | Shariatpur | 136 | 03:00 | 130 | 12:00
| Jaldhaka | 131 | 04:00 | 122 | 07:00 | Sherpur | 138 | 18:30 | 121 | 07:00
| Jamalpur | 140 | 18:30 | 124 | 02:00 | Shikalbaha | 127 | 18:00 | 121 | 10:00
| Jashore | 140 | 04:00 | 131 | 13:00 | Shikalbaha-230 | 141 | 18:30 | 132 | 11:00
| Jhenaidah | 141 | 01:00 | 134 | 12:00 | Shitalakhya | 140 | 04:00 | 133 | 12:00
| Jhenaidah-230 | 142 | 03:00 | 134 | 12:00 | Sholosohor | 139 | 18:00 | 132 | 12:00
| Joydebpur | 140 | 02:00 | 131 | 11:00 | Shyampur | 139 | 01:00 | 131 | 12:00
| Joypurhat | 136 | 02:00 | 131 | 12:00 | Shyampur-230 | 138 | 03:00 | 131 | 12:00
| Juldah | 139 | 18:00 | 132 | 11:00 | Siddhirganj | 136 | 22:00 | 128 | 12:00
| Kabirpur | 139 | 04:00 | 123 | 16:00 | Sirajganj | 139 | 00:00 | 135 | 12:00
| Kachua | 139 | 19:00 | 131 | 16:00 | Sonargaon | 126 | 18:30 | 121 | 00:00
| Kaliakoir | 140 | 04:00 | 126 | 16:00 | Sreemongol | 137 | 08:00 | 131 | 10:00
| Kallyanpur | 137 | 00:00 | 132 | 12:00 | Sreepur | 137 | 03:00 | 131 | 11:00
| Kalurghat | 141 | 18:30 | 133 | 11:00 | Srinagar | 137 | 04:00 | 131 | 12:00
| Kamrangirchar | 137 | 06:00 | 131 | 12:00 | SSM | 142 | 18:00 | 139 | 14:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 128 | 00:00 | 126 | 12:00
| Kazla | 137 | 04:00 | 127 | 13:00 | Sylhet | 133 | 08:00 | 129 | 11:00
| Keranigonj | 138 | 03:00 | 131 | 12:00 | Sylhet-132 | 132 | 03:00 | 128 | 16:00
| Khagrachori | 138 | 18:30 | 131 | 12:00 | Tangail | 130 | 18:30 | 122 | 16:00
| Khulna | 141 | 01:00 | 134 | 12:00 | Thakurgaon | 132 | 18:30 | 120 | 08:00
| Khulna(S) | 143 | 03:00 | 135 | 12:00 | TK | 139 | 18:30 | 132 | 12:00
| Khulshi | 137 | 18:30 | 130 | 12:00 | Tongi | 142 | 04:00 | 134 | 11:00
| Kishoreganj | 134 | 00:00 | 128 | 12:00 | Ullahpara | 141 | 01:00 | 136 | 16:00
| Kodda | 138 | 18:00 | 121 | 16:00 | Ullon | 139 | 04:00 | 130 | 12:00
| KSRM | 140 | 17:00 | 134 | 12:00 | Uttara | 142 | 04:00 | 134 | 12:00
| Kulaura | 135 | 08:00 | 132 | 12:00 | UttaraNew | 140 | 06:00 | 131 | 11:00
| Kurigram | 132 | 04:00 | 124 | 08:00 | Zigatola | 138 | 04:00 | 131 | 12:00

## L-Curve
Date | 2024-11-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1298 | 4790 | 4127 | 8917 |  |  |  | QF-LDC-11
0:30 | 1341 | 4690 | 4016 | 8706 | Date: | 2024-11-18
1:00 | 1384 | 4590 | 3905 | 8495
1:30 | 1341 | 4510.5 | 3753.5 | 8264
2:00 | 1298 | 4431 | 3602 | 8033
2:30 | 1293 | 4408 | 3542.5 | 7950.5 | [5 empty] | Gen. at Eve. Peak | 10934 | 10934 MW (18:00 )
3:00 | 1288 | 4385 | 3483 | 7868 | [6 empty] | 18:00
3:30 | 1312 | 4252.5 | 3450 | 7702.5 | [5 empty] | Gen. at Day Peak | 9704 | 9704 MW (12:00 )
4:00 | 1336 | 4120 | 3417 | 7537 | [6 empty] | 12:00
4:30 | 1347 | 4065.5 | 3415.5 | 7481 | [5 empty] | Highest Generation | 10934
5:00 | 1358 | 4011 | 3414 | 7425 | [6 empty] | 18:00
5:30 | 1341 | 4082 | 3492.5 | 7574.5
6:00 | 1324 | 4153 | 3571 | 7724
6:30 | 1199 | 4352.5 | 3697.5 | 8050
7:00 | 1074 | 4552 | 3824 | 8376
7:30 | 1080 | 4553 | 3937 | 8490
8:00 | 1086 | 4554 | 4050 | 8604
8:30 | 1280 | 4598.5 | 4071 | 8669.5
9:00 | 1474 | 4643 | 4092 | 8735
9:30 | 1471 | 4633 | 4098.5 | 8731.5
10:00 | 1468 | 4623 | 4105 | 8728
10:30 | 1605 | 4817.5 | 4153 | 8970.5
11:00 | 1742 | 5012 | 4201 | 9213
11:30 | 1749 | 5113 | 4345.5 | 9458.5
12:00 | 1756 | 5214 | 4490 | 9704
12:30 | 1709 | 5342.5 | 4532 | 9874.5
13:00 | 1662 | 5471 | 4574 | 10045
13:30 | 1633 | 5392 | 4455 | 9847
14:00 | 1604 | 5313 | 4336 | 9649
14:30 | 1631 | 5299.5 | 4321.5 | 9621
15:00 | 1658 | 5286 | 4307 | 9593
15:30 | 1625 | 5223.5 | 4262 | 9485.5
16:00 | 1592 | 5161 | 4217 | 9378
16:30 | 1509 | 5244.5 | 4270.5 | 9515
17:00 | 1426 | 5328 | 4324 | 9652
17:30 | 1251 | 5848 | 4445 | 10293
18:00 | 1076 | 6368 | 4566 | 10934
18:30 | 1094 | 6300.5 | 4511.5 | 10812
19:00 | 1112 | 6233 | 4457 | 10690
19:30 | 1162 | 6041 | 4490 | 10531
20:00 | 1164 | 5943 | 4490 | 10433 |  |  |  | Executive Engineer
20:30 | 1145 | 5828.5 | 4450.5 | 10279 |  |  |  | Network Operation Division
21:00 | 1126 | 5714 | 4411 | 10125
21:30 | 1142 | 5572 | 4334 | 9906
22:00 | 1158 | 5430 | 4257 | 9687 |  |  |  |  | Page 6 of 7
22:30 | 1185 | 5250.5 | 4207 | 9457.5
23:00 | 1212 | 5071 | 4157 | 9228
23:30 | 1255 | 4930.5 | 4142 | 9072.5
24:00 | 1298 | 4790 | 4127 | 8917
10934 MW (18:00 )
9704 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-11-18 |  |  | Energy |  | 223382636
[16 empty] | Date: | 2024-11-18 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | Nepal | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 2896 | 899 | 0 | 2021 | 0 | 412 | 1774 | 96 | 0 | 0 | 54 | 755 | 0 | 10 | 0
0:30 | 2910.5 | 903 | 0 | 2117 | 0 | 226 | 1713.5 | 93 | 0 | 0 | 54 | 683 | 0 | 6 | 0 |  |  | Date: | 44152
1:00 | 2925 | 907 | 0 | 2213 | 0 | 40 | 1653 | 90 | 0 | 0 | 54 | 611 | 0 | 2 | 0
1:30 | 2943 | 907.5 | 0 | 2200 | 0 | 20 | 1532.5 | 89.5 | 0 | 0 | 51 | 519.5 | 0 | 1 | 0 | [8 empty] | Total Energy | 223.3826 | 223.3826 | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 2961 | 908 | 0 | 2187 | 0 | 0 | 1412 | 89 | 0 | 0 | 48 | 428 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2958 | 907.5 | 0 | 2167 | 0 | 0 | 1357.5 | 88.5 | 0 | 0 | 49 | 423 | 0 | 0 | 0 | [8 empty] | Energy Requirement | 223.3826 | 223.3826
3:00 | 2955 | 907 | 0 | 2147 | 0 | 0 | 1303 | 88 | 0 | 0 | 50 | 418 | 0 | 0 | 0
3:30 | 2879.5 | 907.5 | 0 | 2072.5 | 0 | 0 | 1290 | 87 | 0 | 0 | 47 | 419 | 0 | 0 | 0 | [7 empty] | Shortage
4:00 | 2804 | 908 | 0 | 1998 | 0 | 0 | 1277 | 86 | 0 | 0 | 44 | 420 | 0 | 0 | 0
4:30 | 2778.5 | 907.5 | 0 | 1966 | 0 | 0 | 1277 | 85.5 | 0 | 0 | 46 | 420.5 | 0 | 0 | 0
5:00 | 2753 | 907 | 0 | 1934 | 0 | 0 | 1277 | 85 | 0 | 0 | 48 | 421 | 0 | 0 | 0
5:30 | 2835 | 907 | 0 | 2002.5 | 0 | 0 | 1276.5 | 85 | 0 | 0 | 48 | 420.5 | 0 | 0 | 0
6:00 | 2917 | 907 | 0 | 2071 | 0 | 0 | 1276 | 85 | 0 | 0 | 48 | 420 | 0 | 0 | 0
6:30 | 3003 | 907 | 0 | 2135.5 | 0 | 38 | 1341 | 85 | 0 | 6 | 47 | 465.5 | 22 | 0 | 0 | [6 empty] | Coal
7:00 | 3089 | 907 | 0 | 2200 | 0 | 76 | 1406 | 85 | 0 | 12 | 46 | 511 | 44 | 0 | 0
7:30 | 2926 | 906.5 | 0 | 2121.5 | 0 | 201 | 1508 | 90.5 | 0 | 14 | 41 | 561 | 120.5 | 0 | 0 | [5 empty] | Oil
8:00 | 2763 | 906 | 0 | 2043 | 0 | 326 | 1610 | 96 | 0 | 16 | 36 | 611 | 197 | 0 | 0
8:30 | 2737 | 906.5 | 0 | 2007.5 | 0 | 344 | 1609.5 | 96 | 0 | 32 | 38 | 610.5 | 288.5 | 0 | 0
9:00 | 2711 | 907 | 0 | 1972 | 0 | 362 | 1609 | 96 | 0 | 48 | 40 | 610 | 380 | 0 | 0
9:30 | 2728.5 | 908.5 | 0 | 1945 | 0 | 361.5 | 1544 | 96 | 0 | 48 | 43 | 611.5 | 445.5 | 0 | 0
10:00 | 2746 | 910 | 0 | 1918 | 0 | 361 | 1479 | 96 | 0 | 48 | 46 | 613 | 511 | 0 | 0
10:30 | 2856.5 | 910.5 | 0 | 1983 | 0 | 361.5 | 1510.5 | 95.5 | 0 | 57 | 51 | 613.5 | 531.5 | 0 | 0
11:00 | 2967 | 911 | 0 | 2048 | 0 | 362 | 1542 | 95 | 0 | 66 | 56 | 614 | 552 | 0 | 0
11:30 | 3002 | 910 | 0 | 2140.5 | 0 | 383 | 1616 | 95 | 0 | 61.5 | 56 | 615 | 579.5 | 0 | 0
12:00 | 3037 | 909 | 0 | 2233 | 0 | 404 | 1690 | 95 | 0 | 57 | 56 | 616 | 607 | 0 | 0
12:30 | 3060.5 | 909.5 | 0 | 2217 | 0 | 535 | 1729 | 95 | 0 | 67 | 53 | 631 | 577.5 | 0 | 0
13:00 | 3084 | 910 | 0 | 2201 | 0 | 666 | 1768 | 95 | 0 | 77 | 50 | 646 | 548 | 0 | 0
13:30 | 3084 | 910 | 0 | 2201 | 0 | 666 | 1768 | 95 | 0 | 77 | 50 | 646 | 548 | 0 | 0
14:00 | 3084 | 910 | 0 | 2201 | 0 | 666 | 1768 | 95 | 0 | 77 | 50 | 646 | 548 | 0 | 0
14:30 | 3002.5 | 909.5 | 0 | 2187.5 | 0 | 638 | 1770.5 | 90.5 | 0 | 71.5 | 51 | 678 | 419.5 | 0.5 | 0
15:00 | 2921 | 909 | 0 | 2174 | 0 | 610 | 1773 | 86 | 0 | 66 | 52 | 710 | 291 | 1 | 0
15:30 | 2939 | 909.5 | 0 | 2200.5 | 0 | 592.5 | 1744 | 85.5 | 0 | 45 | 50 | 710.5 | 205 | 4 | 0
16:00 | 2957 | 910 | 0 | 2227 | 0 | 575 | 1715 | 85 | 0 | 24 | 48 | 711 | 119 | 7 | 0
16:30 | 2924 | 904 | 0 | 2197 | 0 | 767 | 1707 | 82.5 | 0 | 100 | 52 | 712 | 62 | 7.5 | 0
17:00 | 2891 | 898 | 0 | 2167 | 0 | 959 | 1699 | 80 | 0 | 176 | 56 | 713 | 5 | 8 | 0
17:30 | 2955.5 | 898 | 0 | 2220.5 | 0 | 1315.5 | 1720.5 | 80 | 0 | 322 | 58 | 714 | 2.5 | 6.5 | 0
18:00 | 3020 | 898 | 0 | 2274 | 0 | 1672 | 1742 | 80 | 0 | 468 | 60 | 715 | 0 | 5 | 0
18:30 | 3014.5 | 897 | 0 | 2227.5 | 0 | 1592 | 1747 | 80.5 | 0 | 451.5 | 59 | 733.5 | 0 | 9.5 | 0
19:00 | 3009 | 896 | 0 | 2181 | 0 | 1512 | 1752 | 81 | 0 | 435 | 58 | 752 | 0 | 14 | 0
19:30 | 3063 | 897 | 0 | 2286 | 0 | 1314 | 1751 | 87 | 0 | 311 | 58 | 756 | 0 | 8 | 0
20:00 | 3012 | 897 | 0 | 2272 | 0 | 1283 | 1751 | 96 | 0 | 297 | 58 | 758 | 0 | 9 | 0
20:30 | 3011 | 897 | 0 | 2266.5 | 0 | 1206.5 | 1756.5 | 96 | 0 | 229.5 | 56 | 755.5 | 0 | 4.5 | 0
21:00 | 3010 | 897 | 0 | 2261 | 0 | 1130 | 1762 | 96 | 0 | 162 | 54 | 753 | 0 | 0 | 0
21:30 | 2989.5 | 897.5 | 0 | 2229.5 | 0 | 998.5 | 1769 | 96 | 0 | 114 | 55 | 754 | 0 | 3 | 0
22:00 | 2969 | 898 | 0 | 2198 | 0 | 867 | 1776 | 96 | 0 | 66 | 56 | 755 | 0 | 6 | 0
22:30 | 2979.5 | 898 | 0 | 2210 | 0 | 644.5 | 1774.5 | 96 | 0 | 33 | 55 | 756.5 | 0 | 10.5 | 0
23:00 | 2990 | 898 | 0 | 2222 | 0 | 422 | 1773 | 96 | 0 | 0 | 54 | 758 | 0 | 15 | 0
23:30 | 2943 | 898.5 | 0 | 2121.5 | 0 | 417 | 1773.5 | 96 | 0 | 0 | 54 | 756.5 | 0 | 12.5 | 0 |  |  | Max Temp. in Dhaka |  | 30.1°C
24:00 | 2896 | 899 | 0 | 2021 | 0 | 412 | 1774 | 96 | 0 | 0 | 54 | 755 | 0 | 10 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on Y13: Author:

## Generation
2024-11-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 89 | 88 | 86 | 85 | 85 | 85 | 96 | 96 | 96 | 95 | 95 | 95 | 93 | 86 | 85 | 80 | 80 |  | 81 | 87 | 96 | 96 | 96 | 96 | 96 | 2110282
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 1 | 10 | [8 empty] | 25396
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 10 | 15 | 19 | 20 | 20 | 19 | 16 | 12 |  | 0 | [9 empty] | 138510
6 | Sikalbaha 225MW CCPP (Gas) | 231 | 233 | 232 | 232 | 232 | 232 | 232 | 232 | 231 | 227 | 226 | 225 | 225 | 225 | 223 | 224 | 226 | 224 |  | 224 | 224 | 226 | 225 | 225 | 229 | 231 | 5365309
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 34 |  | 34 | [6 empty] | 56604
12 | Hathazari 100 MW peaking PP | [17 empty] | 8 |  | 34 | 34 | 34 | 34 |  |  |  | 96624
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 5 | 46 |  | 17 | 17 | 17 |  |  |  |  | 125454
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [17 empty] | 37 |  | 45 | 45 | 45 |  |  |  |  | 108160
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 250 | 250 | 300 | 335 | 280 | 250 | 250 | 335 | 335 | 335 | 280 | 335 | 330 | 300 | 335 |  | 335 | 335 | 335 | 335 | 335 | 335 | 280 | 7571394
18 | Kodda 300 MW PP Unit-2 (Summit) | [26 empty] | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 199 | 199 | 199 | 108 | 108 | 150 | 185 | 185 | 185 | 148 | 148 | 185 | 185 | 185 | 185 | 185 | 185 | 185 |  | 190 | 192 | 194 | 197 | 197 | 199 | 199 | 4265455
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 535 | 420 | 400 | 400 | 400 | 400 | 440 | 500 | 500 | 450 | 500 | 575 | 612 | 612 | 612 | 552 | 570 | 612 |  | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 12730908
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 37 | 33 | 33 | 33 | 37 | 37 | 36 | 36 | 36 | 36 |  | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 941976
33 | Ashuganj 225 MW CCPP | 182 | 190 | 181 | 186 | 188 | 191 | 205 | 182 | 182 | 183 | 199 | 181 | 181 | 183 | 182 | 196 | 183 | 181 |  | 181 | 193 | 182 | 181 | 181 | 180 | 185 | 4602000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 290 | 300 | 290 | 295 | 300 | 310 | 345 | 280 | 280 | 280 | 335 | 310 | 310 | 280 | 290 | 315 | 290 | 310 |  | 290 | 315 | 290 | 290 | 290 | 290 | 295 | 7616200
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 70 | 72 | 70 | 70 | 80 | 80 | 90 | 90 | 90 | 50 | 50 | 50 | 50 | 50 | 70 | 50 | 50 | 50 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1573650
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [26 empty] | 0
| Meghnaghat Unique power | 235 | 239 | 240 | 226 | 226 | 229 | 224 | 228 | 230 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 239 | 5683181
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 400 | 400 | 350 | 350 | 380 | 420 | 360 | 320 | 320 | 400 | 450 | 450 | 370 | 420 | 420 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9773500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 35 | 45 | 67 | 67 | 67 | 66 | 66 | 32 | 29 | 26 | 26 | 26 | 25 | 23 | 25 | 27 | 29 | 29 |  | 31 | 33 | 33 | 34 | 34 | 34 | 34 | 847680
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 16 | 30 | 40 | 37 | 49 | 35 | 39 | 28 | 11 | 0 | [9 empty] | 290840
44 | Fenchugonj CCPP Phase-1 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  | 27 | 27 | 27 | 27 | 27 | 28 | 28 | 642000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 28 | 29 |  | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 680280
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 61 | 62 | 62 | 62 | 62 | 40 | 40 | 40 | 60 | 58 | 59 | 59 | 59 | 60 | 40 | 61 |  | 62 | 61 | 60 | 62 | 62 | 62 | 62 | 1375392
48 | Shahjibazar 86 MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 41 | 41 | 86 | 86 | 86 | 41 | 41 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1868160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 136 | 137 | 137 | 137 | 137 | 137 | 138 | 138 | 137 | 135 | 135 | 133 | 133 | 133 | 131 | 131 | 131 | 131 |  | 134 | 134 | 134 | 134 | 134 | 135 | 135 | 3268230
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [6 empty] | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 42288
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 333072
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 290 | 290 | 295 | 300 | 315 | 315 | 300 | 280 | 295 | 310 | 310 | 300 | 280 | 295 | 295 | 310 | 310 |  | 270 | 315 | 300 | 300 | 285 | 270 | 290 | 7259000
| Bibiyana South 400 MW | 316 | 316 | 316 | 316 | 316 | 316 | 346 | 316 | 316 | 316 | 350 | 346 | 346 | 353 | 345 | 360 | 345 | 345 |  | 320 | 335 | 320 | 320 | 320 | 320 | 316 | 8027800
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 17 | [8 empty] | 42240
59 | Tangail Palli Power Gen 22 MW | 24 | [7 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 10 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 279360
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 54 | 48 | 50 | 44 | 48 | 48 | 46 | 36 | 40 | 46 | 56 | 56 | 50 | 54 | 52 | 48 | 56 | 60 |  | 58 | 58 | 58 | 54 | 56 | 54 | 54 | 1212480
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 32 | 38 | 40 | 40 | 35 | 9 | 6 | 6 | 6 | 2 | 13 | 4 | 2 | 5 | 10 | 2 |  | 17 | 20 | 27 | 29 | 29 | 40 | 36 | 510240
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 12 | 9 | 12 | 18 | 18 | 18 | 15 | 18 |  | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 366960
69 | Summit Ashulia | 19 | 18 | 15 | 15 | 15 | 9 | 18 | 18 | 24 | 23 | 23 | 0 | 22 | 22 | 19 | 20 | 20 | 20 |  | 21 | 21 | 21 | 22 | 0 | 16 | 16 | 444000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 15 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 494280
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 18 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 446760
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 810800
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [16 empty] | 17 | 17 | [8 empty] | 30780
| Chowmuhani 113 MW | [16 empty] | 36 | 92 |  | 93 | 95 | 94 | 92 | 55 | 26 | 26 | 582960
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 54 | 54 | 54 | 54 | 90 | 144 |  | 108 | 54 | 54 | 54 | 54 | 17 | 17 | 777600
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150 MW PP | [6 empty] | 12 | 16 | 48 | 48 | 48 | 48 | 64 | 48 | 48 | 16 | 48 | 115 |  | 82 | 48 | 32 | 16 | 16 |  |  | 701280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 12 | [8 empty] | 33403
| Gazipur 100 MW PP | [13 empty] | 17 | 17 | 17 | 20 | 52 |  | 17 | 17 | 17 |  |  |  |  | 182400
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 27480
| Jodiac Power | [12 empty] | 25 | 35 | 35 | 35 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 531898
| Karnaphuli Power Ltd. | [16 empty] | 4 | 48 |  | 17 | 17 | 17 |  |  |  |  | 121270
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 311 | 312 | 297 | 270 | 273 | 278 | 287 | 253 | 283 | 284 | 298 | 298 | 290 | 315 | 292 | 319 | 269 | 288 |  | 276 | 300 | 292 | 283 | 258 | 296 | 110 | 7014080
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [15 empty] | 4 | 12 | 13 | [8 empty] | 33600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 21 | 33 | 34 | 34 | 5 | 5 | 15 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 31 | 33 | 34 | 34 | 34 | 717336
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 45 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1040120
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 8 | 8 |  | 8 | [6 empty] | 28080
95 | Patenga 50MW PP (Baraka) | [11 empty] | 1 | 11 | 12 | 12 | 12 | 14 | 25 |  | 32 | 33 | 27 | 28 | 26 | 13 | 6 | 230400
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 1 | 19 |  | 44 | 25 | 24 | 25 |  |  |  | 137280
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [26 empty] | 0
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 2 | 17 |  | 17 | [6 empty] | 38318
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 12050
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 8 | 36 |  | 51 | 54 | 35 | 35 | 35 | 17 | 17 | 260640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 16 | [5 empty] | 8 | 41 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 65 | 96 |  | 75 | 75 | 75 | 75 | 75 | 60 | 60 | 1077600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 7 | 17 | 16 | 17 | 17 | 17 | 16 | 16 | 17 | 17 | 36 |  | 76 | 50 | 44 | 16 |  |  |  | 351360
115 | Juldah 100 MW PP Unit-3 (Acorn) | [12 empty] | 16 | 25 | 25 | 25 | 48 | 75 |  | 100 | 100 | 100 | 70 | 50 | 12 | 12 | 599040
116 | Chandpur 200 MW (Desh energy) | [6 empty] | 64 | 211 | 218 | 218 | 218 | 218 | 218 | 218 | 100 | 68 | 68 | 100 |  | 100 | 51 | 51 | 51 | 51 | 17 | 17 | 2436960
117 | Ashuganj 150 MW PP (Midland) | [12 empty] | 15 | 50 | 50 | 50 | 53 | 80 |  | 117 | 122 | 124 | 80 | 50 | 20 | 20 | 801236
118 | Bibiyana-III 400 MW CCPP | 316 | 317 | 312 | 300 | 235 | 225 | 225 | 225 | 296 | 375 | 385 | 386 | 382 | 343 | 386 | 387 | 365 | 385 |  | 384 | 384 | 385 | 383 | 370 | 371 | 323 | 8471000
| Jamalpur 115 MW PP (United) | [6 empty] | 4 | 35 | 8 | 8 | 8 | 12 | 24 | 24 | 8 | 8 | 19 | 54 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 525600
| Anwara 300 MW PP (United) | [7 empty] | 30 | 15 | 15 | 15 | 15 | 100 | 100 | 106 | 87 | 87 | 87 |  | 87 | 51 | 51 | 51 | 51 | 51 | 51 | 1008655
| Juldah unit-2 (Acorn) | [11 empty] | 10 | 12 | 12 | 12 | 25 | 25 | 50 |  | 50 | 50 | 50 | 50 | 50 | 12 | 12 | 365760
| Anlima Energy Ltd. | [11 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 32 |  | 53 | 53 | 53 | 53 | 53 | 20 | 17 | 411491
| Bhairob 54.5 MW | [16 empty] | 8 | 28 |  | 35 | 35 | 35 | 35 | 35 |  |  | 191520
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 9 | 17 | 23 |  | 27 | 26 | 20 | 12 | 5 | 0 | [9 empty] | 163397
| Chandpur 115(Doreen) | [16 empty] | 5 | 47 |  | 51 | 51 | 51 | 51 | 51 |  |  | 291840
| Kanchan Purbachal Power Generation Ltd. | [7 empty] | 2 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 417240
| Mirsharai 150 MW (Oil) | [16 empty] | 54 | 160 |  | 108 | 54 | 54 | 54 |  |  |  | 424873
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 8 | 5 |  | 14 | 8 | 9 | 0 | 6 | 15 | 10 | 70560
| Sonagazi 75 MW Solar Plant | [6 empty] | 8 | 28 | 49 | 64 | 69 | 72 | 64 | 55 | 39 | 18 | 1 | [9 empty] | 467945
Matarbari 2*600 MW (CPGCL)
Meghnaghat (Reliance) 718MW CCPP
| Sreepur 150 MW | [10 empty] | 18 | 9 | 13 | 18 | 18 | 8 | [10 empty] | 76800
120
121 | Eastern Zone Total | 4590 | 4431 | 4385 | 4120 | 4011 | 4153 | 4552 | 4554 | 4643 | 4623 | 5012 | 5214 | 5471 | 5313 | 5286 | 5161 | 5328 | 6368 |  | 6233 | 6041 | 5943 | 5714 | 5430 | 5071 | 4790 | 122680317
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [26 empty] | 0
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 6 | 24 | 45 | 62 | 72 | 75 | 68 | 55 | 37 | 16 | 2 | [9 empty] | 466560
132 | Rampal 1320 MW (BIFPCL) | 367 | 368 | 370 | 370 | 371 | 371 | 371 | 370 | 370 | 370 | 371 | 370 | 370 | 370 | 370 | 370 | 370 | 370 |  | 369 | 369 | 369 | 370 | 370 | 370 | 369 | 8952727
133 | United Payra Power Ltd. | [11 empty] | 7 | 54 | 54 | 54 | 54 | 150 | 150 |  | 150 | 150 | 150 | 150 | 72 | 35 | 35 | 1135200
| Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 180 | 220 | 220 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 5196590
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3284
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 81 | 81 | 81 | 81 | 81 | 131 | 131 | 127 | 82 | 82 | 82 | 127 | 127 | 82 | 82 | 82 | 123 | 123 |  | 123 | 123 | 123 | 127 | 127 | 127 | 127 | 2657000
141 | Bhola 33 MW PP (Venture) | 7 | 6 | 6 | 6 | 6 | 6 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 |  | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 134030
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
| Bheramara HVDC | 907 | 908 | 907 | 908 | 907 | 907 | 907 | 906 | 907 | 910 | 911 | 909 | 910 | 910 | 909 | 910 | 898 | 898 |  | 896 | 897 | 897 | 897 | 898 | 898 | 899 | 21834909
147 | Nepal
148 | Bheramara 410 MW CCPP | 319 | 319 | 319 | 250 | 250 | 300 | 345 | 280 | 240 | 240 | 240 | 324 | 320 | 270 | 270 | 270 | 290 | 290 |  | 285 | 285 | 286 | 281 | 272 | 272 | 273 | 6990624
149 | Payra 1320 MW | 550 | 420 | 330 | 300 | 300 | 300 | 390 | 540 | 540 | 500 | 510 | 570 | 622 | 622 | 622 | 622 | 590 | 590 |  | 600 | 600 | 600 | 610 | 622 | 622 | 622 | 13742200
150
151 | Barapukuria TPP Unit-1 | 69 | 69 | 69 | 70 | 70 | 69 | 69 | 68 | 69 | 67 | 67 | 64 | 65 | 67 | 67 | 67 | 67 | 67 |  | 68 | 68 | 67 | 67 | 68 | 67 | 67 | 1575709
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 132 | 135 | 134 | 137 | 136 | 136 | 136 | 132 | 130 | 92 | 94 | 111 | 99 | 105 | 102 | 104 | 102 | 103 |  | 103 | 102 | 103 | 103 | 104 | 102 | 104 | 2842000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 29580
157 | Sirajganj 68 MW Solar Park | [6 empty] | 3 | 15 | 33 | 47 | 55 | 53 | 46 | 43 | 28 | 10 | 0 | [9 empty] | 340500
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 174 | 175 | 176 | 175 | 175 | 176 | 175 | 176 | 177 | 177 | 176 | 176 | 172 | 140 | 140 | 140 | 152 | 162 |  | 164 | 164 | 164 | 165 | 168 | 170 | 170 | 4066818
Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 156 | 158 | 159 | 164 | 161 | 177 | 178 | 163 | 156 | 150 | 150 | 160 | 193 | 163 | 166 | 162 | 166 | 172 |  | 176 | 176 | 172 | 170 | 170 | 170 | 170 | 4202318
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 350 | 353 | 332 | 354 | 354 | 356 | 357 | 320 | 322 | 324 | 345 | 362 | 337 | 346 | 357 | 380 | 360 | 414 |  | 353 | 384 | 383 | 373 | 349 | 337 | 347 | 8561018
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 |  | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 82926
166 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | [16 empty] | 10 | 24 |  | 40 | 40 | 40 |  |  |  |  | 82049
169 | Santahar 50 MW Peaking PP | [16 empty] | 22 | 30 |  | 30 | 30 | 30 |  |  |  |  | 95011
170 | Natore 52 MW PP (Rajlanka)
171 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 42 | 60 |  | 62 | 60 | 62 | 58 | 50 |  |  | 318048
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [16 empty] | 10 | 35 | [8 empty] | 63648
173 | Confidence Power Bogura Unit-1 113 MW | [26 empty] | 0
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [16 empty] | 34 | 39 | [8 empty] | 68083
178 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 4 |  | 1 | 0 | [9 empty] | 33499
| Energypac Power Venture Thakurgaon Ltd. | [8 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 93 |  | 55 | 55 | 55 | 55 |  |  |  | 590976
| Intraco Solar 30 MW | [6 empty] | 2 | 10 | 18 | 27 | 32 | 24 | 31 | 25 | 6 | 8 | 0 | [9 empty] | 188153
178 | Adani Power Jharkhanda Ltd | 611 | 428 | 418 | 420 | 421 | 420 | 511 | 611 | 610 | 613 | 614 | 616 | 646 | 708 | 710 | 711 | 713 | 715 |  | 752 | 756 | 758 | 753 | 755 | 758 | 755 | 14890909
| Teesta Solar Limited | [6 empty] | 9 | 50 | 108 | 144 | 166 | 178 | 163 | 82 | 81 | 31 | 2 | [9 empty] | 992880
179 | Pabna Solar 100 MW | [6 empty] | 7 | 30 | 56 | 72 | 86 | 94 | 81 | 66 | 43 | 18 | 0 | [9 empty] | 565070
| Western Zone Total | 3905 | 3602 | 3483 | 3417 | 3414 | 3571 | 3824 | 4050 | 4092 | 4105 | 4201 | 4490 | 4574 | 4336 | 4307 | 4217 | 4324 | 4566 |  | 4457 | 4490 | 4490 | 4411 | 4257 | 4157 | 4127 | 100702319
[27 empty] | Total | 223382636