## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-11-20 | Wednesday
|  | Date (day): | 2024-11-20 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12149.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12715 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-11-19 | 2024-11-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 141 | 141 | 130 | 140 |  |  | GT-1 Under S/D
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 9 | 0 | 13 |  | 62 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 329 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 8 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 0 | 35 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 132 | 130 | 132 |  | 17 | Engine problem
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 17 | 35 | 20 |  | Fuel shortage
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 22 | 42 | 47 | 47 |  | 33 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 |  |  | Substation work
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 30 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 15 | 55 | 62 | 96 | 53 |  | Fuel shortage
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 0 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 50 | 17 | 17 | 51 | 111 |  | Fuel shortage
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 36 | 36 | 36 | 19 |  | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 70 | 0 | 0 | 584 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 400 | 400 | 300 | 400 | 183 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1548 | 1920 | 2092 | 2379 | 1944 | 1288
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 14 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 16 | 33 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 96 | 92 | 90 | 92 | 138 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 223 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 45 | 85 | 85 | 20 |  | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 42 | 70 | 70 |  | 28 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 65 | 84 |  | 18 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 30 | 100 | 12 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 2 | 10 | 15
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 14 | 7 | 38 | 40 | 68 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 50 | 50 | 50 | 250 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 33 | 54 | 35 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 34 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 86 | 25 | 86 |  | 14 | Engine problem
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 22 | 40 | 35 | 53 | 63 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 160 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 584 | 612 | 612 | 612 |  | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 0 | 15 | 15 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 0 | 0 | 0 | 0 | 1150 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 915 | 1594 | 1577 | 1926 | 1869 | 1002
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 181 | 200 | 200 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 310 | 310 | 310 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 31 | 36 | 38 | 38 |  | 7 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 194 | 185 | 195 | 195
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 43 | 43 | 43 |  | 8 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 27 | 95 | 90 | 100 | 50 |  | Fuel shortage
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 46 | 30 | 46 |  | 6 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 70 | 93 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 24 | 142 | 200 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 54 | 58 | 66 | 82
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 106 | 106 | 106 |  | 8 | Engine problem
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 46 | 104 | 100 | 100 |  | 13 | Engine problem
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 0 | 17 | 51 | 64 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 72 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1043 | 1426 | 1585 | 1611 | 262 | 809
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 24 | 28 | 30 | 30 | 172 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 95 | 96 | 96 | 104 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 58 | 54 | 58 | 57 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 37 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 23 | 24 | 18 | 24
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 29 | 17 | 35 | 19 |  | Fuel shortage
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 3 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 187 | 234 | 266.6 | 243 | 172 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 28 | 28 | 28 | 28 |  | 42 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 33 | 33 | 33 | 35 | 15 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 |  | 6 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 61 | 60 | 62
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 86 | 86
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 131 | 133 | 130 | 135 |  | 96 | Partial Shutdown due to maintenance
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 13 | 13 |  | 12 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 300 | 300 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 386 | 385 | 385 |  |  | FGMO
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 316 | 345 | 350 | 360
| Sylhet Area Total |  |  |  |  | 2411 | 2366 | 1381 | 1410 | 1420 | 1439 | 35 | 709
100 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 897 | 895 | 914 | 914
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 20 | 35 |  | 19 | Engine problem
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 60 |  | 49 | Engine problem
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 312 | 270 | 270 | 270 | 140 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
106 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
107 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 76 | 0 | 100 | 0
108 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
109 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 368 | 370 | 370 | 370 | 864 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
** | Nepal |  | 0 | Imported power | 40 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1653 | 1570 | 1704 | 1649 | 1355 | 68
110 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 16 | 94 |  | Fuel shortage
111 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 4 | 6 | 10 | 10
112 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 123 | 80 | 80 | 80 |  | 114 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
113 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 550 | 600 | 622 | 622 |  | 622 | Unit-2 S/D.
114 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 132 | 54 | 150
116 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  | 307 | Under maint
117 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 932 | 1038 | 986 | 1098 | 94 | 1043
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 0 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 0 | 25 |  | 46 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 26 | 32 |  | 18 | Engine problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 140 | 162 | 170 | 170 | 40 |  | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 176 | 170 | 175 | 45 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 338 | 316 | 414 | 414 |  |  | FGMO
127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
128 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
129 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 53 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 84 | 113 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 60 | 113 | 113
133 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 755 | 754 | 765 | 765
134 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 53 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 84 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1517 | 1757 | 1941 | 1977 | 528 | 111
135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 66 | 65 | 65 | 65 |  | 20 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 105 | 94 | 100 | 100 |  | 174 | Machine problem
137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 90 | 113
140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
141 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 34 | 95 | 115 | 115
142 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0
143 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 178 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 423 | 324 | 578 | 393 | 40 | 279
| Total |  |  |  |  | 27740 | 27035 | 9599 | 11273 | 12149.6 | 12715 | 6299 | 5309
A. |  | 2024-11-19 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 11273 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7562 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11273 | MW
3 | Day peak Generation : |  |  | 9599 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10844.01 | MW
4 | Evening peak Generation : |  |  | 11273 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 225.2785 | MKWHr | By Solar | 4.0523 | MKWHr
| By Gas : | 118.946 | MKWHr |  | By Oil: | 18.8678 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 40.6455 | MKWHr |  | By Hydro: | 2.2406 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 17.6182 | MKWHr |  | By Wind: | 0.03024 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6299 | MW | Dhaka | 4299.81 | 4299.81 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 5309 | MW | Chittagong | 1111 | 1111 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 11608 | MW | Khulna | 1191 | 1191 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 902.68 | MMCFD | **Import Adani: | Taka | 116456183.02 | Rajshahi | 957.4 | 957.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : |  | 337476067.674 | ii) Oil : | Taka | 338286865.11 | Comilla | 960 | 960 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 289162045.64 | Total | Taka | 1081381161.444 | Mymensingh | 867 | 867 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 24891.9 | MKWHr. | Sylhet | 423 | 423 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1096 | MW (W to E) at | 18:00 | hrs | Barisal | 298.8 | 298.8 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 1090 | MW at | 18:30 | hrs | Rangpur | 736 | 736 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.4°C |  |  | Total | 10844.01 | 10844.01 |  | 0
B. |  | 2024-11-20 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 30.4°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12715 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
4 | Reserve(Generation end) |  |  |  | 1215 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 229.8149 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7657 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector(India) : |  |  |  |  | i) Energy | 21.6989 | MKWHr. | ii) HVDC Flow at Peak Time |  | 895 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.1789 | MKWHr. | iii) Maximum HVDC Flow : |  | 907 | MW at | 24:00 | hrs.
* Import Through HVDC C/B Interconnector(Nepal) : |  |  |  |  | i) Energy | 0 | MKWHr.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.87 |  | (b) Today: | 97.7 |  | (c) Rule Curve: |  | 107.1

## YesterdayGen
2024-11-19 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | Nepal | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Nepal | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 65 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 310 | 0 | 190 | 199 | 75 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 34 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 135 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 4 | 0 | 241 | 0 | 0 | 0 | 0 |  | 898 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 107 | 0 | 0 | 169 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4387 | 4044 | 8431 | 2844 | 898 | 0 | 1969 | 0 | 38 | 1777 | 94 | 0 | 0 | 54 | 753 | 0 | 4 | 0 | 97.92
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 63 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 290 | 0 | 181 | 200 | 75 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | 34 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 135 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 2 | 0 | 240 | 70 | 0 | 0 | 0 |  | 898 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 107 | 0 | 0 | 169 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4236 | 3852 | 8088 | 2743 | 898 | 0 | 1962 | 0 | 0 | 1593 | 93 | 0 | 0 | 46 | 751 | 0 | 2 | 0 | 97.91
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 95 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 33 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 290 | 0 | 181 | 200 | 80 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 48 | 39 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 135 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 6 | 0 | 240 | 80 | 0 | 0 | 0 |  | 898 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 102 | 0 | 0 | 168 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 657 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4168 | 3701 | 7869 | 2706 | 898 | 0 | 2016 | 0 | 0 | 1447 | 91 | 0 | 0 | 48 | 657 | 0 | 6 | 0 | 97.9
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 105 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 33 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 290 | 0 | 182 | 170 | 80 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 48 | 72 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 40 | 86 | 0 | 135 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 5 | 0 | 241 | 80 | 0 | 0 | 0 |  | 898 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 102 | 0 | 0 | 167 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 564 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4106 | 3553 | 7659 | 2714 | 898 | 0 | 1980 | 0 | 0 | 1360 | 90 | 0 | 0 | 48 | 564 | 0 | 5 | 0 | 97.89
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 350 | 140 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 17 | 33 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 295 | 0 | 181 | 170 | 80 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 69 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 40 | 86 | 0 | 135 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 4 | 0 | 241 | 80 | 0 | 0 | 0 |  | 899 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 0 | 102 | 0 | 0 | 167 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 559 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4040 | 3522 | 7562 | 2662 | 899 | 0 | 1953 | 0 | 0 | 1345 | 90 | 0 | 0 | 50 | 559 | 0 | 4 | 0 | 97.88
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 350 | 147 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 17 | 33 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 30 | 0 | 0 | 0 | 290 | 0 | 181 | 130 | 80 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 44 | 69 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 40 | 86 | 0 | 136 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 8 | 2 | 2 | 225 | 2 | 0 | 0 | 0 | 30 | 5 | 0 | 0 | 0 | 2 | 316 | 0 | 0 | 17 | 3 | 0 | 0 | 0 | 0 | 5 | 0 | 17 | 0 | 435 | 2 | 0 | 239 | 80 | 0 | 0 | 0 |  | 898 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 104 | 0 | 0 | 167 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 180 | 0 | 2 | 0 | 0 | 14 | 0 | 0 | 371 | 0 | 0 | 606 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4122 | 3557 | 7679 | 2657 | 898 | 0 | 1859 | 0 | 98 | 1407 | 91 | 0 | 17 | 44 | 606 | 0 | 2 | 0 | 97.87
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 350 | 150 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 15 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 2 | 4 | 0 | 24 | 0 | 0 | 0 | 325 | 0 | 182 | 102 | 80 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 42 | 33 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 138 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 4 | 12 | 17 | 15 | 275 | 19 | 1 | 14 | 1 | 50 | 17 | 9 | 0 | 15 | 24 | 316 | 0 | 4 | 17 | 17 | 0 | 16 | 3 | 14 | 17 | 0 | 17 | 0 | 520 | 0 | 0 | 240 | 80 | 10 | 0 | 0 |  | 898 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 104 | 0 | 0 | 167 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 220 | 0 | 17 | 0 | 6 | 35 | 0 | 0 | 371 | 2 | 0 | 752 | 14 | 0 | 0 | 3 | 7 | 0 |  | 4589 | 4009 | 8598 | 2806 | 898 | 0 | 1946 | 0 | 403 | 1572 | 92 | 0 | 33 | 42 | 752 | 54 | 0 | 0 | 97.86
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 350 | 132 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 17 | 33 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 6 | 6 | 0 | 6 | 0 | 0 | 0 | 290 | 0 | 182 | 153 | 80 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 36 | 27 | 0 | 0 | 1 | 28 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 137 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 7 | 10 | 12 | 17 | 20 | 275 | 45 | 17 | 17 | 1 | 49 | 17 | 17 | 0 | 26 | 25 | 316 | 0 | 21 | 17 | 17 | 0 | 17 | 13 | 16 | 17 | 0 | 17 | 0 | 530 | 0 | 0 | 240 | 80 | 39 | 0 | 0 |  | 899 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 105 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 550 | 180 | 0 | 17 | 1 | 25 | 35 | 0 | 0 | 372 | 11 | 0 | 751 | 69 | 0 | 0 | 17 | 35 | 0 |  | 4743 | 4089 | 8832 | 2702 | 899 | 0 | 1936 | 0 | 513 | 1624 | 94 | 0 | 33 | 36 | 751 | 244 | 0 | 0 | 97.85
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 350 | 123 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 19 | 22 | 17 | 33 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 12 | 6 | 0 | 4 | 0 | 0 | 0 | 295 | 0 | 181 | 157 | 80 | 35 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 46 | 27 | 0 | 0 | 1 | 28 | 30 | 0 | 34 | 0 | 0 | 62 | 86 | 0 | 137 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 15 | 15 | 12 | 17 | 20 | 300 | 45 | 17 | 0 | 3 | 49 | 17 | 0 | 0 | 26 | 25 | 316 | 0 | 35 | 17 | 8 | 0 | 17 | 22 | 16 | 17 | 0 | 17 | 0 | 530 | 0 | 0 | 240 | 120 | 56 | 0 | 0 |  | 898 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 105 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 500 | 180 | 0 | 17 | 3 | 50 | 35 | 0 | 0 | 370 | 20 | 0 | 754 | 120 | 0 | 0 | 38 | 63 | 0 |  | 4839 | 4151 | 8990 | 2724 | 898 | 0 | 1945 | 0 | 494 | 1572 | 95 | 0 | 33 | 46 | 754 | 429 | 0 | 0 | 97.84
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 350 | 130 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 22 | 17 | 33 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 12 | 6 | 0 | 3 | 0 | 0 | 0 | 290 | 0 | 227 | 130 | 70 | 35 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 26 | 0 | 0 | 2 | 28 | 30 | 0 | 34 | 0 | 0 | 40 | 83 | 0 | 137 | 0 | 0 | 0 | 270 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 15 | 18 | 12 | 17 | 20 | 357 | 16 | 17 | 0 | 4 | 52 | 17 | 0 | 0 | 26 | 25 | 316 | 0 | 44 | 0 | 17 | 0 | 17 | 27 | 16 | 17 | 0 | 17 | 0 | 450 | 0 | 0 | 242 | 150 | 66 | 0 | 0 |  | 897 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68 | 0 | 104 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 450 | 180 | 0 | 17 | 4 | 67 | 35 | 0 | 0 | 368 | 30 | 0 | 751 | 161 | 0 | 0 | 53 | 85 | 0 |  | 4774 | 4202 | 8976 | 2767 | 897 | 0 | 1938 | 0 | 440 | 1440 | 95 | 0 | 33 | 50 | 751 | 565 | 0 | 0 | 97.83
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 420 | 153 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 12 | 6 | 0 | 3 | 0 | 0 | 0 | 340 | 0 | 215 | 165 | 50 | 34 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 50 | 26 | 0 | 0 | 2 | 28 | 30 | 0 | 33 | 0 | 0 | 40 | 83 | 0 | 137 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 15 | 19 | 12 | 17 | 20 | 386 | 16 | 17 | 0 | 4 | 52 | 17 | 0 | 0 | 26 | 25 | 375 | 0 | 50 | 0 | 17 | 0 | 17 | 30 | 16 | 17 | 0 | 17 | 0 | 481 | 0 | 0 | 235 | 150 | 72 | 0 | 0 |  | 897 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 104 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 440 | 180 | 0 | 17 | 5 | 80 | 0 | 0 | 0 | 367 | 34 | 0 | 757 | 180 | 0 | 0 | 63 | 94 | 0 |  | 4901 | 4296 | 9197 | 2701 | 897 | 0 | 2154 | 0 | 412 | 1459 | 96 | 0 | 33 | 50 | 757 | 638 | 0 | 0 | 97.82
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 420 | 141 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 14 | 16 | 0 | 3 | 0 | 0 | 0 | 300 | 0 | 183 | 194 | 50 | 31 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 54 | 24 | 0 | 0 | 2 | 28 | 30 | 0 | 33 | 0 | 0 | 60 | 83 | 0 | 131 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 15 | 19 | 30 | 24 | 27 | 385 | 16 | 17 | 0 | 4 | 52 | 33 | 0 | 0 | 46 | 25 | 316 | 0 | 37 | 50 | 22 | 0 | 17 | 30 | 16 | 17 | 0 | 17 | 0 | 584 | 0 | 0 | 0 | 400 | 72 | 0 | 3 |  | 897 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 105 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 550 | 220 | 0 | 35 | 5 | 76 | 34 | 0 | 0 | 368 | 35 | 0 | 755 | 178 | 0 | 0 | 53 | 84 | 0 |  | 5074 | 4525 | 9599 | 2682 | 897 | 0 | 2171 | 0 | 619 | 1673 | 96 | 0 | 52 | 54 | 755 | 600 | 0 | 0 | 97.82
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 143 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 14 | 22 | 17 | 32 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 13 | 32 | 0 | 9 | 0 | 0 | 0 | 300 | 0 | 183 | 195 | 50 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 54 | 11 | 0 | 0 | 2 | 28 | 28 | 0 | 33 | 0 | 0 | 60 | 83 | 0 | 131 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 15 | 18 | 60 | 64 | 33 | 384 | 55 | 34 | 0 | 4 | 60 | 54 | 0 | 0 | 72 | 25 | 316 | 0 | 48 | 90 | 35 | 0 | 17 | 29 | 35 | 22 | 0 | 17 | 0 | 612 | 0 | 0 | 0 | 400 | 68 | 0 | 6 |  | 896 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 104 | 0 | 0 | 158 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 622 | 220 | 0 | 35 | 4 | 72 | 34 | 0 | 0 | 369 | 34 | 0 | 754 | 119 | 0 | 0 | 56 | 76 | 0 |  | 5456 | 4561 | 10017 | 2707 | 896 | 0 | 2225 | 0 | 923 | 1773 | 96 | 0 | 55 | 54 | 754 | 534 | 0 | 0 | 97.81
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 138 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 22 | 17 | 32 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 12 | 32 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 181 | 195 | 50 | 33 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 56 | 10 | 0 | 0 | 2 | 28 | 28 | 0 | 33 | 0 | 0 | 60 | 83 | 0 | 131 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 94 | 0 | 15 | 15 | 60 | 85 | 60 | 386 | 55 | 34 | 0 | 3 | 68 | 54 | 0 | 0 | 73 | 25 | 345 | 0 | 41 | 90 | 35 | 0 | 17 | 25 | 50 | 36 | 0 | 17 | 0 | 612 | 0 | 0 | 0 | 280 | 58 | 0 | 10 |  | 896 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 100 | 0 | 0 | 168 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 622 | 180 | 0 | 35 | 3 | 61 | 35 | 0 | 0 | 367 | 28 | 0 | 755 | 101 | 0 | 0 | 48 | 57 | 0 |  | 5452 | 4405 | 9857 | 2782 | 896 | 0 | 2011 | 0 | 1006 | 1766 | 96 | 0 | 43 | 56 | 755 | 446 | 0 | 0 | 97.82
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 380 | 153 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 21 | 22 | 17 | 32 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 6 | 32 | 0 | 3 | 0 | 0 | 0 | 295 | 0 | 190 | 195 | 50 | 35 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 62 | 10 | 0 | 0 | 1 | 28 | 28 | 0 | 33 | 0 | 0 | 59 | 83 | 0 | 131 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 15 | 11 | 25 | 51 | 80 | 389 | 58 | 17 | 0 | 2 | 68 | 54 | 0 | 0 | 73 | 25 | 360 | 0 | 29 | 54 | 35 | 0 | 17 | 17 | 16 | 36 | 0 | 17 | 0 | 612 | 2 | 0 | 0 | 270 | 42 | 0 | 12 |  | 896 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 99 | 0 | 0 | 168 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 622 | 180 | 0 | 35 | 2 | 41 | 35 | 0 | 0 | 370 | 18 | 0 | 753 | 96 | 0 | 0 | 35 | 50 | 0 |  | 5199 | 4385 | 9584 | 2790 | 896 | 0 | 1987 | 0 | 838 | 1769 | 95 | 0 | 45 | 62 | 753 | 347 | 2 | 0 | 97.8
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 420 | 150 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 17 | 32 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 6 | 33 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 205 | 195 | 70 | 35 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 48 | 18 | 0 | 0 | 0 | 28 | 28 | 0 | 30 | 0 | 0 | 59 | 83 | 0 | 131 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 15 | 5 | 25 | 51 | 80 | 390 | 58 | 17 | 0 | 1 | 68 | 54 | 0 | 0 | 73 | 25 | 375 | 0 | 11 | 54 | 35 | 0 | 17 | 7 | 16 | 36 | 0 | 17 | 0 | 612 | 0 | 0 | 0 | 200 | 20 | 0 | 4 |  | 896 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 96 | 0 | 0 | 165 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 622 | 220 | 0 | 35 | 1 | 17 | 35 | 0 | 0 | 370 | 8 | 0 | 755 | 33 | 0 | 0 | 10 | 20 | 0 |  | 5217 | 4339 | 9556 | 2929 | 896 | 0 | 2076 | 0 | 822 | 1766 | 93 | 0 | 37 | 48 | 755 | 134 | 0 | 0 | 97.8
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 340 | 143 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 21 | 22 | 17 | 32 | 0 | 0 | 92 | 0 | 0 | 0 | 6 | 175 | 0 | 0 | 0 |  | 24 | 24 | 0 | 0 | 6 | 33 | 0 | 9 | 0 | 0 | 0 | 280 | 0 | 182 | 175 | 70 | 36 | 0 | 0 | 43 | 0 | 0 | 1 | 0 | 0 | 0 | 15 | 54 | 29 | 0 | 0 | 0 | 28 | 28 | 0 | 33 | 0 | 0 | 60 | 83 | 0 | 131 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 5 | 0 | 0 | 94 | 0 | 15 | 0 | 30 | 60 | 87 | 310 | 58 | 20 | 10 | 0 | 50 | 54 | 11 | 80 | 80 | 25 | 345 | 0 | 0 | 17 | 35 | 0 | 17 | 1 | 17 | 36 | 0 | 35 | 0 | 612 | 0 | 0 | 0 | 270 | 1 | 0 | 15 |  | 894 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 12 | 0 | 15 | 0 | 0 | 5 | 66 | 0 | 93 | 0 | 0 | 162 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 13 | 0 | 35 | 0 | 0 | 20 | 622 | 180 | 0 | 35 | 0 | 2 | 73 | 0 | 0 | 370 | 0 | 0 | 755 | 2 | 0 | 0 | 0 | 0 | 0 |  | 5323 | 4312 | 9635 | 2820 | 894 | 0 | 1927 | 0 | 1081 | 1763 | 92 | 0 | 243 | 54 | 755 | 6 | 0 | 0 | 97.79
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 141 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 132 | 9 | 0 | 0 | 0 | 0 | 55 | 35 | 0 | 20 | 22 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 14 | 223 | 0 | 0 | 0 |  | 24 | 42 | 0 | 0 | 7 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 50 | 36 | 0 | 0 | 43 | 0 | 46 | 52 | 0 | 0 | 0 | 18 | 58 | 28 | 0 | 0 | 0 | 28 | 30 | 0 | 33 | 0 | 0 | 61 | 84 | 0 | 133 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 30 | 0 | 0 | 95 | 0 | 55 | 0 | 100 | 142 | 95 | 386 | 58 | 105 | 45 | 0 | 50 | 54 | 34 | 106 | 104 | 86 | 345 | 0 | 0 | 17 | 40 | 0 | 29 | 0 | 0 | 36 | 0 | 160 | 0 | 612 | 0 | 0 | 70 | 400 | 0 | 0 | 0 |  | 895 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 40 | 4 | 95 | 0 | 0 | 31 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 94 | 0 | 0 | 162 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 84 | 0 | 70 | 0 | 0 | 60 | 600 | 220 | 0 | 132 | 0 | 0 | 95 | 0 | 0 | 370 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6584 | 4689 | 11273 | 2964 | 895 | 0 | 2195 | 0 | 1959 | 1741 | 92 | 0 | 615 | 58 | 754 | 0 | 0 | 0 | 97.79
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 139 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 48 | 13 | 0 | 0 | 0 | 0 | 55 | 35 | 0 | 19 | 22 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 24 | 42 | 0 | 0 | 32 | 49 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 50 | 38 | 0 | 0 | 43 | 0 | 45 | 25 | 0 | 0 | 0 | 18 | 50 | 30 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 61 | 84 | 0 | 134 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 30 | 0 | 0 | 97 | 0 | 60 | 0 | 50 | 136 | 99 | 386 | 58 | 70 | 17 | 0 | 50 | 54 | 17 | 52 | 95 | 50 | 345 | 14 | 0 | 17 | 53 | 0 | 54 | 0 | 0 | 36 | 0 | 54 | 0 | 612 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 896 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 80 | 6 | 16 | 0 | 0 | 0 | 40 | 0 | 95 | 0 | 0 | 38 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 94 | 0 | 0 | 161 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 50 | 0 | 28 | 0 | 0 | 19 | 600 | 220 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 370 | 0 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6149 | 4578 | 10727 | 2966 | 896 | 0 | 2127 | 0 | 1668 | 1741 | 93 | 0 | 433 | 50 | 753 | 0 | 0 | 0 | 97.77
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 137 | 0 | 0 | 8 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 55 | 17 | 0 | 20 | 22 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 24 | 42 | 0 | 0 | 38 | 33 | 0 | 14 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 70 | 38 | 0 | 0 | 43 | 0 | 38 | 8 | 0 | 0 | 0 | 18 | 54 | 30 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 61 | 84 | 0 | 134 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 35 | 0 | 50 | 136 | 112 | 385 | 58 | 34 | 17 | 0 | 51 | 54 | 0 | 17 | 95 | 50 | 345 | 15 | 0 | 17 | 53 | 0 | 54 | 0 | 0 | 36 | 0 | 54 | 0 | 612 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 896 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 40 | 0 | 95 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 94 | 0 | 0 | 163 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 600 | 220 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 369 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5985 | 4501 | 10486 | 2987 | 896 | 0 | 2188 | 0 | 1427 | 1740 | 93 | 0 | 347 | 54 | 754 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 154 | 0 | 0 | 5 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 20 | 22 | 17 | 33 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 24 | 49 | 0 | 0 | 31 | 33 | 0 | 19 | 0 | 0 | 0 | 330 | 0 | 197 | 195 | 70 | 38 | 0 | 0 | 43 | 0 | 38 | 8 | 0 | 0 | 0 | 18 | 54 | 33 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 61 | 84 | 0 | 134 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 40 | 0 | 50 | 85 | 60 | 385 | 24 | 34 | 17 | 0 | 51 | 54 | 0 | 17 | 94 | 50 | 360 | 15 | 0 | 17 | 53 | 0 | 54 | 0 | 0 | 36 | 0 | 54 | 0 | 612 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 896 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 40 | 0 | 95 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 94 | 0 | 0 | 164 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 220 | 0 | 81 | 0 | 0 | 55 | 0 | 0 | 369 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5909 | 4412 | 10321 | 3042 | 896 | 0 | 2265 | 0 | 1127 | 1740 | 89 | 0 | 354 | 54 | 754 | 0 | 0 | 0 | 97.78
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 141 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 22 | 22 | 17 | 33 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 24 | 64 | 0 | 0 | 12 | 19 | 0 | 25 | 0 | 0 | 0 | 310 | 0 | 181 | 195 | 70 | 38 | 0 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 56 | 33 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 62 | 84 | 0 | 134 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 96 | 0 | 35 | 0 | 50 | 85 | 60 | 384 | 24 | 34 | 17 | 0 | 51 | 54 | 0 | 2 | 95 | 50 | 345 | 15 | 0 | 17 | 53 | 0 | 54 | 0 | 0 | 36 | 0 | 54 | 0 | 612 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 899 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 40 | 0 | 95 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 97 | 0 | 0 | 166 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 220 | 0 | 81 | 0 | 0 | 55 | 0 | 0 | 369 | 0 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5787 | 4417 | 10204 | 2992 | 899 | 0 | 2239 | 0 | 1076 | 1763 | 95 | 0 | 331 | 56 | 753 | 0 | 0 | 0 | 97.77
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 136 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 22 | 17 | 33 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 24 | 24 | 0 | 0 | 12 | 19 | 0 | 22 | 0 | 0 | 0 | 315 | 0 | 188 | 195 | 70 | 36 | 0 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 56 | 34 | 0 | 0 | 0 | 28 | 30 | 0 | 31 | 0 | 0 | 61 | 84 | 0 | 134 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 30 | 0 | 50 | 51 | 60 | 384 | 24 | 17 | 17 | 0 | 52 | 54 | 0 | 0 | 55 | 12 | 346 | 0 | 0 | 17 | 53 | 0 | 54 | 0 | 0 | 36 | 0 | 17 | 0 | 612 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 899 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 95 | 0 | 0 | 166 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 180 | 0 | 81 | 0 | 0 | 55 | 0 | 0 | 372 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5526 | 4263 | 9789 | 3042 | 899 | 0 | 2188 | 0 | 863 | 1768 | 95 | 0 | 124 | 56 | 754 | 0 | 0 | 0 | 97.77
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 149 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 19 | 0 | 20 | 0 | 0 | 0 | 310 | 0 | 180 | 197 | 70 | 38 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 34 | 0 | 0 | 0 | 28 | 30 | 0 | 31 | 0 | 0 | 61 | 84 | 0 | 134 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 17 | 18 | 384 | 24 | 0 | 0 | 0 | 52 | 54 | 0 | 0 | 9 | 0 | 346 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 906 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 0 | 95 | 0 | 0 | 166 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 180 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5011 | 4249 | 9260 | 2975 | 906 | 0 | 2255 | 0 | 415 | 1768 | 96 | 0 | 41 | 50 | 754 | 0 | 0 | 0 | 99.76
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 146 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 310 | 0 | 181 | 197 | 70 | 38 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 34 | 0 | 0 | 0 | 28 | 30 | 0 | 34 | 0 | 0 | 61 | 84 | 0 | 135 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 0 | 0 | 0 | 590 | 0 | 0 | 0 |  | 907 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 96 | 0 | 0 | 166 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4928 | 4026 | 8954 | 2969 | 907 | 0 | 2438 | 0 | 55 | 1671 | 96 | 0 | 16 | 50 | 752 | 0 | 0 | 0 | 99.76
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 9496000 | 3113949 | 0 | 0 | 24218 | 7040721 | 0 | 0 | 0 | 37440 | 559200 | 18000 | 0 | 0 | 0 | 186840 | 176560 | 124688 | 0 | 378600 | 495360 | 400320 | 818500 | 0 | 0 | 2240635 | 0 | 0 | 0 | 30634 | 4339924 | 0 | 0 | 0 |  | 438720 | 187680 | 0 | 0 | 200640 | 404160 | 0 | 493920 | 0 | 0 | 0 | 7577300 | 0 | 4541000 | 4248727 | 1609630 | 920592 | 0 | 0 | 972704 | 0 | 142304 | 103018 | 0 | 0 | 0 | 348050 | 1178880 | 710400 | 0 | 0 | 13650 | 669000 | 688320 | 0 | 804096 | 0 | 0 | 1371168 | 1974720 | 0 | 3178760 | 0 | 0 | 0 | 7118000 | 332976 | 52704 | 0 | 57709 | 0 | 0 | 1310400 | 0 | 400320 | 127710 | 648000 | 1124640 | 980218 | 8472000 | 726000 | 497280 | 188181 | 25078 | 988582 | 773172 | 131310 | 228000 | 1093680 | 526080 | 8076400 | 33600 | 331090 | 554400 | 612218 | 0 | 464760 | 203478 | 271680 | 537840 | 0 | 530255 | 0 | 13292726 | 30240 | 0 | 2665909 | 5514786 | 508718 | 0 | 51600 |  | 21698909 | 0 | 6324192 | 0 | 0 | 0 | 0 | 0 | 480000 | 0 | 0 | 2481000 | 132399 | 17568 | 0 | 0 | 0 | 152220 | 4906 | 532544 | 0 | 0 | 53935 | 0 | 134328 | 0 | 0 | 88722 | 1535564 | 0 | 2510000 | 0 | 0 | 3899545 | 0 | 4059582 | 0 | 0 | 0 | 0 | 0 | 8480727 | 0 | 0 | 194304 | 0 | 108480 | 0 | 35856 | 120672 | 14332700 | 5055330 | 0 | 976800 | 32340 | 504720 | 728064 | 0 | 0 | 8974545 | 207076 | 0 | 17618182 | 1093000 | 0 | 3575 | 386252 | 579710 | 0 |  | 121740768 | 103537747 | 225278515 | 68874766 | 21698909 | 0 | 50071267 | 0 | 16038876 | 40645535 | 2240635 | 0 | 2828972 | 1178880 | 17618182 | 4052253 | 30240 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 30197280 | 10649705.58 | 0 | 0 | 426721.16 | 21474199.05 | 0 | 0 | 0 | 672048 | 10859664 | 335700 | 0 | 0 | 0 | 3411698.4 | 2782585.6 | 2280543.52 | 0 | 283950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580207.96 | 13844357.56 | 0 | 0 | 0 |  | 7717084.8 | 3305044.8 | 0 | 0 | 3926524.8 | 6652473.6 | 0 | 0 | 0 | 0 | 0 | 21140667 | 0 | 15076120 | 14233235.45 | 5199104.9 | 3102395.04 | 0 | 0 | 3900543.04 | 0 | 2548664.64 | 1860505.08 | 0 | 0 | 0 | 261037.5 | 7733452.8 | 2209344 | 0 | 0 | 0 | 2609100 | 2567433.6 | 0 | 3658636.8 | 0 | 0 | 7609982.4 | 10308038.4 | 0 | 8868740.4 | 0 | 0 | 0 | 21994620 | 249732 | 40055.04 | 0 | 1177263.6 | 0 | 0 | 25172784 | 0 | 7049635.2 | 0 | 11540880 | 19512504 | 16252014.44 | 22450800 | 13837560 | 9328972.8 | 3375967.14 | 0 | 16163315.7 | 15030463.68 | 2355701.4 | 4357080 | 21228328.8 | 9369484.8 | 21483224 | 573552 | 0 | 10139976 | 10273018.04 | 0 | 8305261.2 | 0 | 4895673.6 | 9111009.6 | 0 | 7465990.4 | 0 | 92650300.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60973934.29 | 0 | 18656366.4 | 0 | 0 | 0 | 0 | 0 | 9028800 | 0 | 0 | 7839960 | 627571.26 | 302872.32 | 0 | 0 | 0 | 2726260.2 | 90025.1 | 8952064.64 | 0 | 0 | 965975.85 | 0 | 2405814.48 | 0 | 0 | 67162.554 | 16937270.92 | 0 | 21184400 | 0 | 0 | 12868498.5 | 0 | 13518408.06 | 0 | 0 | 0 | 0 | 0 | 24763722.84 | 0 | 0 | 3851105.28 | 0 | 2160921.6 | 0 | 0 | 2394132.48 | 92875896 | 15722076.3 | 0 | 18901080 | 0 | 0 | 12631910.4 | 0 | 0 | 65514178.5 | 0 | 0 | 116456183.02 | 0 | 0 | 0 | 0 | 0 | 0 |  | 617671957.54 | 532416590.994 | 1150088548.534 | 201420638.004 | 60973934.29 | 0 | 136055429.67 | 0 | 289938561 | 289162045.64 | 0 | 0 | 48348304.11 | 7733452.8 | 116456183.02 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 420 | 141 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 14 | 16 | 0 | 3 | 0 | 0 | 0 | 300 | 0 | 183 | 194 | 50 | 31 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 54 | 24 | 0 | 0 | 2 | 28 | 30 | 0 | 33 | 0 | 0 | 60 | 83 | 0 | 131 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 15 | 19 | 30 | 24 | 27 | 385 | 16 | 17 | 0 | 4 | 52 | 33 | 0 | 0 | 46 | 25 | 316 | 0 | 37 | 50 | 22 | 0 | 17 | 30 | 16 | 17 | 0 | 17 | 0 | 584 | 0 | 0 | 0 | 400 | 72 | 0 | 3 |  | 897 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 105 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 550 | 220 | 0 | 35 | 5 | 76 | 34 | 0 | 0 | 368 | 35 | 0 | 755 | 178 | 0 | 0 | 53 | 84 | 0 |  | 9599 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 400 | 141 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 132 | 9 | 0 | 0 | 0 | 0 | 55 | 35 | 0 | 20 | 22 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 14 | 223 | 0 | 0 | 0 | 0 | 24 | 42 | 0 | 0 | 7 | 33 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 50 | 36 | 0 | 0 | 43 | 0 | 46 | 52 | 0 | 0 | 0 | 18 | 58 | 28 | 0 | 0 | 0 | 28 | 30 | 0 | 33 | 0 | 0 | 61 | 84 | 0 | 133 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 30 | 0 | 0 | 95 | 0 | 55 | 0 | 100 | 142 | 95 | 386 | 58 | 105 | 45 | 0 | 50 | 54 | 34 | 106 | 104 | 86 | 345 | 0 | 0 | 17 | 40 | 0 | 29 | 0 | 0 | 36 | 0 | 160 | 0 | 612 | 0 | 0 | 70 | 400 | 0 | 0 | 0 |  | 895 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 40 | 4 | 95 | 0 | 0 | 31 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 94 | 0 | 0 | 162 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 84 | 0 | 70 | 0 | 0 | 60 | 600 | 220 | 0 | 132 | 0 | 0 | 95 | 0 | 0 | 370 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 11273 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 450 | 140 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 132 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 22 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 24 | 70 | 84 | 0 | 40 | 50 | 0 | 15 | 0 | 0 |  | 310 | 0 | 200 | 195 | 70 | 38 | 0 | 0 | 43 | 0 | 46 | 52 | 0 | 0 |  | 18 | 82 | 30 | 0 | 0 | 0 | 28 | 30 | 0 | 35 | 0 | 0 | 62 | 86 | 0 | 135 | 0 | 0 | 0 | 300 | 13 | 5 | 0 | 300 | 0 | 0 | 96 | 0 | 96 | 0 | 100 | 200 | 100 | 385 | 58 | 105 | 85 | 0 | 50 | 54 | 110 | 106 | 100 | 86 | 360 | 17 | 0 | 51 | 53 | 0 | 35 | 0 | 51 | 36 | 0 | 160 | 0 | 612 | 15 | 0 | 0 | 400 |  |  |  |  | 914 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 80 | 10 | 16 | 0 | 0 | 0 | 40 | 25 | 95 | 0 | 0 | 32 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 100 | 0 | 0 | 170 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 370 | 0 | 0 | 765 | 0 | 0 |  |  |  | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 |  | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 130 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 130 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 25 | 22 | 17 | 33 | 0 | 0 | 90 | 0 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 18 | 70 | 65 | 0 | 38 | 50 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 200 | 195 | 50 | 38 | 0 | 0 | 43 | 0 | 30 | 52 | 0 | 0 |  | 18 | 66 | 30 | 0 | 0 | 1.6 | 28 | 30 | 0 | 33 | 0 | 0 | 60 | 86 | 0 | 130 | 0 | 0 | 0 | 300 | 13 | 5 | 0 | 300 | 0 | 0 | 96 | 0 | 62 | 20 | 12 | 200 | 90 | 385 | 54 | 50 | 85 | 5 | 50 | 35 | 110 | 106 | 100 | 25 | 350 | 0 | 50 | 17 | 35 | 0 | 17 | 35 | 17 | 36 | 0 | 17 | 0 | 612 | 15 | 0 | 0 | 300 | 70 |  |  |  | 914 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 26 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 100 | 0 | 0 | 170 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 90 | 0 | 8 | 113 | 622 | 220 |  | 54 | 6 | 100 | 115 | 0 | 0 | 370 | 30 | 0 | 765 | 170 | 0 |  | 29 | 47 | 0 |  |  |  |  | gas | hvdc |  | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 133 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 6 | 0 | 12 | 0 | 0 | 0 | 290 | 0 | 180 | 195 | 80 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 42 | 30 | 0 | 0 | 1 | 28 | 30 | 0 | 33 | 0 | 0 | 62 | 84 | 0 | 135 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 9 | 8 | 0 | 10 | 322 | 45 | 0 | 0 | 1 | 32 | 35 | 0 | 0 | 5 | 0 | 340 | 0 | 21 | 17 | 35 | 0 | 0 | 13 | 0 | 36 | 0 | 0 | 0 | 612 | 0 | 0 | 0 | 290 | 34 | 0 | 0 | 0 | 906 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 99 | 0 | 0 | 166 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 550 | 220 | 0 | 11 | 2 | 27 | 0 | 0 | 0 | 371 | 12 | 0 | 763 | 69 | 0 | 0 | 24 | 38 | 0 | 0 |  |  |  | 118946033 | 21698909 |  | 0 | 40645535 | 18867848 | 1178880 | 4052253 | 30240 | 2240635 |  |  |  | 207660333
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [10 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [11 empty] | 118.946 | 21.6989 |  | 0 | 40.6455 | 18.8678 | 1.1789 | 4.0523 | 0.03024 | 2.2406
| Minimum Generation |  | 7562 | 5:00
| Highest Generation |  | 11273 | 18:00 | [129 empty] | 0 | [77 empty] | 207.6603
| Day Peak Generation |  | 9599 | 12:00
| Evening Peak Generation |  | 11273 | 18:00 | [207 empty] | 202699852
| HVDC Max Flow |  | 907 | 24:00 | [207 empty] | 202.6999
| HVDC EvPeak Flow |  | 895 | 18:00
| Load factor L.F |  | 83.27% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-11-20
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-11-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9599 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7657
Evening Peak Generation : |  |  | 11273 | MW Hour : | 18:00 | Available Max Generation : |  | 12715
E.P. Demand (at gen end) : |  |  | 11273 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 11500
Maximum Generation : |  |  | 11273 | MW Hour : | 18:00 | Reserve(Generation end) |  | 1215
Total Gen. (MKWH) : |  |  | 225.2785 | System Load Factor : | 83.27% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1090 | MW at | 18:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-11-20
Actual : |  | 97.7 | Ft.(MSL) , | Rule curve : | 107.1 | Ft.( MSL )
Gas Consumed : |  | Total = | 902.68 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 337476067.674 | Adani : | 116456183.02
|  |  | Coal : | 289162045.64 | Oil: | 338286865.11 | Total: | 1081381161.444
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3758.0485 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1027.7912 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1438.2562 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1248.7433 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1028.1895 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 763.9927 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 429.0126 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 356.8265 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 697.9062 |  |  | 0 | 0%
Total |  | 0 |  | 10748.7667 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:12 | 15:28 | Khulna (S)-Rampal Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to Annual Maintenance Work.
and from Rampal 400/230kV end Due to Maintenance by Khulna ALDC
08:13 | 16:13 | Kaliakoir 400/230/132kV S/S 230kV Bus 1 Scheduled S/D Due to Annual Maintenance..
08:20 | 15:43 | Chapai 132/33kV S/S Chapai Rahanpur ckt 2 Scheduled S/D Due to Annual Maintenance..
08:22 | 16:01 | Benapole 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance of busbar 2
08:23 | 15:45 | Rahanpur 400/132kV S/S Rahanpur-Chapainawabganj 132 KV Line Ckt-02 Scheduled S/D Due to বাৎসরিক সংরক্ষণ
08:26 | 15:54 | Rajshahi 230/132/33kV S/S 132 kV Main BUS-02 Scheduled S/D
08:29 | 14:47 | Khulna(S) 230/132kV S/S 230 KV Main Bus 2 Scheduled S/D Due to Annual Maintenance Work.
08:31 | 14:16 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Annual Maintenance Work.
08:31 | 15:14 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Annual Maintenance
08:33 | 11:38 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-01 (704T) LT Scheduled S/D
08:34 | 17:03 | Baghabari-Ishurdi 230 kV Ckt-1 Scheduled S/D from Baghabari 230/132kV end Due to Annual Maintenance and
from Ishurdi 230/132kV end Due to A/M
08:35 | 11:37 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-01 (704T) HT Scheduled S/D
08:35 | 15:25 | Tangail 132/33kV S/S Tr-4 HT Scheduled S/D Due to annual maintenance
08:35 | 15:25 | Tangail 132/33kV S/S Tr-4 LT Scheduled S/D Due to annual maintenance
08:38 | 16:23 | Purbasadipur-Saidpur 132kV Ckt-2 Scheduled S/D from Purbasadipur 132/33kV end Due to annual maintenance and
from Saidpur 132/33kV end Due to Annual maintenance.
08:38 | 16:43 | Fenchuganj-Sreemangal 132kV Ckt-2 Scheduled S/D from Sreemongol 132/33kV end Due to annual Maintenance.
and from Fenchuganj 230/132/33kV end Due to Annual maintenance.
08:42 | 16:56 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to Annual maintenance
08:46 | 16:59 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Scheduled S/D Due to Due to Annual Maintenance
08:51 | 16:29 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Annual Maintenance.
08:55 | 16:35 | Bogura 230/132kV S/S T-02 LT Scheduled S/D Due to Annual Maintenance
08:55 | 16:34 | Bogura 230/132kV S/S T-02 HT Scheduled S/D Due to Annual Maintenance
09:03 |  | Rangamati 132/33kV S/S Main Bus 02 Scheduled S/D Due to Annual maintenance
09:12 | 17:48 | Bhulta 400/230kV S/S ATR-01 HT Scheduled S/D Due to Annual Annual maintenance
09:20 | 17:19 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due to Annual Maintenance.
and from Mymensingh 132/33kV end Due to Annual Maintenance on Jamalpur Grid
09:21 | 16:05 | Satmasjid 132/33kV S/S Auxiliary Tr-1 HT Scheduled S/D Due to Annual Maintenance
09:24 | 16:04 | Satmasjid 132/33kV S/S 132/33 KV Transformer-1 HT Scheduled S/D Due to Annual Maintenance
09:30 | 19:21 | Gopalganj 400/132kV S/S 400kV Bus-01 Scheduled S/D
09:40 | 14:45 | Sonargaon 132/33kV S/S BUS B Scheduled S/D Due to Annual maintenance work purpose
09:50 | 16:39 | Rajbari 132/33kV S/S Bheramara-2 Scheduled S/D
09:56 | 14:30 | BIPTC S/S 10CF24 Scheduled S/D Due to Annual Maintenance
10:16 | 20:12 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Forced S/D from Siddhirganj 132/33kV end Due to Will work
on the other side.
10:17 | 17:07 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Coxsbazar 132/33kV end Due to Annual Maintenance
(Dohazari side) and from Dohazari 132/33kV end Due to Annual maintenance.
10:24 | 18:07 | Gopalganj 132/33kV S/S Gopalganj 100 MW PS Project Work S/D Due to New BCV Relay test by siemens
10:27 | 13:55 | Keranigonj 230/132/33kV S/S ATR-3 HT Tripped showing PRV,Trip relay relays Due to PRV-2
10:27 | 13:55 | Keranigonj 230/132/33kV S/S ATR-3 LT Tripped showing PRV, Trip Relay relays Due to PRV-2
10:54 | 17:04 | Shyampur-Shyampur(New) 132kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to Annual Maintenance of DPDC
11:21 | 13:55 | Keranigonj 230/132/33kV S/S ATR-3 HT Scheduled S/D Due to PRV maintenance
11:21 | 13:55 | Keranigonj 230/132/33kV S/S ATR-3 LT Scheduled S/D Due to PRV maintenance
11:32 | 12:30 | Sonargaon 132/33kV S/S Tr-1 LT Forced S/D Due to 33kV Astafeed feeder corrective maintenance work. |  |  |  |  | 40.0MW load interruption.
Shutdown taken by PBS.
11:32 | 12:30 | Sonargaon 132/33kV S/S Tr-1 HT Forced S/D Due to 33kV Astafeed feeder corrective maintenance work
. Shutdown taken by PBS.
11:39 | 15:51 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-02 (714T) HT Scheduled S/D
11:39 | 15:52 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-02 (714T) LT Scheduled S/D
11:59 | 13:01 | Shahjadpur 132/33kV S/S T-4(435T) LT Forced S/D Due to 33kv incomming CT Oil leakage Maintenance Work.
12:00 | 13:00 | Shahjadpur 132/33kV S/S T-4(435T) HT Forced S/D Due to 33kv Incomming CT Oil leakage Maintenance work.
12:00 |  | Day Peak Generation = 9,602MW
| 12:43 | Amnura 132/33kV S/S T-1 (406T) HT is restored.
| 12:50 | Amnura 132/33kV S/S T-1 (406T) LT is restored.
13:30 | 16:34 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) LT Scheduled S/D
13:31 | 16:33 | Rajshahi 230/132/33kV S/S 132/33 kV T-02 (416T) HT Scheduled S/D
| 13:49 | Barishal-Bhandaria 132 kV Ckt-1 is restored.
| 13:49 | Bhandaria 132/33kV S/S Main Bus Bar is restored.
| 13:51 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
| 13:53 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
14:40 | 15:03 | BIPTC S/S 10CF14 Forced S/D
14:42 | 15:36 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Forced S/D Due to 33 KV CB sf6 gas refile works.
14:42 | 15:35 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Forced S/D Due to 33KV CB SF6 Gas refile works.
| 14:51 | Khulshi-Madunaghat 132kV Ckt-1 is restored.
14:58 | 15:16 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Tripped showing Over current proction P142 relays Due to |  |  |  |  | 15.0MW load interruption.
33 kv kahalo feeder over current fault
14:58 | 15:15 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Tripped showing Over current proction P142 relays Due to
33 kv kahalo feeder over current fault
| 14:59 | Haripur-Haripur (360MW) 230kV Ckt-2 is restored.
| 15:04 | Barguna 132/33kV S/S Transformer-2 HT is restored.
| 15:05 | Barguna 132/33kV S/S Transformer-2 LT is restored.
15:15 | 18:26 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to 33 kv CT hotspot check
15:15 | 18:02 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to 33 kv CT hotspot check
15:30 | 16:41 | Sonargaon 132/33kV S/S Tr-1 LT Forced S/D Due to 33kv Astafeed feeder corrective maintenance work |  |  |  |  | 40.0MW load interruption.
(underground cable connection). Shutdown taken by PBS.
15:30 | 16:41 | Sonargaon 132/33kV S/S Tr-1 HT Forced S/D Due to 33kv Astafeed feeder corrective maintenance work
(underground cable connection). Shutdown taken by PBS.
| 15:39 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 is restored.
| 15:40 | Barapukuria-Rangpur 132 kV Ckt-2 is restored.
| 15:40 | Barapukuria-Rangpur 132 kV Ckt-1 is restored.
16:35 | 18:23 | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) LT
Scheduled S/D Due to A/M
16:36 | 18:22 | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) HT Scheduled S/D Due to A/M
18:00 |  | Evening Peak Generation: 11273 MW.
| 04:12 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor is restored.
05:00 |  | Minimum generation 7657 MW
06:52 |  | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to Annual maintenance work.
07:35 |  | Khulshi-Madunaghat 132kV Ckt-2 Scheduled S/D from Khulshi 132/33kV end Due to Annual maintenance (Bay)
07:40 |  | Nawabganj 132/33kV S/S 132kV Main Bus-1 Scheduled S/D Due to For annual maintenance work.
07:41 |  | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Annual Maintenance Work.
07:52 |  | Naogaon 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance.
07:53 |  | Naogaon 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-11-19
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 0 | 0 | Gas shortage
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9496000
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 141 | 3113949 | FGMO
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 24218 | Reserve
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 9 | 18000 | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7040721
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 37440 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 186840 | Engine problem
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 559200 | Low demand
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 176560
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 124688 | Engine problem
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 873960 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 400320 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 818500
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | 33 kV feeder fault.
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 30 | 57709 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 55 | 400320 | Low demand
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 497280
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 33600 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 554400 | Low demand
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 203478
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 537840 | Fuel shortage
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 70 | 2665909 | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 400 | 5514786 | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 1920 | 33335718
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 14 | 30634 | Low demand
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 127710
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 404160 | Trandformer O/L
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 92 | 2240635 | Low water level
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 223 | 4339924
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 45 | 188181 | Low demand
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 42 | 187680 | Low demand
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 648000
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 493920
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 7 | 200640 | Low demand
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25078
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 50 | 988582 | Fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 773172
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 131310 | High Voltage
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 86 | 526080 | 33 kV feeder fault.
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 40 | 612218 | Fuel shortage
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 160 | 530255
55 | SS Power I |  | IPP | 2*612 | 1224 | 612 | 13292726 | Coal shortage
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 30240
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 0 | 0 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1594 | 25771145
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4541000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7577300 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 920592 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 185 | 4248727
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 972704 | Engine problem
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 95 | 980218 | Fuel shortage
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 46 | 142304 | Engine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1609630 | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 142 | 1124640 | High Voltage
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 58 | 1178880
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 103018
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 348050 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 228000
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 104 | 1093680
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 271680 | High Voltage
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 508718
| Cumilla Area Total |  |  |  | 2917 | 1426 | 25849141
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 28 | 710400 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13650
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 95 | 1310400 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 726000 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 331090
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 438720 | Fuel shortage
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 29 | 464760 | Fuel shortage
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 51600
| Mymensingh Area Total |  |  |  | 646 | 234 | 4046620
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 28 | 669000 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 688320 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 0 | 0 | 0 | Contact expired
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 33 | 804096 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 52704 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1371168
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1974720
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 133 | 3178760 | ST under Maint
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 332976 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7118000 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 386 | 8472000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 345 | 8076400 | FGMO
| Sylhet Area Total |  |  |  | 2366 | 1410 | 32738144
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 895 | 21698909
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 480000 | Reserve
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 270 | 6324192 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 504720
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 370 | 8974545 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Nepal |  | Imported power | 40 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1570 | 37982366
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 17568 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 6 | 132399 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 80 | 2481000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 14332700 | Unit-2 under overhauling
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5055330
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 132 | 976800
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Under maint.
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3575
| Barisal Area Total |  |  |  | 2236 | 1038 | 22999372
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 152220 | Reserve
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 4906 | Low demand
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 53935 | Fuel shortage
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 162 | 3899545 | Gas shortage
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 176 | 4059582
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 316 | 8480727
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 134328 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 88722 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 532544 | High Voltage
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 84 | 194304 | Low demand
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 60 | 120672 | Low demand
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32340
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 754 | 17618182
135 | Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 386252
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 579710
| Rajshahi Area Total |  |  |  | 3449 | 1757 | 36337969
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 65 | 1535564
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 94 | 2510000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 108480 | Low demand
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35856
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 95 | 728064 | Fuel shortage
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 207076
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 1093000
| Rangpur Area Total |  |  |  | 950 | 324 | 6218040
| Total |  |  |  | 27035 | 11273 | 225278515
| Eastern Grid Total |  |  |  | 16701 | 6584 | 121740768
| Western Grid Total |  |  |  | 10334 | 4689 | 103537747
| National Grid Total |  |  |  | 27035 | 11273 | 225278515
*Data collected from respective power station over telephone.
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-11-19
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7630.21 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3128.8 | MW
i) Dhaka area |  |  | 4262.71 |  | MW | i) Khulna area |  |  |  | 1144.4 | MW
ii) Chattogram area |  |  | 1096.5 |  | MW | ii) Barishal area |  |  |  | 293 | MW
iii) Cumilla area |  |  | 955 |  | MW | iii) Rajshahi area |  |  |  | 962.4 | MW
iv) Mymensingh area |  |  | 890 |  | MW | iv) Rangpur area |  |  |  | 729 | MW
v) Sylhet area |  |  | 426 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10759.01 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 3 | 06:00 | 67 | Jashore | 96 | 18:00 | 133 | Rajbari | 50 | 18:00
2 | AKSML | 107 | 11:00 | 68 | Jhenaidah | 87 | 18:00 | 134 | Rajendrapur | 94 | 18:30
3 | Aftabnagar | 28 | 13:00 | 69 | Joydebpur | 178 | 18:00 | 135 | Rajshahi | 72 | 18:00
4 | Agargaon | 85 | 14:00 | 70 | Joypurhat | 38 | 18:00 | 136 | Rajshahi-230 | 58 | 13:00
5 | Agrabad | 82 | 18:30 | 71 | Juldah | 11 | 17:00 | 137 | Ramganj | 80 | 18:30
6 | Amnura | 39 | 19:00 | 72 | KSRM | 51 | 01:00 | 138 | Rampur | 33 | 18:30
7 | Ashuganj | 75.5 | 22:00 | 73 | Kabirpur | 264 | 16:00 | 139 | Rangamati | 13 | 18:00
8 | BSRM | 134 | 11:00 | 74 | Kachua | 53 | 18:00 | 140 | Rangpur | 111 | 18:00
9 | Bagerhat | 71 | 18:00 | 75 | Kallyanpur | 81 | 14:00 | 141 | Ruppur | 5.6 | 15:00
10 | Bakulia | 85 | 18:00 | 76 | Kalurghat | 36 | 15:00 | 142 | SSM | 0 | 00:00
11 | Banani | 50.8 | 13:00 | 77 | Kamrangirchar | 61 | 13:00 | 143 | Saidpur | 88 | 18:30
12 | Bangabhaban | 12 | 10:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 81 | 18:00
13 | Barapukuria | 44 | 18:00 | 79 | Kazla | 99 | 13:00 | 145 | Satmasjid | 79 | 18:00
14 | Barguna | 14 | 00:00 | 80 | Keranigonj | 62 | 13:00 | 146 | Savar | 166 | 18:00
15 | Barishal | 84 | 13:00 | 81 | Khagrachori | 24 | 18:00 | 147 | SevenRings | 10.69 | 13:00
16 | Barishal-230 | 62 | 20:00 | 82 | Khulna | 53 | 18:00 | 148 | ShahCement | 18 | 18:00
17 | Baroaulia | 60 | 16:00 | 83 | Khulshi | 130 | 14:00 | 149 | Shahjadpur | 53 | 18:00
18 | Baroirhat | 44 | 14:00 | 84 | Kishoreganj | 108 | 18:00 | 150 | Shahjibazar | 87 | 18:00
19 | Bashundhara | 141 | 13:00 | 85 | Kodda | 153 | 18:00 | 151 | Shahmirpur | 47 | 18:00
20 | BashundharaCement | 11 | 07:00 | 86 | Kulaura | 32 | 18:00 | 152 | Shariatpur | 52 | 20:00
21 | Beanibazar | 46 | 18:00 | 87 | Kurigram | 44 | 18:00 | 153 | Sherpur | 100 | 18:00
22 | Benapole | 40 | 18:00 | 88 | Kushtia | 106 | 18:00 | 154 | Shikalbaha | 20 | 00:00
23 | Bhaluka | 116 | 18:00 | 89 | Lalbag | 70 | 18:00 | 155 | Shitalakhya | 69.2 | 13:00
24 | Bhandaria | 38 | 18:00 | 90 | Lalmonirhat | 42 | 18:00 | 156 | Sholosohor | 38 | 17:00
25 | Bhangura | 23 | 18:00 | 91 | MI_Cement | 12.7 | 13:00 | 157 | Shyampur | 150 | 23:00
26 | Bheramara(GK) | 39 | 18:00 | 92 | Madanganj | 31 | 18:00 | 158 | Siddhirganj | 110 | 12:00
27 | Bhulta | 242.5 | 17:00 | 93 | Madaripur | 62 | 22:00 | 159 | Sirajganj | 70 | 19:30
28 | Bog-Sherpur | 54 | 18:30 | 94 | Madartek | 53.44 | 20:00 | 160 | Sonargaon | 69 | 15:00
29 | Bogura | 112 | 18:30 | 95 | Madunaghat | 43 | 18:00 | 161 | Sreemongol | 48 | 18:00
30 | Borhanuddin | 51 | 21:00 | 96 | Magura | 44 | 18:00 | 162 | Sreepur | 71 | 18:00
31 | Brahmanbaria | 116 | 18:00 | 97 | Mahasthangarh | 48 | 18:00 | 163 | Srinagar | 29.8 | 21:00
32 | Cantonment | 91 | 18:30 | 98 | Manikganj | 92 | 18:00 | 164 | Sunamganj | 38 | 18:00
33 | Chandpur | 45 | 18:00 | 99 | Maniknagar | 56 | 13:00 | 165 | Sylhet | 34 | 18:00
34 | Chandraghona | 27 | 18:00 | 100 | Matarbari | 36 | 18:00 | 166 | Sylhet-132 | 89 | 18:00
35 | Chapai | 41 | 18:00 | 101 | Matuail | 62 | 12:00 | 167 | TK | 23.5 | 18:00
36 | Charsaidpur | 41 | 00:00 | 102 | Millgate | 103 | 12:00 | 168 | Tangail | 132 | 18:00
37 | Chauddagram | 46 | 18:00 | 103 | Mirpur | 112 | 18:00 | 169 | Thakurgaon | 76 | 18:00
38 | Chhatak | 23 | 18:00 | 104 | Mirsorai | 5 | 00:00 | 170 | Tongi | 110 | 17:00
39 | Chowmuhani | 138 | 18:00 | 105 | Mirzapur | 38 | 18:00 | 171 | Ullahpara | 28 | 18:00
40 | Chuadanga | 71 | 18:00 | 106 | Mithapukur | 44 | 18:00 | 172 | Ullon | 37 | 18:30
41 | Coxsbazar | 95 | 18:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 69 | 13:00
42 | Cumilla(N) | 124 | 18:00 | 108 | Mogbazar | 93.4 | 13:00 | 174 | UttaraNew | 39 | 13:00
43 | Cumilla(S) | 123 | 15:00 | 109 | Mongla | 33 | 10:00 | 175 | Zigatola | 70 | 13:00
44 | Daudkandi | 113 | 20:00 | 110 | Motijheel | 36 | 13:00
45 | Dhaka | 32 | 13:00 | 111 | Munshiganj | 73 | 13:00
46 | Dhamrai | 110 | 12:00 | 112 | Mymensingh | 169 | 18:00
47 | Dhanmondi | 93 | 13:00 | 113 | Naogaon | 85 | 18:00
48 | Dohazari | 68 | 21:00 | 114 | Narail | 35 | 18:00
49 | Faridpur | 109 | 18:00 | 115 | Narinda | 58 | 13:00
50 | Fatullah | 74 | 15:00 | 116 | Narshingdi | 158 | 19:30
51 | Fenchuganj | 27 | 18:00 | 117 | Natore | 100 | 18:00
52 | Feni | 77 | 18:30 | 118 | Nawabganj | 28.2 | 21:00
53 | GPH | 5 | 00:00 | 119 | Netrakona | 91 | 18:30
54 | Ghatail | 46 | 18:00 | 120 | New | 38 | 11:00
55 | Ghorashal | 50 | 19:00 | 121 | Niamatpur | 39 | 18:00
56 | Goalpara | 22 | 12:00 | 122 | Noapara | 29 | 18:00
57 | Gollamari | 72 | 15:00 | 123 | PHP | 10 | 11:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-11-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 403 | 05:00 | 381 | 16:00 | Kaliakoir | 382 | 04:00 | 368 | 16:00
| Ashuganj | 415 | 6:00 | 401 | 23:00 | Madunaghat | 409 | 18:00 | 402 | 11:00
| Bhulta | 410 | 05:00 | 400 | 11:00 | Meghnaghat | 397 | 04:00 | 384 | 11:00
| Bibiana | 398 | 06:00 | 389 | 09:00 | Payra | 418 | 05:00 | 410 | 16:00
| BIPTC | 403 | 03:00 | 393 | 18:00 | Rahanpur | 401 | 05:00 | 392 | 16:00
| Bogura | 394 | 04:00 | 384 | 11:00 | Rampal | 413 | 06:00 | 42 | 06:00
| Gopalganj | 411 | 05:00 | 400 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 243 | 06:00 | 233 | 11:00 | Haripur | 239 | 08:00 | 232 | 11:00
| AKSML | 241 | 19:00 | 233 | 01:00 | Hasnabad | 243 | 03:00 | 233 | 11:00
| Aminbazar | 242 | 05:00 | 231 | 15:00 | Hathazari | 243 | 18:00 | 236 | 23:00
| Ashuganj | 242 | 06:00 | 235 | 11:00 | Ishurdi | 243 | 06:00 | 230 | 11:00
| Ashuganj-400 | 242 | 6:00 | 235 | 11:00 | Jhenaidah | 238 | 05:00 | 225 | 11:00
| Baghabari | 239 | 06:00 | 233 | 09:00 | Kaliakoir | 240 | 04:00 | 231 | 16:00
| Barapukuria | 229 | 06:00 | 224 | 00:00 | Keranigonj | 242 | 06:00 | 232 | 11:00
| Barapukuria-230 | 229 | 6:00 | 224 | 0:00 | Khulna(S) | 239 | 04:00 | 229 | 11:00
| Barishal | 244 | 04:00 | 238 | 11:00 | Madunaghat | 243 | 18:00 | 237 | 11:00
| Bheramara | 240 | 05:00 | 227 | 11:00 | Maniknagar | 241 | 06:00 | 229 | 22:00
| Bhulta | 242 | 05:00 | 232 | 11:00 | Meghnaghat | 248 | 02:00 | 240 | 11:00
| Bibiana | 232 | 05:00 | 223 | 11:00 | Meghnaghat-400 | 244 | 05:00 | 235 | 11:00
| BIPTC | 243 | 06:00 | 228 | 11:00 | Mirsorai | 244 | 17:00 | 233 | 00:00
| Bogura | 240 | 06:00 | 235 | 11:00 | Rajshahi | 241 | 05:00 | 227 | 11:00
| Bogura-400 | 241 | 04:00 | 236 | 11:00 | Rampal | 237 | 06:00 | 227 | 11:00
| Borhanuddin | 246 | 03:00 | 242 | 19:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 242 | 18:00 | 232 | 01:00 | Rampura | 242 | 06:00 | 231 | 12:00
| Cumilla(N) | 239 | 04:00 | 229 | 11:00 | Shikalbaha | 242 | 18:00 | 232 | 11:00
| Faridpur | 244 | 05:00 | 236 | 11:00 | Shyampur | 243 | 06:00 | 233 | 11:00
| Fenchuganj | 230 | 05:00 | 225 | 16:00 | Siddhirganj | 241 | 03:00 | 234 | 12:00
| Ghorashal | 242 | 04:00 | 240 | 00:00 | Sirajgonj | 247 | 06:00 | 240 | 11:00
| Ghorashal-230 | 240 | 05:00 | 229 | 11:00 | Sreepur | 239 | 05:00 | 231 | 11:00
| Gopalganj | 243 | 06:00 | 236 | 16:00 | Tongi | 238 | 04:00 | 230 | 11:00
| GPH | 242 | 18:00 | 233 | 02:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 139 | 03:00 | 130 | 16:00 | Kushtia | 140 | 02:00 | 135 | 11:00
| Agargaon | 141 | 05:00 | 134 | 11:00 | Lalbag | 139 | 06:00 | 132 | 11:00
| Agrabad | 139 | 18:30 | 134 | 11:00 | Lalmonirhat | 132 | 04:00 | 119 | 07:00
| AKS | 136 | 05:00 | 133 | 13:00 | Madanganj | 135 | 05:00 | 125 | 17:00
| Aminbazar | 143 | 05:00 | 134 | 10:00 | Madaripur | 135 | 00:00 | 133 | 12:00
| Amnura | 134 | 19:30 | 129 | 16:00 | Madartek | 140 | 06:00 | 130 | 12:00
| Ashuganj | 142 | 05:00 | 139 | 11:00 | Madunaghat | 141 | 18:30 | 135 | 01:00
| Bagerhat | 139 | 04:00 | 133 | 12:00 | Magura | 142 | 04:00 | 133 | 12:00
| Bakulia | 140 | 18:00 | 134 | 00:00 | Mahasthangarh | 137 | 04:00 | 131 | 11:00
| Banani | 140 | 05:00 | 131 | 11:00 | Manikganj | 136 | 06:00 | 120 | 16:00
| Bangabhaban | 137 | 04:00 | 130 | 11:00 | Maniknagar | 138 | 06:00 | 130 | 11:00
| Barapukuria | 137 | 06:00 | 127 | 07:00 | Matarbari | 129 | 09:00 | 120 | 12:00
| Barguna | 141 | 19:00 | 134 | 11:00 | Matuail | 137 | 05:00 | 130 | 16:00
| Barishal | 136 | 06:00 | 131 | 11:00 | Millgate | 141 | 04:00 | 128 | 15:00
| Barishal-230 | 136 | 04:00 | 131 | 16:00 | Mirpur | 142 | 06:00 | 135 | 11:00
| Baroaulia | 139 | 05:00 | 134 | 11:00 | Mirzapur | 131 | 18:00 | 125 | 11:00
| Baroirhat | 138 | 18:00 | 130 | 10:00 | Mithapukur | 135 | 04:00 | 125 | 08:00
| Bashundhara | 141 | 04:00 | 128 | 16:00 | MI_Cement | 141 | 05:00 | 134 | 16:00
| BashundharaCement | 135 | 05:00 | 125 | 17:00 | Modern | 138 | 06:00 | 134 | 16:00
| Beanibazar | 132 | 06:00 | 128 | 15:00 | Mogbazar | 140 | 05:00 | 131 | 11:00
| Benapole | 140 | 03:00 | 132 | 11:00 | Mongla | 137 | 00:00 | 132 | 11:00
| Bhaluka | 134 | 04:00 | 129 | 11:00 | Motijheel | 137 | 04:00 | 130 | 11:00
| Bhandaria | 132 | 03:00 | 127 | 16:00 | Munshiganj | 136 | 05:00 | 128 | 16:00
| Bhangura | 143 | 04:00 | 137 | 11:00 | Mymensingh | 136 | 14:00 | 125 | 01:00
| Bheramara | 140 | 03:00 | 136 | 11:00 | Naogaon | 138 | 06:00 | 131 | 11:00
| Bheramara(GK) | 139 | 00:00 | 136 | 11:00 | Narail | 143 | 05:00 | 134 | 12:00
| Bhulta | 130 | 06:00 | 122 | 16:00 | Narinda | 137 | 7:00 | 130 | 13:00
| Bog-Sherpur | 139 | 03:00 | 133 | 11:00 | Narshingdi | 135 | 09:00 | 125 | 11:00
| Bogura | 140 | 05:00 | 134 | 12:00 | Natore | 139 | 03:00 | 133 | 11:00
| Bogura-230 | 139 | 05:00 | 134 | 11:00 | Nawabganj | 139 | 06:00 | 132 | 11:00
| Brahmanbaria | 137 | 06:00 | 132 | 15:00 | Netrakona | 134 | 01:00 | 126 | 03:00
| Cantonment | 141 | 06:00 | 132 | 15:00 | New | 141 | 03:00 | 129 | 15:00
| Chandpur | 140 | 17:00 | 128 | 23:00 | Niamatpur | 135 | 05:00 | 132 | 08:00
| Chandraghona | 139 | 05:00 | 135 | 11:00 | Noapara | 142 | 05:00 | 134 | 11:00
| Chapai | 134 | 04:00 | 130 | 08:00 | Pabna | 142 | 05:00 | 135 | 11:00
| Charsaidpur | 135 | 07:00 | 128 | 16:00 | Palashbari | 135 | 05:00 | 127 | 11:00
| Chauddagram | 138 | 17:00 | 130 | 11:00 | Panchagarh | 135 | 17:00 | 115 | 11:00
| Chhatak | 131 | 04:00 | 126 | 15:00 | Patuakhali | 140 | 19:30 | 135 | 01:00
| Chowmuhani | 137 | 17:00 | 126 | 06:00 | Payra | 139 | 19:30 | 134 | 09:00
| Chuadanga | 140 | 03:00 | 130 | 13:00 | PHP | 138 | 18:00 | 129 | 11:00
| Coxsbazar | 128 | 09:00 | 120 | 12:00 | Postogola | 143 | 05:00 | 137 | 11:00
| Cumilla(N) | 139 | 19:30 | 133 | 11:00 | Purbachal | 142 | 04:00 | 128 | 15:00
| Cumilla(S) | 138 | 18:00 | 128 | 15:00 | Purbasadipur | 133 | 06:00 | 118 | 11:00
| Daudkandi | 132 | 19:00 | 122 | 11:00 | Rahanpur | 135 | 02:00 | 133 | 16:00
| Dhaka | 139 | 03:00 | 131 | 11:00 | Rahim | 134 | 07:00 | 128 | 16:00
| Dhamrai | 139 | 05:00 | 131 | 11:00 | Rajbari | 136 | 03:00 | 131 | 16:00
| Dhanmondi | 140 | 06:00 | 131 | 11:00 | Rajendrapur | 133 | 18:30 | 121 | 15:00
| Dohazari | 136 | 17:00 | 130 | 16:00 | Rajshahi | 138 | 02:00 | 130 | 11:00
| Faridpur | 136 | 03:00 | 132 | 11:00 | Rajshahi-230 | 140 | 06:00 | 126 | 08:00
| Fatullah | 140 | 05:00 | 134 | 16:00 | Ramganj | 137 | 17:00 | 126 | 11:00
| Fenchuganj | 136 | 04:00 | 133 | 16:00 | Rampur | 139 | 19:00 | 134 | 02:00
| Feni | 138 | 17:00 | 130 | 02:00 | Rampura | 140 | 06:00 | 131 | 12:00
| Ghatail | 132 | 19:30 | 125 | 16:00 | Rangamati | 139 | 18:30 | 134 | 11:00
| Ghorashal | 143 | 07:00 | 137 | 11:00 | Rangpur | 135 | 06:00 | 123 | 11:00
| Goalpara | 144 | 05:00 | 134 | 12:00 | Ruppur | 142 | 05:00 | 136 | 11:00
| Gollamari | 142 | 04:00 | 135 | 11:00 | Saidpur | 134 | 05:00 | 125 | 07:00
| Gopalganj | 139 | 05:00 | 134 | 11:00 | Satkhira | 142 | 05:00 | 134 | 11:00
| Gopalganj-400 | 137 | 04:00 | 133 | 11:00 | Satmasjid | 140 | 04:00 | 134 | 15:00
| Gulshan | 140 | 06:00 | 130 | 15:00 | Savar | 140 | 07:00 | 135 | 11:00
| Halishahar | 139 | 18:00 | 133 | 11:00 | SevenRings | 143 | 05:00 | 137 | 12:00
| Haripur | 134 | 00:00 | 130 | 11:00 | ShahCement | 136 | 06:00 | 128 | 16:00
| HaripurSBU | 142 | 17:00 | 130 | 11:00 | Shahjadpur | 143 | 00:00 | 140 | 10:00
| Hasnabad | 143 | 05:00 | 136 | 11:00 | Shahjibazar | 137 | 06:00 | 131 | 18:00
| Hathazari | 142 | 18:00 | 138 | 00:00 | Shahmirpur | 139 | 04:00 | 134 | 23:00
| Ishurdi | 142 | 05:00 | 136 | 11:00 | Shariatpur | 136 | 04:00 | 131 | 16:00
| Jaldhaka | 133 | 17:00 | 122 | 07:00 | Sherpur | 139 | 19:30 | 123 | 01:00
| Jamalpur | 140 | 13:00 | 122 | 01:00 | Shikalbaha | 128 | 19:30 | 123 | 16:00
| Jashore | 140 | 06:00 | 132 | 11:00 | Shikalbaha-230 | 140 | 17:00 | 134 | 11:00
| Jhenaidah | 143 | 06:00 | 135 | 11:00 | Shitalakhya | 141 | 05:00 | 134 | 16:00
| Jhenaidah-230 | 143 | 04:00 | 135 | 11:00 | Sholosohor | 139 | 07:00 | 133 | 11:00
| Joydebpur | 140 | 05:00 | 132 | 12:00 | Shyampur | 138 | 01:00 | 132 | 11:00
| Joypurhat | 137 | 05:00 | 130 | 11:00 | Shyampur-230 | 143 | 06:00 | 135 | 11:00
| Juldah | 140 | 19:30 | 134 | 01:00 | Siddhirganj | 137 | 06:00 | 130 | 11:00
| Kabirpur | 139 | 02:00 | 122 | 16:00 | Sirajganj | 139 | 01:00 | 134 | 11:00
| Kachua | 140 | 18:00 | 130 | 01:00 | Sonargaon | 132 | 19:00 | 117 | 11:00
| Kaliakoir | 140 | 04:00 | 127 | 16:00 | Sreemongol | 135 | 02:00 | 131 | 18:00
| Kallyanpur | 138 | 03:00 | 133 | 11:00 | Sreepur | 136 | 05:00 | 130 | 11:00
| Kalurghat | 140 | 18:30 | 134 | 11:00 | Srinagar | 138 | 05:00 | 131 | 11:00
| Kamrangirchar | 138 | 04:00 | 131 | 16:00 | SSM | 142 | 17:00 | 138 | 13:00
| Kaptai | 140 | 1:00 | 136 | 11:00 | Sunamganj | 129 | 07:00 | 125 | 13:00
| Kazla | 137 | 05:00 | 129 | 12:00 | Sylhet | 132 | 04:00 | 128 | 13:00
| Keranigonj | 139 | 06:00 | 131 | 11:00 | Sylhet-132 | 131 | 01:00 | 129 | 11:00
| Khagrachori | 138 | 06:00 | 133 | 11:00 | Tangail | 130 | 18:00 | 124 | 09:00
| Khulna | 142 | 05:00 | 134 | 12:00 | Thakurgaon | 136 | 17:00 | 116 | 11:00
| Khulna(S) | 144 | 05:00 | 136 | 11:00 | TK | 140 | 18:00 | 134 | 11:00
| Khulshi | 138 | 18:00 | 132 | 11:00 | Tongi | 142 | 04:00 | 130 | 15:00
| Kishoreganj | 136 | 05:00 | 130 | 11:00 | Ullahpara | 142 | 05:00 | 137 | 11:00
| Kodda | 137 | 03:00 | 121 | 15:00 | Ullon | 139 | 04:00 | 130 | 11:00
| KSRM | 140 | 18:30 | 135 | 15:00 | Uttara | 142 | 05:00 | 135 | 11:00
| Kulaura | 136 | 06:00 | 132 | 12:00 | UttaraNew | 141 | 04:00 | 127 | 15:00
| Kurigram | 132 | 04:00 | 118 | 07:00 | Zigatola | 138 | 04:00 | 131 | 11:00

## L-Curve
Date | 2024-11-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1334 | 4928 | 4026 | 8954 |  |  |  | QF-LDC-11
0:30 | 1397 | 4657.5 | 4035 | 8692.5 | Date: | 2024-11-19
1:00 | 1460 | 4387 | 4044 | 8431
1:30 | 1455 | 4311.5 | 3948 | 8259.5
2:00 | 1450 | 4236 | 3852 | 8088
2:30 | 1430 | 4202 | 3776.5 | 7978.5 | [5 empty] | Gen. at Eve. Peak | 11273 | 11273 MW (18:00 )
3:00 | 1410 | 4168 | 3701 | 7869 | [6 empty] | 18:00
3:30 | 1376 | 4137 | 3627 | 7764 | [5 empty] | Gen. at Day Peak | 9599 | 9599 MW (12:00 )
4:00 | 1342 | 4106 | 3553 | 7659 | [6 empty] | 12:00
4:30 | 1343 | 4073 | 3537.5 | 7610.5 | [5 empty] | Highest Generation | 11273
5:00 | 1344 | 4040 | 3522 | 7562 | [6 empty] | 18:00
5:30 | 1302 | 4081 | 3539.5 | 7620.5
6:00 | 1260 | 4122 | 3557 | 7679
6:30 | 1208 | 4355.5 | 3783 | 8138.5
7:00 | 1156 | 4589 | 4009 | 8598
7:30 | 1164 | 4666 | 4049 | 8715
8:00 | 1172 | 4743 | 4089 | 8832
8:30 | 1343 | 4791 | 4120 | 8911
9:00 | 1514 | 4839 | 4151 | 8990
9:30 | 1628 | 4806.5 | 4176.5 | 8983
10:00 | 1742 | 4774 | 4202 | 8976
10:30 | 1777 | 4837.5 | 4249 | 9086.5
11:00 | 1812 | 4901 | 4296 | 9197
11:30 | 1737 | 4987.5 | 4410.5 | 9398
12:00 | 1662 | 5074 | 4525 | 9599
12:30 | 1585 | 5265 | 4543 | 9808
13:00 | 1508 | 5456 | 4561 | 10017
13:30 | 1510 | 5454 | 4483 | 9937
14:00 | 1512 | 5452 | 4405 | 9857
14:30 | 1592 | 5325.5 | 4395 | 9720.5
15:00 | 1672 | 5199 | 4385 | 9584
15:30 | 1607 | 5208 | 4362 | 9570
16:00 | 1542 | 5217 | 4339 | 9556
16:30 | 1543 | 5270 | 4325.5 | 9595.5
17:00 | 1544 | 5323 | 4312 | 9635
17:30 | 1320 | 5953.5 | 4500.5 | 10454
18:00 | 1096 | 6584 | 4689 | 11273
18:30 | 1107 | 6366.5 | 4633.5 | 11000
19:00 | 1118 | 6149 | 4578 | 10727
19:30 | 1146 | 5985 | 4501 | 10486
20:00 | 1160 | 5909 | 4412 | 10321 |  |  |  | Executive Engineer
20:30 | 1188 | 5848 | 4414.5 | 10262.5 |  |  |  | Network Operation Division
21:00 | 1216 | 5787 | 4417 | 10204
21:30 | 1196 | 5656.5 | 4340 | 9996.5
22:00 | 1176 | 5526 | 4263 | 9789 |  |  |  |  | Page 6 of 7
22:30 | 1257 | 5268.5 | 4256 | 9524.5
23:00 | 1338 | 5011 | 4249 | 9260
23:30 | 1336 | 4969.5 | 4137.5 | 9107
24:00 | 1334 | 4928 | 4026 | 8954
11273 MW (18:00 )
9599 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-11-19 |  |  | Energy |  | 225278515
[17 empty] | 2024-11-19 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | Nepal | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 2969 | 907 | 0 | 2438 | 0 | 55 | 1671 | 96 | 0 | 16 | 50 | 752 | 0 | 0 | 0
0:30 | 2906.5 | 902.5 | 0 | 2203.5 | 0 | 46.5 | 1724 | 95 | 0 | 8 | 52 | 752.5 | 0 | 2 | 0 |  |  | Date: | 44153
1:00 | 2844 | 898 | 0 | 1969 | 0 | 38 | 1777 | 94 | 0 | 0 | 54 | 753 | 0 | 4 | 0
1:30 | 2793.5 | 898 | 0 | 1965.5 | 0 | 19 | 1685 | 93.5 | 0 | 0 | 50 | 752 | 0 | 3 | 0 | [8 empty] | Total Energy | 225.2785 | 225.2785 | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 2743 | 898 | 0 | 1962 | 0 | 0 | 1593 | 93 | 0 | 0 | 46 | 751 | 0 | 2 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2724.5 | 898 | 0 | 1989 | 0 | 0 | 1520 | 92 | 0 | 0 | 47 | 704 | 0 | 4 | 0 | [8 empty] | Energy Requirement | 225.2785 | 225.2785
3:00 | 2706 | 898 | 0 | 2016 | 0 | 0 | 1447 | 91 | 0 | 0 | 48 | 657 | 0 | 6 | 0
3:30 | 2710 | 898 | 0 | 1998 | 0 | 0 | 1403.5 | 90.5 | 0 | 0 | 48 | 610.5 | 0 | 5.5 | 0 | [7 empty] | Shortage
4:00 | 2714 | 898 | 0 | 1980 | 0 | 0 | 1360 | 90 | 0 | 0 | 48 | 564 | 0 | 5 | 0
4:30 | 2688 | 898.5 | 0 | 1966.5 | 0 | 0 | 1352.5 | 90 | 0 | 0 | 49 | 561.5 | 0 | 4.5 | 0
5:00 | 2662 | 899 | 0 | 1953 | 0 | 0 | 1345 | 90 | 0 | 0 | 50 | 559 | 0 | 4 | 0
5:30 | 2659.5 | 898.5 | 0 | 1906 | 0 | 49 | 1376 | 90.5 | 0 | 8.5 | 47 | 582.5 | 0 | 3 | 0
6:00 | 2657 | 898 | 0 | 1859 | 0 | 98 | 1407 | 91 | 0 | 17 | 44 | 606 | 0 | 2 | 0
6:30 | 2731.5 | 898 | 0 | 1902.5 | 0 | 250.5 | 1489.5 | 91.5 | 0 | 25 | 43 | 679 | 27 | 1 | 0 | [6 empty] | Coal
7:00 | 2806 | 898 | 0 | 1946 | 0 | 403 | 1572 | 92 | 0 | 33 | 42 | 752 | 54 | 0 | 0
7:30 | 2754 | 898.5 | 0 | 1941 | 0 | 458 | 1598 | 93 | 0 | 33 | 39 | 751.5 | 149 | 0 | 0 | [5 empty] | Oil
8:00 | 2702 | 899 | 0 | 1936 | 0 | 513 | 1624 | 94 | 0 | 33 | 36 | 751 | 244 | 0 | 0
8:30 | 2713 | 898.5 | 0 | 1940.5 | 0 | 503.5 | 1598 | 94.5 | 0 | 33 | 41 | 752.5 | 336.5 | 0 | 0
9:00 | 2724 | 898 | 0 | 1945 | 0 | 494 | 1572 | 95 | 0 | 33 | 46 | 754 | 429 | 0 | 0
9:30 | 2745.5 | 897.5 | 0 | 1941.5 | 0 | 467 | 1506 | 95 | 0 | 33 | 48 | 752.5 | 497 | 0 | 0
10:00 | 2767 | 897 | 0 | 1938 | 0 | 440 | 1440 | 95 | 0 | 33 | 50 | 751 | 565 | 0 | 0
10:30 | 2734 | 897 | 0 | 2046 | 0 | 426 | 1449.5 | 95.5 | 0 | 33 | 50 | 754 | 601.5 | 0 | 0
11:00 | 2701 | 897 | 0 | 2154 | 0 | 412 | 1459 | 96 | 0 | 33 | 50 | 757 | 638 | 0 | 0
11:30 | 2691.5 | 897 | 0 | 2162.5 | 0 | 515.5 | 1566 | 96 | 0 | 42.5 | 52 | 756 | 619 | 0 | 0
12:00 | 2682 | 897 | 0 | 2171 | 0 | 619 | 1673 | 96 | 0 | 52 | 54 | 755 | 600 | 0 | 0
12:30 | 2694.5 | 896.5 | 0 | 2198 | 0 | 771 | 1723 | 96 | 0 | 53.5 | 54 | 754.5 | 567 | 0 | 0
13:00 | 2707 | 896 | 0 | 2225 | 0 | 923 | 1773 | 96 | 0 | 55 | 54 | 754 | 534 | 0 | 0
13:30 | 2707 | 896 | 0 | 2225 | 0 | 923 | 1773 | 96 | 0 | 55 | 54 | 754 | 534 | 0 | 0
14:00 | 2707 | 896 | 0 | 2225 | 0 | 923 | 1773 | 96 | 0 | 55 | 54 | 754 | 534 | 0 | 0
14:30 | 2748.5 | 896 | 0 | 2106 | 0 | 880.5 | 1771 | 95.5 | 0 | 50 | 58 | 753.5 | 440.5 | 1 | 0
15:00 | 2790 | 896 | 0 | 1987 | 0 | 838 | 1769 | 95 | 0 | 45 | 62 | 753 | 347 | 2 | 0
15:30 | 2859.5 | 896 | 0 | 2031.5 | 0 | 830 | 1767.5 | 94 | 0 | 41 | 55 | 754 | 240.5 | 1 | 0
16:00 | 2929 | 896 | 0 | 2076 | 0 | 822 | 1766 | 93 | 0 | 37 | 48 | 755 | 134 | 0 | 0
16:30 | 2874.5 | 895 | 0 | 2001.5 | 0 | 951.5 | 1764.5 | 92.5 | 0 | 140 | 51 | 755 | 70 | 0 | 0
17:00 | 2820 | 894 | 0 | 1927 | 0 | 1081 | 1763 | 92 | 0 | 243 | 54 | 755 | 6 | 0 | 0
17:30 | 2892 | 894.5 | 0 | 2061 | 0 | 1520 | 1752 | 92 | 0 | 429 | 56 | 754.5 | 3 | 0 | 0
18:00 | 2964 | 895 | 0 | 2195 | 0 | 1959 | 1741 | 92 | 0 | 615 | 58 | 754 | 0 | 0 | 0
18:30 | 2965 | 895.5 | 0 | 2161 | 0 | 1813.5 | 1741 | 92.5 | 0 | 524 | 54 | 753.5 | 0 | 0 | 0
19:00 | 2966 | 896 | 0 | 2127 | 0 | 1668 | 1741 | 93 | 0 | 433 | 50 | 753 | 0 | 0 | 0
19:30 | 2987 | 896 | 0 | 2188 | 0 | 1427 | 1740 | 93 | 0 | 347 | 54 | 754 | 0 | 0 | 0
20:00 | 3042 | 896 | 0 | 2265 | 0 | 1127 | 1740 | 89 | 0 | 354 | 54 | 754 | 0 | 0 | 0
20:30 | 3017 | 897.5 | 0 | 2252 | 0 | 1101.5 | 1751.5 | 92 | 0 | 342.5 | 55 | 753.5 | 0 | 0 | 0
21:00 | 2992 | 899 | 0 | 2239 | 0 | 1076 | 1763 | 95 | 0 | 331 | 56 | 753 | 0 | 0 | 0
21:30 | 3017 | 899 | 0 | 2213.5 | 0 | 969.5 | 1765.5 | 95 | 0 | 227.5 | 56 | 753.5 | 0 | 0 | 0
22:00 | 3042 | 899 | 0 | 2188 | 0 | 863 | 1768 | 95 | 0 | 124 | 56 | 754 | 0 | 0 | 0
22:30 | 3008.5 | 902.5 | 0 | 2221.5 | 0 | 639 | 1768 | 95.5 | 0 | 82.5 | 53 | 754 | 0 | 0 | 0
23:00 | 2975 | 906 | 0 | 2255 | 0 | 415 | 1768 | 96 | 0 | 41 | 50 | 754 | 0 | 0 | 0
23:30 | 2972 | 906.5 | 0 | 2346.5 | 0 | 235 | 1719.5 | 96 | 0 | 28.5 | 50 | 753 | 0 | 0 | 0 |  |  | Max Temp. in Dhaka |  | 30.4°C
24:00 | 2969 | 907 | 0 | 2438 | 0 | 55 | 1671 | 96 | 0 | 16 | 50 | 752 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on Y13: Author:

## Generation
2024-11-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 94 | 93 | 91 | 90 | 90 | 91 | 92 | 94 | 95 | 95 | 96 | 96 | 96 | 96 | 95 | 93 | 92 | 92 |  | 93 | 93 | 89 | 95 | 95 | 96 | 96 | 2240635
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 6 | 14 | [8 empty] | 30634
| Teknaf 20MW PP (Solartech) | [6 empty] | 4 | 10 | 15 | 18 | 19 | 19 | 18 | 15 | 11 | 5 | 0 | [9 empty] | 127710
6 | Sikalbaha 225MW CCPP (Gas) | 231 | 232 | 231 | 230 | 230 | 230 | 232 | 231 | 231 | 228 |  |  |  | 81 | 86 | 97 | 175 | 223 |  | 223 | 223 | 224 | 224 | 224 | 230 | 231 | 4339924
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [26 empty] | 0
12 | Hathazari 100 MW peaking PP | [16 empty] | 24 | 42 |  | 42 | 42 | 49 | 64 | 24 |  |  | 187680
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [6 empty] | 14 | 17 | [8 empty] | 10 | 45 |  | 17 | 17 | 17 | 17 | 17 |  |  | 188181
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [17 empty] | 46 |  | 45 | 38 | 38 |  |  |  |  | 142304
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 250 | 250 | 250 | 250 | 250 | 250 | 280 | 280 | 280 | 280 | 320 | 329 | 325 | 328 | 280 | 315 | 334 | 335 |  | 335 | 335 | 335 | 335 | 335 | 280 | 280 | 7040721
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 5 | 30 |  | 30 | [6 empty] | 57709
19 | Ashuganj 195 MW PP (APSCL-United) | 199 | 200 | 200 | 170 | 170 | 130 | 102 | 153 | 157 | 130 | 165 | 194 | 195 | 195 | 195 | 195 | 175 | 185 |  | 185 | 185 | 195 | 195 | 195 | 197 | 197 | 4248727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 530 | 440 | 400 | 405 | 435 | 520 | 530 | 530 | 450 | 481 | 584 | 612 | 612 | 612 | 612 | 612 | 612 |  | 612 | 612 | 612 | 612 | 612 | 612 | 590 | 13292726
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 44 | 44 | 41 | 41 | 41 | 43 | 44 | 35 | 35 | 34 | 31 | 33 | 33 | 35 | 35 | 36 | 36 |  | 38 | 38 | 38 | 38 | 36 | 38 | 38 | 920592
33 | Ashuganj 225 MW CCPP | 190 | 181 | 181 | 182 | 181 | 181 | 182 | 182 | 181 | 227 | 215 | 183 | 183 | 181 | 190 | 205 | 182 | 181 |  | 181 | 181 | 197 | 181 | 188 | 180 | 181 | 4541000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 290 | 290 | 290 | 295 | 290 | 325 | 290 | 295 | 290 | 340 | 300 | 300 | 280 | 295 | 320 | 280 | 310 |  | 310 | 310 | 330 | 310 | 315 | 310 | 310 | 7577300
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 75 | 75 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 50 |  | 50 | 70 | 70 | 70 | 70 | 70 | 70 | 1609630
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [26 empty] | 0
| Meghnaghat Unique power | 241 | 240 | 240 | 241 | 241 | 239 | 240 | 240 | 240 | 242 | 235 | [6 empty] | 70 | [8 empty] | 2665909
| Summit Meghanghat-2 589 MW(Gas) |  | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 120 | 150 | 150 | 400 | 400 | 280 | 270 | 200 | 270 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 590 | 5514786
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 400 | 400 | 400 | 350 | 350 | 350 | 350 | 350 | 350 | 420 | 420 | 450 | 450 | 380 | 420 | 340 | 400 |  | 400 | 400 | 400 | 400 | 450 | 450 | 450 | 9496000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 34 | 34 | 39 | 72 | 69 | 69 | 33 | 27 | 27 | 26 | 26 | 24 | 11 | 10 | 10 | 18 | 29 | 28 |  | 30 | 30 | 33 | 33 | 34 | 34 | 34 | 710400
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 21 | 35 | 44 | 50 | 37 | 48 | 41 | 29 | 11 | 0 | [9 empty] | 331090
44 | Fenchugonj CCPP Phase-1 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 669000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 28 | 28 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688320
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 40 | 40 | 40 | 62 | 62 | 62 | 40 | 40 | 60 | 60 | 60 | 59 | 59 | 60 | 61 |  | 61 | 61 | 61 | 62 | 61 | 61 | 61 | 1371168
48 | Shahjibazar 86 MW PP (Shahjibazar) | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1974720
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 135 | 135 | 135 | 135 | 135 | 136 | 138 | 137 | 137 | 137 | 137 | 131 | 131 | 131 | 131 | 131 | 131 | 133 |  | 134 | 134 | 134 | 134 | 134 | 134 | 135 | 3178760
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 52704
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 332976
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 285 | 290 | 280 | 275 | 285 | 290 | 280 | 285 | 270 | 305 | 300 | 300 | 285 | 290 | 315 | 310 | 295 |  | 285 | 280 | 295 | 295 | 290 | 280 | 300 | 7118000
| Bibiyana South 400 MW | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 375 | 316 | 316 | 345 | 360 | 375 | 345 | 345 |  | 345 | 345 | 360 | 345 | 346 | 346 | 346 | 8076400
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 35 |  | 35 | 17 | 17 | 17 |  |  |  | 124688
59 | Tangail Palli Power Gen 22 MW | 6 | [5 empty] | 10 | 14 | 24 | 24 | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 438720
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 54 | 46 | 48 | 48 | 50 | 44 | 42 | 36 | 46 | 50 | 50 | 54 | 54 | 56 | 62 | 48 | 54 | 58 |  | 50 | 54 | 54 | 56 | 56 | 50 | 50 | 1178880
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 40 | 40 | 40 | 30 | 24 | 6 | 4 | 3 | 3 | 3 | 9 | 2 | 3 | 2 | 9 | 2 |  | 10 | 14 | 19 | 25 | 22 | 20 | 27 | 493920
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 15 | 15 | 15 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 348050
69 | Summit Ashulia | 16 | 15 | 15 | 15 | 14 | 13 | 15 | 20 | 19 | 0 | 0 | 0 | 14 | 18 | 21 | 21 | 21 | 20 |  | 19 | 20 | 20 | 22 | 22 | 19 | 17 | 378600
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 495360
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 400320
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818500
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [16 empty] | 80 | 106 |  | 52 | 17 | 17 | 2 |  |  |  | 228000
| Chowmuhani 113 MW | [6 empty] | 15 | 26 | 26 | 26 | 26 | 46 | 72 | 73 | 73 | 73 | 80 | 104 |  | 95 | 95 | 94 | 95 | 55 | 9 |  | 1093680
| Manikgonj 162MW PP(MPGL) | [5 empty] | 17 | 17 | 17 | 17 |  |  | 50 | 90 | 90 | 54 | 54 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  |  | 554400
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150 MW PP | [6 empty] | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 16 | 16 | 16 | 48 | 132 |  | 48 | 48 | 48 | 48 | 32 | 16 | 16 | 559200
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 52 |  | 25 | 8 | 8 | 8 | 8 |  |  | 103018
| Gazipur 100 MW PP | [6 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 17 | 17 | 20 | 105 |  | 70 | 34 | 34 | 34 | 17 |  |  | 497280
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 25078
| Jodiac Power | [5 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 33 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 |  | 773172
| Karnaphuli Power Ltd. | [6 empty] | 9 | 17 | [8 empty] | 11 | 34 |  | 17 | [6 empty] | 131310
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 9 |  | 13 | [6 empty] | 18000
86 | Meghnaghat CCPP ( Summit) | 65 | 63 | 95 | 105 | 140 | 147 | 150 | 132 | 123 | 130 | 153 | 141 | 143 | 138 | 153 | 150 | 143 | 141 |  | 139 | 137 | 154 | 141 | 136 | 149 | 146 | 3113949
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [19 empty] | 14 | 15 | 15 | 15 |  |  |  | 33600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 33 | 33 | 33 | 30 | 33 | 33 |  | 34 | 34 | 34 | 34 | 31 | 31 | 34 | 804096
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 972704
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 8 | 8 | [5 empty] | 8 |  | 8 | 8 | 8 |  |  |  |  | 37440
95 | Patenga 50MW PP (Baraka) | [5 empty] | 1 | 4 | 6 | 6 | 6 | 6 | 16 | 32 | 32 | 32 | 33 | 33 | 33 |  | 49 | 33 | 33 | 19 | 19 | 19 |  | 404160
96 | Chattogram 108 MW PP (ECPV) | [6 empty] | 2 | 6 | 12 | 12 | 12 | 14 | 13 | 12 | 6 | 6 | 6 | 7 |  | 32 | 38 | 31 | 12 | 12 |  |  | 200640
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [20 empty] | 8 | 5 | 15 |  |  |  | 24218
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 55 |  | 55 | 55 | 17 | 17 | 17 |  |  | 176560
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 13650
103 | Kamalaghat 54 MW PP(Banco Energy) | [6 empty] | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 186840
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 16 |  |  |  |  | 5 | 45 | 65 | 65 | 45 | 45 | 65 | 97 | 94 | 65 | 65 | 94 | 95 |  | 97 | 97 | 97 | 96 | 65 | 65 | 24 | 1310400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 7 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 55 |  | 60 | 35 | 40 | 35 | 30 |  |  | 400320
115 | Juldah 100 MW PP Unit-3 (Acorn) | [5 empty] | 8 | 12 | 12 | 12 | 12 | 12 | 30 | 60 | 60 | 25 | 25 | 30 | 100 |  | 50 | 50 | 50 | 50 | 50 |  |  | 648000
116 | Chandpur 200 MW (Desh energy) | [5 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 24 | 64 | 85 | 51 | 51 | 60 | 142 |  | 136 | 136 | 85 | 85 | 51 | 17 |  | 1124640
117 | Ashuganj 150 MW PP (Midland) | [5 empty] | 2 | 15 | 20 | 20 | 20 | 20 | 27 | 33 | 60 | 80 | 80 | 87 | 95 |  | 99 | 112 | 60 | 60 | 60 | 18 |  | 980218
118 | Bibiyana-III 400 MW CCPP | 323 | 314 | 276 | 277 | 225 | 225 | 275 | 275 | 300 | 357 | 386 | 385 | 384 | 386 | 389 | 390 | 310 | 386 |  | 386 | 385 | 385 | 384 | 384 | 384 | 384 | 8472000
| Jamalpur 115 MW PP (United) | [5 empty] | 2 | 19 | 45 | 45 | 16 | 16 | 16 | 55 | 55 | 58 | 58 | 58 | 58 |  | 58 | 58 | 24 | 24 | 24 | 24 | 8 | 726000
| Anwara 300 MW PP (United) | 16 |  |  |  |  | 30 | 50 | 49 | 49 | 52 | 52 | 52 | 60 | 68 | 68 | 68 | 50 | 50 |  | 50 | 51 | 51 | 51 | 52 | 52 |  | 988582
| Juldah unit-2 (Acorn) | [5 empty] | 2 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 86 |  | 50 | 50 | 50 | 50 | 12 |  |  | 526080
| Anlima Energy Ltd. | [5 empty] | 3 | 17 | 17 | 8 | 17 | 17 | 22 | 35 | 35 | 35 | 35 | 35 | 40 |  | 53 | 53 | 53 | 53 | 53 | 17 |  | 612218
| Bhairob 54.5 MW | [5 empty] | 0 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 29 |  | 54 | 54 | 54 | 54 | 54 |  |  | 464760
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 13 | 22 | 27 | 30 | 30 | 29 | 25 | 17 | 7 | 1 | [9 empty] | 203478
| Chandpur 115(Doreen) | [6 empty] | 14 | 16 | 16 | 16 | 16 | 16 | 35 | 50 | 16 | 16 | 17 | [9 empty] | 271680
| Kanchan Purbachal Power Generation Ltd. | [5 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 |  | 537840
| Mirsharai 150 MW (Oil) | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 160 |  | 54 | 54 | 54 | 54 | 17 |  |  | 530255
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 4 | 2 | 6 | 5 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30240
| Sonagazi 75 MW Solar Plant | [6 empty] | 10 | 39 | 56 | 66 | 72 | 72 | 68 | 58 | 42 | 20 | 1 | [9 empty] | 508718
Matarbari 2*600 MW (CPGCL)
Meghnaghat (Reliance) 718MW CCPP
| Sreepur 150 MW | [11 empty] | 3 | 6 | 10 | 12 | 4 | 15 | [9 empty] | 51600
120
121 | Eastern Zone Total | 4387 | 4236 | 4168 | 4106 | 4040 | 4122 | 4589 | 4743 | 4839 | 4774 | 4901 | 5074 | 5456 | 5452 | 5199 | 5217 | 5323 | 6584 |  | 6149 | 5985 | 5909 | 5787 | 5526 | 5011 | 4928 | 121740768
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | [17 empty] | 35 |  | 41 | [6 empty] | 480000
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha)
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 6 | 25 | 50 | 67 | 80 | 76 | 72 | 61 | 41 | 17 | 2 | [9 empty] | 504720
132 | Rampal 1320 MW (BIFPCL) | 369 | 369 | 368 | 371 | 370 | 371 | 371 | 372 | 370 | 368 | 367 | 368 | 369 | 367 | 370 | 370 | 370 | 370 |  | 370 | 369 | 369 | 369 | 372 | 371 | 368 | 8974545
133 | United Payra Power Ltd. | [5 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 132 |  | 150 | 150 | 81 | 81 | 81 | 81 |  | 976800
| Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 180 | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 220 | 180 | 220 |  | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 5055330
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | [6 empty] | 17568
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3575
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 81 | 81 | 81 | 81 | 81 | 81 | 127 | 80 | 80 | 80 | 100 | 123 | 123 | 123 | 123 | 123 | 80 | 80 |  | 80 | 80 | 80 | 80 | 127 | 127 | 127 | 2481000
141 | Bhola 33 MW PP (Venture) | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 4 | 3 | 3 | 4 | 4 | 5 | 4 | 4 | 4 | 5 | 6 |  | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 132399
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
| Bheramara HVDC | 898 | 898 | 898 | 898 | 899 | 898 | 898 | 899 | 898 | 897 | 897 | 897 | 896 | 896 | 896 | 896 | 894 | 895 |  | 896 | 896 | 896 | 899 | 899 | 906 | 907 | 21698909
147 | Nepal
148 | Bheramara 410 MW CCPP | 273 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 312 | 303 | 250 | 250 | 266 | 266 | 270 |  | 270 | 270 | 270 | 270 | 265 | 268 | 265 | 6324192
149 | Payra 1320 MW | 622 | 520 | 470 | 420 | 400 | 430 | 510 | 550 | 500 | 450 | 440 | 550 | 622 | 622 | 622 | 622 | 622 | 600 |  | 600 | 600 | 600 | 620 | 622 | 622 | 550 | 14332700
150
151 | Barapukuria TPP Unit-1 | 67 | 67 | 67 | 67 | 68 | 67 | 67 | 67 | 67 | 68 | 67 | 66 | 66 | 65 | 66 | 66 | 66 | 65 |  | 65 | 65 | 65 | 65 | 67 | 68 | 67 | 1535564
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 107 | 107 | 102 | 102 | 102 | 104 | 104 | 105 | 105 | 104 | 104 | 105 | 104 | 100 | 99 | 96 | 93 | 94 |  | 94 | 94 | 94 | 97 | 95 | 95 | 96 | 2510000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 40 |  | 40 | 40 | 40 | 40 |  |  |  | 152220
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 32340
157 | Sirajganj 68 MW Solar Park | [6 empty] | 3 | 17 | 38 | 53 | 63 | 53 | 56 | 48 | 35 | 10 | 0 | [9 empty] | 386252
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 169 | 169 | 168 | 167 | 167 | 167 | 167 | 140 | 140 | 140 | 140 | 140 | 158 | 168 | 168 | 165 | 162 | 162 |  | 161 | 163 | 164 | 166 | 166 | 166 | 166 | 3899545
Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 170 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 158 | 180 | 181 | 180 | 177 | 176 |  | 175 | 174 | 173 | 170 | 167 | 163 | 159 | 4059582
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 347 | 322 | 322 | 315 | 308 | 250 | 322 | 348 | 320 | 320 | 380 | 338 | 344 | 318 | 353 | 414 | 336 | 316 |  | 321 | 385 | 414 | 395 | 350 | 414 | 380 | 8480727
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP | [17 empty] | 4 | [8 empty] | 4906
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 2 | 2 | 5 | 5 | 5 | 2 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 88722
166 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | [16 empty] | 12 | 31 |  | 38 | [6 empty] | 53935
169 | Santahar 50 MW Peaking PP | [16 empty] | 15 | 30 |  | 30 | 30 | 30 | 30 |  |  |  | 134328
170 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
171 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 94 | 95 |  | 95 | 95 | 95 | 95 | 51 | 25 |  | 532544
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [16 empty] | 13 | 84 |  | 50 | 50 | [5 empty] | 194304
173 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 20 | 60 |  | 19 | [6 empty] | 120672
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [16 empty] | 35 | 70 |  | 28 | [6 empty] | 108480
178 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 35856
| Energypac Power Venture Thakurgaon Ltd. | [5 empty] | 14 | 35 | 35 | 35 | 35 |  | 34 | 34 | 35 | 35 | 35 | 73 | 95 |  | 55 | 55 | 55 | 55 | 55 |  |  | 728064
| Intraco Solar 30 MW | [6 empty] | 2 | 11 | 20 | 30 | 34 | 35 | 34 | 28 | 18 | 8 | 0 | [9 empty] | 207076
178 | Adani Power Jharkhanda Ltd | 753 | 751 | 657 | 564 | 559 | 606 | 752 | 751 | 754 | 751 | 757 | 755 | 754 | 755 | 753 | 755 | 755 | 754 |  | 753 | 754 | 754 | 753 | 754 | 754 | 752 | 17618182
| Teesta Solar Limited | [6 empty] | 14 | 69 | 120 | 161 | 180 | 178 | 119 | 101 | 96 | 33 | 2 | [9 empty] | 1093000
179 | Pabna Solar 100 MW | [6 empty] | 7 | 35 | 63 | 85 | 94 | 84 | 76 | 57 | 50 | 20 | 0 | [9 empty] | 579710
| Western Zone Total | 4044 | 3852 | 3701 | 3553 | 3522 | 3557 | 4009 | 4089 | 4151 | 4202 | 4296 | 4525 | 4561 | 4405 | 4385 | 4339 | 4312 | 4689 |  | 4578 | 4501 | 4412 | 4417 | 4263 | 4249 | 4026 | 103537747
[27 empty] | Total | 225278515