## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-03-01 | Friday
|  | Date (day): | 2019-03-01 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11357 | MW |  |  | (b) At Evening Peak Hour : |  | 12856 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-02-28 | 2019-03-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit #1 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under Maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under Maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 350 | 360 | 360
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 78 | 60 | 60 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 107 | 111 | 108 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 20 | 20 | 40 | 40 | 78 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 351 | 375 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under Maint.
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  | 305 | Under Maint.
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 14 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 110 | 110 | 110 | 110 | 5 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 37 | 93 | 100 | 100 |  |  | FGMO
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 114 | 115 | 115 | 115 |  | 102 | Machine problem
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 7 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | Under maint.
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 50 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 18 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 7 | 52 | 52 |  | 56 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 58 | 58 | 58 |  | 22 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 11 | 16 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 29 | 30 | 30 | 30
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 40 | 41 | 41 |  |  | Engine problem
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 40 | 40 | 40 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 1621 | 1994 | 3778 | 4113 | 188 | 1306
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 100 | 120 | 140 | 40 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 19 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 25 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 72 | 74 | 74 | 74 |  | 156 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 234 | 227 | 225 | 225 |  | 0
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint.
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 8 | 40 | 41 | 41 |  | 10 | Engine problem
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 17 | 0 | 72
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 77
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 0 | 70 |  | 30 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 75 | 75 | 75 | 75 |  | 25 | Engine problem
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 25 | 15 | 30
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 106 | 106
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 551 | 797 | 770 | 1004 | 220 | 411
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 100 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 120 | 100 | 120 | 9 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 187 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 250 | 360 | 360
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 200 | 0 | 320 | 320
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 40 | 40 | 40 |  | 5 | Engine problem
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | Engine problem
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 5 | 85 | 5 | 85
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 95 | 95 | 95 |  | 68 | ST under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 0 | 0 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 90 | 114 | 107 | 128
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 22 | 22
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1036 | 1082 | 1948 | 2227 | 463 | 124
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 131 | 158 | 202 | 202
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 18 | 80 | 80 |  | 15 | Enjgine problem
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 7 | 100 | 200
78 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 122 | 122
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 161 | 205 | 528 | 626 | 0 | 15
79 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
80 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 55 | 74 | 74 | 74
81 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
82 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 221 | 225 | 300 | 300
83 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 31 | 51 | 51
84 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 39 | 44 | 44
85 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
86 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 65 | 66 | 66
87 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 85 | 85 | 86
88 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 48 | 50 | 50
89 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 105 | 104 | 110 | 110
90 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
91 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 24 | 24 | 24 | 24 |  | 26 | Engine problem
92 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 16 | 25 | 25
93 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 305 | 341 | 341
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
94 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 0 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1128 | 1250 | 1434 | 1435 | 0 | 26
95 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 654 | 859 | 618 | 766
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
96 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 115 | 115
97 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 6 | 0 | 50
98 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
99 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 0 | 70
100 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 350 | 410 | 410
101 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
103 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 934 | 1400 | 1388 | 1702 | 0 | 0
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 100 | 100 |  | 10 | Engine problem
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 20 | 26 | 26 |  | 7 | Engine problem
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 177 | 173 | 194 | 194
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 74 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 202 | 267 | 415 | 445 | 0 | 17
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 70 | 70 | 70
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage.
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 26 | 0 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 47
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 40 | 40 | 40 |  | 10 | Engine problem
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 32
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 160 | 192 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 135 | 192 | 175 | 200 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 136 | 194 | 190 | 200
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 | 282 |  | Under S/D
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 37
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 17 | 14 | 17
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 43 | 43 |  |  | Engine problem
124 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 26 | 100 | 100
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 0 | 0
| Confidence CPBL-2 |  | HFO | IPP | 113 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 1835 | 1825 | 483 | 833 | 947 | 1119 | 382 | 10
126 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
127 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 149 | 149 | 125 |  | Coal shortage
128 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 17
129 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 19
| Rangpur Area Total |  |  |  |  | 564 | 484 | 150 | 167 | 149 | 185 | 125 | 170
| Total |  |  |  |  | 18079 | 17536 | 6266 | 7995 | 11357 | 12856 | 1378 | 2079
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5831.0244 | 7440 | 10568.6154 | 11963.5572
A. |  | 2019-02-28 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 7995 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4402 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7995 | MW
3 | Day peak Generation : |  |  | 6266 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7440 | MW
4 | Evening peak Generation : |  |  | 7995 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 144.7185 | MKWHr | By Solar | 0.097805 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 118.7522 | MKWHr |  | By Oil: | 4.4215 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6729 | MKWHr |  | By Hydro: | 1.7813 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1378 | MW | Dhaka | 2619 | 2619 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2079 | MW | Chittagong | 896 | 896 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3457 | MW | Khulna | 926 | 926 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1060.17 | MMCFD |  |  | Rajshahi | 800 | 800 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 84247018.188 | ii) Oil : | Taka | 24612355.86 | Comilla | 602 | 602 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14177394 | Total | Taka | 123036768.048 | Mymensingh | 572 | 572 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.3525 | MKWHr. | Sylhet | 314 | 314 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | 60 | MW (E to W) at | 19:00 | hrs | Barisal | 156 | 156 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -310 | MW at | 8:00 | hrs | Rangpur | 555 | 555 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 24.6° C |  |  | Total | 7440 | 7440 |  | 0
B. |  | 2019-03-01 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 26.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12856 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6000 | MW
4 | Reserve(Generation end) |  |  |  | 4856 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 144.809 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4939 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.9855 | MKWHr. | ii) HVDC Flow at Peak Time |  | 859 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0074 | MKWHr. | iii) Maximum HVDC Flow : |  | 860 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.96 |  | (b) Today: | 91.87 |  | (c) Rule Curve: |  | 93
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-02-28
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | United Jamalpur PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 0 | 240 | 0 | 0 | 270 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 0 | 30 | 0 | 0 | 42 | 30 | 0 | 120 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 80 | 0 | 220 | 150 | 159 | 0 | 50 | 10 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 14 | 72 | 162 | 0 | 0 | 0 | 60 | 52 | 5 | 5 | 100 | 220 | 57 | 5 | 5 | 84 | 0 | 6 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 362 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 14 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 5 | 0 | 0 | 149 | 0 | 0 | 187 | 0 | 135 | 0 | 12 | 0 | 158 | 0 | 0 | 0 | 0 | 0 |  | 3438 | 1505 | 4943 | 3511 | 362 | 770 | 7 | 149 | 72 | 0 | 72 | 0 | 0 | 91.97
2:00 | 35 | 0 | 0 | 0 | 240 | 0 | 0 | 270 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 0 | 30 | 0 | 0 | 43 | 30 | 0 | 120 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 0 | 220 | 150 | 158 | 0 | 50 | 10 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 14 | 68 | 162 | 0 | 0 | 0 | 40 | 40 | 5 | 5 | 100 | 221 | 41 | 5 | 5 | 84 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 13 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 5 | 0 | 0 | 149 | 0 | 0 | 130 | 0 | 135 | 0 | 12 | 0 | 154 | 0 | 0 | 0 | 0 | 0 |  | 3385 | 1435 | 4820 | 3378 | 361 | 784 | 7 | 149 | 73 | 0 | 68 | 0 | 0 | 91.97
3:00 | 35 | 0 | 0 | 0 | 240 | 0 | 0 | 280 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 0 | 30 | 0 | 0 | 44 | 30 | 0 | 120 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 0 | 180 | 150 | 173 | 0 | 50 | 10 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 14 | 60 | 108 | 0 | 0 | 0 | 40 | 40 | 5 | 5 | 100 | 169 | 5 | 5 | 5 | 85 | 0 | 6 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 14 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 149 | 0 | 0 | 130 | 0 | 135 | 0 | 12 | 0 | 159 | 0 | 0 | 0 | 0 | 0 |  | 3066 | 1478 | 4544 | 3153 | 361 | 740 | 7 | 149 | 74 | 0 | 60 | 0 | 0 | 91.97
4:00 | 35 | 0 | 0 | 0 | 240 | 0 | 0 | 315 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 30 | 0 | 0 | 45 | 30 | 0 | 120 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 0 | 220 | 150 | 168 | 0 | 50 | 10 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 14 | 58 | 109 | 0 | 0 | 0 | 20 | 30 | 5 | 5 | 100 | 174 | 5 | 5 | 5 | 84 | 0 | 6 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 149 | 0 | 0 | 130 | 0 | 135 | 0 | 12 | 0 | 143 | 0 | 0 | 0 | 0 | 0 |  | 3034 | 1432 | 4466 | 3058 | 361 | 758 | 7 | 149 | 75 | 0 | 58 | 0 | 0 | 91.96
5:00 | 35 | 0 | 0 | 0 | 249 | 0 | 0 | 270 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 0 | 30 | 0 | 0 | 45 | 30 | 0 | 120 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 0 | 220 | 150 | 167 | 0 | 50 | 10 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 14 | 58 | 110 | 0 | 0 | 0 | 20 | 30 | 5 | 5 | 100 | 174 | 5 | 5 | 5 | 85 | 0 | 6 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 149 | 0 | 0 | 130 | 0 | 135 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 |  | 3020 | 1382 | 4402 | 3011 | 361 | 741 | 7 | 149 | 75 | 0 | 58 | 0 | 0 | 91.96
6:00 | 35 | 0 | 0 | 0 | 249 | 0 | 0 | 270 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 0 | 30 | 0 | 0 | 44 | 30 | 0 | 120 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 0 | 80 | 0 | 220 | 172 | 180 | 0 | 50 | 10 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 14 | 64 | 110 | 0 | 0 | 0 | 20 | 30 | 5 | 5 | 100 | 169 | 5 | 5 | 5 | 89 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 361 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3 | 0 | 0 | 0 | 149 | 0 | 0 | 130 | 0 | 135 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 |  | 3102 | 1332 | 4434 | 3009 | 361 | 770 | 7 | 149 | 74 | 0 | 64 | 0 | 0 | 91.96
7:00 | 35 | 0 | 0 | 0 | 250 | 65 | 0 | 347 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 0 | 30 | 0 | 0 | 44 | 30 | 0 | 120 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 80 | 0 | 220 | 172 | 159 | 0 | 50 | 40 | 5 | 5 | 0 | 5 | 0 | 0 | 11 | 0 | 0 | 14 | 66 | 108 | 0 | 0 | 0 | 20 | 30 | 43 | 32 | 100 | 172 | 20 | 5 | 45 | 89 | 0 | 24 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.7 | 0 | 0 | 0 | 0 | 0 |  | 361 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 8 | 0 | 0 | 0 | 149 | 0 | 0 | 130 | 0 | 135 | 0 | 12 | 0 | 136 | 0 | 0 | 0 | 0 | 0 |  | 3440.7 | 1363 | 4803.7 | 3146 | 361 | 999 | 7 | 149 | 74 | 0 | 66 | 1.7 | 0 | 91.95
8:00 | 35 | 0 | 0 | 0 | 300 | 104 | 81 | 360 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 0 | 30 | 0 | 0 | 43 | 30 | 0 | 120 | 0 | 234 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 0 | 80 | 0 | 220 | 176 | 159 | 0 | 50 | 40 | 5 | 5 | 0 | 5 | 0 | 0 | 22 | 5 | 25 | 10 | 70 | 110 | 0 | 22 | 0.2 | 20 | 30 | 45 | 50 | 100 | 171 | 57 | 5 | 45 | 112 | 0 | 24 | 10 | 320 | 17 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 9.3 | 10 | 0 | 0 | 0 | 0 |  | 361 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 130 | 0 | 135 | 0 | 12 | 0 | 136 | 0 | 0 | 0 | 0 | 0 |  | 3913.5 | 1388 | 5301.5 | 3439 | 361 | 1173 | 27 | 149 | 73 | 0 | 70 | 9.5 | 0 | 91.95
9:00 | 35 | 0 | 0 | 0 | 300 | 104 | 81 | 385 | 0 | 0 | 20 | 380 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 0 | 30 | 0 | 0 | 43 | 30 | 0 | 120 | 0 | 236 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 2 | 0 | 80 | 0 | 250 | 200 | 174 | 0 | 80 | 40 | 5 | 5 | 0 | 5 | 0 | 0 | 22 | 8 | 25 | 14 | 78 | 108 | 0 | 22 | 1.4 | 60 | 60 | 11 | 48 | 163 | 221 | 69 | 5 | 45 | 97 | 0 | 24 | 10 | 330 | 18 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 4.7 | 60 | 0 | 0 | 0 | 0 |  | 361 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 149 | 0 | 135 | 0 | 12 | 0 | 136 | 0 | 0 | 0 | 0 | 0 |  | 4338.1 | 1478 | 5816.1 | 3789 | 361 | 1277 | 83 | 149 | 73 | 0 | 78 | 6.1 | 0 | 91.95
10:00 | 35 | 0 | 0 | 0 | 300 | 104 | 82 | 371 | 0 | 0 | 20 | 400 | 0 | 0 | 0 | 0 | 0 | 110 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 0 | 30 | 0 | 0 | 42 | 30 | 0 | 120 | 0 | 233 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 0 | 80 | 0 | 250 | 200 | 194 | 0 | 80 | 40 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 25 | 15 | 84 | 112 | 0 | 22 | 1.7 | 60 | 50 | 11 | 50 | 163 | 221 | 66 | 5 | 45 | 85 | 0 | 24 | 10 | 340 | 17 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8.4 | 75 | 0 | 0 | 0 | 0 |  | 416 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 170 | 0 | 135 | 0 | 12 | 0 | 136 | 0 | 0 | 0 | 0 | 0 |  | 4391.1 | 1575 | 5966.1 | 3828 | 416 | 1309 | 98 | 149 | 72 | 0 | 84 | 10.1 | 0 | 91.94
11:00 | 35 | 0 | 0 | 0 | 270 | 104 | 80 | 348 | 0 | 0 | 20 | 400 | 0 | 0 | 0 | 0 | 16 | 110 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 0 | 30 | 0 | 0 | 41 | 30 | 0 | 120 | 0 | 234 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 18 | 2 | 0 | 80 | 0 | 250 | 200 | 197 | 0 | 100 | 40 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 8 | 25 | 15 | 82 | 114 | 0 | 22 | 1.1 | 60 | 50 | 11 | 50 | 130 | 224 | 62 | 5 | 45 | 96 | 0 | 24 | 10 | 300 | 17 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | 75 | 0 | 0 | 0 | 0 |  | 654 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 157 | 0 | 135 | 0 | 11 | 0 | 136 | 0 | 0 | 0 | 0 | 0 |  | 4322.1 | 1759 | 6081.1 | 3774 | 654 | 1232 | 98 | 149 | 71 | 0 | 82 | 21.1 | 0 | 91.94
12:00 | 35 | 0 | 0 | 0 | 270 | 107 | 78 | 351 | 0 | 0 | 20 | 400 | 0 | 0 | 0 | 0 | 114 | 110 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 23 | 0 | 29 | 0 | 0 | 42 | 30 | 0 | 120 | 0 | 234 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 80 | 0 | 250 | 200 | 197 | 0 | 100 | 40 | 5 | 5 | 0 | 5 | 0 | 0 | 16 | 8 | 25 | 15 | 90 | 131 | 0 | 22 | 1 | 60 | 55 | 11 | 50 | 130 | 221 | 61 | 5 | 45 | 105 | 0 | 24 | 10 | 320 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | 75 | 0 | 0 | 0 | 0 |  | 654 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 135 | 0 | 11 | 0 | 136 | 0 | 0 | 0 | 0 | 0 |  | 4497 | 1769 | 6266 | 3922 | 654 | 1259 | 98 | 150 | 72 | 0 | 90 | 21 | 0 | 91.94
13:00 | 35 | 0 | 0 | 0 | 270 | 107 | 78 | 363 | 0 | 0 | 20 | 450 | 0 | 0 | 0 | 0 | 116 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 32 | 0 | 29 | 0 | 0 | 43 | 30 | 0 | 120 | 0 | 233 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 80 | 0 | 250 | 88 | 187 | 0 | 100 | 40 | 5 | 5 | 0 | 5 | 6 | 0 | 19 | 8 | 25 | 15 | 90 | 131 | 0 | 22 | 0.5 | 60 | 72 | 11 | 50 | 163 | 223 | 67 | 5 | 46 | 86 | 0 | 24 | 10 | 320 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 9.9 | 75 | 0 | 0 | 0 | 0 |  | 654 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 165 | 0 | 190 | 0 | 11 | 0 | 194 | 0 | 0 | 17 | 0 | 0 |  | 4412.4 | 1930 | 6342.4 | 3906 | 654 | 1339 | 115 | 149 | 73 | 6 | 90 | 10.4 | 0 | 91.93
14:00 | 35 | 0 | 0 | 0 | 270 | 111 | 40 | 350 | 0 | 0 | 20 | 400 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 32 | 0 | 33 | 0 | 0 | 42 | 30 | 10 | 120 | 0 | 227 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 12 | 80 | 0 | 250 | 40 | 185 | 0 | 100 | 40 | 5 | 5 | 0 | 5 | 8 | 0 | 19 | 11 | 25 | 15 | 94 | 131 | 0 | 22 | 1.1 | 60 | 72 | 11 | 10 | 130 | 220 | 40 | 5 | 47 | 90 | 0 | 24 | 10 | 290 | 25 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 6.9 | 75 | 0 | 0 | 0 | 0 |  | 654 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 17 | 8 | 0 | 0 | 150 | 0 | 0 | 158 | 0 | 181 | 0 | 11 | 0 | 187 | 0 | 0 | 17 | 0 | 0 |  | 4239 | 1877 | 6116 | 3821 | 654 | 1161 | 148 | 150 | 72 | 8 | 94 | 8 | 0 | 91.93
15:00 | 35 | 0 | 0 | 0 | 270 | 52 | 40 | 345 | 0 | 0 | 20 | 370 | 0 | 0 | 0 | 0 | 115 | 110 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 0 | 0 | 0 | 0 | 42 | 30 | 20 | 120 | 0 | 226 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 12 | 80 | 0 | 250 | 0 | 192 | 0 | 100 | 40 | 5 | 5 | 0 | 5 | 0 | 0 | 19 | 11 | 25 | 15 | 94 | 132 | 0 | 22 | 0.7 | 60 | 72 | 11 | 10 | 130 | 220 | 40 | 5 | 10 | 91 | 0 | 24 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 4.2 | 75 | 0 | 0 | 0 | 0 |  | 661 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 156 | 0 | 179 | 0 | 11 | 0 | 154 | 0 | 0 | 3 | 0 | 0 |  | 4083.9 | 1846 | 5929.9 | 3772 | 661 | 1043 | 134 | 149 | 72 | 0 | 94 | 4.9 | 0 | 91.93
16:00 | 35 | 0 | 0 | 0 | 270 | 22 | 40 | 345 | 0 | 0 | 20 | 370 | 0 | 0 | 0 | 0 | 115 | 110 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 25 | 33 | 8 | 33 | 0 | 0 | 43 | 30 | 40 | 120 | 0 | 226 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 50 | 80 | 0 | 250 | 0 | 193 | 0 | 100 | 10 | 5 | 5 | 0 | 5 | 0 | 0 | 22 | 11 | 25 | 15 | 86 | 135 | 0 | 22 | 0.5 | 60 | 72 | 11 | 10 | 100 | 221 | 40 | 5 | 10 | 85 | 0 | 24 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 5.4 | 75 | 0 | 0 | 0 | 0 |  | 661 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 163 | 0 | 185 | 0 | 11 | 0 | 156 | 0 | 0 | 0 | 0 | 43 |  | 4037.9 | 1860 | 5897.9 | 3778 | 661 | 972 | 173 | 149 | 73 | 0 | 86 | 5.9 | 0 | 91.92
17:00 | 35 | 0 | 0 | 0 | 270 | 22 | 40 | 355 | 0 | 0 | 20 | 340 | 0 | 0 | 0 | 0 | 115 | 110 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 8 | 30 | 0 | 0 | 43 | 30 | 73 | 120 | 0 | 226 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 17 | 13 | 55 | 80 | 0 | 250 | 0 | 184 | 0 | 100 | 10 | 5 | 5 | 0 | 5 | 0 | 0 | 22 | 8 | 25 | 15 | 90 | 133 | 0 | 22 | 0.1 | 60 | 72 | 11 | 10 | 100 | 222 | 40 | 5 | 10 | 83 | 0 | 24 | 0 | 305 | 8 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1.4 | 75 | 0 | 0 | 0 | 0 |  | 661 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 170 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 185 | 0 | 177 | 0 | 11 | 0 | 161 | 0 | 0 | 0 | 0 | 0 |  | 4074.5 | 1836 | 5910.5 | 3844 | 661 | 956 | 130 | 149 | 73 | 6 | 90 | 1.5 | 0 | 91.92
18:00 | 35 | 0 | 0 | 0 | 270 | 51 | 40 | 370 | 0 | 0 | 20 | 340 | 0 | 0 | 0 | 0 | 115 | 110 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 0 | 0 | 25 | 33 | 8 | 30 | 8 | 0 | 44 | 30 | 100 | 120 | 0 | 227 | 0 | 0 | 0 | 0 | 40 | 2 | 3 | 7 | 13 | 3 | 17 | 21 | 80 | 80 | 0 | 250 | 0 | 202 | 0 | 100 | 10 | 5 | 5 | 0 | 5 | 8 | 0 | 22 | 8 | 25 | 15 | 106 | 158 | 0 | 22 | 0 | 60 | 72 | 11 | 10 | 100 | 224 | 40 | 5 | 10 | 98 | 0 | 24 | 0 | 305 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 |  | 801 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 177 | 13 | 0 | 0 | 20 | 70 | 0 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 173 | 0 | 190 | 0 | 11 | 0 | 164 | 0 | 0 | 17 | 0 | 0 |  | 4294 | 2130 | 6424 | 4046 | 801 | 995 | 220 | 149 | 74 | 33 | 106 | 0 | 0 | 91.92
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 0 | 350 | 111 | 60 | 375 | 0 | 0 | 20 | 450 | 0 | 0 | 0 | 14 | 115 | 110 | 93 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 50 | 18 | 0 | 0 | 25 | 33 | 11 | 30 | 40 | 40 | 44 | 30 | 100 | 120 | 19 | 227 | 0 | 0 | 0 | 0 | 40 | 17 | 34 | 10 | 12 | 25 | 19 | 25 | 100 | 120 | 0 | 250 | 0 | 187 | 0 | 95 | 40 | 5 | 5 | 0 | 85 | 8 | 0 | 22 | 11 | 25 | 15 | 114 | 158 | 18 | 22 | 0 | 60 | 74 | 31 | 39 | 163 | 225 | 65 | 85 | 48 | 104 | 0 | 24 | 0 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 |  | 859 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 6 | 40 | 40 | 173 | 20 | 0 | 0 | 0 | 70 | 26 | 0 | 26 | 40 | 0 | 0 | 43 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 18 | 192 | 0 | 192 | 0 | 74 | 0 | 194 | 0 | 0 | 105 | 0 | 0 |  | 5328 | 2667 | 7995 | 4485 | 859 | 1569 | 570 | 149 | 74 | 175 | 114 | 0 | 0 | 91.91
19:30 | 35 | 0 | 0 | 0 | 350 | 111 | 40 | 345 | 0 | 0 | 20 | 450 | 0 | 0 | 0 | 0 | 115 | 110 | 62 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 54 | 18 | 0 | 22 | 25 | 33 | 16 | 30 | 52 | 40 | 44 | 30 | 100 | 120 | 25 | 227 | 0 | 0 | 0 | 0 | 41 | 0 | 34 | 0 | 12 | 50 | 17 | 31 | 100 | 120 | 0 | 220 | 0 | 185 | 0 | 100 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 15 | 114 | 159 | 88 | 22 | 0 | 60 | 74 | 31 | 50 | 130 | 222 | 54 | 85 | 48 | 104 | 0 | 24 | 0 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 |  | 858 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 6 | 40 | 40 | 171 | 23 | 16 | 0 | 0 | 70 | 26 | 0 | 26 | 40 | 0 | 0 | 43 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 18 | 180 | 0 | 177 | 0 | 74 | 0 | 185 | 0 | 0 | 105 | 0 | 0 |  | 5309 | 2647 | 7956 | 4371 | 858 | 1531 | 709 | 149 | 74 | 150 | 114 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 0 | 350 | 111 | 40 | 345 | 0 | 0 | 20 | 450 | 0 | 0 | 0 | 0 | 115 | 115 | 60 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 54 | 0 | 0 | 22 | 25 | 33 | 0 | 30 | 25 | 40 | 44 | 30 | 100 | 100 | 25 | 227 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 0 | 0 | 50 | 17 | 33 | 100 | 100 | 0 | 220 | 0 | 181 | 0 | 95 | 40 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 15 | 106 | 164 | 80 | 22 | 0 | 60 | 75 | 31 | 50 | 130 | 220 | 59 | 85 | 48 | 104 | 0 | 24 | 0 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 |  | 858 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 6 | 40 | 40 | 164 | 22 | 16 | 0 | 0 | 70 | 0 | 0 | 25 | 40 | 0 | 0 | 43 | 0 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 19 | 180 | 0 | 177 | 0 | 74 | 0 | 184 | 0 | 0 | 105 | 0 | 0 |  | 5178 | 2611 | 7789 | 4310 | 858 | 1516 | 652 | 149 | 74 | 124 | 106 | 0 | 0 | 91.9
21:00 | 35 | 0 | 0 | 0 | 350 | 111 | 40 | 355 | 0 | 0 | 20 | 450 | 0 | 0 | 0 | 0 | 115 | 110 | 65 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 33 | 0 | 30 | 8 | 40 | 44 | 30 | 90 | 90 | 25 | 188 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 33 | 18 | 33 | 85 | 100 | 0 | 250 | 0 | 193 | 0 | 100 | 37 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 15 | 106 | 210 | 21 | 22 | 0 | 60 | 74 | 31 | 30 | 130 | 223 | 70 | 10 | 49 | 114 | 0 | 24 | 0 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 |  | 858 | 0 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 176 | 26 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 0 | 43 | 0 | 20 | 17 | 11 | 0 | 0 | 149 | 0 | 19 | 191 | 0 | 188 | 0 | 95 | 0 | 194 | 0 | 0 | 105 | 0 | 0 |  | 4985 | 2693 | 7678 | 4489 | 858 | 1461 | 522 | 149 | 74 | 19 | 106 | 0 | 0 | 91.9
22:00 | 35 | 0 | 0 | 0 | 350 | 111 | 40 | 353 | 0 | 0 | 20 | 400 | 0 | 0 | 0 | 0 | 115 | 110 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 33 | 25 | 30 | 8 | 40 | 44 | 30 | 90 | 0 | 25 | 152 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 25 | 19 | 30 | 80 | 80 | 0 | 260 | 0 | 184 | 0 | 80 | 20 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 15 | 104 | 158 | 21 | 22 | 0 | 60 | 74 | 31 | 30 | 130 | 222 | 38 | 10 | 49 | 83 | 0 | 24 | 0 | 280 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 |  | 860 | 0 | 442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 164 | 23 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 0 | 43 | 0 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 0 | 179 | 0 | 185 | 0 | 98 | 0 | 192 | 0 | 0 | 53 | 0 | 0 |  | 4594 | 2603 | 7197 | 4192 | 860 | 1389 | 429 | 149 | 74 | 0 | 104 | 0 | 0 | 91.9
23:00 | 35 | 0 | 0 | 0 | 350 | 111 | 40 | 349 | 0 | 0 | 20 | 370 | 0 | 0 | 0 | 0 | 115 | 110 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 25 | 30 | 0 | 40 | 40 | 30 | 100 | 0 | 25 | 153 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 24 | 18 | 22 | 80 | 80 | 0 | 200 | 0 | 185 | 0 | 80 | 20 | 5 | 5 | 0 | 85 | 0 | 0 | 22 | 11 | 25 | 15 | 94 | 168 | 7 | 22 | 0 | 58 | 74 | 31 | 30 | 130 | 220 | 66 | 10 | 49 | 85 | 0 | 23 | 0 | 275 | 26 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 |  | 712 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 22 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 184 | 0 | 180 | 0 | 97 | 0 | 186 | 0 | 0 | 0 | 0 | 0 |  | 4441 | 2217 | 6658 | 4086 | 712 | 1343 | 204 | 149 | 70 | 0 | 94 | 0 | 0 | 91.89
24:00 | 35 | 0 | 0 | 0 | 320 | 111 | 40 | 349 | 0 | 0 | 10 | 370 | 0 | 0 | 0 | 0 | 115 | 110 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 0 | 30 | 0 | 40 | 40 | 30 | 100 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 80 | 80 | 0 | 140 | 0 | 195 | 0 | 80 | 20 | 5 | 5 | 0 | 5 | 0 | 0 | 22 | 11 | 0 | 15 | 84 | 168 | 0 | 22 | 0 | 60 | 74 | 5 | 5 | 100 | 221 | 40 | 5 | 49 | 85 | 0 | 24 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 |  | 712 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 21 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 184 | 0 | 180 | 0 | 31 | 0 | 186 | 0 | 0 | 0 | 0 | 0 |  | 4007 | 2105 | 6112 | 3845 | 712 | 1129 | 123 | 149 | 70 | 0 | 84 | 0 | 0 | 91.89
KWH | 735000 | 0 | 0 | 0 | 6795727 | 1543090 | 1227744 | 8283130 | 0 | 0 | 408200 | 8755050 | 0 | 0 | 0 | 23823 | 1803619 | 2631510 | 669000 | 0 | 0 | 15120 | 0 | 0 | 64320 | 0 | 0 | 181080 | 35765 | 0 | 296928 | 500000 | 722880 | 107330 | 701000 | 108396 | 219338 | 1053295 | 728000 | 800000 | 2600000 | 136207 | 4966512 | 0 | 0 | 0 | 0 | 492480 | 33248 | 69858 | 13320 | 26880 | 166080 | 352320 | 439680 | 701906 | 1998790 | 0 | 5734700 | 2307000 | 4425000 | 0 | 1822330 | 601128 | 134880 | 120000 | 0 | 527657 | 20808 | 0 | 309348 | 149040 | 423100 | 363790 | 2007360 | 3206680 | 207360 | 361332 | 8000 | 1151000 | 1363310 | 422400 | 594000 | 3279444 | 4714000 | 1089120 | 362880 | 722520 | 2280160 | 0 | 462420 | 80640 | 7757250 | 274200 | 134832 | 0 | 0 | 0 | 0 | 223200 | 0 | 0 | 89805 | 1122240 | 0 | 0 | 0 | 0 |  | 13985455 | 0 | 7408800 | 0 | 0 | 0 | 0 | 0 | 12960 | 104064 | 158625 | 4111000 | 331100 | 49920 | 0 | 0 | 672000 | 43371 | 0 | 58004 | 194370 | 0 | 0 | 289920 | 0 | 407040 | 288756 | 151344 | 0 | 0 | 3672900 | 0 | 43000 | 4160609 | 0 | 4071055 | 0 | 651377 | 0 | 4066218 | 0 | 0 | 456960 | 0 | 70080 |  | 99259560 | 45458928 | 144718488 | 90644286 | 13985455 | 28107928 | 4036146 | 3672900 | 1781295 | 385313 | 2007360 | 97805 | 0
Fuel Cost | 632100 | 0 | 0 | 0 | 4349265.28 | 1249902.9 | 1154079.36 | 5052709.3 | 0 | 0 | 559234 | 5865883.5 | 0 | 0 | 0 | 145558.53 | 1172352.35 | 2526249.6 | 742590 | 0 | 0 | 99640.8 | 0 | 0 | 385276.8 | 0 | 0 | 1291100.4 | 223531.25 | 0 | 222696 | 375000 | 0 | 0 | 0 | 1025426.16 | 252238.7 | 0 | 0 | 880000 | 2860000 | 1289880.29 | 3277897.92 | 0 | 0 | 0 | 0 | 4328899.2 | 358080.96 | 679718.34 | 82450.8 | 173644.8 | 1086163.2 | 299472 | 0 | 638734.46 | 1818898.9 | 0 | 3555514 | 1591830 | 3097500 | 0 | 1749436.8 | 402755.76 | 115996.8 | 110400 | 0 | 501274.15 | 225558.72 | 0 | 238197.96 | 111780 | 325787 | 272842.5 | 13730342.4 | 2405010 | 1905638.4 | 278225.64 | 0 | 1197040 | 1417842.4 | 405504 | 534600 | 2557966.32 | 3299800 | 1241596.8 | 388281.6 | 794772 | 2599382.4 | 0 | 430050.6 | 74995.2 | 4964640 | 205650 | 102472.32 | 0 | 0 | 0 | 0 | 1595880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 71325820.5 | 0 | 4963896 | 0 | 0 | 0 | 0 | 0 | 145929.6 | 1225873.92 | 1249965 | 2836590 | 327789 | 369408 | 0 | 0 | 705600 | 496597.95 | 0 | 519715.84 | 1681300.5 | 0 | 0 | 2876006.4 | 0 | 447744 | 271430.64 | 114567.408 | 0 | 0 | 14177394 | 0 | 1151110 | 2829214.12 | 0 | 2849738.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97527239.57 | 110565691.378 | 208092930.948 | 64051708.118 | 71325820.5 | 20195310.07 | 19809770.53 | 14177394 | 0 | 4802585.33 | 13730342.4 | 0 | 0
Yesterday Day Peak | 35 | 0 | 0 | 0 | 270 | 107 | 78 | 351 | 0 | 0 | 20 | 400 | 0 | 0 | 0 | 0 | 114 | 110 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 23 | 0 | 29 | 0 | 0 | 42 | 30 | 0 | 120 | 0 | 234 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 0 | 80 | 0 | 250 | 200 | 197 | 0 | 100 | 40 | 5 | 5 | 0 | 5 | 0 | 0 | 16 | 8 | 25 | 15 | 90 | 131 | 0 | 22 | 1 | 60 | 55 | 11 | 50 | 130 | 221 | 61 | 5 | 45 | 105 | 0 | 24 | 10 | 320 | 23 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | 75 | 0 | 0 | 0 | 0 |  | 654 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 14 | 8 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 135 | 0 | 11 | 0 | 136 | 0 | 0 | 0 | 0 | 0 |  | 6266 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 0 | 350 | 111 | 60 | 375 | 0 | 0 | 20 | 450 | 0 | 0 | 0 | 14 | 115 | 110 | 93 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 50 | 18 | 0 | 0 | 25 | 33 | 11 | 30 | 40 | 40 | 44 | 30 | 100 | 120 | 19 | 227 | 0 | 0 | 0 | 0 | 40 | 17 | 34 | 10 | 12 | 25 | 19 | 25 | 100 | 120 | 0 | 250 | 0 | 187 | 0 | 95 | 40 | 5 | 5 | 0 | 85 | 8 | 0 | 22 | 11 | 25 | 15 | 114 | 158 | 18 | 22 | 0 | 60 | 74 | 31 | 39 | 163 | 225 | 65 | 85 | 48 | 104 | 0 | 24 | 0 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 |  | 859 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 6 | 40 | 40 | 173 | 20 | 0 | 0 | 0 | 70 | 26 | 0 | 26 | 40 | 0 | 0 | 43 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 18 | 192 | 0 | 192 | 0 | 74 | 0 | 194 | 0 | 0 | 105 | 0 | 0 |  | 7995 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 0 | 360 | 108 | 78 | 412 | 0 | 110 | 40 | 450 | 0 | 100 | 100 | 55 | 115 | 110 | 100 | 100 | 100 | 102 | 149 | 100 | 52 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 30 | 41 | 40 | 44 | 30 | 140 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 41 | 72 | 77 | 70 | 106 | 50 | 19 | 30 | 100 | 120 | 0 | 360 | 320 | 221 | 8 | 95 | 40 | 5 | 5 | 0 | 85 | 50 | 52 | 22 | 11 | 33 | 22 | 128 | 202 | 80 | 22 | 0 | 60 | 74 | 51 | 44 | 163 | 300 | 66 | 86 | 50 | 110 | 20 | 24 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 75 | 200 | 150 | 0 | 122 |  | 766 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 50 | 70 | 40 | 194 | 26 | 100 | 30 | 0 | 70 | 50 | 47 | 100 | 40 | 50 | 32 | 43 | 37 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 19 | 200 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 0 | 105 | 0
Forecast for Day | 35 | 0 | 0 | 0 | 360 | 108 | 60 | 412 | 0 | 110 | 40 | 450 | 0 | 100 | 100 | 55 | 115 | 110 | 100 | 100 | 100 | 102 | 149 | 100 | 52 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 16 | 30 | 41 | 40 | 44 | 30 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 106 | 50 | 19 | 15 | 100 | 100 | 0 | 360 | 320 | 221 | 0 | 95 | 40 | 5 | 5 | 0 | 5 | 0 | 52 | 22 | 11 | 33 | 22 | 107 | 202 | 80 | 22 | 2 | 60 | 74 | 51 | 44 | 163 | 300 | 66 | 85 | 50 | 110 | 20 | 24 | 10 | 341 | 25 | 11 | 100 | 200 | 200 | 50 | 100 | 50 | 149 | 20 | 75 | 200 | 150 | 0 | 122 |  | 618 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 194 | 26 | 100 | 0 | 0 | 70 | 0 | 0 | 100 | 40 | 50 | 32 | 43 | 0 | 22 | 14 | 11 | 0 | 0 | 149 |  | 0 | 200 | 0 | 175 | 0 | 95 | 100 | 190 | 0 | 0 | 105 | 0
Generation at 08:00(Today) | 35 | 0 | 0 | 0 | 280 | 13 | 20 | 340 | 0 | 0 | 10 | 330 | 0 | 0 | 0 | 0 | 115 | 110 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 16 | 30 | 0 | 40 | 41 | 30 | 100 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 18 | 14 | 80 | 80 | 0 | 300 | 0 | 162 | 0 | 50 | 5 | 5 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 15 | 68 | 148 | 0 | 0 | 1.1 | 35 | 74 | 5 | 5 | 100 | 220 | 53 | 5 | 5 | 85 | 0 | 7 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7.7 | 10 | 0 | 0 | 0 | 0 | 0 | 611 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 16 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 5 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 165 | 0 | 155 | 0 | 11 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 4402 | 5:00
| Highest Generation |  | 7995 | 19:00
| Day Peak Generation |  | 6266 | 12:00
| Evening Peak Generation |  | 7995 | 19:00
| HVDC Max Flow |  | 860 | 22:00
| HVDC EvPeak Flow |  | 859 | 19:00
| Load factor L.F |  | 75.42%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-03-01
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-02-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6266 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 4939 | MW
Evening Peak Generation : |  | 7995 | MW Hour : | 19:00 | Available Max Generation : |  | 12856 | MW
E.P. Demand (at gen end) : |  | 7995 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 8000 | MW
Maximum Generation : |  | 7995 | MW Hour : | 19:00 | Reserve(Generation end) |  | 4856 | MW
Total Gen. (MKWH) : |  | 144.7185 | System Load Factor : | 75.42% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -310 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-03-01
Actual : | 91.87 | Ft.(MSL) , | Rule curve : | 93 | Ft.( MSL )
Gas Consumed : | Total = | 1060.17 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 84247018.188
|  | Coal : | 14177394 | Oil : | 24612355.86 | Total : | 123036768.048
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2789.6916 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 940.2522 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 840.9385 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 759.3276 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 686.4863 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 553.949 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 320.5471 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 142.9129 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 427.1812 |  |  | 0 | 0%
Total | 0 |  | 7461.2863 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Khulna ST 110 MW
3) Ghorasal Unit-1,3,4
4) Bhagabari 100 MW
5) Sikalbaha 150MW Peaking
6) Haripur 360 MW
7) Siddhirganj Peaking 210 MW
8) Katpotti 51 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Amnura 132/33 kV T2 transformer was under shut down from 09:10 to 20:47 due to 33 kV loop changing.
b) Rangpur-Palashbari 132 kV Ckt-2 was under shut down from 10"40 to 18:35 for project work.
c) Siddhirganj 335 MW was synchronized at 10:13.
d) Siddhirganj GT-1 tripped at 12:15 due to Y-phase LA burst at Siddhirganj S/S end.
e) Jamalpur 132/33 kV T3 transformer was under shut down at 09:39 for C/M.
f) Bibiyana 400/230 kV ICT-2 transformer was under shut down from 09:16 to 17:50 for D/W.
g) Halishor 132/33 kV T1 & T3 transformers tripped at 12:40 from both end showing E/F and O/C relays and was |  |  |  | About 45 MW Power interruption occurred under Halishor S/S
switched on at 13:15. |  |  |  | area from 12:40 to 13:15.
h) Kabirpur 132/33 kV T1 & T2 transformers tripped at 14:05 due to CB pole of 33 kV Kabirpur feeder and was |  |  |  | About 40 MW Power interruption occurred under Kabirpur S/S
switched on at 14:39. |  |  |  | area from 14:05 to 14:39.
i) Tongi GT was synchronized at 18:28.
j) Shitalakhya 132/33 kV T1 transformer tripped at 16:55 showing buchholz relay and was switched on at 20:18.
k) Aminbazar-Hasnabad 230 kV Ckt-1 was switched on at 21:29.
l) Bibiyana 400 kV main bus-1 was switched on at 15:01.
l) Meghnaghat 230 kV CB-835(Mid CB) associated with Haripur-2 Dia, was switched on at 21:44.
m) Raozan unit-2 was shut down at 21:46.
n) Rangpur-Palashbari 132 kV Ckt-1 was shut down at 07:10(01/03/2019) for D/W.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-02-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 735000 | #1 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 6795727
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 60 | 1227744 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 111 | 1543090
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 20 | 408200 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 375 | 8283130 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 450 | 8755050
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Machine problem
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 14 | 23823 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 296928 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 110 | 2631510
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 93 | 669000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 115 | 1803619 | Machine problem
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 7 | 15120 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 0 | 0 | Machine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 50 | 181080
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 18 | 35765 | Low demand
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 7 | 64320
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 58 | 1222880 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 11 | 107330 | Engine problem
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 30 | 701000
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 40 | 108396 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 40 | 219338
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 0 | 0 | Reserve
| Dhaka area Total |  |  |  | 5798 | 1994 | 35828050
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 100 | 800000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 120 | 2600000 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 19 | 136207 | Low demand
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 89805
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 25 | 166080 | Low demand
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 74 | 1781295 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 227 | 4966512
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 40 | 492480 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 17 | 33248 | Low demand
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 34 | 69858 | Low demand
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 13320 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 75 | 1122240 | Engine problem
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 352320
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 439680
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 12 | 26880 | Low demand
| Chattogram area Total |  |  |  | 1681 | 797 | 13089925
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 701906 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 120 | 1998790
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 187 | 4425000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 250 | 5734700
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 2307000 | Under maint.
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 601128 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 134880 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 0 | 0 | Reserve
| Midland 150MW |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 527657
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 8 | 20808 | Low demand
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 1822330
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 0 | 0 | Reserve
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 309348
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 149040
** | Tripura |  | Imported power | 0 | 160 | 114 | 2007360
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 423100 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 363790 | Engine problem
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1082 | 21646837
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 158 | 3206680 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 361332
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 18 | 207360 | Low demand
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 8000
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 7 | 223200 | Low demand
| United Jamalpur PPL |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 205 | 4006572
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1151000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 74 | 1363310
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3279444
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 225 | 4714000 | FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 31 | 422400 | Engine problem
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 39 | 594000 | Engine problem
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 134832
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 65 | 1089120 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 85 | 362880
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 48 | 722520
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 104 | 2280160
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 24 | 462420
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 16 | 274200 | Engine problem
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 305 | 7757250 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 0 | 80640
| Sylhet Area Total |  |  |  | 1549 | 1250 | 24688176
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 859 | 13985455
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Reserve
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 6 | 12960 | Low demand
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Under maint.
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 40 | 104064 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 350 | 7408800 | Frequency Control.
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 158625
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 456960
| Khulna Area Total |  |  |  | 2209 | 1400 | 22126864
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 0 | 49920 | Reserve
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 20 | 331100 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 173 | 4111000
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 74 | 651377 | Low demand
| Barisal Area Total |  |  |  | 462 | 267 | 5143397
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 70 | 672000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 26 | 43371 | Low demand
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 194370 | Low demand
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 192 | 4160609 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 192 | 4071055 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 194 | 4066218 | FGMO
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 407040
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 17 | 288756
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 151344
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 289920 | Engine problem
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 26 | 58004 | Low demand
| Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
| Confidence CPBL-2 |  | IPP | 113 MW | 0 | 0 | 70080 | On test
| Rajshahi Area Total |  |  |  | 1825 | 833 | 14472767
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3672900
122 | Rangpur GT |  | PDB | 1*20 | 20 | 0 | 0 | Reserve
123 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 43000
| Rangpur Area Total |  |  |  | 484 | 167 | 3715900
| Total |  |  |  | 17536 | 7995 | 144718488
| Eastern Grid Total |  |  |  | 12556 | 5328 | 99259560
| Western Grid Total |  |  |  | 4980 | 2667 | 45458928
| National Grid Total |  |  |  | 17536 | 7995 | 144718488
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-02-28 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5003 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2437 | MW
i) Dhaka area |  |  | 2619 | MW | i) Khulna area |  |  | 926 | MW
ii) Chittagong area |  |  | 896 | MW | ii) Rajshahi area |  |  | 800 | MW
iii) Comilla area |  |  | 602 | MW | iii) Barisal area |  |  | 156 | MW
iv) Mymensingh area |  |  | 572 | MW | iv) Rangpur area |  |  | 555 | MW
v) Sylhet area |  |  | 314 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7440 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 80 | 1900 | Netrokona | 62 | 2000 | Central s/s | 66 | 1900
Munsiganj | 68 | 2100 | Jamalpur | 83 | 2000 | Noapara | 70 | 1930
Sonargaon | 50 | 1930 | Sherpur | 74 | 2200 | Jessore | 100 | 1900
Shyampur | 152 | 1200 | Srimongal | 22 | 1830 | Jhenida | 70 | 1900
Bhulta | 155 | 2100 | Shahjibazar | 77 | 1830 | Bottail | 80 | 1830
Madanganj | 41 | 2400 | Fenchuganj | 31 | 1900 | G.K Project | 32 | 1830
Shitalakhya | 79 | 1100 | Kulawara | 26 | 1830 | Faridpur | 111 | 1930
Rahim steel | 8 | 1000 | Sylhet | 91 | 1930 | Madaripur | 81 | 2000
Matuail | 74 | 1000 | Chatak | 20 | 1900 | Gopalganj | 59 | 1900
Ghorasal | 49 | 2100 | Sunamganj | 22 | 1900 | Bagerhat | 45 | 1900
Narsingdi | 88 | 2000 | Biani Bazar | 29 | 1830 | Mongla | 30 | 1600
Haripur (SBU) | 82 | 1300 | Comilla (S) | 116 | 1830 | Satkhira | 64 | 2000
Ullon | 47 | 2000 | Comilla(N) | 67 | 1930 | Gallamari | 39 | 1300
Hasnabad | 143 | 2000 | Chandpur | 56 | 2100 | Magura | 42 | 1830
Magbazar | 74 | 2100 | Feni | 87 | 2000 | Chuadanga | 55 | 1900
Maniknagar | 68 | 1800 | Chowmuhani | 120 | 2000 | Barisal | 82 | 2100
Bangabhaban | 12 | 1800 | Ashuganj | 20 | 2000 | Patuakhali | 56 | 2100
Narinda | 76 | 1900 | Daudkandi | 86 | 1930 | Bhandaria | 30 | 2200
Dhanmondi | 52 | 1800 | B.Baria | 76 | 2000 | Ishurdi | 37 | 1930
Lalbag | 57 | 1800 | Ramganj | 22 | 1900 | Ruppur Paromanobik | 1 | 100
Madartek | 31 | 1900 | Madunaghat | 44 | 900 | Natore | 72 | 1930
Mirpur | 58 | 1900 | Hathazari | 69 | 1830 | Bogra | 181 | 1900
Kalyanpur | 57 | 1830 | Khulshi | 169 | 1300 | Noagaon | 79 | 2000
Gulshan | 60 | 1830 | Halishahar | 96 | 1830 | Rajshahi | 104 | 1900
Uttara | 19 | 1900 | Baraulia | 151 | 900 | C.Nawabganj | 47 | 1900
Uttara(New) | 7 | 1900 | Sikalbaha | 28 | 1830 | Amnura | 25 | 1930
Kamrangirchar | 56 | 1900 | Dohazari | 64 | 1830 | Pabna | 74 | 1930
Savar | 99 | 1200 | Cox'sbazar | 74 | 2000 | Shahjadpur | 67 | 1930
Bhasantec | 86 | 1900 | Chandraghona | 20 | 1830 | Serajganj | 49 | 2000
Agargaon | 32 | 1830 | Kaptai | 3.5 | 1830 | Niyamatpur | 49 | 1930
Satmosjid | 58 | 1300 | A. Khaer Stl. | 0 | 0 | Joypurhat | 36 | 1930
Tongi | 95 | 1800 | Bakulia | 71 | 1830 | Mohastangor | 4 | 700
Kabirpur | 120 | 900 | Julda | 21 | 800 | Rangpur | 100 | 1830
Basundhara | 78 | 1400 | TK chemical | 3 | 1000 | Lalmonirhat | 70 | 2000
Manikganj | 60 | 2000 | Modern Steel | 14 | 200 | Saidpur | 93 | 1900
Joydevpur | 143 | 1930 | Shahmirpur | 20 | 1000 | Purbasadipur | 82 | 1930
New Tongi | 73 | 1000 | Khagrachhari | 14 | 1800 | Thakurgaon | 60 | 1900
Kodda | 183 | 1200 | Matarbari | 19 | 1930 | Palashbari | 69 | 1900
Dhamrai | 28 | 2000 | Baroiar Hat | 18 | 1830 | Barapukuria | 41 | 1830
Valuka | 48 | 1900 | Rangamati | 8 | 1800 | Panchagar | 35 | 1830
Tangail | 106 | 2100 | Abul Khair 230 | 122 | 500 | Joldhaka | 15 | 1900
Mymensing | 147 | 1900 | BSRM | 106 | 1100
Kishorganj | 72 | 1900 | Goalpara | 15 | 1900
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-02-28
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 410 | 4:00 | 398 | 16:00 | Kaliakoir | 399 | 4:00 | 387 | 12:00
Bheramara | 403 | 2:00 | 389 | 19:00 | Bhulta | 405 | 6:00 | 392 | 18:30
Ashuganj(N) | 407 | 4:00 | 396 | 13:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 238 | 1:00 | 235 | 12:00 | Hathazari | 220 | 6:00 | 214 | 11:00
Ishurdi | 238 | 3:00 | 230 | 18:30 | Megnaghat | 232 | 1:00 | 230 | 9:00
Ashuganj | 244 | 6:00 | 235 | 16:00 | Fenchuganj | 241 | 22:00 | 238 | 13:00
Serajganj | 230 | 1:00 | 224 | 18:30 | Siddhirganj | 234 | 3:00 | 227 | 13:00
Baghabari | 233 | 4:00 | 228 | 13:00 | Maniknagar | 232 | 2:00 | 225 | 15:00
Barapukuria | 237 | 4:00 | 226 | 18:30 | Old Airport | 237 | 4:00 | 228 | 12:00
Bogra | 231 | 4:00 | 219 | 18:30 | Barisal | 238 | 3:00 | 229 | 12:00
Khulna South | 240 | 4:00 | 223 | 18:30 | AKSML | 222 | 4:00 | 216 | 15:00
Rampura | 231 | 3:00 | 227 | 10:00 | BSRM | 226 | 4:00 | 219 | 13:00
Haripur | 231 | 3:00 | 226 | 12:00 | Bibiyana | 243 | 4:00 | 235 | 11:00
Hasnabad | 235 | 5:00 | 225 | 11:00 | Bhulta | 234 | 2:00 | 227 | 11:00
Aminbazar | 236 | 2:00 | 230 | 12:00 | Ashuganj (S) | 242 | 4:00 | 233 | 19:00
Tongi | 234 | 4:00 | 224 | 12:00 | Kaliakoir | 237 | 7:00 | 229 | 12:00
Comilla (N) | 240 | 4:00 | 235 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 500 | 133 | 1200 | Madanhat | 132 | 200 | 129 | 1100
Munsiganj | 137 | 500 | 132 | 1200 | Hathazari | 133 | 2000 | 128 | 1200
Megnaghat | 136 | 100 | 133 | 1000 | Khulshi | 130 | 2000 | 125 | 1000
Shyampur | 138 | 300 | 133 | 1100 | Halishahar | 133 | 1900 | 126 | 1100
Bhulta | 132 | 300 | 128 | 1300 | Baraulia | 131 | 2000 | 127 | 1000
Madanganj | 138 | 700 | 130 | 1100 | Sikalbaha | 131 | 1830 | 127 | 1100
Shitalakhya | 139 | 500 | 131 | 1200 | Dohazari | 130 | 1900 | 125 | 1000
Rahim steal | 137 | 300 | 133 | 1100 | Cox'sbazar | 126 | 900 | 120 | 300
Matuail | 136 | 200 | 131 | 1300 | Chandraghona | 132 | 400 | 128 | 1200
Ghorasal | 145 | 100 | 140 | 1200 | Kaptai | 132 | 100 | 130 | 800
Narsinghdi | 138 | 900 | 133 | 1800 | A. Khaer Stl. | 130 | 1830 | 126 | 1100
Haripur (SBU) | 137 | 200 | 132 | 1500 | Bakulia | 129 | 1930 | 124 | 1200
Ullon | 134 | 600 | 130 | 1600 | Julda | 131 | 1900 | 126 | 300
Hasnabad | 138 | 500 | 130 | 1200 | TK Chemical | 134 | 1900 | 128 | 800
Magbazar | 135 | 600 | 130 | 1200 | Modern Steel | 131 | 1900 | 125 | 1100
Maniknagar | 135 | 600 | 131 | 1200 | Shahmirpur | 131 | 2000 | 127 | 1000
Bangabhaban | 138 | 700 | 130 | 1200 | Khagrachhari | 131 | 500 | 127 | 1200
Narinda | 134 | 500 | 130 | 1800 | Matarbari | 127 | 1700 | 123 | 100
Dhanmondi | 134 | 600 | 130 | 1600 | Baroiar Hat | 132 | 100 | 130 | 1300
Lalbag | 138 | 700 | 130 | 1200 | Rangamati | 132 | 2000 | 128 | 1100
Madartek | 134 | 500 | 130 | 1800 | Goalpara | 138 | 2200 | 127 | 1100
Mirpur | 136 | 700 | 134 | 1200 | Central s/s | 137 | 2200 | 125 | 1200
Kalyanpur | 138 | 600 | 133 | 1200 | Noapara | 136 | 2200 | 121 | 1200
Gulshan | 134 | 700 | 129 | 1300 | Jessore | 135 | 2200 | 118 | 1200
Uttara | 138 | 300 | 130 | 1300 | Jhenida | 136 | 100 | 123 | 1900
Uttara New | 135 | 500 | 129 | 1200 | Bottail | 139 | 100 | 133 | 1830
Kamrangirchar | 138 | 600 | 130 | 1200 | G.K.Project | 142 | 300 | 139 | 1200
Savar | 134 | 600 | 129 | 1200 | Faridpur | 140 | 500 | 128 | 2100
Bhasantec | 140 | 500 | 135 | 1200 | Madaripur | 142 | 400 | 128 | 2100
Agargaon | 141 | 400 | 132 | 1830 | Gopalganj | 142 | 600 | 123 | 2100
Satmosjid | 141 | 400 | 132 | 1800 | Bagerhat | 136 | 2200 | 125 | 1200
Tongi | 140 | 400 | 133 | 1200 | Mongla | 134 | 2100 | 124 | 900
Kabirpur | 136 | 300 | 131 | 1830 | Satkhira | 136 | 500 | 123 | 1200
Basundhara | 131 | 500 | 125 | 1800 | Gallamari | 139 | 2200 | 125 | 1200
Manikganj | 140 | 100 | 134 | 1830 | Magura | 134 | 200 | 117 | 1200
Joydevpur | 143 | 700 | 135 | 1300 | Chuadanga | 136 | 200 | 119 | 1900
New Tongi | 140 | 700 | 131 | 1800 | Barisal | 137 | 200 | 130 | 1200
Kodda | 142 | 300 | 132 | 1600 | Patuakhali | 140 | 300 | 130 | 1830
Dhamrai | 137 | 400 | 130 | 1830 | Bhandaria | 138 | 600 | 127 | 1200
Valuka | 130 | 100 | 121 | 1800 | Ishurdi | 141 | 100 | 136 | 1830
Tangail | 138 | 300 | 130 | 1800 | Ruppur Paromanobik | 143 | 300 | 136 | 2000
Mymensing | 136 | 500 | 127 | 1830 | Natore | 139 | 500 | 133 | 1200
Kishorganj | 138 | 400 | 129 | 1830 | Bogra | 140 | 400 | 132 | 2000
Netrokona | 136 | 600 | 127 | 1830 | Noagaon | 136 | 300 | 130 | 1830
Jamalpur | 132 | 100 | 122 | 1800 | Rajshahi | 136 | 600 | 130 | 1100
Sherpur | 132 | 600 | 119 | 1800 | C.Nawabganj | 131 | 100 | 126 | 800
Srimongal | 142 | 700 | 138 | 1000 | Amnura | 132 | 100 | 128 | 1200
Shahjibazar | 140 | 900 | 137 | 1600 | Pabna | 137 | 300 | 130 | 900
Fenchuganj | 139 | 2200 | 136 | 1000 | Shahjadpur | 145 | 300 | 140 | 700
Khulawara | 138 | 400 | 135 | 1500 | Serajganj | 140 | 300 | 134 | 1200
Sylhet | 137 | 700 | 134 | 1830 | Niyamatpur | 137 | 500 | 128 | 1830
Chatak | 137 | 200 | 135 | 1800 | Joypurhat | 139 | 200 | 130 | 1830
Sunamganj | 137 | 500 | 133 | 1830 | Mohastangor | 139 | 300 | 131 | 1830
Biani Bazar | 137 | 100 | 134 | 1800 | Rangpur | 136 | 400 | 125 | 1100
Comilla(s) | 130 | 700 | 125 | 1400 | Lalmonirhat | 133 | 400 | 117 | 1830
Comilla(n) | 140 | 1700 | 137 | 1000 | Saidpur | 132 | 300 | 123 | 1800
Chandpur | 137 | 700 | 136 | 1500 | Purbasadipur | 135 | 500 | 123 | 1830
Feni | 135 | 700 | 130 | 2100 | Thakurgaon | 130 | 300 | 112 | 1830
Chowmuhani | 134 | 700 | 126 | 2100 | Palashbari | 137 | 500 | 126 | 1900
Ashuganj | 142 | 300 | 138 | 1830 | Barapukuria | 137 | 400 | 126 | 1830
Daudkandi | 138 | 700 | 133 | 2100 | Panchagar | 127 | 400 | 109 | 1830
B.Baria | 140 | 600 | 135 | 1800 | Joldhaka | 131 | 100 | 121 | 1100

## L-Curve
Date | 2019-02-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 300 | 4007 | 2105 | 6112 |  |  |  | QF-LDC-12
0:30 | 215 | 3722.5 | 1805 | 5527.5 | Date: | 2019-02-28
1:00 | 130 | 3438 | 1505 | 4943
1:30 | 130 | 3411.5 | 1470 | 4881.5
2:00 | 130 | 3385 | 1435 | 4820
2:30 | 90 | 3225.5 | 1456.5 | 4682 | [5 empty] | Gen. at Eve. Peak | 7995 | 7995 MW (19:00 )
3:00 | 50 | 3066 | 1478 | 4544 | [6 empty] | 19:00
3:30 | 40 | 3050 | 1455 | 4505 | [5 empty] | Gen. at Day Peak | 6266 | 6266 MW (12:00 )
4:00 | 30 | 3034 | 1432 | 4466 | [6 empty] | 12:00
4:30 | 25 | 3027 | 1407 | 4434 | [5 empty] | Highest Generation | 7995
5:00 | 20 | 3020 | 1382 | 4402 | [6 empty] | 19:00
5:30 | 20 | 3061 | 1357 | 4418
6:00 | 20 | 3102 | 1332 | 4434
6:30 | 75 | 3271.35 | 1347.5 | 4618.85
7:00 | 130 | 3440.7 | 1363 | 4803.7
7:30 | 220 | 3677.1 | 1375.5 | 5052.6
8:00 | 310 | 3913.5 | 1388 | 5301.5
8:30 | 255 | 4125.8 | 1433 | 5558.8
9:00 | 200 | 4338.1 | 1478 | 5816.1
9:30 | 150 | 4364.6 | 1526.5 | 5891.1
10:00 | 100 | 4391.1 | 1575 | 5966.1
10:30 | 122 | 4356.6 | 1667 | 6023.6
11:00 | 144 | 4322.1 | 1759 | 6081.1
11:30 | 82 | 4409.55 | 1764 | 6173.55
12:00 | 20 | 4497 | 1769 | 6266
12:30 | 67 | 4454.7 | 1849.5 | 6304.2
13:00 | 114 | 4412.4 | 1930 | 6342.4
13:30 | 132 | 4325.7 | 1903.5 | 6229.2
14:00 | 150 | 4239 | 1877 | 6116
14:30 | 175 | 4161.45 | 1861.5 | 6022.95
15:00 | 200 | 4083.9 | 1846 | 5929.9
15:30 | 250 | 4060.9 | 1853 | 5913.9
16:00 | 300 | 4037.9 | 1860 | 5897.9
16:30 | 250 | 4056.2 | 1848 | 5904.2
17:00 | 200 | 4074.5 | 1836 | 5910.5
17:30 | 270 | 4184.25 | 1983 | 6167.25
18:00 | 340 | 4294 | 2130 | 6424
18:30 | 200 | 4811 | 2398.5 | 7209.5
19:00 | 60 | 5328 | 2667 | 7995
19:30 | 40 | 5309 | 2647 | 7956
20:00 | 40 | 5178 | 2611 | 7789 |  |  |  | Executive Engineer
20:30 | 135 | 5081.5 | 2652 | 7733.5 |  |  |  | Network Operation Division
21:00 | 230 | 4985 | 2693 | 7678
21:30 | 275 | 4789.5 | 2648 | 7437.5
22:00 | 320 | 4594 | 2603 | 7197 |  |  |  |  | Page 6 of 7
22:30 | 290 | 4517.5 | 2410 | 6927.5
23:00 | 260 | 4441 | 2217 | 6658
23:30 | 280 | 4224 | 2161 | 6385
24:00 | 300 | 4007 | 2105 | 6112
7995 MW (19:00 )
6266 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-02-28 |  | Energy | 144718488
[10 empty] | 2019-02-28 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3845 | 712 | 1129 | 123 | 149 | 70 | 0 | 0 | 84
0:30 | 3678 | 537 | 949.5 | 65 | 149 | 71 | 0 | 0 | 78 | Date: | 2019-02-28
1:00 | 3511 | 362 | 770 | 7 | 149 | 72 | 0 | 0 | 72
1:30 | 3444.5 | 361.5 | 777 | 7 | 149 | 72.5 | 0 | 0 | 70 | [7 empty] | Total Energy | 144.7185 | Total Energy Gen 144.718 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 144.718 MKWHr
2:00 | 3378 | 361 | 784 | 7 | 149 | 73 | 0 | 0 | 68 | [7 empty] | Energy not Served | 0
2:30 | 3265.5 | 361 | 762 | 7 | 149 | 73.5 | 0 | 0 | 64 | [7 empty] | Energy Requirement | 144.7185
3:00 | 3153 | 361 | 740 | 7 | 149 | 74 | 0 | 0 | 60
3:30 | 3105.5 | 361 | 749 | 7 | 149 | 74.5 | 0 | 0 | 59 | [6 empty] | Shortage
4:00 | 3058 | 361 | 758 | 7 | 149 | 75 | 0 | 0 | 58
4:30 | 3034.5 | 361 | 749.5 | 7 | 149 | 75 | 0 | 0 | 58
5:00 | 3011 | 361 | 741 | 7 | 149 | 75 | 0 | 0 | 58
5:30 | 3010 | 361 | 755.5 | 7 | 149 | 74.5 | 0 | 0 | 61
6:00 | 3009 | 361 | 770 | 7 | 149 | 74 | 0 | 0 | 64
6:30 | 3077.5 | 361 | 884.5 | 7 | 149 | 74 | 0 | 0 | 65 |  |  |  |  | Coal
7:00 | 3146 | 361 | 999 | 7 | 149 | 74 | 0 | 0 | 66
7:30 | 3292.5 | 361 | 1086 | 17 | 149 | 73.5 | 0 | 0 | 68 |  |  |  | Oil |  |  |  | ,
8:00 | 3439 | 361 | 1173 | 27 | 149 | 73 | 0 | 0 | 70
8:30 | 3614 | 361 | 1225 | 55 | 149 | 73 | 0 | 0 | 74
9:00 | 3789 | 361 | 1277 | 83 | 149 | 73 | 0 | 0 | 78
9:30 | 3808.5 | 388.5 | 1293 | 90.5 | 149 | 72.5 | 0 | 0 | 81
10:00 | 3828 | 416 | 1309 | 98 | 149 | 72 | 0 | 0 | 84
10:30 | 3801 | 535 | 1270.5 | 98 | 149 | 71.5 | 0 | 0 | 83
11:00 | 3774 | 654 | 1232 | 98 | 149 | 71 | 0 | 0 | 82
11:30 | 3848 | 654 | 1245.5 | 98 | 149.5 | 71.5 | 0 | 0 | 86
12:00 | 3922 | 654 | 1259 | 98 | 150 | 72 | 0 | 0 | 90
12:30 | 3914 | 654 | 1299 | 106.5 | 149.5 | 72.5 | 3 | 0 | 90
13:00 | 3906 | 654 | 1339 | 115 | 149 | 73 | 6 | 0 | 90
13:30 | 3906 | 654 | 1339 | 115 | 149 | 73 | 6 | 0 | 90
14:00 | 3906 | 654 | 1339 | 115 | 149 | 73 | 6 | 0 | 90
14:30 | 3839 | 657.5 | 1191 | 124.5 | 149 | 72.5 | 3 | 0 | 92
15:00 | 3772 | 661 | 1043 | 134 | 149 | 72 | 0 | 0 | 94
15:30 | 3775 | 661 | 1007.5 | 153.5 | 149 | 72.5 | 0 | 0 | 90
16:00 | 3778 | 661 | 972 | 173 | 149 | 73 | 0 | 0 | 86
16:30 | 3811 | 661 | 964 | 151.5 | 149 | 73 | 3 | 0 | 88
17:00 | 3844 | 661 | 956 | 130 | 149 | 73 | 6 | 0 | 90
17:30 | 3945 | 731 | 975.5 | 175 | 149 | 73.5 | 19.5 | 0 | 98
18:00 | 4046 | 801 | 995 | 220 | 149 | 74 | 33 | 0 | 106
18:30 | 4265.5 | 830 | 1282 | 395 | 149 | 74 | 104 | 0 | 110
19:00 | 4485 | 859 | 1569 | 570 | 149 | 74 | 175 | 0 | 114
19:30 | 4371 | 858 | 1531 | 709 | 149 | 74 | 150 | 0 | 114
20:00 | 4310 | 858 | 1516 | 652 | 149 | 74 | 124 | 0 | 106
20:30 | 4399.5 | 858 | 1488.5 | 587 | 149 | 74 | 71.5 | 0 | 106
21:00 | 4489 | 858 | 1461 | 522 | 149 | 74 | 19 | 0 | 106
21:30 | 4340.5 | 859 | 1425 | 475.5 | 149 | 74 | 9.5 | 0 | 105
22:00 | 4192 | 860 | 1389 | 429 | 149 | 74 | 0 | 0 | 104
22:30 | 4139 | 786 | 1366 | 316.5 | 149 | 72 | 0 | 0 | 99
23:00 | 4086 | 712 | 1343 | 204 | 149 | 70 | 0 | 0 | 94
23:30 | 3965.5 | 712 | 1236 | 163.5 | 149 | 70 | 0 | 0 | 89 | Max Temp. in Dhaka |  | 24.6° C
24:00 | 3845 | 712 | 1129 | 123 | 149 | 70 | 0 | 0 | 84
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 144.718 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 144.718 MKWHr
Note on W13: Author:

## Generation
2019-02-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 42 | 43 | 44 | 45 | 45 | 44 | 44 | 43 | 43 | 42 | 41 | 42 | 43 | 42 | 42 | 43 | 43 | 44 |  | 44 | 44 | 44 | 44 | 44 | 40 | 40 | 1053295
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 728000
3 | Chattogram ST-1 (Raozan) | [12 empty] | 0 | 10 | 20 | 40 | 73 | 100 |  | 100 | 100 | 100 | 90 | 90 | 100 | 100 | 800000
4 | Chittgong ST-2 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 100 | 90 | 0 | 0 |  | 2600000
5 | Raozan 25 MW (RPCL) | [17 empty] | 0 |  | 19 | 25 | 25 | 25 | 25 | 25 | 0 | 136207
| Teknaf Solartech 20MW | [5 empty] | 0 | 1.7 | 9.3 | 4.7 | 8.4 | 20 | 20 | 9.9 | 6.9 | 4.2 | 5.4 | 1.4 | 0 | [8 empty] | 89805
6 | Sikalbaha 225MW (Gas) | 228 | 228 | 227 | 169 | 162 | 164 | 181 | 234 | 236 | 233 | 234 | 234 | 233 | 227 | 226 | 226 | 226 | 227 |  | 227 | 227 | 227 | 188 | 152 | 153 | 153 | 4966512
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [17 empty] | 3 |  | 34 | 34 | 34 | 0 | 0 |  |  | 69858
12 | Hathazari peaking | [17 empty] | 2 |  | 17 | 0 | 0 |  |  |  |  | 33248
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [12 empty] | 6 | 8 | 0 |  |  | 8 |  | 8 | 0 | 0 |  |  |  |  | 20808
15 | Siddhirgonj ST 210MW | 110 | 110 | 115 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 115 | 110 | 110 | 110 | 110 | 2631510
16 | Siddhirgonj GT Unit-1& 2 | [9 empty] | 34 | 37 | 37 | 0 | 0 | 37 | 37 | 37 | 37 |  | 93 | 62 | 60 | 65 | 60 | 39 | 39 | 669000
17 | Siddhirganj CCPP-335 MW | 115 | 115 | 0 | [7 empty] | 16 | 114 | 116 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1803619
18 | Summit Gazipur -2
19 | Ashuganj 195MW Modular
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 735000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 240 | 240 | 240 | 240 | 249 | 249 | 250 | 300 | 300 | 300 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 350 | 350 | 350 | 350 | 350 | 350 | 320 | 6795727
26
28 | Ashuganj ST: Unit- 3 | [13 empty] | 12 | 12 | 50 | 55 | 80 |  | 100 | 100 | 100 | 85 | 80 | 80 | 80 | 701906
29 | Ashuganj ST: Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 120 | 120 | 100 | 100 | 80 | 80 | 80 | 1998790
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 10 | 10 | 10 |  | 40 | 40 | 40 | 37 | 20 | 20 | 20 | 601128
33 | Ashuganj CCPP 225 MW | 159 | 158 | 173 | 168 | 167 | 180 | 159 | 159 | 174 | 194 | 197 | 197 | 187 | 185 | 192 | 193 | 184 | 202 |  | 187 | 185 | 181 | 193 | 184 | 185 | 195 | 4425000
34 | Ashuganj CCPP(South) | 150 | 150 | 150 | 150 | 150 | 172 | 172 | 176 | 200 | 200 | 200 | 200 | 88 | 40 | 0 | 0 | [10 empty] | 2307000
| Ashuganj CCPP(North) | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 220 | 220 | 250 | 260 | 200 | 140 | 5734700
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 134880
36 | Chandpur CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 95 | 100 | 95 | 100 | 80 | 80 | 80 | 1822330
37 | Tongi GT | [19 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 219338
38 | Haripur GT: Unit-1, 2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 10 | 408200
39 | Haripur 412 MW CCPP | 270 | 270 | 280 | 315 | 270 | 270 | 347 | 360 | 385 | 371 | 348 | 351 | 363 | 350 | 345 | 345 | 355 | 370 |  | 375 | 345 | 345 | 355 | 353 | 349 | 349 | 8283130
40 | Meghnaghat CCPP 450MW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 380 | 400 | 400 | 400 | 450 | 400 | 370 | 370 | 340 | 340 |  | 450 | 450 | 450 | 450 | 400 | 370 | 370 | 8755050
41 | Haripur Power CCPP 360MW
42 | Mymensingh RPCL 210MW | 162 | 162 | 108 | 109 | 110 | 110 | 108 | 110 | 108 | 112 | 114 | 131 | 131 | 131 | 132 | 135 | 133 | 158 |  | 158 | 159 | 164 | 210 | 158 | 168 | 168 | 3206680
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 60 | 40 | 40 | 20 | 20 | 20 | 20 | 20 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 1151000
45 | Fenchugonj CCPP-2 | 52 | 40 | 40 | 30 | 30 | 30 | 30 | 30 | 60 | 50 | 50 | 55 | 72 | 72 | 72 | 72 | 72 | 72 |  | 74 | 74 | 75 | 74 | 74 | 74 | 74 | 1363310
46 | Shajibazar 330 MW | 220 | 221 | 169 | 174 | 174 | 169 | 172 | 171 | 221 | 221 | 224 | 221 | 223 | 220 | 220 | 221 | 222 | 224 |  | 225 | 222 | 220 | 223 | 222 | 220 | 221 | 4714000
47 | Shahjibazar GT: Unit- 8, 9 | 57 | 41 | 5 | 5 | 5 | 5 | 20 | 57 | 69 | 66 | 62 | 61 | 67 | 40 | 40 | 40 | 40 | 40 |  | 65 | 54 | 59 | 70 | 38 | 66 | 40 | 1089120
48 | Shahjibazar 86MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 85 | 85 | 85 | 10 | 10 | 10 | 5 | 362880
49 | Shahjibazar (EPL) 50MW | 5 | 5 | 5 | 5 | 5 | 5 | 45 | 45 | 45 | 45 | 45 | 45 | 46 | 47 | 10 | 10 | 10 | 10 |  | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 722520
50 | Sylhet GT 150 MW | 84 | 84 | 85 | 84 | 85 | 89 | 89 | 112 | 97 | 85 | 96 | 105 | 86 | 90 | 91 | 85 | 83 | 98 |  | 104 | 104 | 104 | 114 | 83 | 85 | 85 | 2280160
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 6 | 6 | 6 | 6 | 6 | 6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 23 | 24 | 462420
53 | Sylhet (Desh) 10MW | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | [9 empty] | 80640
54 | Hobiganj 11MW | [6 empty] | 0 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 0 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 134832
55 | Fenchugonj (Barakatullah) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 43 | 45 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 31 | 31 | 31 | 31 | 31 | 31 | 5 | 422400
56 | Shahjahanulla 25 MW | [7 empty] | 17 | 18 | 17 | 17 | 23 | 24 | 25 | 24 | 0 | 8 | 0 |  | 16 | 16 | 16 | 16 | 25 | 26 | 0 | 274200
57 | Summit Bibiana- 2 | 285 | 300 | 255 | 275 | 270 | 300 | 285 | 320 | 330 | 340 | 300 | 320 | 320 | 290 | 300 | 300 | 305 | 305 |  | 305 | 300 | 285 | 300 | 280 | 275 | 295 | 7757250
58 | Southern 55MW
59 | Sikalbaha (Energis) | [7 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 41 | 41 | 40 | 40 | 40 |  | 40 | 41 | 45 | 50 | 41 | 41 | 41 | 492480
60 | Barabkunda (Regent) | 17 | 0 |  |  | 0 | 11 | 17 | 18 | 19 | 19 | 18 | 19 | 19 | 19 | 17 | 17 | 17 | 17 |  | 19 | 17 | 17 | 18 | 19 | 18 | 18 | 352320
61 | Narshingdi (Doreen) | [7 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 14 | 22 | 0 |  | 0 | 22 | 22 | 22 | 22 | 22 | 0 | 296928
62 | Tangail (Doreen) 22MW | [7 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 361332
63 | Tripura | 72 | 68 | 60 | 58 | 58 | 64 | 66 | 70 | 78 | 84 | 82 | 90 | 90 | 94 | 94 | 86 | 90 | 106 |  | 114 | 114 | 106 | 106 | 104 | 94 | 84 | 2007360
64 | Malancha, Ctg. EPZ (United) | 10 | 10 | 10 | 10 | 10 | 10 | 35 | 15 | 2 | 4 | 2 | 3 | 0 | 8 | 5 | 5 | 13 | 21 |  | 25 | 31 | 33 | 33 | 30 | 22 | 21 | 439680
65 | Feni (Doreen) 22MW | [6 empty] | 11 | 22 | 22 | 0 | 0 | 16 | 19 | 19 | 19 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 309348
66 | Feni, Mohipal (Doreen) | [7 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 149040
67 | Jangalia (Summit) 33MW | [6 empty] | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 423100
68 | Summit Cumilla 25MW | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 10 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 363790
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 500000
70 | Summit Madhabdi | 33 | 33 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 23 | 32 | 32 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 722880
71 | Summit Maona | [15 empty] | 8 | 8 | 8 |  | 11 | 16 | 0 | 0 | 25 | 25 | 0 | 107330
72 | Summit Rupganj | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 33 | 0 | 33 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 701000
73 | Ghorashal (Regent) | [5 empty] | 0 | 65 | 104 | 104 | 104 | 104 | 107 | 107 | 111 | 52 | 22 | 22 | 51 |  | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 1543090
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [17 empty] | 8 |  | 40 | 52 | 25 | 8 | 8 | 0 | 0 | 108396
79 | Kodda 149MW
80 | Jamalpur 95MW | [17 empty] | 0 |  | 18 | 88 | 80 | 21 | 21 | 7 | 0 | 207360
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 85 | 85 | 85 | 85 | 85 | 85 | 5 | 527657
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL)
88 | Ghorashal 78MW (MAX) | [6 empty] | 0 | 81 | 81 | 82 | 80 | 78 | 78 | 40 | 40 | 40 | 40 | 40 |  | 60 | 40 | 40 | 40 | 40 | 40 | 40 | 1227744
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | [17 empty] | 7 |  | 10 | 0 | 0 |  |  |  |  | 13320
92 | Fenchuganj (EPL) 44MW | 5 | 5 | 5 | 5 | 5 | 5 | 32 | 50 | 48 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 |  | 39 | 50 | 50 | 30 | 30 | 30 | 5 | 594000
93 | Ashuganj (Midland) 51MW
94 | Gagnagar (Orion) | [16 empty] | 0 | 0 |  | 7 | 0 | 0 |  |  |  |  | 15120
95 | Patenga 50MW | [16 empty] | 0 | 3 |  | 25 | 50 | 50 | 33 | 25 | 24 | 0 | 166080
96 | Chattogram ECPV 108 MW | [16 empty] | 0 | 13 |  | 12 | 12 | 0 | 0 |  |  |  | 26880
97 | Katpotti 51 MW
98 | Bosila 108MW | [19 empty] | 7 | 43 | 47 | 24 | 0 | 0 |  | 64320
99 | Madanganj-55 MW | [17 empty] | 0 |  | 14 | 0 | 0 |  |  |  |  | 23823
100 | Northern 55 MW | [17 empty] | 5 |  | 18 | 18 | 0 | 0 |  |  |  | 35765
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 163 | 130 | 130 | 163 | 130 | 130 | 100 | 100 | 100 |  | 163 | 130 | 130 | 130 | 130 | 130 | 100 | 3279444
102 | Sarishabari (Solar) | [7 empty] | 0.2 | 1.4 | 1.7 | 1.1 | 1 | 0.5 | 1.1 | 0.7 | 0.5 | 0.1 | 0 |  | 0 | 0 | 0 |  |  |  |  | 8000
103 | Banco Energy 54MW | [17 empty] | 17 |  | 50 | 54 | 54 | 35 | 35 | 0 | 0 | 181080
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 223200
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW
115 | Juldah 100 MW Unit-3 | [7 empty] | 10 | 60 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1122240
116 | Chandpur Desh 200MW
117 | Midland 150MW
118 | Bibiyana-3 285MW
United Jamalpur PPL
120 | Eastern Zone Total | 3438 | 3385 | 3066 | 3034 | 3020 | 3102 | 3440.7 | 3913.5 | 4338.1 | 4391.1 | 4322.1 | 4497 | 4412.4 | 4239 | 4083.9 | 4037.9 | 4074.5 | 4294 |  | 5328 | 5309 | 5178 | 4985 | 4594 | 4441 | 4007 | 99259560
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [19 empty] | 6 | 6 | 6 | 0 |  |  |  | 12960
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [12 empty] | 17 | 17 | 3 | 0 |  | 17 |  | 105 | 105 | 105 | 105 | 53 | 0 |  | 456960
130
131
132
133
| Summit Barisal 110 MW | [20 empty] | 16 | 16 | 16 | 16 | 0 |  | 49920
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 12 | 12 | 12 | 12 | 0 | 0 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 74 | 74 | 74 | 95 | 98 | 97 | 31 | 651377
| Bhola CCPP 194MW | 175 | 168 | 150 | 152 | 151 | 152 | 152 | 152 | 173 | 177 | 176 | 177 | 165 | 164 | 177 | 177 | 170 | 177 |  | 173 | 171 | 164 | 176 | 164 | 166 | 177 | 4111000
140 | Bhola (Venture) 33MW | 14 | 13 | 14 | 12 | 12 | 11 | 12 | 11 | 11 | 9 | 9 | 14 | 13 | 10 | 11 | 11 | 11 | 13 |  | 20 | 23 | 22 | 26 | 23 | 22 | 21 | 331100
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [17 empty] | 8 |  | 40 | 40 | 40 | 40 | 40 | 0 |  | 158625
143 | Gopalganj Peaking | [16 empty] | 6 | 20 |  | 40 | 40 | 40 | 0 |  |  |  | 104064
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 362 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 361 | 416 | 654 | 654 | 654 | 654 | 661 | 661 | 661 | 801 |  | 859 | 858 | 858 | 858 | 860 | 712 | 712 | 13985455
147 | Bheramara 360 MW | 230 | 230 | 290 | 330 | 300 | 250 | 250 | 250 | 300 | 320 | 280 | 280 | 320 | 290 | 290 | 250 | 250 | 250 |  | 350 | 350 | 350 | 435 | 442 | 380 | 350 | 7408800
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 149 | 150 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3672900
153 | Baghabari GT 71MW | 70 | 70 | 70 | 0 | [13 empty] | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 672000
156 | Baghabari GT 100MW | [17 empty] | 20 |  | 0
| Baghabari Peaking 50MW | [19 empty] | 26 | 26 | 0 | 0 |  |  |  | 43371
157 | Sirajgonj Unit-1 225MW (Gas) | 187 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 149 | 170 | 157 | 160 | 165 | 158 | 156 | 163 | 185 | 173 |  | 192 | 180 | 180 | 191 | 179 | 184 | 184 | 4160609
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 190 | 181 | 179 | 185 | 177 | 190 |  | 192 | 177 | 177 | 188 | 185 | 180 | 180 | 4071055
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 158 | 154 | 159 | 143 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 194 | 187 | 154 | 156 | 161 | 164 |  | 194 | 185 | 184 | 194 | 192 | 186 | 186 | 4066218
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 5 | 5 | 5 | 5 | 5 | 5 | 18 | 22 | 22 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 20 | 22 | 21 | 21 | 407040
163 | Bogra (EPL) | 3 | 3 | 3 | 3 | 3 | 3 | 8 | 14 | 14 | 14 | 14 | 14 | 14 | 17 | 17 | 16 | 17 | 17 |  | 17 | 17 | 16 | 17 | 16 | 17 | 16 | 288756
164 | Ullapara (Summit) | 5 | 5 | 0 |  |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 151344
165 | Amnura 50MW | [17 empty] | 12 |  | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 194370
166 | Katakhali (Northern)
167 | Katakhali Peaking
168 | Santahar Peaking
169 | Rajlanka 52 MW | [6 empty] | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 43 | 43 | 43 | 43 | 43 | 25 | 0 | 289920
170 | Chapainawabganj-100 MW | [19 empty] | 26 | 26 | 25 | 0 | 0 |  |  | 58004
171 | Paramount Baghabari
172 | Confidence CPBL-2 | [15 empty] | 43 | 0 | 0 | [8 empty] | 70080
173 | Rangpur GT
175 | Saidpur GT | [19 empty] | 18 | 18 | 19 | 19 | 0 | 0 |  | 43000
176
177
178
178 | Western Zone Total | 1505 | 1435 | 1478 | 1432 | 1382 | 1332 | 1363 | 1388 | 1478 | 1575 | 1759 | 1769 | 1930 | 1877 | 1846 | 1860 | 1836 | 2130 | 0 | 2667 | 2647 | 2611 | 2693 | 2603 | 2217 | 2105 | 45458928