## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-11-23 | Saturday
|  | Date (day): | 2024-11-23 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12836.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13187 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-11-22 | 2024-11-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 352 | 423 | 400 | 400 |  | 0
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage.
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 13 |  | 62 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 35 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 16 | 130 | 132 |  | 17 | Engine problem
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 17 | 35 | 20 |  | Fuel shortage
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 17 | 27 | 47 | 47 |  | 33 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 25 |  | 8 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 0 |  |  | 33 kV S/S work.
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 15 | 50 | 96 | 53 |  | Fuel shortage
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 0 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 17 | 54 | 108 |  | Fuel shortage
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 28 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 36 | 36 | 19 |  | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 500 | 583 | 500 | 500 | 83
| JERA Meghnaghat Power Limited |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1400 | 1585 | 2215 | 2415 | 2511 | 880
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 12 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 96 | 96 | 93 | 93 | 137 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 225 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 85 | 85 | 20 |  | Fuel shortage
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 |  | 34 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 68 |  | 34 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 30 | 100 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 35 | 36 | 4 | 10
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 50 | 50 | 58 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 50 | 100 | 200 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 36 | 100 | 100 |  | 0
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 35 | 53 | 63 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 452 | 550 | 612 | 612 |  | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 0 | 15 | 15 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 0 | 0 | 0 | 0 | 1150 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 830 | 985 | 1740 | 1974 | 1808 | 1010
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 181 | 200 | 200 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 300 | 300 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 43 | 44 | 44 |  | 1
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 152 | 150 | 180 | 180
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 20 | 31 | 51 | 51 |  | 0
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 130 | 130 | 20 |  | Fuel shortage
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 30 | 46 |  | 6 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 90 | 90 | 73 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 200 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 44 | 44 | 66 | 82
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 106 | 106 |  | 8 | Engine problem
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 8 | 95 | 95 |  | 18 | Engine problem
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 15 | 92 | 92 | 23 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 64 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 871 | 887 | 1724 | 1686 | 171 | 800
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 74 | 100 | 75 | 127 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 45 | 96 | 96 | 104 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 24 | 55 | 65 | 50 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 43 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 17 | 24 | 24
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 53 | 1 |  | Fuel shortage
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 0 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 186 | 160 | 343.6 | 313 | 127 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 28 | 28 |  | 42 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 28 | 30 | 30 |  | 60 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 113 | 113 | 112 | 112 |  | 51 | ST Under maint.
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 62 | 60 | 62
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 51 | 42 | 86 | 86
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 65 | 112 | 120 | 120 |  | 111 | ST Under maint.
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 13 | 13 | 13 |  | 12 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 300 | 300 | 300 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 345 | 385 | 385 |  |  | FGMO
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 336 | 346 | 360 | 383
| Sylhet Area Total |  |  |  |  | 2411 | 2366 | 1343 | 1368 | 1501 | 1526 | 65 | 615
100 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 908 | 908 | 928 | 928
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 35 |  | 19 | Engine problem
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 60 |  | 49 | Engine problem
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | under maint
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
106 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
107 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 100 | 0
108 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
109 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 368 | 514 | 370 | 370 | 864 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
** | Nepal |  | 0 | Imported power | 40 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1354 | 1422 | 1448 | 1393 | 1625 | 68
110 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 16 | 94 |  | Fuel shortage
111 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 5 | 6 | 10 | 10
112 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 127 | 127 | 80 | 127 |  | 67 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
113 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 320 | 470 | 622 | 622 |  | 622 | Unit-2 S/D.
114 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 54 | 150
116 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 213 | 307 | 307 | 307 |  | 0
117 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 885 | 1130 | 1293 | 1452 | 94 | 689
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 26 | 32 |  | 18 | Engine problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 170 | 173 | 170 | 175 | 35 |  | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 156 | 161 | 170 | 175 | 45 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 324 | 414 | 414 |  |  | FGMO
127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
128 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
129 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 53 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
133 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 416 | 767 | 765 | 765
134 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 57 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 88 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1243 | 1430 | 1941 | 1982 | 523 | 111
135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 67 | 67 | 68 | 68 |  | 17
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 |  | 124 | Machine problem
137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 90 | 113
140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
141 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 0 | 115 | 115
142 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0
143 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 161 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 418 | 216 | 631 | 446 | 40 | 226
| Total |  |  |  |  | 27740 | 27035 | 8530 | 9183 | 12836.6 | 13187 | 6964 | 4399
A. |  | 2024-11-22 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 9183 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7259 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9183 | MW
3 | Day peak Generation : |  |  | 8530 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8888.46 | MW
4 | Evening peak Generation : |  |  | 9183 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 200.2578 | MKWHr | By Solar | 3.6812 | MKWHr
| By Gas : | 114.3782 | MKWHr |  | By Oil: | 2.7466 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 40.4185 | MKWHr |  | By Hydro: | 2.2551 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 13.4345 | MKWHr |  | By Wind: | 0.08496 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6964 | MW | Dhaka | 3233.76 | 3233.76 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4399 | MW | Chittagong | 912 | 912 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 11363 | MW | Khulna | 1050.9 | 1050.9 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 821.49 | MMCFD | **Import Adani: | Taka | 88802362.28 | Rajshahi | 863.8 | 863.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : |  | 306152036.428 | ii) Oil : | Taka | 51108062.31 | Comilla | 815 | 815 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 293954091.11 | Total | Taka | 740016552.128 | Mymensingh | 772 | 772 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 12566.4 | MKWHr. | Sylhet | 348 | 348 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1242 | MW (W to E) at | 18:00 | hrs | Barisal | 267 | 267 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 1098 | MW at | 7:00 | hrs | Rangpur | 626 | 626 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.8°C |  |  | Total | 8888.46 | 8888.46 |  | 0
B. |  | 2024-11-23 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 29.8°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13187 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
4 | Reserve(Generation end) |  |  |  | 2687 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 228.9782 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6915 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector(India) : |  |  |  |  | i) Energy | 22.1527 | MKWHr. | ii) HVDC Flow at Peak Time |  | 908 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.1059 | MKWHr. | iii) Maximum HVDC Flow : |  | 908 | MW at | 1:00 | hrs.
* Import Through HVDC C/B Interconnector(Nepal) : |  |  |  |  | i) Energy | 0 | MKWHr.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.42 |  | (b) Today: | 97.21 |  | (c) Rule Curve: |  | 106.8
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-11-22 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | JERA Meghnaghat Power Limited | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | Nepal | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Nepal | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 285 | 0 | 180 | 200 | 70 | 44 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 62 | 22 | 0 | 136 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 8 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 595 | 0 | 0 | 0 |  | 908 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 150 | 0 | 0 | 164 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 150 | 757 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4402 | 4039 | 8441 | 2867 | 908 | 0 | 2220 | 0 | 72 | 1475 | 96 | 0 | 0 | 46 | 757 | 0 | 0 | 0 | 97.47
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 285 | 0 | 181 | 193 | 70 | 44 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 44 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 22 | 0 | 136 | 0 | 0 | 0 | 270 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 600 | 0 | 0 | 0 |  | 907 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 147 | 0 | 0 | 160 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 150 | 702 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4247 | 3875 | 8122 | 2845 | 907 | 0 | 2081 | 0 | 6 | 1441 | 96 | 0 | 0 | 44 | 702 | 0 | 0 | 0 | 97.46
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 285 | 0 | 181 | 128 | 80 | 44 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 22 | 0 | 136 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 8 | 0 | 0 | 600 | 0 | 0 | 0 |  | 906 | 0 | 269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 153 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 150 | 583 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4186 | 3658 | 7844 | 2755 | 906 | 0 | 2036 | 0 | 0 | 1416 | 96 | 0 | 0 | 44 | 583 | 0 | 8 | 0 | 97.45
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 33 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 285 | 0 | 182 | 88 | 85 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 22 | 0 | 136 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 7 | 0 | 0 | 500 | 0 | 0 | 0 |  | 908 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 69 | 0 | 150 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 150 | 499 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4133 | 3436 | 7569 | 2673 | 908 | 0 | 1827 | 0 | 0 | 1520 | 95 | 0 | 0 | 40 | 499 | 0 | 7 | 0 | 97.44
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 280 | 0 | 184 | 78 | 85 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 36 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 22 | 0 | 136 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 12 | 0 | 0 | 350 | 0 | 0 | 0 |  | 906 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 69 | 0 | 153 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 150 | 411 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3998 | 3323 | 7321 | 2638 | 906 | 0 | 1617 | 0 | 0 | 1608 | 93 | 0 | 0 | 36 | 411 | 0 | 12 | 0 | 97.43
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 290 | 0 | 193 | 78 | 90 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 22 | 0 | 120 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 14 | 0 | 0 | 350 | 0 | 0 | 0 |  | 907 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 0 | 153 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 150 | 410 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4090 | 3169 | 7259 | 2479 | 907 | 0 | 1667 | 0 | 26 | 1606 | 92 | 0 | 16 | 42 | 410 | 0 | 14 | 0 | 97.42
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 335 | 0 | 200 | 78 | 90 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 36 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 86 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 3 | 0 | 12 | 0 | 300 | 45 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 3 | 0 | 331 | 0 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 614 | 15 | 0 | 0 | 400 | 7 | 0 | 0 |  | 907 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 0 | 152 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 180 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 371 | 1 | 150 | 412 | 4 | 0 | 0 | 2 | 5 | 0 |  | 4331 | 3233 | 7564 | 2414 | 907 | 0 | 1899 | 0 | 125 | 1615 | 92 | 0 | 16 | 36 | 412 | 33 | 15 | 0 | 97.41
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 325 | 0 | 189 | 127 | 90 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 32 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 86 | 0 | 20 | 0 | 0 | 0 | 310 | 0 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 7 | 9 | 0 | 17 | 0 | 275 | 45 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 0 | 14 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 612 | 7 | 0 | 0 | 500 | 30 | 0 | 0 |  | 907 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 0 | 154 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 330 | 180 | 0 | 0 | 1 | 26 | 0 | 0 | 0 | 372 | 10 | 150 | 502 | 28 | 0 | 0 | 14 | 29 | 0 |  | 4512 | 3497 | 8009 | 2379 | 907 | 0 | 2042 | 0 | 154 | 1686 | 93 | 0 | 32 | 34 | 502 | 173 | 7 | 0 | 97.4
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 290 | 0 | 185 | 88 | 80 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 30 | 28 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 51 | 0 | 20 | 0 | 0 | 0 | 270 | 0 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 14 | 0 | 0 | 0 | 303 | 45 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 28 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 544 | 5 | 0 | 0 | 350 | 47 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 0 | 154 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 310 | 180 | 0 | 0 | 2 | 47 | 0 | 0 | 0 | 370 | 18 | 150 | 512 | 92 | 0 | 0 | 34 | 52 | 0 |  | 4065 | 3555 | 7620 | 2305 | 907 | 0 | 1674 | 0 | 125 | 1596 | 93 | 0 | 16 | 30 | 512 | 357 | 5 | 0 | 97.39
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 17 | 33 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 285 | 0 | 225 | 88 | 70 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32 | 33 | 0 | 0 | 2 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 51 | 0 | 20 | 0 | 0 | 0 | 290 | 0 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 17 | 0 | 0 | 0 | 306 | 45 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 37 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 484 | 6 | 0 | 0 | 350 | 59 | 0 | 0 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 0 | 151 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 300 | 180 | 0 | 0 | 3 | 64 | 0 | 0 | 0 | 370 | 29 | 150 | 512 | 148 | 0 | 0 | 48 | 73 | 0 |  | 3997 | 3666 | 7663 | 2280 | 906 | 0 | 1692 | 0 | 108 | 1523 | 94 | 0 | 0 | 32 | 512 | 510 | 6 | 0 | 97.38
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 17 | 33 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 315 | 0 | 203 | 88 | 50 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 36 | 33 | 0 | 0 | 2 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 11 | 0 | 64 | 0 | 0 | 0 | 305 | 0 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 18 | 0 | 0 | 0 | 343 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 43 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 452 | 1 | 0 | 0 | 400 | 64 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 66 | 0 | 120 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 300 | 180 | 0 | 0 | 4 | 71 | 0 | 0 | 0 | 368 | 33 | 150 | 417 | 122 | 0 | 0 | 52 | 86 | 0 |  | 4253 | 3616 | 7869 | 2406 | 908 | 0 | 1916 | 0 | 108 | 1456 | 94 | 0 | 0 | 36 | 417 | 527 | 1 | 0 | 97.37
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 310 | 0 | 180 | 152 | 50 | 35 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | 33 | 0 | 0 | 2 | 0 | 30 | 0 | 5 | 113 | 0 | 61 | 51 | 0 | 65 | 0 | 0 | 0 | 295 | 0 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 18 | 0 | 0 | 0 | 385 | 45 | 17 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 43 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 452 | 0 | 0 | 0 | 500 | 64 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 150 | 0 | 0 | 170 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 320 | 220 | 0 | 0 | 4 | 78 | 0 | 0 | 0 | 368 | 35 | 213 | 416 | 161 | 0 | 0 | 57 | 88 | 0 |  | 4630 | 3900 | 8530 | 2602 | 908 | 0 | 2166 | 0 | 125 | 1570 | 96 | 0 | 16 | 44 | 416 | 587 | 0 | 0 | 97.36
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 310 | 0 | 184 | 190 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 33 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 113 | 0 | 60 | 86 | 0 | 65 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 18 | 0 | 0 | 0 | 385 | 45 | 17 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 42 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 503 | 1 | 0 | 0 | 500 | 58 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 150 | 0 | 0 | 196 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 480 | 220 | 0 | 0 | 4 | 75 | 0 | 0 | 0 | 369 | 33 | 307 | 454 | 154 | 0 | 0 | 50 | 79 | 0 |  | 4841 | 4291 | 9132 | 2728 | 907 | 0 | 2349 | 0 | 125 | 1876 | 96 | 0 | 0 | 50 | 454 | 546 | 1 | 0 | 97.35
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 280 | 0 | 181 | 145 | 50 | 40 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | 33 | 0 | 0 | 1 | 0 | 28 | 0 | 5 | 80 | 0 | 40 | 42 | 0 | 66 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 14 | 0 | 0 | 0 | 323 | 45 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 32 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 478 | 5 | 0 | 0 | 400 | 49 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 150 | 0 | 0 | 150 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 470 | 180 | 0 | 0 | 3 | 53 | 0 | 0 | 0 | 369 | 25 | 233 | 458 | 122 | 0 | 0 | 38 | 48 | 0 |  | 4218 | 3828 | 8046 | 2404 | 907 | 0 | 1806 | 0 | 131 | 1767 | 96 | 0 | 16 | 44 | 458 | 412 | 5 | 0 | 97.37
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 285 | 0 | 182 | 107 | 70 | 40 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 33 | 0 | 0 | 1 | 0 | 28 | 0 | 5 | 80 | 0 | 40 | 42 | 0 | 73 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 0 | 323 | 8 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 20 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 400 | 4 | 0 | 0 | 400 | 35 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 150 | 0 | 0 | 150 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 400 | 180 | 0 | 0 | 2 | 37 | 0 | 0 | 0 | 371 | 17 | 200 | 412 | 76 | 0 | 0 | 29 | 42 | 0 |  | 3995 | 3582 | 7577 | 2398 | 907 | 0 | 1754 | 0 | 73 | 1588 | 96 | 0 | 16 | 42 | 412 | 287 | 4 | 0 | 97.33
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 320 | 0 | 202 | 88 | 70 | 40 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 39 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 80 | 0 | 40 | 42 | 0 | 87 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 4 | 0 | 0 | 0 | 323 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 7 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 388 | 4 | 0 | 0 | 400 | 12 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 0 | 150 | 0 | 0 | 150 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 350 | 180 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 371 | 8 | 150 | 415 | 37 | 0 | 0 | 8 | 15 | 0 |  | 3996 | 3399 | 7395 | 2496 | 907 | 0 | 1789 | 0 | 39 | 1477 | 96 | 0 | 16 | 42 | 415 | 114 | 4 | 0 | 97.33
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 15 | 7 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 2 | 0 | 36 | 0 | 0 | 0 | 310 | 0 | 181 | 88 | 70 | 40 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 81 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 113 | 0 | 40 | 42 | 0 | 90 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 6 | 4 | 0 | 323 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 12 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 450 | 1 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 148 | 0 | 0 | 150 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 421 | 0 | 200 | 595 | 3 | 0 | 0 | 0 | 2 | 0 |  | 4202 | 3634 | 7836 | 2508 | 908 | 0 | 1891 | 0 | 111 | 1666 | 96 | 0 | 16 | 38 | 595 | 7 | 0 | 0 | 97.31
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 12 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 0 | 12 | 0 | 36 | 0 | 0 | 0 | 310 | 0 | 181 | 150 | 70 | 43 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 44 | 74 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 113 | 0 | 62 | 42 | 0 | 112 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 15 | 0 | 30 | 17 | 0 | 345 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 36 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 583 | 0 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 149 | 0 | 0 | 173 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 307 | 767 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4985 | 4198 | 9183 | 2795 | 908 | 0 | 2230 | 0 | 270 | 2057 | 96 | 0 | 16 | 44 | 767 | 0 | 0 | 0 | 97.3
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 12 | 0 | 23 | 0 | 0 | 0 | 285 | 0 | 181 | 184 | 70 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | 76 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 80 | 0 | 62 | 42 | 0 | 119 | 0 | 0 | 0 | 265 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 50 | 0 | 0 | 383 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 36 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535 | 0 | 0 | 0 | 590 | 0 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68 | 0 | 150 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518 | 0 | 307 | 764 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4886 | 4150 | 9036 | 2785 | 907 | 0 | 2171 | 0 | 193 | 2078 | 92 | 0 | 0 | 46 | 764 | 0 | 0 | 0 | 97.27
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 15 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 12 | 0 | 23 | 0 | 0 | 0 | 285 | 0 | 183 | 184 | 70 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 48 | 76 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 62 | 42 | 0 | 145 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 50 | 0 | 0 | 384 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 12 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 0 | 0 | 0 | 585 | 0 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68 | 0 | 147 | 0 | 0 | 163 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 459 | 0 | 250 | 764 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4877 | 4129 | 9006 | 2808 | 908 | 0 | 2288 | 0 | 159 | 1939 | 92 | 0 | 0 | 48 | 764 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 285 | 0 | 184 | 187 | 70 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 76 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 62 | 42 | 0 | 160 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 590 | 0 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68 | 0 | 149 | 0 | 0 | 170 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 0 | 250 | 759 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4801 | 4144 | 8945 | 2845 | 907 | 0 | 2286 | 0 | 85 | 1931 | 92 | 0 | 0 | 40 | 759 | 0 | 0 | 0 | 97.28
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 285 | 0 | 181 | 189 | 80 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | 76 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 62 | 42 | 0 | 160 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 590 | 0 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68 | 0 | 150 | 0 | 0 | 176 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 464 | 0 | 250 | 760 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4814 | 4201 | 9015 | 2906 | 907 | 0 | 2295 | 0 | 77 | 1932 | 92 | 0 | 0 | 46 | 760 | 0 | 0 | 0 | 97.27
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 285 | 0 | 181 | 199 | 90 | 44 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 76 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 62 | 42 | 0 | 160 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 590 | 0 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68 | 0 | 151 | 0 | 0 | 176 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 200 | 759 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4673 | 4010 | 8683 | 2910 | 907 | 0 | 2288 | 0 | 0 | 1684 | 93 | 0 | 0 | 42 | 759 | 0 | 0 | 0 | 97.26
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 300 | 0 | 191 | 197 | 90 | 44 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 42 | 80 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 63 | 42 | 0 | 85 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 590 | 0 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68 | 0 | 152 | 0 | 0 | 178 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 150 | 694 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4633 | 3818 | 8451 | 2880 | 907 | 0 | 2304 | 0 | 0 | 1531 | 93 | 0 | 0 | 42 | 694 | 0 | 0 | 0 | 97.25
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 17 | 33 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 290 | 0 | 181 | 108 | 90 | 44 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 44 | 91 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 42 | 0 | 120 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 590 | 0 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68 | 0 | 151 | 0 | 0 | 182 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 150 | 652 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4547 | 3744 | 8291 | 2879 | 907 | 0 | 2227 | 0 | 0 | 1488 | 94 | 0 | 0 | 44 | 652 | 0 | 0 | 0 | 97.24
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8816400 | 0 |  | 0 | 8888000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157920 | 0 | 0 | 0 | 0 | 24840 | 0 | 0 | 0 | 340800 | 344520 | 410400 | 826100 | 0 | 0 | 2255144 | 0 | 0 | 0 | 0 | 5212374 | 0 | 0 | 0 |  | 324240 | 0 | 0 | 0 | 0 | 35520 | 0 | 849600 | 0 | 0 | 0 | 7526800 | 0 | 4613000 | 3261818 | 1754210 | 746712 | 0 | 0 | 702936 | 0 | 0 | 0 | 0 | 0 | 0 | 387480 | 1105920 | 1078080 | 0 | 0 | 10900 | 0 | 693600 | 0 | 203112 | 2135864 | 0 | 1173120 | 994560 | 0 | 2238990 | 0 | 0 | 0 | 7128000 | 299568 | 56976 | 0 | 0 | 0 | 0 | 789600 | 0 | 53280 | 119475 | 120000 | 78240 | 30109 | 8528000 | 530400 | 132480 | 0 | 21039 | 25091 | 56513 | 0 | 0 | 151200 | 77760 | 8100900 | 0 | 268530 | 7200 | 22582 | 0 | 0 | 167392 | 21120 | 52200 | 0 | 0 | 0 | 11307271 | 84960 | 0 | 0 | 11781364 | 427800 | 0 | 0 |  | 22152727 | 0 | 1524384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2458000 | 132632 | 0 | 0 | 0 | 0 | 0 | 0 | 34656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85374 | 1565672 | 0 | 3621000 | 0 | 0 | 3853545 | 0 | 3951655 | 0 | 0 | 0 | 0 | 0 | 8479054 | 0 | 0 | 0 | 0 | 0 | 0 | 36193 | 0 | 9786181 | 4800270 | 0 | 21600 | 28200 | 473040 | 0 | 0 | 0 | 9556364 | 211731 | 4582000 | 13434548 | 1039250 | 0 | 3342 | 339000 | 535340 | 0 |  | 107552010 | 92705758 | 200257768 | 65020988 | 22152727 | 0 | 49357210 | 0 | 2553975 | 40418488 | 2255144 | 0 | 192576 | 1105920 | 13434548 | 3681232 | 84960 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25391232 | 0 |  | 0 | 28263840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3066806.4 | 0 | 0 | 0 | 0 | 453578.4 | 0 | 0 | 0 | 255600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16627473.06 | 0 | 0 | 0 |  | 5703381.6 | 0 | 0 | 0 | 0 | 584659.2 | 0 | 0 | 0 | 0 | 0 | 20999772 | 0 | 15315160 | 10927090.3 | 5666098.3 | 2516419.44 | 0 | 0 | 2818773.36 | 0 | 0 | 0 | 0 | 0 | 0 | 290610 | 7254835.2 | 3352828.8 | 0 | 0 | 0 | 0 | 2587128 | 0 | 924159.6 | 7304654.88 | 0 | 6510816 | 5191603.2 | 0 | 6246782.1 | 0 | 0 | 0 | 22025520 | 224676 | 43301.76 | 0 | 0 | 0 | 0 | 15168216 | 0 | 938260.8 | 0 | 2137200 | 1357464 | 499207.22 | 22599200 | 10109424 | 2485324.8 | 0 | 0 | 410237.85 | 1098612.72 | 0 | 0 | 2934792 | 1384905.6 | 21548394 | 0 | 0 | 131688 | 378925.96 | 0 | 0 | 0 | 380582.4 | 884268 | 0 | 0 | 0 | 78811678.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 62249162.87 | 0 | 4496932.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7767280 | 628675.68 | 0 | 0 | 0 | 0 | 0 | 0 | 582567.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64628.118 | 17269362.16 | 0 | 30561240 | 0 | 0 | 12716698.5 | 0 | 13159011.15 | 0 | 0 | 0 | 0 | 0 | 24758837.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63414452.88 | 14928839.7 | 0 | 417960 | 0 | 0 | 0 | 0 | 0 | 69761457.2 | 0 | 34135900 | 88802362.28 | 0 | 0 | 0 | 0 | 0 | 0 |  | 363805181.82 | 445715368.378 | 809520550.198 | 188380042.028 | 62249162.87 | 0 | 117771994.4 | 0 | 47458688.55 | 293954091.11 | 0 | 0 | 3649373.76 | 7254835.2 | 88802362.28 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 310 | 0 | 180 | 152 | 50 | 35 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | 33 | 0 | 0 | 2 | 0 | 30 | 0 | 5 | 113 | 0 | 61 | 51 | 0 | 65 | 0 | 0 | 0 | 295 | 0 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 18 | 0 | 0 | 0 | 385 | 45 | 17 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 43 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 452 | 0 | 0 | 0 | 500 | 64 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 150 | 0 | 0 | 170 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 320 | 220 | 0 | 0 | 4 | 78 | 0 | 0 | 0 | 368 | 35 | 213 | 416 | 161 | 0 | 0 | 57 | 88 | 0 |  | 8530 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 12 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 12 | 0 | 36 | 0 | 0 | 0 | 310 | 0 | 181 | 150 | 70 | 43 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 44 | 74 | 0 | 0 | 0 | 0 | 28 | 0 | 5 | 113 | 0 | 62 | 42 | 0 | 112 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 15 | 0 | 30 | 17 | 0 | 345 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 36 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 583 | 0 | 0 | 0 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 149 | 0 | 0 | 173 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 307 | 767 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9183 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 8 | 132 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 22 | 25 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 24 | 64 | 68 | 0 | 50 | 50 | 0 | 10 | 0 | 0 |  | 300 | 0 | 200 | 180 | 90 | 44 | 0 | 0 | 51 | 0 | 46 | 52 | 0 | 0 |  | 18 | 82 | 75 | 0 | 0 | 0 | 28 | 30 | 0 | 5 | 112 | 0 | 62 | 86 | 0 | 120 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 300 | 0 | 0 | 96 | 0 | 96 | 0 | 100 | 200 | 130 | 385 | 65 | 105 | 85 | 0 | 100 | 54 | 110 | 106 | 95 | 100 | 383 | 17 | 0 | 54 | 53 | 0 | 53 | 0 | 92 | 36 | 0 | 160 | 0 | 612 | 15 | 0 | 0 | 500 |  |  |  |  | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 127 | 10 | 16 | 0 | 0 | 0 | 40 | 25 | 95 | 0 | 0 | 32 | 0 | 30 | 0 | 0 | 5 | 68 | 0 | 150 | 0 | 0 | 175 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 370 | 0 | 307 | 765 | 0 | 0 |  |  |  | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 |  | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 8 | 130 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 25 | 22 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 24 | 56 | 51 | 0 | 50 | 50 | 0 | 4 | 0 | 0 | 0 | 300 | 0 | 200 | 180 | 90 | 44 | 0 | 0 | 51 | 0 | 30 | 52 | 0 | 0 |  | 18 | 66 | 100 | 0 | 0 | 1.6 | 28 | 30 | 0 | 5 | 112 | 0 | 60 | 86 | 0 | 120 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 300 | 0 | 0 | 96 | 0 | 50 | 20 | 100 | 200 | 130 | 385 | 55 | 50 | 85 | 5 | 50 | 54 | 110 | 106 | 95 | 100 | 360 | 0 | 50 | 17 | 35 | 0 | 17 | 35 | 92 | 36 | 0 | 17 | 0 | 612 | 15 | 0 | 0 | 500 | 70 |  |  |  | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 26 | 0 | 30 | 0 | 0 | 5 | 68 | 0 | 150 | 0 | 0 | 170 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 90 | 0 | 8 | 113 | 622 | 220 |  | 54 | 6 | 100 | 115 | 0 | 0 | 370 | 30 | 307 | 765 | 170 | 0 |  | 29 | 47 | 0 |  |  |  |  | gas | hvdc |  | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 290 | 0 | 181 | 182 | 90 | 41 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 113 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 11 | 0 | 121 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 9 | 0 | 0 | 0 | 325 | 35 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 12 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 453 | 6 | 0 | 0 | 550 | 22 | 0 | 0 | 0 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 68 | 0 | 152 | 0 | 0 | 164 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 90 | 0 | 1 | 0 | 360 | 180 | 0 | 0 | 1 | 20 | 50 | 0 | 0 | 371 | 5 | 307 | 514 | 31 | 0 | 0 | 14 | 26 | 0 | 0 |  |  |  | 114378198 | 22152727 |  | 0 | 40418488 | 2746551 | 1105920 | 3681232 | 84960 | 2255144 |  |  |  | 186823220
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [10 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 |  | 299798 | [7 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [14 empty] | 499227 |  | 499229 |  |  | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [11 empty] | 114.3782 | 22.1527 |  | 0 | 40.4185 | 2.7466 | 1.1059 | 3.6812 | 0.08496 | 2.2551
| Minimum Generation |  | 7259 | 6:00
| Highest Generation |  | 9183 | 18:00 | [129 empty] | 0 | [77 empty] | 186.8232
| Day Peak Generation |  | 8530 | 12:00
| Evening Peak Generation |  | 9183 | 18:00 | [207 empty] | 202699852
| HVDC Max Flow |  | 908 | 1:00 | [207 empty] | 202.6999
| HVDC EvPeak Flow |  | 908 | 18:00
| Load factor L.F |  | 90.86% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-11-23
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-11-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8530 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6915
Evening Peak Generation : |  |  | 9183 | MW Hour : | 18:00 | Available Max Generation : |  | 13187
E.P. Demand (at gen end) : |  |  | 9183 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10500
Maximum Generation : |  |  | 9183 | MW Hour : | 18:00 | Reserve(Generation end) |  | 2687
Total Gen. (MKWH) : |  |  | 200.2578 | System Load Factor : | 90.86% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1098 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-11-23
Actual : |  | 97.21 | Ft.(MSL) , | Rule curve : | 106.8 | Ft.( MSL )
Gas Consumed : |  | Total = | 821.49 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 306152036.428 | Adani : | 88802362.28
|  |  | Coal : | 293954091.11 | Oil: | 51108062.31 | Total: | 740016552.128
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3758.0485 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1027.7912 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1438.2562 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1248.7433 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1028.1895 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 763.9927 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 429.0126 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 356.8265 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 697.9062 |  |  | 0 | 0%
Total |  | 0 |  | 10748.7667 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
8:21 | 08:42 | BIPTC S/S 10CF25 Forced S/D.
08:40 | 21:30 | Kodda 132/33kV S/S Bus-1 Scheduled S/D Due to Annual maintenanc.
08:49 | 09:57 | Kodda 132/33kV S/S Tr-1 (406T) HT Scheduled S/D Due to Annual Maintenance.
08:49 | 10:09 | Kodda 132/33kV S/S Tr-1 (406T) LT Scheduled S/D Due to Annual Maintenance.
08:50 |  | Bheramara 410 MW CCPP Shutdown with remarks:- GT.
08:56 | 16:31 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Scheduled S/D from Srinagar 132/33kV end Due to Annual
Maintenance at Keraniganj Grid Substation. and from Keranigonj 230/132/33kV end Due to Annual Maintenance .
09:03 |  | Khulshi-Madunaghat 132kV Ckt-1 Project Work S/D from Khulshi 132/33kV end Due to GIS building Construction work
under the ESPNCA Project.
09:04 | 12:11 | Siddhirganj 132/33kV S/S 132kV MTR 2 Scheduled S/D Due to Maintenance work.
09:04 | 12:12 | Siddhirganj 230/132kV S/S MTR 2 HT Scheduled S/D Due to oil refill work in MTR-2(OLTC) and B phase HT bushing clamp change.
09:22 | 10:17 | Joydebpur-Kodda B 132 kV Ckt-1 Forced S/D from Joydebpur 132/33kV end.
09:24 |  | Joydebpur-Kodda B 132 kV Ckt-2 Tripped from Joydebpur 132/33kV end showing General trip Dist start-R,S,T Dtt 1
send Dist trip Z2,Z3,Z start 67 N Blocked relays.
| 09:36 | Rampura 230/132kV S/S 132 kV Busbar-1 is restored.
| 09:38 | Bashundhara-Rampura 132 kV Ckt-2 is restored.
09:56 | 17:05 | Maniknagar 132/33kV S/S Motijheel Ckt-1 Scheduled S/D Due to Annual Maintenance.
10:19 | 15:16 | Kodda 132/33kV S/S Summit 149 MW PS Scheduled S/D Due to Annual Maintenance.
10:28 |  | Joydebpur-Kodda B 132 kV Ckt-1 Tripped from Joydebpur 132/33kV end showing General trip Dist start- R,S,T 67 N
Blocked DTT 1 send Dist trip Z2,Z3,Z start relays.
| 11:44 | Mymensingh RPCL-Tangail 132kV Ckt-1 is restored.
| 11:45 | Mymensingh RPCL-Tangail 132kV Ckt-2 is restored.
11:55 | 14:47 | Barishal 230/132kV S/S T-5 LT Forced S/D Due to S/D Taken by PBS-1 due to Bus Section Red hot repair. | [5 empty] | 6 MW load interrup.
12:03 | 14:46 | Barishal 230/132kV S/S T-5 HT Forced S/D Due to S/D Taken by PBS-1 due to Bus Section Red hot repair.
12:10 |  | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D Due to Order by NLDC for Load Management .
13:07 |  | Madunaghat 400kV - Madunaghat GIS 230kV ckt-1 was charged from Madunaghat 400kV end.
13:08 |  | Madunaghat 400kV - Madunaghat GIS 230kV ckt-2 was charged from Madunaghat 400kV end.
| 14:10 | Madunaghat 400kV- Madunaghat GIS 230kV ckt-1 was switched on.
| 14:11 | Madunaghat 400kV- Madunaghat GIS 230kV ckt-2 was switched on.
| 14:37 | Madunaghat GIS 230/132kV ATR-1 was switched ON.
| 14:49 | Madunaghat GIS 230/132kV ATR-2 was switched ON.
| 15:00 | Madunaghat GIS 230/132kV ATR-3 was switched ON.
15:17 | 15:55 | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D Due to Annual Maintenance.
15:17 | 15:57 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to Annual Maintenance.
15:59 | 16:44 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to Due to bus-1 annual maintenance.
15:59 | 16:44 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to Due to bus-1 annual maintenance.
15:59 | 16:44 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to Due to bus-1 annual maintenance.
15:59 | 16:35 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to Due to bus-1 annual maintenance.
| 16:27 | BSRM-Cumilla(N) 230 kV Ckt-1 is restored.
| 16:27 | BSRM-Cumilla(N) 230 kV Ckt-2 is restored.
16:39 | 18:05 | Shyampur 132/33kV S/S GT-3 HT Forced S/D Due to Neutral Cable Fault.
16:47 | 17:18 | Kodda-Rajendrapur 132kV Ckt-1 Scheduled S/D from Kodda 132/33kV end Due to Due tobBus-1 annual maintenance.
20:05 |  | Bheramara 230/132kV S/S GTG (NW) Tripped showing 86A, 86B relays Due to Fault of NWPGCL End side.
| 21:41 | Kabirpur -Kodda 132kV Ckt-1 is restored.
22:09 |  | Sylhet CCPP 225 MW ST tripped.
07:12 |  | Sreemongol 132/33kV S/S 132/33kv T-1AB LT Scheduled S/D Due to For PBS Project Work.
07:12 |  | Sreemongol 132/33kV S/S 132/33kv T-1AB HT Scheduled S/D Due to For PBS project work.
07:23 |  | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 Scheduled S/D Due to Annual maintenance.
07:42 |  | Jhenaidah 132/33kV S/S Transformer T-2 LT Project Work S/D. | [5 empty] | 21 MW load interrup.
07:43 |  | Jhenaidah 132/33kV S/S Transformer T-2 HT Project Work S/D.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-11-22
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 423 | 8816400
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8888000 | Frequency control
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | NENP Reserve
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 24840 | Low demand
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 157920 | Low demand
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 27 | 685320 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 410400 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 826100
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | 33 kV Feeder fault.
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 15 | 53280 | Low demand
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 132480 | Low demand
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | Reserve
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 7200 | Reserve
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 167392
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 52200 | Low demand
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 583 | 11781364
| JERA Meghnaghat Power Limited |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 1585 | 32002896
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 119475
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 12 | 35520 | Low demand
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 96 | 2255144 | Low water level
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5212374
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 0 | 0 | Reserve
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 30 | 120000 | Low demand
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 36 | 849600
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21039
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 25091 | Reserve
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 56513 | Reserve
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Reserve
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 77760 | 33 kV Feeder fault.
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 22582 | Reserve
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Reserve
55 | SS Power I |  | IPP | 2*612 | 1224 | 550 | 11307271 | Coal shortage
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 84960
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 0 | 0 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 985 | 20187329
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 181 | 4613000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7526800 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 43 | 746712
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 150 | 3261818 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 31 | 702936 | Gas shortage
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 30109 | Reserve
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1754210 | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 78240 | Low demand
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 44 | 1105920
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 387480 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 8 | 151200 | Low demand
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 15 | 21120 | Low demand
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 427800
| Cumilla Area Total |  |  |  | 2917 | 887 | 20807345
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 74 | 1078080 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10900
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 45 | 789600 | Low demand
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 24 | 530400 | Low demand
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 268530
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 17 | 324240 | Low demand
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 0 | Reserve
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 646 | 160 | 3001750
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 693600 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 113 | 2135864 | ST under Maint
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 0 | 0 | 0 | Contact expired
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 203112 | NENP
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 56976 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1173120
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 42 | 994560 | Gas shortage
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 112 | 2238990 | ST under Maint
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 299568 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7128000 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 345 | 8528000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 346 | 8100900 | FGMO
| Sylhet Area Total |  |  |  | 2366 | 1368 | 31552690
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 908 | 22152727
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 1524384 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 473040
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 514 | 9556364 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Nepal |  | Imported power | 40 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1422 | 33706515
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 6 | 132632 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 127 | 2458000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 470 | 9786181 | Unit-2 under overhauling
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4800270
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 21600 | Reserve
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 4582000
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3342
| Barisal Area Total |  |  |  | 2236 | 1130 | 21784025
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 173 | 3853545 | FGMO
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 161 | 3951655
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 324 | 8479054 | FGMO
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 85374 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 34656 | Reserve
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28200
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 767 | 13434548
135 | Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 339000
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 535340
| Rajshahi Area Total |  |  |  | 3449 | 1430 | 30741372
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 67 | 1565672
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3621000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | Reserve
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36193
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 0 | 0 | Reserve
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 211731
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 1039250
| Rangpur Area Total |  |  |  | 950 | 216 | 6473846
| Total |  |  |  | 27035 | 9183 | 200257768
| Eastern Grid Total |  |  |  | 16701 | 4985 | 107552010
| Western Grid Total |  |  |  | 10334 | 4198 | 92705758
| National Grid Total |  |  |  | 27035 | 9183 | 200257768
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-11-2024
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7638.14 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3193.6 | MW
i) Dhaka area |  |  | 4239.64 |  | MW | i) Khulna area |  |  |  | 1175 | MW
ii) Chattogram area |  |  | 1122.5 |  | MW | ii) Barishal area |  |  |  | 301 | MW
iii) Cumilla area |  |  | 981 |  | MW | iii) Rajshahi area |  |  |  | 984.6 | MW
iv) Mymensingh area |  |  | 851 |  | MW | iv) Rangpur area |  |  |  | 733 | MW
v) Sylhet area |  |  | 444 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10831.74 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 00:00 | 67 | Jashore | 86 | 13:00 | 133 | Rajbari | 46 | 18:00
2 | AKSML | 102 | 09:00 | 68 | Jhenaidah | 84 | 18:00 | 134 | Rajendrapur | 74 | 01:00
3 | Aftabnagar | 26 | 12:00 | 69 | Joydebpur | 122 | 13:00 | 135 | Rajshahi | 66 | 13:00
4 | Agargaon | 73 | 13:00 | 70 | Joypurhat | 36 | 18:00 | 136 | Rajshahi-230 | 55 | 12:00
5 | Agrabad | 68 | 18:30 | 71 | Juldah | 12 | 00:00 | 137 | Ramganj | 80 | 13:00
6 | Amnura | 36 | 18:30 | 72 | KSRM | 32 | 18:00 | 138 | Rampur | 30 | 00:00
7 | Ashuganj | 58 | 00:00 | 73 | Kabirpur | 194 | 00:00 | 139 | Rangamati | 13 | 18:00
8 | BSRM | 138 | 00:00 | 74 | Kachua | 45 | 19:30 | 140 | Rangpur | 93 | 13:00
9 | Bagerhat | 58 | 18:00 | 75 | Kallyanpur | 75 | 12:00 | 141 | Ruppur | 5 | 15:00
10 | Bakulia | 71 | 00:00 | 76 | Kalurghat | 22 | 00:00 | 142 | SSM | 0 | 00:00
11 | Banani | 34 | 12:00 | 77 | Kamrangirchar | 44.8 | 00:00 | 143 | Saidpur | 64 | 12:00
12 | Bangabhaban | 3 | 10:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 76 | 18:00
13 | Barapukuria | 37 | 09:00 | 79 | Kazla | 84 | 13:00 | 145 | Satmasjid | 79 | 13:00
14 | Barguna | 14 | 21:00 | 80 | Keranigonj | 49 | 13:00 | 146 | Savar | 114 | 00:00
15 | Barishal | 70 | 13:00 | 81 | Khagrachori | 24 | 18:00 | 147 | SevenRings | 11.79 | 23:00
16 | Barishal-230 | 63 | 14:00 | 82 | Khulna | 58 | 13:00 | 148 | ShahCement | 27 | 11:00
17 | Baroaulia | 52 | 12:00 | 83 | Khulshi | 118 | 09:00 | 149 | Shahjadpur | 41 | 18:00
18 | Baroirhat | 38 | 13:00 | 84 | Kishoreganj | 98 | 18:00 | 150 | Shahjibazar | 65 | 00:00
19 | Bashundhara | 130 | 12:00 | 85 | Kodda | 109 | 00:00 | 151 | Shahmirpur | 32 | 02:00
20 | BashundharaCement | 6 | 01:00 | 86 | Kulaura | 30 | 19:00 | 152 | Shariatpur | 51 | 21:00
21 | Beanibazar | 44 | 18:00 | 87 | Kurigram | 43 | 18:00 | 153 | Sherpur | 84 | 08:00
22 | Benapole | 38 | 18:30 | 88 | Kushtia | 90 | 18:00 | 154 | Shikalbaha | 15 | 00:00
23 | Bhaluka | 86 | 00:00 | 89 | Lalbag | 63 | 00:00 | 155 | Shitalakhya | 50.5 | 00:00
24 | Bhandaria | 35.5 | 21:00 | 90 | Lalmonirhat | 36 | 19:00 | 156 | Sholosohor | 30 | 12:00
25 | Bhangura | 20 | 18:00 | 91 | MI_Cement | 16.3 | 10:00 | 157 | Shyampur | 150 | 03:00
26 | Bheramara(GK) | 36 | 18:00 | 92 | Madanganj | 30 | 13:00 | 158 | Siddhirganj | 74 | 00:00
27 | Bhulta | 207 | 00:00 | 93 | Madaripur | 61 | 21:00 | 159 | Sirajganj | 52 | 18:00
28 | Bog-Sherpur | 48 | 00:00 | 94 | Madartek | 56.54 | 13:00 | 160 | Sonargaon | 69 | 00:00
29 | Bogura | 101 | 19:00 | 95 | Madunaghat | 36 | 18:00 | 161 | Sreemongol | 52 | 18:00
30 | Borhanuddin | 50 | 21:00 | 96 | Magura | 40 | 18:00 | 162 | Sreepur | 54 | 00:00
31 | Brahmanbaria | 104 | 18:00 | 97 | Mahasthangarh | 42 | 18:00 | 163 | Srinagar | 29.66 | 21:00
32 | Cantonment | 80 | 13:00 | 98 | Manikganj | 76 | 21:00 | 164 | Sunamganj | 34 | 19:00
33 | Chandpur | 42 | 13:00 | 99 | Maniknagar | 46 | 13:00 | 165 | Sylhet | 28 | 13:00
34 | Chandraghona | 30 | 16:00 | 100 | Matarbari | 38 | 18:00 | 166 | Sylhet-132 | 77 | 13:00
35 | Chapai | 42 | 20:00 | 101 | Matuail | 47 | 00:00 | 167 | TK | 22 | 18:00
36 | Charsaidpur | 41 | 02:00 | 102 | Millgate | 78 | 12:00 | 168 | Tangail | 122 | 18:00
37 | Chauddagram | 48 | 13:00 | 103 | Mirpur | 100 | 13:00 | 169 | Thakurgaon | 66 | 18:00
38 | Chhatak | 21 | 19:00 | 104 | Mirsorai | 8 | 00:00 | 170 | Tongi | 93 | 00:00
39 | Chowmuhani | 126 | 20:00 | 105 | Mirzapur | 34 | 12:00 | 171 | Ullahpara | 30 | 19:00
40 | Chuadanga | 65 | 18:00 | 106 | Mithapukur | 38 | 18:00 | 172 | Ullon | 36 | 12:00
41 | Coxsbazar | 92 | 13:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 55 | 13:00
42 | Cumilla(N) | 112 | 18:00 | 108 | Mogbazar | 75.5 | 12:00 | 174 | UttaraNew | 38 | 13:00
43 | Cumilla(S) | 97 | 00:00 | 109 | Mongla | 22 | 00:00 | 175 | Zigatola | 61 | 13:00
44 | Daudkandi | 96 | 00:00 | 110 | Motijheel | 28 | 13:00
45 | Dhaka | 12 | 00:00 | 111 | Munshiganj | 74 | 13:00
46 | Dhamrai | 84 | 00:00 | 112 | Mymensingh | 166 | 13:00
47 | Dhanmondi | 88 | 12:00 | 113 | Naogaon | 77 | 18:00
48 | Dohazari | 71 | 18:00 | 114 | Narail | 37 | 18:00
49 | Faridpur | 90 | 20:00 | 115 | Narinda | 39 | 12:00
50 | Fatullah | 62 | 00:00 | 116 | Narshingdi | 136 | 19:30
51 | Fenchuganj | 24 | 18:00 | 117 | Natore | 88 | 18:00
52 | Feni | 66 | 18:00 | 118 | Nawabganj | 30 | 13:00
53 | GPH | 14 | 13:00 | 119 | Netrakona | 83 | 19:30
54 | Ghatail | 44 | 18:00 | 120 | New | 25.8 | 11:00
55 | Ghorashal | 40 | 00:00 | 121 | Niamatpur | 38 | 20:00
56 | Goalpara | 24 | 13:00 | 122 | Noapara | 25 | 18:00
57 | Gollamari | 52 | 13:00 | 123 | PHP | 10 | 19:30

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-11-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 408 | 20:00 | 394 | 12:00 | Kaliakoir | 389 | 08:00 | 376 | 12:00
| Ashuganj | 418 | 6:00 | 403 | 12:00 | Madunaghat | 406 | 09:00 | 398 | 13:00
| Bhulta | 412 | 08:00 | 402 | 12:00 | Meghnaghat | 402 | 04:00 | 391 | 13:00
| Bibiana | 399 | 08:00 | 390 | 13:00 | Payra | 419 | 03:00 | 411 | 13:00
| BIPTC | 402 | 03:00 | 391 | 18:00 | Rahanpur | 402 | 05:00 | 391 | 18:00
| Bogura | 396 | 05:00 | 381 | 18:00 | Rampal | 414 | 02:00 | 403 | 13:00
| Gopalganj | 414 | 03:00 | 400 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 243 | 03:00 | 236 | 13:00 | Haripur | 242 | 09:00 | 235 | 12:00
| AKSML | 239 | 00:00 | 233 | 13:00 | Hasnabad | 242 | 03:00 | 235 | 13:00
| Aminbazar | 244 | 08:00 | 237 | 11:00 | Hathazari | 240 | 05:00 | 237 | 12:00
| Ashuganj | 244 | 08:00 | 239 | 11:00 | Ishurdi | 242 | 03:00 | 233 | 13:00
| Ashuganj-400 | 245 | 6:00 | 233 | 13:00 | Jhenaidah | 238 | 03:00 | 228 | 13:00
| Baghabari | 240 | 04:00 | 233 | 18:00 | Kaliakoir | 244 | 08:00 | 230 | 12:00
| Barapukuria | 229 | 04:00 | 223 | 18:00 | Keranigonj | 242 | 03:00 | 236 | 11:00
| Barapukuria-230 | 229 | 04:00 | 223 | 18:00 | Khulna(S) | 242 | 03:00 | 232 | 13:00
| Barishal | 244 | 03:00 | 240 | 12:00 | Madunaghat | 239 | 04:00 | 234 | 13:00
| Bheramara | 240 | 03:00 | 231 | 18:00 | Maniknagar | 241 | 07:00 | 235 | 12:00
| Bhulta | 243 | 03:00 | 237 | 12:00 | Meghnaghat | 250 | 07:00 | 243 | 10:00
| Bibiana | 230 | 08:00 | 225 | 13:00 | Meghnaghat-400 | 244 | 03:00 | 239 | 12:00
| BIPTC | 242 | 03:00 | 231 | 13:00 | Mirsorai | 241 | 04:00 | 233 | 13:00
| Bogura | 242 | 04:00 | 234 | 18:00 | Rajshahi | 240 | 04:00 | 231 | 18:00
| Bogura-400 | 242 | 05:00 | 233 | 18:00 | Rampal | 238 | 06:00 | 229 | 13:00
| Borhanuddin | 246 | 04:00 | 242 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 241 | 04:00 | 234 | 00:00 | Rampura | 243 | 06:00 | 236 | 13:00
| Cumilla(N) | 238 | 06:00 | 231 | 13:00 | Shikalbaha | 238 | 06:00 | 232 | 13:00
| Faridpur | 244 | 08:00 | 238 | 13:00 | Shyampur | 243 | 03:00 | 238 | 11:00
| Fenchuganj | 234 | 10:00 | 229 | 13:00 | Siddhirganj | 244 | 08:00 | 238 | 11:00
| Ghorashal | 246 | 04:00 | 240 | 00:00 | Sirajgonj | 247 | 06:00 | 242 | 18:00
| Ghorashal-230 | 241 | 06:00 | 234 | 13:00 | Sreepur | 239 | 03:00 | 236 | 12:00
| Gopalganj | 243 | 00:00 | 236 | 13:00 | Tongi | 239 | 15:00 | 234 | 12:00
| GPH | 240 | 04:00 | 234 | 13:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 139 | 18:00 | 134 | 12:00 | Kushtia | 141 | 06:00 | 134 | 13:00
| Agargaon | 145 | 18:30 | 136 | 13:00 | Lalbag | 139 | 03:00 | 134 | 13:00
| Agrabad | 137 | 08:00 | 133 | 19:30 | Lalmonirhat | 131 | 14:00 | 124 | 19:00
| AKS | 135 | 03:00 | 132 | 12:00 | Madanganj | 135 | 08:00 | 132 | 12:00
| Aminbazar | 144 | 08:00 | 137 | 09:00 | Madaripur | 136 | 07:00 | 133 | 12:00
| Amnura | 134 | 04:00 | 130 | 10:00 | Madartek | 137 | 03:00 | 133 | 13:00
| Ashuganj | 141 | 05:00 | 140 | 00:00 | Madunaghat | 139 | 08:00 | 134 | 13:00
| Bagerhat | 137 | 02:00 | 132 | 18:00 | Magura | 141 | 01:00 | 134 | 13:00
| Bakulia | 137 | 08:00 | 133 | 13:00 | Mahasthangarh | 138 | 04:00 | 131 | 18:00
| Banani | 138 | 04:00 | 132 | 13:00 | Manikganj | 134 | 18:30 | 126 | 11:00
| Bangabhaban | 138 | 04:00 | 134 | 14:00 | Maniknagar | 138 | 08:00 | 133 | 13:00
| Barapukuria | 137 | 04:00 | 132 | 18:00 | Matarbari | 130 | 10:00 | 121 | 20:00
| Barguna | 139 | 00:00 | 134 | 13:00 | Matuail | 137 | 07:00 | 133 | 12:00
| Barishal | 135 | 04:00 | 131 | 13:00 | Millgate | 144 | 15:00 | 133 | 11:00
| Barishal-230 | 136 | 03:00 | 133 | 12:00 | Mirpur | 143 | 08:00 | 137 | 13:00
| Baroaulia | 138 | 01:00 | 133 | 13:00 | Mirzapur | 132 | 08:00 | 126 | 16:00
| Baroirhat | 136 | 00:00 | 127 | 13:00 | Mithapukur | 135 | 14:00 | 127 | 18:00
| Bashundhara | 138 | 06:00 | 133 | 12:00 | MI_Cement | 142 | 03:00 | 134 | 11:00
| BashundharaCement | 135 | 08:00 | 132 | 12:00 | Modern | 137 | 06:00 | 133 | 19:30
| Beanibazar | 134 | 10:00 | 130 | 00:00 | Mogbazar | 140 | 07:00 | 133 | 12:00
| Benapole | 138 | 05:00 | 131 | 13:00 | Mongla | 138 | 05:00 | 132 | 13:00
| Bhaluka | 134 | 01:00 | 131 | 13:00 | Motijheel | 138 | 04:00 | 134 | 14:00
| Bhandaria | 134 | 04:00 | 130 | 13:00 | Munshiganj | 135 | 17:00 | 130 | 11:00
| Bhangura | 142 | 03:00 | 139 | 17:00 | Mymensingh | 136 | 06:00 | 124 | 22:00
| Bheramara | 140 | 03:00 | 134 | 18:00 | Naogaon | 138 | 05:00 | 132 | 18:00
| Bheramara(GK) | 140 | 04:00 | 134 | 13:00 | Narail | 141 | 03:00 | 133 | 13:00
| Bhulta | 130 | 08:00 | 126 | 11:00 | Narinda | 138 | 08:00 | 133 | 13:00
| Bog-Sherpur | 139 | 03:00 | 134 | 18:00 | Narshingdi | 136 | 08:00 | 128 | 21:00
| Bogura | 140 | 05:00 | 135 | 18:00 | Natore | 139 | 02:00 | 133 | 13:00
| Bogura-230 | 141 | 04:00 | 134 | 18:00 | Nawabganj | 139 | 02:00 | 135 | 11:00
| Brahmanbaria | 138 | 07:00 | 134 | 00:00 | Netrakona | 134 | 06:00 | 125 | 16:00
| Cantonment | 141 | 03:00 | 136 | 13:00 | New | 138 | 02:00 | 134 | 11:00
| Chandpur | 136 | 02:00 | 124 | 13:00 | Niamatpur | 136 | 06:00 | 131 | 18:00
| Chandraghona | 138 | 05:00 | 135 | 12:00 | Noapara | 139 | 06:00 | 132 | 13:00
| Chapai | 134 | 03:00 | 130 | 18:00 | Pabna | 141 | 03:00 | 136 | 18:00
| Charsaidpur | 137 | 08:00 | 131 | 13:00 | Palashbari | 134 | 03:00 | 127 | 18:00
| Chauddagram | 137 | 07:00 | 128 | 13:00 | Panchagarh | 132 | 03:00 | 116 | 18:00
| Chhatak | 132 | 04:00 | 129 | 00:00 | Patuakhali | 139 | 00:00 | 134 | 01:00
| Chowmuhani | 138 | 00:00 | 123 | 13:00 | Payra | 138 | 00:00 | 135 | 12:00
| Chuadanga | 140 | 06:00 | 132 | 12:00 | PHP | 135 | 00:00 | 126 | 13:00
| Coxsbazar | 128 | 08:00 | 122 | 19:30 | Postogola | 143 | 06:00 | 138 | 11:00
| Cumilla(N) | 139 | 06:00 | 133 | 13:00 | Purbachal | 138 | 03:00 | 132 | 13:00
| Cumilla(S) | 138 | 06:00 | 129 | 12:00 | Purbasadipur | 131 | 05:00 | 118 | 18:00
| Daudkandi | 137 | 07:00 | 128 | 00:00 | Rahanpur | 137 | 05:00 | 133 | 18:00
| Dhaka | 138 | 06:00 | 133 | 12:00 | Rahim | 136 | 17:00 | 132 | 18:00
| Dhamrai | 139 | 03:00 | 136 | 11:00 | Rajbari | 137 | 03:00 | 133 | 13:00
| Dhanmondi | 138 | 03:00 | 134 | 12:00 | Rajendrapur | 133 | 09:00 | 123 | 12:00
| Dohazari | 133 | 05:00 | 129 | 12:00 | Rajshahi | 140 | 02:00 | 134 | 18:00
| Faridpur | 136 | 02:00 | 133 | 13:00 | Rajshahi-230 | 141 | 05:00 | 125 | 18:00
| Fatullah | 140 | 04:00 | 136 | 11:00 | Ramganj | 134 | 07:00 | 121 | 13:00
| Fenchuganj | 139 | 18:30 | 135 | 00:00 | Rampur | 137 | 00:00 | 133 | 01:00
| Feni | 135 | 00:00 | 127 | 13:00 | Rampura | 138 | 06:00 | 133 | 13:00
| Ghatail | 132 | 05:00 | 124 | 16:00 | Rangamati | 137 | 04:00 | 134 | 13:00
| Ghorashal | 143 | 04:00 | 141 | 15:00 | Rangpur | 135 | 03:00 | 126 | 18:00
| Goalpara | 140 | 00:00 | 134 | 12:00 | Ruppur | 142 | 04:00 | 135 | 20:00
| Gollamari | 140 | 03:00 | 135 | 12:00 | Saidpur | 135 | 14:00 | 125 | 18:00
| Gopalganj | 138 | 03:00 | 133 | 12:00 | Satkhira | 139 | 04:00 | 132 | 13:00
| Gopalganj-400 | 137 | 00:00 | 133 | 13:00 | Satmasjid | 140 | 02:00 | 136 | 12:00
| Gulshan | 137 | 05:00 | 133 | 12:00 | Savar | 140 | 00:00 | 138 | 12:00
| Halishahar | 137 | 00:00 | 133 | 20:00 | SevenRings | 143 | 03:00 | 140 | 13:00
| Haripur | 137 | 08:00 | 133 | 12:00 | ShahCement | 137 | 08:00 | 131 | 13:00
| HaripurSBU | 137 | 08:00 | 133 | 12:00 | Shahjadpur | 145 | 02:00 | 142 | 12:00
| Hasnabad | 142 | 01:00 | 137 | 13:00 | Shahjibazar | 138 | 07:00 | 134 | 00:00
| Hathazari | 140 | 05:00 | 136 | 19:30 | Shahmirpur | 137 | 04:00 | 134 | 12:00
| Ishurdi | 142 | 03:00 | 137 | 13:00 | Shariatpur | 137 | 05:00 | 133 | 12:00
| Jaldhaka | 133 | 14:00 | 120 | 18:00 | Sherpur | 137 | 06:00 | 120 | 23:00
| Jamalpur | 138 | 06:00 | 122 | 22:00 | Shikalbaha | 127 | 00:00 | 121 | 13:00
| Jashore | 139 | 03:00 | 131 | 13:00 | Shikalbaha-230 | 138 | 05:00 | 134 | 13:00
| Jhenaidah | 141 | 05:00 | 136 | 12:00 | Shitalakhya | 142 | 03:00 | 134 | 11:00
| Jhenaidah-230 | 143 | 05:00 | 135 | 13:00 | Sholosohor | 137 | 04:00 | 134 | 13:00
| Joydebpur | 141 | 03:00 | 134 | 21:00 | Shyampur | 136 | 00:00 | 135 | 09:00
| Joypurhat | 137 | 03:00 | 133 | 18:00 | Shyampur-230 | 139 | 03:00 | 135 | 11:00
| Juldah | 137 | 08:00 | 134 | 12:00 | Siddhirganj | 137 | 07:00 | 133 | 12:00
| Kabirpur | 136 | 08:00 | 127 | 11:00 | Sirajganj | 141 | 09:00 | 134 | 22:00
| Kachua | 137 | 07:00 | 127 | 13:00 | Sonargaon | 136 | 08:00 | 125 | 00:00
| Kaliakoir | 142 | 08:00 | 127 | 12:00 | Sreemongol | 137 | 08:00 | 133 | 12:00
| Kallyanpur | 139 | 04:00 | 135 | 12:00 | Sreepur | 136 | 08:00 | 134 | 00:00
| Kalurghat | 138 | 03:00 | 134 | 16:00 | Srinagar | 140 | 08:00 | 135 | 11:00
| Kamrangirchar | 139 | 02:00 | 134 | 12:00 | SSM | 141 | 08:00 | 139 | 12:00
| Kaptai | 140 | 5:00 | 133 | 13:00 | Sunamganj | 132 | 08:00 | 128 | 00:00
| Kazla | 138 | 09:00 | 132 | 13:00 | Sylhet | 135 | 07:00 | 131 | 00:00
| Keranigonj | 139 | 03:00 | 135 | 11:00 | Sylhet-132 | 134 | 09:00 | 131 | 00:00
| Khagrachori | 137 | 04:00 | 134 | 00:00 | Tangail | 130 | 04:00 | 124 | 16:00
| Khulna | 139 | 04:00 | 134 | 13:00 | Thakurgaon | 132 | 03:00 | 116 | 18:00
| Khulna(S) | 140 | 03:00 | 135 | 13:00 | TK | 138 | 09:00 | 134 | 15:00
| Khulshi | 136 | 19:00 | 132 | 13:00 | Tongi | 138 | 04:00 | 135 | 10:00
| Kishoreganj | 136 | 07:00 | 133 | 00:00 | Ullahpara | 141 | 14:00 | 139 | 22:00
| Kodda | 139 | 06:00 | 122 | 11:00 | Ullon | 138 | 03:00 | 133 | 12:00
| KSRM | 139 | 09:00 | 134 | 21:00 | Uttara | 142 | 04:00 | 138 | 11:00
| Kulaura | 137 | 06:00 | 134 | 00:00 | UttaraNew | 137 | 08:00 | 133 | 11:00
| Kurigram | 134 | 14:00 | 120 | 18:00 | Zigatola | 139 | 04:00 | 134 | 13:00

## L-Curve
Date | 2024-11-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1320 | 4547 | 3744 | 8291 |  |  |  | QF-LDC-11
0:30 | 1305 | 4474.5 | 3891.5 | 8366 | Date: | 2024-11-22
1:00 | 1290 | 4402 | 4039 | 8441
1:30 | 1292 | 4324.5 | 3957 | 8281.5
2:00 | 1294 | 4247 | 3875 | 8122
2:30 | 1292 | 4216.5 | 3766.5 | 7983 | [5 empty] | Gen. at Eve. Peak | 9183 | 9183 MW (18:00 )
3:00 | 1290 | 4186 | 3658 | 7844 | [6 empty] | 18:00
3:30 | 1290 | 4159.5 | 3547 | 7706.5 | [5 empty] | Gen. at Day Peak | 8530 | 8530 MW (12:00 )
4:00 | 1290 | 4133 | 3436 | 7569 | [6 empty] | 12:00
4:30 | 1297 | 4065.5 | 3379.5 | 7445 | [5 empty] | Highest Generation | 9183
5:00 | 1304 | 3998 | 3323 | 7321 | [6 empty] | 18:00
5:30 | 1309 | 4044 | 3246 | 7290
6:00 | 1314 | 4090 | 3169 | 7259
6:30 | 1206 | 4210.5 | 3201 | 7411.5
7:00 | 1098 | 4331 | 3233 | 7564
7:30 | 1138 | 4421.5 | 3365 | 7786.5
8:00 | 1178 | 4512 | 3497 | 8009
8:30 | 1358 | 4288.5 | 3526 | 7814.5
9:00 | 1538 | 4065 | 3555 | 7620
9:30 | 1653 | 4031 | 3610.5 | 7641.5
10:00 | 1768 | 3997 | 3666 | 7663
10:30 | 1765 | 4125 | 3641 | 7766
11:00 | 1762 | 4253 | 3616 | 7869
11:30 | 1650 | 4441.5 | 3758 | 8199.5
12:00 | 1538 | 4630 | 3900 | 8530
12:30 | 1544 | 4735.5 | 4095.5 | 8831
13:00 | 1550 | 4841 | 4291 | 9132
13:30 | 1604 | 4529.5 | 4059.5 | 8589
14:00 | 1658 | 4218 | 3828 | 8046
14:30 | 1671 | 4106.5 | 3705 | 7811.5
15:00 | 1684 | 3995 | 3582 | 7577
15:30 | 1624 | 3995.5 | 3490.5 | 7486
16:00 | 1564 | 3996 | 3399 | 7395
16:30 | 1505 | 4099 | 3516.5 | 7615.5
17:00 | 1446 | 4202 | 3634 | 7836
17:30 | 1344 | 4593.5 | 3916 | 8509.5
18:00 | 1242 | 4985 | 4198 | 9183
18:30 | 1313 | 4935.5 | 4174 | 9109.5
19:00 | 1384 | 4886 | 4150 | 9036
19:30 | 1390 | 4877 | 4129 | 9006
20:00 | 1348 | 4801 | 4144 | 8945 |  |  |  | Executive Engineer
20:30 | 1287 | 4807.5 | 4172.5 | 8980 |  |  |  | Network Operation Division
21:00 | 1226 | 4814 | 4201 | 9015
21:30 | 1231 | 4743.5 | 4105.5 | 8849
22:00 | 1236 | 4673 | 4010 | 8683 |  |  |  |  | Page 6 of 7
22:30 | 1266 | 4653 | 3914 | 8567
23:00 | 1296 | 4633 | 3818 | 8451
23:30 | 1308 | 4590 | 3781 | 8371
24:00 | 1320 | 4547 | 3744 | 8291
9183 MW (18:00 )
8530 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-11-22 |  |  | Energy |  | 200257768
[17 empty] | 2024-11-22 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | Nepal | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 2879 | 907 | 0 | 2227 | 0 | 0 | 1488 | 94 | 0 | 0 | 44 | 652 | 0 | 0 | 0
0:30 | 2873 | 907.5 | 0 | 2223.5 | 0 | 36 | 1481.5 | 95 | 0 | 0 | 45 | 704.5 | 0 | 0 | 0 |  |  | Date: | 44156
1:00 | 2867 | 908 | 0 | 2220 | 0 | 72 | 1475 | 96 | 0 | 0 | 46 | 757 | 0 | 0 | 0
1:30 | 2856 | 907.5 | 0 | 2150.5 | 0 | 39 | 1458 | 96 | 0 | 0 | 45 | 729.5 | 0 | 0 | 0 | [8 empty] | Total Energy | 200.2578 | 200.2578 | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 2845 | 907 | 0 | 2081 | 0 | 6 | 1441 | 96 | 0 | 0 | 44 | 702 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2800 | 906.5 | 0 | 2058.5 | 0 | 3 | 1428.5 | 96 | 0 | 0 | 44 | 642.5 | 0 | 4 | 0 | [8 empty] | Energy Requirement | 200.2578 | 200.2578
3:00 | 2755 | 906 | 0 | 2036 | 0 | 0 | 1416 | 96 | 0 | 0 | 44 | 583 | 0 | 8 | 0
3:30 | 2714 | 907 | 0 | 1931.5 | 0 | 0 | 1468 | 95.5 | 0 | 0 | 42 | 541 | 0 | 7.5 | 0 | [7 empty] | Shortage
4:00 | 2673 | 908 | 0 | 1827 | 0 | 0 | 1520 | 95 | 0 | 0 | 40 | 499 | 0 | 7 | 0
4:30 | 2655.5 | 907 | 0 | 1722 | 0 | 0 | 1564 | 94 | 0 | 0 | 38 | 455 | 0 | 9.5 | 0
5:00 | 2638 | 906 | 0 | 1617 | 0 | 0 | 1608 | 93 | 0 | 0 | 36 | 411 | 0 | 12 | 0
5:30 | 2558.5 | 906.5 | 0 | 1642 | 0 | 13 | 1607 | 92.5 | 0 | 8 | 39 | 410.5 | 0 | 13 | 0
6:00 | 2479 | 907 | 0 | 1667 | 0 | 26 | 1606 | 92 | 0 | 16 | 42 | 410 | 0 | 14 | 0
6:30 | 2446.5 | 907 | 0 | 1783 | 0 | 75.5 | 1610.5 | 92 | 0 | 16 | 39 | 411 | 16.5 | 14.5 | 0 | [6 empty] | Coal
7:00 | 2414 | 907 | 0 | 1899 | 0 | 125 | 1615 | 92 | 0 | 16 | 36 | 412 | 33 | 15 | 0
7:30 | 2396.5 | 907 | 0 | 1970.5 | 0 | 139.5 | 1650.5 | 92.5 | 0 | 24 | 35 | 457 | 103 | 11 | 0 | [5 empty] | Oil
8:00 | 2379 | 907 | 0 | 2042 | 0 | 154 | 1686 | 93 | 0 | 32 | 34 | 502 | 173 | 7 | 0
8:30 | 2342 | 907 | 0 | 1858 | 0 | 139.5 | 1641 | 93 | 0 | 24 | 32 | 507 | 265 | 6 | 0
9:00 | 2305 | 907 | 0 | 1674 | 0 | 125 | 1596 | 93 | 0 | 16 | 30 | 512 | 357 | 5 | 0
9:30 | 2292.5 | 906.5 | 0 | 1683 | 0 | 116.5 | 1559.5 | 93.5 | 0 | 8 | 31 | 512 | 433.5 | 5.5 | 0
10:00 | 2280 | 906 | 0 | 1692 | 0 | 108 | 1523 | 94 | 0 | 0 | 32 | 512 | 510 | 6 | 0
10:30 | 2343 | 907 | 0 | 1804 | 0 | 108 | 1489.5 | 94 | 0 | 0 | 34 | 464.5 | 518.5 | 3.5 | 0
11:00 | 2406 | 908 | 0 | 1916 | 0 | 108 | 1456 | 94 | 0 | 0 | 36 | 417 | 527 | 1 | 0
11:30 | 2504 | 908 | 0 | 2041 | 0 | 116.5 | 1513 | 95 | 0 | 8 | 40 | 416.5 | 557 | 0.5 | 0
12:00 | 2602 | 908 | 0 | 2166 | 0 | 125 | 1570 | 96 | 0 | 16 | 44 | 416 | 587 | 0 | 0
12:30 | 2665 | 907.5 | 0 | 2257.5 | 0 | 125 | 1723 | 96 | 0 | 8 | 47 | 435 | 566.5 | 0.5 | 0
13:00 | 2728 | 907 | 0 | 2349 | 0 | 125 | 1876 | 96 | 0 | 0 | 50 | 454 | 546 | 1 | 0
13:30 | 2728 | 907 | 0 | 2349 | 0 | 125 | 1876 | 96 | 0 | 0 | 50 | 454 | 546 | 1 | 0
14:00 | 2728 | 907 | 0 | 2349 | 0 | 125 | 1876 | 96 | 0 | 0 | 50 | 454 | 546 | 1 | 0
14:30 | 2563 | 907 | 0 | 2051.5 | 0 | 99 | 1732 | 96 | 0 | 8 | 46 | 433 | 416.5 | 2.5 | 0
15:00 | 2398 | 907 | 0 | 1754 | 0 | 73 | 1588 | 96 | 0 | 16 | 42 | 412 | 287 | 4 | 0
15:30 | 2447 | 907 | 0 | 1771.5 | 0 | 56 | 1532.5 | 96 | 0 | 16 | 42 | 413.5 | 200.5 | 4 | 0
16:00 | 2496 | 907 | 0 | 1789 | 0 | 39 | 1477 | 96 | 0 | 16 | 42 | 415 | 114 | 4 | 0
16:30 | 2502 | 907.5 | 0 | 1840 | 0 | 75 | 1571.5 | 96 | 0 | 16 | 40 | 505 | 60.5 | 2 | 0
17:00 | 2508 | 908 | 0 | 1891 | 0 | 111 | 1666 | 96 | 0 | 16 | 38 | 595 | 7 | 0 | 0
17:30 | 2651.5 | 908 | 0 | 2060.5 | 0 | 190.5 | 1861.5 | 96 | 0 | 16 | 41 | 681 | 3.5 | 0 | 0
18:00 | 2795 | 908 | 0 | 2230 | 0 | 270 | 2057 | 96 | 0 | 16 | 44 | 767 | 0 | 0 | 0
18:30 | 2790 | 907.5 | 0 | 2200.5 | 0 | 231.5 | 2067.5 | 94 | 0 | 8 | 45 | 765.5 | 0 | 0 | 0
19:00 | 2785 | 907 | 0 | 2171 | 0 | 193 | 2078 | 92 | 0 | 0 | 46 | 764 | 0 | 0 | 0
19:30 | 2808 | 908 | 0 | 2288 | 0 | 159 | 1939 | 92 | 0 | 0 | 48 | 764 | 0 | 0 | 0
20:00 | 2845 | 907 | 0 | 2286 | 0 | 85 | 1931 | 92 | 0 | 0 | 40 | 759 | 0 | 0 | 0
20:30 | 2875.5 | 907 | 0 | 2290.5 | 0 | 81 | 1931.5 | 92 | 0 | 0 | 43 | 759.5 | 0 | 0 | 0
21:00 | 2906 | 907 | 0 | 2295 | 0 | 77 | 1932 | 92 | 0 | 0 | 46 | 760 | 0 | 0 | 0
21:30 | 2908 | 907 | 0 | 2291.5 | 0 | 38.5 | 1808 | 92.5 | 0 | 0 | 44 | 759.5 | 0 | 0 | 0
22:00 | 2910 | 907 | 0 | 2288 | 0 | 0 | 1684 | 93 | 0 | 0 | 42 | 759 | 0 | 0 | 0
22:30 | 2895 | 907 | 0 | 2296 | 0 | 0 | 1607.5 | 93 | 0 | 0 | 42 | 726.5 | 0 | 0 | 0
23:00 | 2880 | 907 | 0 | 2304 | 0 | 0 | 1531 | 93 | 0 | 0 | 42 | 694 | 0 | 0 | 0
23:30 | 2879.5 | 907 | 0 | 2265.5 | 0 | 0 | 1509.5 | 93.5 | 0 | 0 | 43 | 673 | 0 | 0 | 0 |  |  | Max Temp. in Dhaka |  | 29.8°C
24:00 | 2879 | 907 | 0 | 2227 | 0 | 0 | 1488 | 94 | 0 | 0 | 44 | 652 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on Y13: Author:

## Generation
2024-11-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 96 | 96 | 96 | 95 | 93 | 92 | 92 | 93 | 93 | 94 | 94 | 96 | 96 | 96 | 96 | 96 | 96 | 96 |  | 92 | 92 | 92 | 92 | 93 | 93 | 94 | 2255144
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 9 | 14 | 17 | 18 | 18 | 18 | 14 | 10 | 4 | 0 | [9 empty] | 119475
6 | Sikalbaha 225MW CCPP (Gas) | 226 | 226 | 229 | 228 | 230 | 229 | 228 | 228 | 206 | 188 | 189 | 225 | 222 | 196 | 194 | 194 | 194 | 225 |  | 224 | 227 | 227 | 227 | 229 | 230 | 230 | 5212374
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [26 empty] | 0
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [26 empty] | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [26 empty] | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 200 | 193 | 128 | 88 | 78 | 78 | 78 | 127 | 88 | 88 | 88 | 152 | 190 | 145 | 107 | 88 | 88 | 150 |  | 184 | 184 | 187 | 189 | 199 | 197 | 108 | 3261818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 285 | 355 | 375 | 530 | 610 | 612 | 614 | 612 | 544 | 484 | 452 | 452 | 503 | 478 | 400 | 388 | 460 | 550 |  | 535 | 515 | 500 | 500 | 407 | 403 | 400 | 11307271
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 44 | 44 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 35 | 40 | 40 | 40 | 40 | 40 | 43 |  | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 746712
33 | Ashuganj 225 MW CCPP | 180 | 181 | 181 | 182 | 184 | 193 | 200 | 189 | 185 | 225 | 203 | 180 | 184 | 181 | 182 | 202 | 181 | 181 |  | 181 | 183 | 184 | 181 | 181 | 191 | 181 | 4613000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 285 | 280 | 290 | 335 | 325 | 290 | 285 | 315 | 310 | 310 | 280 | 285 | 320 | 310 | 310 |  | 285 | 285 | 285 | 285 | 285 | 300 | 290 | 7526800
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 70 | 70 | 80 | 85 | 85 | 90 | 90 | 90 | 80 | 70 | 50 | 50 | 50 | 50 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 80 | 90 | 90 | 90 | 1754210
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 351 | 350 | 302 | 302 | 302 | 317 | 353 | 354 | 350 | 322 | 334 | 352 | 384 | 363 | 327 | 327 | 360 | 423 |  | 431 | 421 | 421 | 423 | 424 | 424 | 422 | 8816400
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 595 | 600 | 600 | 500 | 350 | 350 | 400 | 500 | 350 | 350 | 400 | 500 | 500 | 400 | 400 | 400 | 450 | 583 |  | 590 | 585 | 590 | 590 | 590 | 590 | 590 | 11781364
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 360 | 360 | 320 | 320 | 320 | 360 | 360 | 300 | 300 | 420 | 420 | 420 | 300 | 300 | 300 | 300 | 420 |  | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 8888000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 32 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 39 | 81 | 74 |  | 76 | 76 | 76 | 76 | 76 | 80 | 91 | 1078080
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 14 | 28 | 37 | 43 | 43 | 42 | 32 | 20 | 7 | 0 | [9 empty] | 268530
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 28 | 28 |  | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 693600
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 61 | 60 | 40 | 40 | 40 | 40 | 62 |  | 62 | 62 | 62 | 62 | 62 | 63 | 40 | 1173120
48 | Shahjibazar 86 MW PP (Shahjibazar) | 22 | 22 | 22 | 22 | 22 | 22 | 86 | 86 | 51 | 51 | 11 | 51 | 86 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 994560
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 136 | 136 | 136 | 136 | 136 | 120 |  | 20 | 20 | 20 | 64 | 65 | 65 | 66 | 73 | 87 | 90 | 112 |  | 119 | 145 | 160 | 160 | 160 | 85 | 120 | 2238990
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 56976
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | [6 empty] | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 299568
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 270 | 290 | 300 | 280 | 300 | 315 | 310 | 270 | 290 | 305 | 295 | 310 | 280 | 275 | 295 | 300 | 300 |  | 265 | 305 | 295 | 295 | 285 | 290 | 295 | 7128000
| Bibiyana South 400 MW | 320 | 320 | 320 | 316 | 316 | 316 | 331 | 320 | 316 | 316 | 351 | 336 | 346 | 326 | 326 | 349 | 316 | 346 |  | 346 | 346 | 346 | 346 | 346 | 355 | 346 | 8100900
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Tangail Palli Power Gen 22 MW | 24 | 6 | [5 empty] | 3 | 18 | 18 | 18 | 18 | 18 | 24 | 24 | 6 | 6 | 17 |  | 24 | 24 | 24 | 24 |  |  |  | 324240
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 46 | 44 | 44 | 40 | 36 | 42 | 36 | 34 | 30 | 32 | 36 | 44 | 50 | 44 | 42 | 42 | 38 | 44 |  | 46 | 48 | 40 | 46 | 42 | 42 | 44 | 1105920
64 | Malancha, Ctg. EPZ (United) | 35 | 35 | 35 | 36 | 37 | 37 | 30 | 30 | 36 | 34 | 35 | 35 | 35 | 38 | 38 | 38 | 36 | 36 |  | 23 | 23 | 23 | 30 | 33 | 36 | 35 | 849600
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 16 | 16 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 387480
69 | Summit Ashulia | 16 | 16 | 15 | 15 | 15 | 14 | 12 | 12 | 12 | 12 | 17 | 17 | 19 | 15 | 15 | 17 | 15 | 15 |  | 14 | 6 | 13 | 12 | 12 | 12 | 12 | 340800
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 15 | 0 | 7 |  | 0 | 7 | 7 | 7 | 7 | 12 |  | 15 | 15 | 15 | 15 | 22 | 22 | 22 | 344520
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 410400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 826100
73 | Ghorashal 108 MW PP (Regent)
Feni Lanka Power
| Chowmuhani 113 MW | 8 | [5 empty] | 3 | 17 | [8 empty] | 2 | 8 |  | 8 | 8 | 8 |  |  |  |  | 151200
| Manikgonj 162MW PP(MPGL) | [26 empty] | 7200
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP
79 | Kodda 150 MW PP | [5 empty] | 16 | 16 | 32 | 16 |  |  | 16 |  | 16 | 16 | 16 | 16 | 16 | [8 empty] | 157920
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [8 empty] | 132480
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 3 | 3 |  | 4 | 3 | 2 | 1 | 0 | [10 empty] | 21039
| Jodiac Power | [26 empty] | 56513
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 203112
93 | Ashuganj 51 MW PP (Midland) | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 51 | 10 | 10 | 10 | 10 | 31 |  | 51 | 43 | 43 | 43 | 51 | 43 | 51 | 702936
94 | Gagnagar 102 MW PP (Digital Power)
95 | Patenga 50MW PP (Baraka) | [16 empty] | 2 | 12 |  | 12 | 12 | [5 empty] | 35520
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | 0 | [5 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [26 empty] | 0
100 | Manikganj 55 MW PP (Northern) | [26 empty] | 0
101 | Kushiara 163 MW CCPP (KP) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 113 | 113 | 80 | 80 | 80 | 113 | 113 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2135864
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 10900
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 2 | 17 | [8 empty] | 24840
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 24 |  |  |  |  | 20 | 65 | 65 | 45 | 45 | 45 | 45 | 45 | 45 | 24 | 8 | 37 | 45 |  | 45 | 45 | 45 | 45 |  |  |  | 789600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 7 | 17 | [8 empty] | 15 | [8 empty] | 53280
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 6 | 30 |  | 50 | 50 | [5 empty] | 120000
116 | Chandpur 200 MW (Desh energy) | [6 empty] | 12 | 17 | [8 empty] | 4 | 17 | [8 empty] | 78240
117 | Ashuganj 150 MW PP (Midland) | [26 empty] | 30109
118 | Bibiyana-III 400 MW CCPP | 331 | 334 | 334 | 334 | 300 | 300 | 300 | 275 | 303 | 306 | 343 | 385 | 385 | 323 | 323 | 323 | 323 | 345 |  | 383 | 384 | 384 | 382 | 382 | 383 | 382 | 8528000
| Jamalpur 115 MW PP (United) | [5 empty] | 6 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 8 | 8 | 15 | 24 |  | 18 | 8 | 8 | 8 |  |  |  | 530400
| Anwara 300 MW PP (United) | 16 | [25 empty] | 25091
| Juldah unit-2 (Acorn) | [16 empty] | 12 | 36 |  | 36 | 12 | [5 empty] | 77760
| Anlima Energy Ltd. | [26 empty] | 22582
| Bhairob 54.5 MW | [26 empty] | 0
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 9 | 16 | 22 | 27 | 28 | 25 | 21 | 14 | 6 | 0 | [9 empty] | 167392
| Chandpur 115(Doreen) | [16 empty] | 1 | 15 | [8 empty] | 21120
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 7 | 17 | [8 empty] | 52200
| Mirsharai 150 MW (Oil) | [20 empty] | 0 | [5 empty] | 0
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 8 | 7 | 12 | 14 | 15 | 7 | 5 | 6 | 1 | 0 | 1 | 5 | 4 | 4 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84960
| Sonagazi 75 MW Solar Plant | [6 empty] | 7 | 30 | 47 | 59 | 64 | 64 | 58 | 49 | 35 | 12 | 1 | [9 empty] | 427800
Matarbari 2*600 MW (CPGCL)
JERA Meghnaghat Power Limited
Sreepur 150 MW
120
121 | Eastern Zone Total | 4402 | 4247 | 4186 | 4133 | 3998 | 4090 | 4331 | 4512 | 4065 | 3997 | 4253 | 4630 | 4841 | 4218 | 3995 | 3996 | 4202 | 4985 |  | 4886 | 4877 | 4801 | 4814 | 4673 | 4633 | 4547 | 107552010
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | [26 empty] | 0
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha)
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 5 | 26 | 47 | 64 | 71 | 78 | 75 | 53 | 37 | 16 | 1 | [9 empty] | 473040
132 | Rampal 1320 MW (BIFPCL) | 373 | 373 | 371 | 371 | 376 | 373 | 371 | 372 | 370 | 370 | 368 | 368 | 369 | 369 | 371 | 371 | 421 | 514 |  | 518 | 459 | 464 | 464 | 408 | 408 | 369 | 9556364
133 | United Payra Power Ltd. | [26 empty] | 21600
| Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 180 | 180 | 220 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4800270
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 213 | 307 | 233 | 200 | 150 | 200 | 307 |  | 307 | 250 | 250 | 250 | 200 | 150 | 150 | 4582000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3342
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 80 | 83 | 80 | 127 | 127 | 83 | 80 | 80 | 80 | 127 |  | 100 | 100 | 100 | 127 | 127 | 127 | 127 | 2458000
141 | Bhola 33 MW PP (Venture) | 7 | 6 | 6 | 6 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 3 | 3 | 4 | 6 |  | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 132632
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
| Bheramara HVDC | 908 | 907 | 906 | 908 | 906 | 907 | 907 | 907 | 907 | 906 | 908 | 908 | 907 | 907 | 907 | 907 | 908 | 908 |  | 907 | 908 | 907 | 907 | 907 | 907 | 907 | 22152727
147 | Nepal
148 | Bheramara 410 MW CCPP | 264 | 265 | 269 | 220 | 220 | 40 | 8 | 18 | [18 empty] | 1524384
149 | Payra 1320 MW | 450 | 350 | 300 | 250 | 250 | 250 | 260 | 330 | 310 | 300 | 300 | 320 | 480 | 470 | 400 | 350 | 370 | 470 |  | 500 | 500 | 500 | 500 | 450 | 350 | 350 | 9786181
150
151 | Barapukuria TPP Unit-1 | 67 | 66 | 67 | 69 | 69 | 68 | 68 | 68 | 68 | 68 | 66 | 67 | 67 | 67 | 67 | 68 | 67 | 67 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1565672
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 150 | 147 | 153 | 150 | 153 | 153 | 152 | 154 | 154 | 151 | 120 | 150 | 150 | 150 | 150 | 150 | 148 | 149 |  | 150 | 147 | 149 | 150 | 151 | 152 | 151 | 3621000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 28200
157 | Sirajganj 68 MW Solar Park | [6 empty] | 2 | 14 | 34 | 48 | 52 | 57 | 50 | 38 | 29 | 8 | 0 | [9 empty] | 339000
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 164 | 160 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 170 | 196 | 150 | 150 | 150 | 150 | 173 |  | 160 | 163 | 170 | 176 | 176 | 178 | 182 | 3853545
Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 166 | 166 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 156 | 194 | 140 | 140 | 140 | 140 | 161 |  | 160 | 164 | 171 | 193 | 176 | 178 | 182 | 3951655
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 320 | 320 | 320 | 280 | 250 | 280 | 350 | 350 | 300 | 300 | 378 | 350 | 414 | 321 | 314 | 348 | 363 | 324 |  | 325 | 414 | 414 | 414 | 396 | 414 | 414 | 8479054
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 85374
166 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP
169 | Santahar 50 MW Peaking PP
170 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
171 | Chapainawabganj 100 MW Peaking PP | [26 empty] | 34656
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2
173 | Confidence Power Bogura Unit-1 113 MW | [26 empty] | 0
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [26 empty] | 0
178 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 5 | 5 | 5 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 36193
| Energypac Power Venture Thakurgaon Ltd. | [26 empty] | 0
| Intraco Solar 30 MW | [6 empty] | 1 | 10 | 18 | 29 | 33 | 35 | 33 | 25 | 17 | 8 | 0 | [9 empty] | 211731
178 | Adani Power Jharkhanda Ltd | 757 | 702 | 583 | 499 | 411 | 410 | 412 | 502 | 512 | 512 | 417 | 416 | 454 | 458 | 412 | 415 | 595 | 767 |  | 764 | 764 | 759 | 760 | 759 | 694 | 652 | 13434548
| Teesta Solar Limited | [6 empty] | 4 | 28 | 92 | 148 | 122 | 161 | 154 | 122 | 76 | 37 | 3 | [9 empty] | 1039250
179 | Pabna Solar 100 MW | [6 empty] | 5 | 29 | 52 | 73 | 86 | 88 | 79 | 48 | 42 | 15 | 2 | [9 empty] | 535340
| Western Zone Total | 4039 | 3875 | 3658 | 3436 | 3323 | 3169 | 3233 | 3497 | 3555 | 3666 | 3616 | 3900 | 4291 | 3828 | 3582 | 3399 | 3634 | 4198 |  | 4150 | 4129 | 4144 | 4201 | 4010 | 3818 | 3744 | 92705758
[27 empty] | Total | 200257768