## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-11-28 | Thursday
|  | Date (day): | 2024-11-28 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13304.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13564 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-11-27 | 2024-11-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 413 | 412 | 400 | 412
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | under maint
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 25 | 130 | 155 | 335 |  | GT-2 S/D
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 80 | 96 | 150 | 200 | 10
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 30 | 335 | 0 | 0 | 335 |  | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 0 | 0 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 14 | 35 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 64 | 32 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 45 | 47 | 47 |  | 33 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 31 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 16 | 25 | 25 |  |  | Fuel Shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 15 | 50 | 52 | 149
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 34 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 0 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 72 | 100 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 36 | 36 | 36 | 19 |  | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 360 | 550 | 550 | 550 | 33
| JERA Meghnaghat Power Limited |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1171 | 1822 | 2145 | 2592 | 2080 | 1326
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 13 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 23 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 96 | 96 | 96 | 96 | 134 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 225 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 85 | 85 |  | 20 | Engine problem
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 |  | 34 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 51 | 68 |  | 34 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 20 | 100 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 11 | 5 | 3 | 15
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 7 | 50 | 50 | 58 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 65 | 50 | 65 | 235 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 19 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 48 | 100 | 100
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 53 | 35 | 53 | 63 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 35 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 1240 | 970 | 1224 | 820 |  |  | Coal shortage
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 3 | 15 | 15 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 0 | 0 | 0 | 0 | 1150 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1586 | 1657 | 2354 | 2155 | 1820 | 418
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 180 | 200 | 200 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 310 | 310 | 310 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 42 | 42 | 42
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 187 | 189 | 180 | 180
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 38 | 140 | 140 |  | 10 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 16 | 30 | 45 |  | 7 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 200 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 56 | 57 | 66 | 82
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 49 | 95 | 95 |  | 18 | Engine problem
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 48 | 16 | 51 | 64 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 68 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1000 | 1073 | 1634 | 1630 | 232 | 802
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 10 | 11 | 30 | 30 | 172 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 83 | 96 | 96 | 104 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 64 | 55 | 55 | 60 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 24 | 24
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 54 | 17 | 53
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 21 | 20 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 116 | 256 | 273.6 | 258 | 172 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 0 | 0 | 0 |  | 90 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 113 | 113 | 112 | 112 |  | 51 | ST Under maint.
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 0 | 5 | 5 | 45 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 61 | 62 | 62
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 42 | 50 | 50 | 50
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 119 | 66 | 174 | 174 |  | 57 | ST Under maint.
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 13 | 13 |  | 12 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 275 | 300 | 300 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 342 | 385 | 385 |  |  | FGMO
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 277 | 360 | 380
| Sylhet Area Total |  |  |  |  | 2411 | 2366 | 1464 | 1199 | 1463 | 1483 | 65 | 619
100 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 904 | 904 | 922 | 922
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 35 |  | 19 | Engine problem
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 60 |  | 49 | Engine problem
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 286 | 244 | 250 | 250 | 160 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
106 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 100 | 0
108 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
109 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 426 | 618 | 500 | 618 | 616 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
** | Nepal |  | 0 | Imported power | 40 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1686 | 1766 | 1822 | 1885 | 1232 | 68
110 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 | 110 |  | Fuel shortage
111 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 2 | 6 | 10 | 10
112 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 134 | 100 | 134 | 134 |  | 60 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
113 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 440 | 540 | 622 | 622 |  | 622 | Unit-2 S/D.
114 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 180 | 0 | 0
115 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 72 | 54 | 150
116 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 218 | 307 | 307 | 307
117 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1014 | 1205 | 1127 | 1223 | 110 | 682
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 26 | 32 |  | 18 | Engine problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 135 | 159 | 165 | 160 | 50 |  | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 141 | 170 | 175 | 45 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 414 | 414 |  |  | FGMO
127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 30 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
128 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 5 | 11
129 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 53 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 95 | 95
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
133 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 412 | 686 | 765 | 765
134 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 61 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 86 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1248 | 1498 | 1918 | 1955 | 538 | 105
135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 152 | 154 | 155 | 155 |  | 119 | Machine problem
137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 90 | 113
140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
141 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 36 | 115 | 115
142 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0
143 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 176 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 367 | 190 | 568 | 383 | 40 | 289
| Total |  |  |  |  | 27740 | 27035 | 9652 | 10666 | 13304.6 | 13564 | 6289 | 4309
A. |  | 2024-11-27 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10666 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7131 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10666 | MW
3 | Day peak Generation : |  |  | 9652 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10439.13 | MW
4 | Evening peak Generation : |  |  | 10666 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 218.5145 | MKWHr | By Solar | 3.8312 | MKWHr
| By Gas : | 117.383 | MKWHr |  | By Oil: | 7.2903 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 51.8019 | MKWHr |  | By Hydro: | 2.2739 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 12.7909 | MKWHr |  | By Wind: | 0.10896 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6289 | MW | Dhaka | 4236.13 | 4236.13 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4309 | MW | Chittagong | 989.5 | 989.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10598 | MW | Khulna | 1152.8 | 1152.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 864.03 | MMCFD | **Import Adani: | Taka | 84547908.49 | Rajshahi | 954.2 | 954.2 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : |  | 321854741.338 | ii) Oil : | Taka | 130863722.75 | Comilla | 909.5 | 909.5 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 367321674.37 | Total | Taka | 904588046.948 | Mymensingh | 849 | 849 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 11066.55 | MKWHr. | Sylhet | 390 | 390 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 956 | MW (W to E) at | 18:00 | hrs | Barisal | 291 | 291 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 956 | MW at | 18:00 | hrs | Rangpur | 667 | 667 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.1°C |  |  | Total | 10439.13 | 10439.13 |  | 0
B. |  | 2024-11-28 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29.1°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13564 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9700 | MW
4 | Reserve(Generation end) |  |  |  | 2764 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 221.2598 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7235 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector(India) : |  |  |  |  | i) Energy | 21.7287 | MKWHr. | ii) HVDC Flow at Peak Time |  | 904 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.3056 | MKWHr. | iii) Maximum HVDC Flow : |  | 905 | MW at | 13:00 | hrs.
* Import Through HVDC C/B Interconnector(Nepal) : |  |  |  |  | i) Energy | 0 | MKWHr.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.56 |  | (b) Today: | 96.44 |  | (c) Rule Curve: |  | 106.5
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-11-27 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | JERA Meghnaghat Power Limited | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | Nepal | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Nepal | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 290 | 0 | 181 | 175 | 50 | 39 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 52 | 35 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 42 | 0 | 120 | 0 | 0 | 0 | 270 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625 | 5 | 0 | 0 | 590 | 0 | 0 | 0 |  | 900 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 157 | 0 | 0 | 165 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 200 | 411 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4330 | 3753 | 8083 | 3037 | 900 | 0 | 1767 | 0 | 40 | 1779 | 92 | 0 | 0 | 52 | 411 | 0 | 5 | 0 | 96.59
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 290 | 0 | 180 | 78 | 50 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 48 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 11 | 0 | 120 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 4 | 0 | 0 | 590 | 0 | 0 | 0 |  | 900 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 165 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 150 | 413 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4074 | 3627 | 7701 | 2946 | 900 | 0 | 1673 | 0 | 6 | 1618 | 93 | 0 | 0 | 48 | 413 | 0 | 4 | 0 | 96.58
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 290 | 0 | 180 | 78 | 50 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 35 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 11 | 0 | 120 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 7 | 0 | 0 | 500 | 0 | 0 | 0 |  | 903 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 163 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 150 | 414 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3969 | 3415 | 7384 | 2867 | 903 | 0 | 1514 | 0 | 0 | 1536 | 93 | 0 | 0 | 50 | 414 | 0 | 7 | 0 | 96.58
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 290 | 0 | 180 | 78 | 50 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 48 | 46 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 11 | 0 | 120 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 7 | 0 | 0 | 500 | 0 | 0 | 0 |  | 902 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 157 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 150 | 417 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3835 | 3399 | 7234 | 2693 | 902 | 0 | 1546 | 0 | 0 | 1527 | 94 | 0 | 0 | 48 | 417 | 0 | 7 | 0 | 96.57
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 290 | 0 | 180 | 78 | 50 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 48 | 46 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 11 | 0 | 121 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 8 | 0 | 0 | 500 | 0 | 0 | 0 |  | 902 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 155 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 150 | 412 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3767 | 3364 | 7131 | 2626 | 902 | 0 | 1513 | 0 | 0 | 1527 | 95 | 0 | 0 | 48 | 412 | 0 | 8 | 0 | 96.57
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 290 | 0 | 180 | 78 | 50 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 54 | 46 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 80 | 0 | 40 | 11 | 0 | 120 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 9 | 0 | 0 | 470 | 0 | 0 | 0 |  | 902 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 158 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 200 | 508 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3830 | 3609 | 7439 | 2714 | 902 | 0 | 1487 | 0 | 6 | 1647 | 96 | 0 | 16 | 54 | 508 | 0 | 9 | 0 | 96.56
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 355 | 0 | 214 | 125 | 50 | 39 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 48 | 44 | 0 | 0 | 0 | 0 | 30 | 0 | 5 | 113 | 0 | 40 | 42 | 0 | 120 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 33 | 0 | 9 | 3 | 0 | 0 | 0 | 225 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 590 | 11 | 0 | 0 | 500 | 5 | 0 | 0 |  | 902 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 157 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 220 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 410 | 2 | 200 | 511 | 10 | 0 | 0 | 6 | 5 | 0 |  | 4301 | 3883 | 8184 | 2968 | 902 | 0 | 1776 | 0 | 85 | 1727 | 96 | 0 | 16 | 48 | 511 | 44 | 11 | 0 | 96.56
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 102 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 17 | 33 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 310 | 0 | 180 | 182 | 50 | 42 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 46 | 32 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 113 | 0 | 62 | 42 | 0 | 122 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 16 | 9 | 0 | 0 | 2 | 280 | 55 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 15 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 685 | 5 | 0 | 0 | 380 | 8 | 0 | 0 |  | 902 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 157 | 0 | 0 | 156 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 510 | 180 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 513 | 10 | 250 | 577 | 58 | 0 | 0 | 14 | 33 | 0 |  | 4526 | 4244 | 8770 | 2991 | 902 | 0 | 1594 | 0 | 222 | 2115 | 96 | 0 | 32 | 46 | 577 | 190 | 5 | 0 | 96.55
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 102 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 22 | 17 | 32 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 280 | 0 | 181 | 182 | 50 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 48 | 27 | 0 | 0 | 1 | 0 | 30 | 0 | 5 | 113 | 0 | 61 | 42 | 0 | 120 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 15 | 6 | 0 | 0 | 0 | 310 | 16 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 8 | 0 | 318 | 0 | 29 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 875 | 0 | 0 | 0 | 360 | 51 | 0 | 0 |  | 902 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 155 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 500 | 180 | 0 | 0 | 2 | 27 | 0 | 0 | 0 | 422 | 19 | 238 | 579 | 107 | 0 | 0 | 38 | 60 | 0 |  | 4690 | 4163 | 8853 | 2924 | 902 | 0 | 1549 | 0 | 185 | 2190 | 96 | 0 | 16 | 48 | 579 | 364 | 0 | 0 | 96.55
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 102 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 20 | 31 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 280 | 0 | 181 | 157 | 50 | 42 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 54 | 26 | 0 | 0 | 2 | 0 | 30 | 0 | 5 | 113 | 0 | 61 | 42 | 0 | 120 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 19 | 0 | 0 | 0 | 310 | 16 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 39 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 0 | 0 | 360 | 66 | 0 | 0 |  | 901 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 154 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 400 | 180 | 0 | 0 | 4 | 64 | 0 | 0 | 0 | 372 | 28 | 150 | 462 | 147 | 0 | 0 | 51 | 82 | 0 |  | 4974 | 3925 | 8899 | 2857 | 901 | 0 | 1515 | 0 | 165 | 2300 | 96 | 0 | 16 | 54 | 462 | 533 | 0 | 0 | 96.54
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 102 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 22 | 25 | 30 | 8 | 0 | 96 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 295 | 0 | 195 | 187 | 50 | 42 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 54 | 24 | 0 | 0 | 2 | 0 | 30 | 0 | 5 | 80 | 0 | 59 | 42 | 0 | 120 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 16 | 0 | 0 | 0 | 311 | 16 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 46 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 1237 | 1 | 0 | 0 | 360 | 67 | 0 | 0 |  | 902 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 153 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 420 | 220 | 0 | 0 | 5 | 77 | 0 | 0 | 0 | 373 | 33 | 150 | 413 | 170 | 0 | 0 | 57 | 93 | 0 |  | 5035 | 4083 | 9118 | 2925 | 902 | 0 | 1605 | 0 | 173 | 2333 | 96 | 0 | 16 | 54 | 413 | 600 | 1 | 0 | 96.53
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 80 | 0 | 102 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 22 | 25 | 30 | 25 | 0 | 96 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 340 | 0 | 200 | 187 | 50 | 36 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 56 | 10 | 0 | 0 | 2 | 0 | 30 | 0 | 5 | 113 | 0 | 59 | 42 | 0 | 119 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 13 | 0 | 0 | 0 | 386 | 16 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 35 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 1240 | 0 | 0 | 0 | 360 | 68 | 0 | 21 |  | 904 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 152 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 440 | 220 | 0 | 0 | 5 | 70 | 0 | 0 | 0 | 426 | 34 | 218 | 412 | 176 | 0 | 0 | 61 | 86 | 0 |  | 5337 | 4315 | 9652 | 3193 | 904 | 0 | 1700 | 0 | 190 | 2476 | 96 | 0 | 37 | 56 | 412 | 588 | 0 | 0 | 96.53
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 201 | 0 | 102 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 22 | 25 | 31 | 34 | 0 | 94 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 300 | 0 | 181 | 187 | 50 | 37 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 64 | 10 | 0 | 0 | 2 | 0 | 30 | 0 | 5 | 113 | 0 | 60 | 42 | 0 | 80 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 23 | 11 | 0 | 0 | 0 | 386 | 28 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 48 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 1240 | 0 | 0 | 0 | 350 | 64 | 0 | 14 |  | 905 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 147 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 510 | 220 | 0 | 0 | 4 | 72 | 0 | 0 | 0 | 458 | 32 | 250 | 414 | 163 | 0 | 0 | 56 | 96 | 0 |  | 5336 | 4461 | 9797 | 3140 | 905 | 0 | 1694 | 0 | 246 | 2608 | 94 | 0 | 46 | 64 | 414 | 586 | 0 | 0 | 96.53
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 180 | 0 | 102 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 22 | 25 | 31 | 16 | 0 | 94 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 310 | 0 | 197 | 187 | 50 | 37 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 66 | 10 | 0 | 0 | 2 | 0 | 28 | 0 | 22 | 113 | 0 | 40 | 86 | 0 | 20 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 8 | 0 | 0 | 0 | 386 | 8 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 29 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 1238 | 0 | 0 | 0 | 350 | 36 | 0 | 15 |  | 905 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 151 | 0 | 0 | 170 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 490 | 180 | 0 | 0 | 3 | 32 | 0 | 0 | 0 | 418 | 23 | 188 | 414 | 135 | 0 | 0 | 44 | 70 | 0 |  | 5152 | 4040 | 9192 | 3032 | 905 | 0 | 1591 | 0 | 163 | 2485 | 94 | 0 | 31 | 66 | 414 | 411 | 0 | 0 | 96.53
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 184 | 0 | 50 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 22 | 25 | 31 | 16 | 0 | 94 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 285 | 0 | 182 | 187 | 50 | 37 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 53 | 10 | 0 | 0 | 2 | 0 | 28 | 0 | 33 | 113 | 0 | 59 | 86 | 0 | 20 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 10 | 0 | 17 | 8 | 0 | 0 | 0 | 386 | 18 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 27 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 1233 | 0 | 0 | 0 | 400 | 39 | 0 | 16 |  | 903 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 150 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 400 | 180 | 0 | 0 | 2 | 20 | 0 | 0 | 0 | 408 | 17 | 180 | 454 | 95 | 0 | 0 | 31 | 52 | 0 |  | 5209 | 3924 | 9133 | 3084 | 903 | 0 | 1701 | 0 | 123 | 2371 | 94 | 0 | 36 | 53 | 454 | 314 | 0 | 0 | 96.52
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 0 | 10 | 0 | 0 | 0 | 270 | 0 | 128 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 15 | 25 | 31 | 16 | 0 | 94 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 280 | 0 | 182 | 187 | 50 | 38 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 53 | 10 | 0 | 0 | 0 | 0 | 28 | 0 | 33 | 113 | 0 | 59 | 86 | 0 | 50 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 1 | 0 | 0 | 0 | 386 | 45 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 9 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1240 | 0 | 0 | 0 | 400 | 14 | 0 | 18 |  | 905 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 154 | 0 | 0 | 150 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 180 | 0 | 2 | 0 | 12 | 0 | 0 | 0 | 411 | 7 | 180 | 461 | 36 | 0 | 0 | 10 | 24 | 0 |  | 5347 | 3783 | 9130 | 3216 | 905 | 0 | 1704 | 0 | 151 | 2375 | 94 | 0 | 50 | 53 | 461 | 121 | 0 | 0 | 96.51
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 |  | 0 | 0 | 19 | 0 | 0 | 0 | 335 | 0 | 115 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 23 | 15 | 25 | 31 | 16 | 0 | 94 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 0 | 6 | 0 | 5 | 0 | 0 | 0 | 310 | 0 | 181 | 187 | 50 | 37 | 0 | 0 | 51 | 0 | 0 | 3 | 0 | 0 | 0 | 15 | 59 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 60 | 50 | 0 | 64 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 25 | 0 | 6 | 11 | 20 | 342 | 55 | 17 | 2 | 0 | 30 | 54 | 1 | 0 | 4 | 17 | 296 | 0 | 0 | 19 | 11 | 0 | 9 | 0 | 8 | 17 | 0 | 17 | 0 | 1005 | 0 | 0 | 0 | 400 | 1 | 0 | 18 |  | 904 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 5 | 0 | 0 | 153 | 0 | 0 | 156 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 180 | 0 | 54 | 0 | 2 | 30 | 0 | 0 | 500 | 0 | 230 | 502 | 3 | 0 | 0 | 0 | 1 | 0 |  | 5381 | 4028 | 9409 | 3224 | 904 | 0 | 1655 | 0 | 505 | 2328 | 94 | 0 | 131 | 59 | 502 | 7 | 0 | 0 | 96.51
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 0 | 25 | 0 | 0 | 0 | 335 | 0 | 96 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 14 | 0 | 17 | 0 | 23 | 22 | 25 | 31 | 16 | 0 | 96 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 7 | 23 | 0 | 5 | 0 | 0 | 0 | 310 | 0 | 180 | 189 | 50 | 42 | 0 | 0 | 51 | 0 | 16 | 8 | 0 | 0 | 0 | 18 | 57 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 61 | 50 | 0 | 66 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 83 | 0 | 50 | 0 | 20 | 17 | 38 | 342 | 64 | 34 | 17 | 0 | 65 | 54 | 19 | 0 | 49 | 48 | 277 | 0 | 0 | 72 | 53 | 0 | 54 | 0 | 48 | 36 | 0 | 35 | 0 | 970 | 3 | 0 | 0 | 550 | 0 | 0 | 20 |  | 904 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 14 | 0 | 22 | 0 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 159 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 72 | 0 | 0 | 36 | 0 | 0 | 618 | 0 | 307 | 686 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6007 | 4659 | 10666 | 3196 | 904 | 0 | 1858 | 0 | 1038 | 2589 | 96 | 0 | 239 | 57 | 686 | 0 | 3 | 0 | 96.5
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 0 | 37 | 0 | 0 | 0 | 335 | 0 | 100 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 23 | 22 | 25 | 31 | 16 | 0 | 96 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 17 | 26 | 0 | 12 | 0 | 0 | 0 | 335 | 0 | 198 | 177 | 50 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 58 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 61 | 50 | 0 | 66 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 83 | 0 | 45 | 0 | 12 | 0 | 60 | 342 | 64 | 17 | 0 | 0 | 65 | 54 | 17 | 0 | 73 | 12 | 296 | 0 | 0 | 54 | 72 | 0 | 28 | 0 | 16 | 18 | 0 | 0 | 0 | 770 | 6 | 0 | 0 | 480 | 0 | 0 | 0 |  | 904 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 151 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 220 | 0 | 54 | 0 | 0 | 50 | 0 | 0 | 619 | 0 | 307 | 757 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5603 | 4805 | 10408 | 3281 | 904 | 0 | 1851 | 0 | 894 | 2446 | 96 | 0 | 115 | 58 | 757 | 0 | 6 | 0 | 96.49
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 0 | 90 | 0 | 0 | 0 | 335 | 0 | 96 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 23 | 22 | 25 | 31 | 16 | 0 | 96 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 26 | 0 | 25 | 0 | 0 | 0 | 310 | 0 | 181 | 177 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 58 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 62 | 50 | 0 | 72 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 25 | 0 | 12 | 0 | 60 | 342 | 64 | 17 | 0 | 0 | 65 | 54 | 17 | 0 | 73 | 12 | 310 | 0 | 0 | 54 | 72 | 0 | 17 | 0 | 16 | 18 | 0 | 0 | 0 | 677 | 10 | 0 | 0 | 480 | 0 | 0 | 0 |  | 904 | 0 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 144 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 220 | 0 | 54 | 0 | 0 | 56 | 0 | 0 | 617 | 0 | 307 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5481 | 4808 | 10289 | 3247 | 904 | 0 | 1917 | 0 | 824 | 2364 | 96 | 0 | 115 | 58 | 754 | 0 | 10 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 0 | 112 | 0 | 0 | 0 | 335 | 0 | 101 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 23 | 22 | 25 | 31 | 16 | 0 | 96 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 26 | 0 | 25 | 0 | 0 | 0 | 355 | 0 | 187 | 177 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 60 | 50 | 0 | 73 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 25 | 0 | 12 | 0 | 50 | 342 | 64 | 0 | 0 | 0 | 30 | 54 | 0 | 0 | 27 | 12 | 320 | 0 | 0 | 17 | 35 | 0 | 17 | 0 | 16 | 18 | 0 | 0 | 0 | 610 | 13 | 0 | 0 | 480 | 0 | 0 | 0 |  | 904 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 141 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 307 | 757 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5288 | 4762 | 10050 | 3309 | 904 | 0 | 1939 | 0 | 569 | 2308 | 96 | 0 | 99 | 56 | 757 | 0 | 13 | 0 | 96.49
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 0 | 152 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 22 | 25 | 31 | 8 | 0 | 96 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 12 | 0 | 28 | 0 | 0 | 0 | 310 | 0 | 181 | 178 | 50 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 61 | 50 | 0 | 96 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 15 | 0 | 0 | 0 | 30 | 340 | 64 | 0 | 0 | 0 | 30 | 54 | 0 | 0 | 27 | 0 | 320 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 611 | 10 | 0 | 0 | 590 | 0 | 0 | 0 |  | 904 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 141 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 307 | 758 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5128 | 4764 | 9892 | 3178 | 904 | 0 | 2093 | 0 | 416 | 2314 | 96 | 0 | 67 | 56 | 758 | 0 | 10 | 0 | 96.49
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 0 | 126 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 22 | 22 | 31 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 12 | 0 | 36 | 0 | 0 | 0 | 290 | 0 | 180 | 192 | 50 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 62 | 51 | 0 | 102 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 15 | 0 | 0 | 0 | 30 | 340 | 45 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 26 | 0 | 320 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 3 | 0 | 0 | 590 | 0 | 0 | 0 |  | 905 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 151 | 0 | 0 | 142 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 110 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 307 | 759 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4932 | 4534 | 9466 | 3122 | 905 | 0 | 1903 | 0 | 302 | 2306 | 96 | 0 | 16 | 54 | 759 | 0 | 3 | 0 | 96.48
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 |  | 0 | 0 | 157 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 22 | 17 | 32 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 345 | 0 | 211 | 197 | 50 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 61 | 51 | 0 | 111 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 10 | 0 | 0 | 583 | 0 | 0 | 0 |  | 904 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 138 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 0 | 200 | 744 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4888 | 4120 | 9008 | 3179 | 904 | 0 | 1960 | 0 | 93 | 1956 | 94 | 0 | 16 | 52 | 744 | 0 | 10 | 0 | 96.47
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 135 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 17 | 32 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 310 | 0 | 180 | 199 | 50 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 40 | 51 | 0 | 171 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 9 | 0 | 0 | 550 | 0 | 0 | 0 |  | 903 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 138 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 250 | 570 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4808 | 3879 | 8687 | 3206 | 903 | 0 | 1860 | 0 | 48 | 1939 | 96 | 0 | 0 | 56 | 570 | 0 | 9 | 0 | 96.46
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9644400 | 0 |  | 0 | 0 | 696524 | 0 | 0 | 0 | 2803283 | 0 | 2742000 | 0 | 813024 | 507840 | 0 | 0 | 0 | 0 | 63720 | 0 | 30300 | 0 | 494400 | 511920 | 506880 | 769400 | 202560 | 0 | 2273891 | 0 | 0 | 0 | 0 | 5121044 | 0 | 0 | 0 |  | 427680 | 0 | 33050 | 0 | 24960 | 113280 | 0 | 540000 | 0 | 0 | 0 | 7581500 | 0 | 4566000 | 3830545 | 1190690 | 799128 | 0 | 0 | 938056 | 0 | 19472 | 14755 | 0 | 0 | 0 | 327930 | 1305600 | 551040 | 0 | 0 | 12150 | 0 | 497280 | 0 | 206712 | 2470827 | 0 | 1275072 | 1019520 | 0 | 3045950 | 0 | 0 | 0 | 7086500 | 339168 | 58128 | 0 | 0 | 0 | 0 | 764400 | 0 | 367200 | 106245 | 67200 | 36000 | 257600 | 8152000 | 726000 | 76800 | 35964 | 24961 | 250909 | 312361 | 63650 | 0 | 280560 | 99840 | 7788000 | 0 | 292380 | 167040 | 279764 | 0 | 119520 | 172465 | 131520 | 135000 | 0 | 35127 | 0 | 20329089 | 108960 | 0 | 0 | 11277273 | 437000 | 0 | 102000 |  | 21728727 | 0 | 6418944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2610000 | 128782 | 0 | 0 | 0 | 0 | 0 | 0 | 221840 | 0 | 0 | 19547 | 0 | 35793 | 0 | 0 | 190224 | 0 | 0 | 3781000 | 0 | 0 | 3789100 | 0 | 3672073 | 0 | 0 | 0 | 0 | 0 | 8952436 | 0 | 0 | 0 | 0 | 0 | 0 | 34593 | 0 | 11255273 | 4790310 | 0 | 319200 | 29100 | 428400 | 134784 | 0 | 0 | 11134550 | 204113 | 5302000 | 12790909 | 1097310 | 0 | 2960 | 366000 | 623562 | 0 |  | 118453007 | 100061530 | 218514537 | 75445554 | 21728727 | 0 | 41937485 | 0 | 6315591 | 51801912 | 2273891 | 0 | 974669 | 1305600 | 12790909 | 3831239 | 108960 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27775872 | 0 |  | 0 | 0 | 2382112.08 | 0 | 0 | 0 | 8550013.15 | 0 | 14669700 | 0 | 14593780.8 | 9862252.8 | 0 | 0 | 0 | 0 | 1163527.2 | 0 | 554187 | 0 | 370800 | 0 | 0 | 0 | 3627849.6 | 0 | 0 | 0 | 0 | 0 | 0 | 16336130.36 | 0 | 0 | 0 |  | 7522891.2 | 0 | 591925.5 | 0 | 488467.2 | 1864588.8 | 0 | 0 | 0 | 0 | 0 | 21152385 | 0 | 15159120 | 12832325.75 | 3845928.7 | 2693061.36 | 0 | 0 | 3761604.56 | 0 | 348743.52 | 266475.3 | 0 | 0 | 0 | 245947.5 | 8564736 | 1713734.4 | 0 | 0 | 0 | 0 | 1854854.4 | 0 | 940539.6 | 8450228.34 | 0 | 7076649.6 | 5321894.4 | 0 | 8498200.5 | 0 | 0 | 0 | 21897285 | 254376 | 44177.28 | 0 | 0 | 0 | 0 | 14684124 | 0 | 6466392 | 0 | 1196832 | 624600 | 4271008 | 21602800 | 13837560 | 1440768 | 645194.16 | 0 | 4102362.15 | 6072297.84 | 1141881 | 0 | 5445669.6 | 1778150.4 | 20716080 | 0 | 0 | 3055161.6 | 4694439.92 | 0 | 2135822.4 | 0 | 2369990.4 | 2286900 | 0 | 494588.16 | 0 | 141693750.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 61057722.87 | 0 | 18935884.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8247600 | 610426.68 | 0 | 0 | 0 | 0 | 0 | 0 | 3729130.4 | 0 | 0 | 350086.77 | 0 | 641052.63 | 0 | 0 | 143999.568 | 0 | 0 | 31911640 | 0 | 0 | 12504030 | 0 | 12228003.09 | 0 | 0 | 0 | 0 | 0 | 26141113.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72934169.04 | 14897864.1 | 0 | 6176520 | 0 | 0 | 2338502.4 | 0 | 0 | 81282215 | 0 | 39499900 | 84547908.49 | 0 | 0 | 0 | 0 | 0 | 0 |  | 496032736.86 | 478177768.958 | 974210505.818 | 224619347.708 | 61057722.87 | 0 | 97235393.63 | 0 | 114845942.97 | 367321674.37 | 0 | 0 | 16017779.78 | 8564736 | 84547908.49 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 80 | 0 | 102 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 22 | 25 | 30 | 25 | 0 | 96 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 340 | 0 | 200 | 187 | 50 | 36 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 56 | 10 | 0 | 0 | 2 | 0 | 30 | 0 | 5 | 113 | 0 | 59 | 42 | 0 | 119 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 13 | 0 | 0 | 0 | 386 | 16 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 35 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 1240 | 0 | 0 | 0 | 360 | 68 | 0 | 21 |  | 904 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 152 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 440 | 220 | 0 | 0 | 5 | 70 | 0 | 0 | 0 | 426 | 34 | 218 | 412 | 176 | 0 | 0 | 61 | 86 | 0 |  | 9652 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 0 | 25 | 0 | 0 | 0 | 335 | 0 | 96 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 14 | 0 | 17 | 0 | 23 | 22 | 25 | 31 | 16 | 0 | 96 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 7 | 23 | 0 | 5 | 0 | 0 | 0 | 310 | 0 | 180 | 189 | 50 | 42 | 0 | 0 | 51 | 0 | 16 | 8 | 0 | 0 | 0 | 18 | 57 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 61 | 50 | 0 | 66 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 83 | 0 | 50 | 0 | 20 | 17 | 38 | 342 | 64 | 34 | 17 | 0 | 65 | 54 | 19 | 0 | 49 | 48 | 277 | 0 | 0 | 72 | 53 | 0 | 54 | 0 | 48 | 36 | 0 | 35 | 0 | 970 | 3 | 0 | 0 | 550 | 0 | 0 | 20 |  | 904 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 14 | 0 | 22 | 0 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 159 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 72 | 0 | 0 | 36 | 0 | 0 | 618 | 0 | 307 | 686 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10666 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 0 | 155 | 0 | 0 | 55 | 0 | 0 | 200 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 22 | 25 | 33 | 25 | 0 | 96 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 24 | 64 | 68 | 0 | 50 | 50 | 0 | 15 | 0 | 0 |  | 310 | 0 | 200 | 180 | 50 | 42 | 0 | 0 | 51 | 0 | 45 | 52 | 0 | 0 |  | 18 | 82 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 112 | 0 | 62 | 50 | 0 | 174 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 300 | 0 | 0 | 96 | 0 | 149 | 0 | 100 | 200 | 140 | 385 | 55 | 105 | 85 | 0 | 65 | 54 | 110 | 114 | 95 | 100 | 380 | 17 | 0 | 162 | 53 | 0 | 53 | 0 | 51 | 36 | 0 | 160 | 0 | 820 | 15 | 0 | 0 | 550 |  |  |  |  | 922 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 40 | 25 | 95 | 0 | 0 | 32 | 0 | 30 | 0 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 160 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 95 | 0 | 113 | 0 | 0 | 113 | 622 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 618 | 0 | 307 | 765 | 0 | 0 |  |  |  | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 |  | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 55 | 0 | 0 | 150 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 25 | 22 | 25 | 33 | 25 | 0 | 96 | 0 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 24 | 56 | 51 | 0 | 50 | 50 | 0 | 3 | 0 | 0 | 0 | 310 | 0 | 200 | 180 | 50 | 42 | 0 | 0 | 51 | 0 | 30 | 52 | 0 | 0 |  | 18 | 66 | 30 | 0 | 0 | 1.6 | 0 | 0 | 0 | 5 | 112 | 0 | 62 | 50 | 0 | 174 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 300 | 0 | 0 | 96 | 0 | 52 | 20 | 100 | 200 | 140 | 385 | 55 | 50 | 85 | 5 | 50 | 54 | 110 | 114 | 95 | 100 | 360 | 0 | 50 | 100 | 35 | 0 | 17 | 35 | 16 | 36 | 0 | 17 | 0 | 1224 | 15 | 0 | 0 | 550 | 70 |  |  |  | 922 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 26 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 165 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 95 | 0 | 90 | 0 | 8 | 113 | 622 | 0 |  | 54 | 6 | 100 | 115 | 0 | 0 | 500 | 30 | 307 | 765 | 170 | 0 |  | 29 | 47 | 0 |  |  |  |  | gas | hvdc |  | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 22 | 17 | 32 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 285 | 0 | 181 | 182 | 50 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 26 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 80 | 0 | 40 | 51 | 0 | 174 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 9 | 0 | 0 | 0 | 310 | 56 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 17 | 0 | 0 | 0 | 0 | 11 | 0 | 2 | 0 | 0 | 0 | 820 | 0 | 0 | 0 | 550 | 19 | 0 | 0 | 0 | 905 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 155 | 0 | 0 | 160 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 450 | 0 | 0 | 0 | 1 | 16 | 0 | 0 | 0 | 410 | 11 | 250 | 579 | 28 | 0 | 0 | 16 | 31 | 0 | 0 |  |  |  | 117383039 | 21728727 |  | 0 | 51801912 | 7290260 | 1305600 | 3831239 | 108960 | 2273891 |  |  |  | 205723628
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [10 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 |  | 299798 | [7 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [14 empty] | 499227 |  | 499229 |  |  | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [11 empty] | 117.383 | 21.7287 |  | 0 | 51.8019 | 7.2903 | 1.3056 | 3.8312 | 0.10896 | 2.2739
| Minimum Generation |  | 7131 | 5:00
| Highest Generation |  | 10666 | 18:00 | [129 empty] | 0 | [77 empty] | 205.7236
| Day Peak Generation |  | 9652 | 12:00
| Evening Peak Generation |  | 10666 | 18:00 | [207 empty] | 202699852
| HVDC Max Flow |  | 905 | 13:00 | [207 empty] | 202.6999
| HVDC EvPeak Flow |  | 904 | 18:00
| Load factor L.F |  | 85.36% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-11-28
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-11-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9652 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7235
Evening Peak Generation : |  |  | 10666 | MW Hour : | 18:00 | Available Max Generation : |  | 13564
E.P. Demand (at gen end) : |  |  | 10666 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10800
Maximum Generation : |  |  | 10666 | MW Hour : | 18:00 | Reserve(Generation end) |  | 2764
Total Gen. (MKWH) : |  |  | 218.5145 | System Load Factor : | 85.36% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 956 | MW at | 18:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-11-28
Actual : |  | 96.44 | Ft.(MSL) , | Rule curve : | 106.5 | Ft.( MSL )
Gas Consumed : |  | Total = | 864.03 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 321854741.338 | Adani : | 84547908.49
|  |  | Coal : | 367321674.37 | Oil: | 130863722.75 | Total: | 904588046.948
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3725.7237 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1018.712 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1425.4791 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1237.5835 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1019.0346 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 757.155 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 425.2106 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 353.6298 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 691.6548 |  |  | 0 | 0%
Total |  | 0 |  | 10654.1832 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:00 |  | Bogura 400/230kV S/S ATR-03 HT Project Work S/D Due to LA Change Bus-2 B phase
08:02 |  | Bogura 400/230kV S/S 400 KV BUS-02 Project Work S/D Due to LA Chance B-Phase
08:15 | 17:11 | Gopalganj (O) - Gopalgan (N) Ckt-1 Scheduled S/D from Gopalganj 400/132kV end Due to
Annual maintenance at Gopalganj 132kV end. and from Gopalganj 132/33kV end Due to Annual
Maintenance
08:16 | 16:00 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to SD taken
by Cox'sBazar GSS and from Coxsbazar 132/33kV end Due to Annual maintenance (Cox Side)
08:19 | 18:02 | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Annual
Maintenance Work and from Kaliakoir 400/230/132kV end Due to Annual Maintenance.
08:23 | 18:15 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Annual Maintenance.
08:25 | 17:16 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-02 (714T) LT Scheduled S/D Due to A/M
08:25 | 17:15 | Rajshahi 230/132/33kV S/S 230/132 kV ATR-02 (714T) HT Scheduled S/D Due to A/M
08:29 | 16:24 | Sreepur 230/132/33kV S/S 230 kV Bus-1 Scheduled S/D Due to Annual Maintenance
08:30 | 14:30 | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end Due to
Annual Maintenance work. and from Khulna (C) end Due to Due to Annual Maintenance
08:40 | 17:47 | Kallyanpur 132/33kV S/S GT-2 (132kV) LT Scheduled S/D Due to For DPDC
08:41 | 17:46 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to For DPDC
08:45 | 16:17 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end Due to
Annual maintenance
08:45 | 16:30 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D Due to
Annual maintenance
08:45 | 16:30 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to
Annual maintenance
08:45 | 16:27 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance
08:46 | 16:26 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance
08:46 | 15:13 | Meghnaghat 230/132kV S/S Bus1 Scheduled S/D Due to For Annual maintenance
08:59 | 14:20 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to Annual maintenance
08:59 | 14:12 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to Annual maintenance
09:02 | 16:27 | Bhulta 400/230kV S/S 230kV Bus-01 Scheduled S/D
09:08 | 16:26 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Scheduled S/D from Purbasadipur 132/33kV end Due
to Annual Maintenance and from Thakurgaon 132/33kV end Due to Annual maintenance
09:08 | 16:48 | Barapukuria-Rangpur 132 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual maintenance work and from Rangpur 132/33kVend.
09:10 | 15:22 | Savar 132/33kV S/S Capacitor Bank-3 Scheduled S/D Due to Annual Maintenance
09:10 | 15:22 | Savar 132/33kV S/S Capacitor Bank-1 Scheduled S/D Due to Annual Maintenance
09:10 | 15:22 | Savar 132/33kV S/S Capacitor Bank-2 Scheduled S/D Due to Annual Maintenance
09:12 | 13:28 | Sylhet (South) S/S Trafo-1 LT Scheduled S/D Due to annual maintenance purpose
09:13 | 13:27 | Sylhet (South) S/S Trafo-1 HT Scheduled S/D Due to annual maintenance purpose
09:47 | 17:15 | Aminbazar-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Annual maintenance at Aminbazar end. and from Aminbazar 400/230/132kV end Due to Dead
Line checking
09:48 |  | Mymensingh 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to Annual maintenance
works
09:49 |  | Mymensingh 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Annual maintenance
works
10:00 | 17:28 | Bhulta-Rampura 230 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Work by
Haripur substation because of deadline Check. and from Bhulta 400/230kV end Due to S/D
taken by Haripur Grid SS for dead line checking.
10:03 | 17:14 | Gopalganj 400/132kV S/S 230 kV Bus-01 Scheduled S/D
10:55 | 15:50 | Aminbazar 400/230/132kV S/S ATR-01 HT Scheduled S/D Due to Annual meintanance
10:55 | 17:01 | Aminbazar 400/230/132kV S/S ATR-01 LT Scheduled S/D Due to Annual maintenance
11:20 | 13:39 | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Relay Testing
11:20 | 13:40 | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Relay Testing
11:53 |  | Siddirganj CCPP 335MW GT was sync.
12:00 |  | Day peak Generation is 9652 MW
13:56 | 15:16 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Relay Testing
13:56 | 15:16 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Relay Testing
14:39 | 17:02 | Cumilla(S) 132/33kV S/S Tripura Ckt-1 Scheduled S/D Due to For installation of ABT meter
under SAMAST project inTripura end.
15:10 |  | Siddirganj CCPP 335MW ST was sync.
15:47 |  | Meghnaghat Summit CCPP 335 MW GT-2 was sync.
15:52 |  | Sylhet CCPP 225 MW ST was sync.
| 16:05 | Shahjadpur 132/33kV S/S T-2(415T) HT is restored.
| 16:06 | Shahjadpur 132/33kV S/S T-2(415T) LT is restored.
16:36 | 17:14 | Barguna 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Incomer-2 এর সিটিতে Abnormal
Sound হয়ার কারনে
16:36 | 17:15 | Barguna 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Incomer-2 এর সিটিতে Abnormal
Sound হয়ার কারনে জরুরী ভিক্তিতে Transfomer -2 এর Shutdown প্রয়োজন ।
17:14 | 18:16 | Cumilla(S) 132/33kV S/S Tripura Ckt-2 Scheduled S/D Due to working on Tripura end
18:00 |  | Evening Peak Generation: 10666 MW.
18:00 |  | peak generation 10666 MW
18:49 |  | Meghnaghat Summit CCPP 335 MW ST was sync.
19:08 |  | Cumilla (North)- Muradnagar 132kV ckt-1 was switched ON.
19:10 |  | Daudkandi - Muradnagar 132kV ckt-1 was switched ON.
19:12 |  | Muradnagar 132kV bus-coupler was closed.
19:28 |  | Muradnagar 132/33kV T-2 was charged.
21:24 |  | Bhola Nutan Biddyut CCPP GT-2 was shutdown.
23:03 |  | Bhola Nutan Biddyut CCPP ST was shutdown.
00:46 |  | Bhola Nutan Biddyut CCPP GT-1 was shutdown.
05:00 |  | Min. Gen. 7236 MW
06:01 |  | GPH 230/33kV S/S HATHAZARI-2 Scheduled S/D Due to LILO PERFORMING , ERS STABILIZATION
06:45 |  | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Dead line cheeking
06:52 |  | Cumilla(N)-Daudkandi 132 kV Ckt-2 Project Work S/D from Cumilla(N) 230/132/33kV end Due
to 132/33 KV Muradnogor SS commissioning
06:52 |  | Cumilla(N)-Daudkandi 132 kV Ckt-1 Project Work S/D from Cumilla(N) 230/132/33kV end Due
to 132/33 KV Muradnogor S/S commissioning
07:14 |  | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to Due to
annual maintenance work
07:30 |  | Keranigonj 230/132/33kV S/S Earthing Trafo-2 LT Scheduled S/D
07:30 |  | Keranigonj 230/132/33kV S/S Earthing Trafo-2 HT Scheduled S/D Due to None
07:31 |  | Keranigonj 230/132/33kV S/S ATR-2 LT Scheduled S/D Due to Annual Maintenance.
07:31 |  | Keranigonj 230/132/33kV S/S ATR-2 HT Scheduled S/D Due to Annual Maintenance.
07:43 |  | Bakulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Bakulia 132/33kV end Due to Annual
Diameter Maintenance of Bakalia- Khulshi (express) Ckt.
07:44 |  | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to
Annual Maintenance.
07:50 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Scheduled S/D from Purbasadipur 132/33kV end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-11-27
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 412 | 9644400
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 25 | 696524 | St Syn Proces
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 96 | 2742000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 2803283 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 813024 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 14 | 63720 | Low demand
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 507840 | Low demand
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 30300 | Reserve
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1006320 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 506880 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 769400
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 202560 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 50 | 367200 | Low demand
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 76800 | Low demand
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 167040 | Low demand
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 172465
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 135000
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 550 | 11277273
| JERA Meghnaghat Power Limited |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 1822 | 31982029
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 106245
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 23 | 113280 | Low demand
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 96 | 2273891 | Low water level
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5121044
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 35964 | Low demand
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Low demand
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 33050 | Low demand
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 20 | 67200 | Low demand
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 5 | 540000
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 7 | 24960 | Low demand
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24961
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 65 | 250909 | High viltage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 312361
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 19 | 63650 | Low demand
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 48 | 99840 | Fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 279764 | Low demand
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 35 | 35127 | Low demand
55 | SS Power I |  | IPP | 2*612 | 1224 | 970 | 20329089
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 3 | 108960
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 0 | 0 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1657 | 29820295
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4566000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7581500 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 799128 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 189 | 3830545
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 938056
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 38 | 257600 | Low demand
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 16 | 19472 | Low demand
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1190690 | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 36000 | Low demand
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 57 | 1305600
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 14755 | Low demand
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 327930 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 49 | 280560 | Low demand
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 48 | 131520 | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 437000
| Cumilla Area Total |  |  |  | 2917 | 1073 | 21716356
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 11 | 551040 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12150
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 83 | 764400 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 64 | 726000 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 292380
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 427680
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 54 | 119520
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 20 | 102000
| Mymensingh Area Total |  |  |  | 646 | 256 | 2995170
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 497280 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 113 | 2470827 | ST under Maint
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 0 | 0 | 0 | Contact expired
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 206712
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 58128 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1275072
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 1019520 | Gas shortage
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 66 | 3045950 | ST under Maint
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 339168 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7086500 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 342 | 8152000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 277 | 7788000 | FGMO
| Sylhet Area Total |  |  |  | 2366 | 1199 | 31939157
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 904 | 21728727
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 244 | 6418944 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 428400
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 618 | 11134550 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Nepal |  | Imported power | 40 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1766 | 39710621
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 6 | 128782 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 100 | 2610000 | Low demand
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 540 | 11255273 | Unit-2 under overhauling
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 180 | 4790310 | Low demand
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 72 | 319200 | Low demand
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 5302000
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 2960
| Barisal Area Total |  |  |  | 2236 | 1205 | 24408525
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | NENP
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 19547 | Low demand
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 159 | 3789100 | FGMO
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 141 | 3672073
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 8952436 | FGMO
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 35793 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 190224
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 221840 | Low demand
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 29100
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 686 | 12790909
135 | Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 366000
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 623562
| Rajshahi Area Total |  |  |  | 3449 | 1498 | 30690584
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 154 | 3781000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | Reserve
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34593
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 36 | 134784 | Low demand
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 204113
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 1097310
| Rangpur Area Total |  |  |  | 950 | 190 | 5251800
| Total |  |  |  | 27035 | 10666 | 218514537
| Eastern Grid Total |  |  |  | 16701 | 6007 | 118453007
| Western Grid Total |  |  |  | 10334 | 4659 | 100061530
| National Grid Total |  |  |  | 27035 | 10666 | 218514537
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-11-27
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7317.03 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3122.9 | MW
i) Dhaka area |  |  | 4102.53 |  | MW | i) Khulna area |  |  |  | 1159 | MW
ii) Chattogram area |  |  | 1042.5 |  | MW | ii) Barishal area |  |  |  | 283.7 | MW
iii) Cumilla area |  |  | 923 |  | MW | iii) Rajshahi area |  |  |  | 957.2 | MW
iv) Mymensingh area |  |  | 845 |  | MW | iv) Rangpur area |  |  |  | 723 | MW
v) Sylhet area |  |  | 404 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10439.93 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 20:00 | 67 | Jashore | 91 | 13:00 | 133 | Rajbari | 52 | 18:00
2 | AKSML | 105 | 01:00 | 68 | Jhenaidah | 83 | 18:00 | 134 | Rajendrapur | 96 | 18:30
3 | Aftabnagar | 26 | 13:00 | 69 | Joydebpur | 129 | 18:00 | 135 | Rajshahi | 81 | 18:00
4 | Agargaon | 79 | 13:00 | 70 | Joypurhat | 41 | 18:00 | 136 | Rajshahi-230 | 43 | 13:00
5 | Agrabad | 70 | 18:00 | 71 | Juldah | 11 | 02:00 | 137 | Ramganj | 80 | 18:00
6 | Amnura | 35 | 18:00 | 72 | KSRM | 31 | 10:00 | 138 | Rampur | 27 | 18:00
7 | Ashuganj | 86.5 | 18:30 | 73 | Kabirpur | 228 | 18:00 | 139 | Rangamati | 12 | 18:00
8 | BSRM | 89 | 18:30 | 74 | Kachua | 45 | 19:30 | 140 | Rangpur | 96 | 18:30
9 | Bagerhat | 61 | 18:00 | 75 | Kallyanpur | 66 | 18:00 | 141 | Ruppur | 6 | 12:00
10 | Bakulia | 69 | 18:00 | 76 | Kalurghat | 28 | 10:00 | 142 | SSM | 0 | 00:00
11 | Banani | 48.8 | 13:00 | 77 | Kamrangirchar | 55.8 | 13:00 | 143 | Saidpur | 90 | 18:00
12 | Bangabhaban | 10 | 10:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 80 | 18:00
13 | Barapukuria | 44 | 19:00 | 79 | Kazla | 96 | 12:00 | 145 | Satmasjid | 79 | 13:00
14 | Barguna | 14 | 19:30 | 80 | Keranigonj | 60 | 13:00 | 146 | Savar | 184 | 12:00
15 | Barishal | 87 | 13:00 | 81 | Khagrachori | 20 | 18:00 | 147 | SevenRings | 17.32 | 06:00
16 | Barishal-230 | 54 | 18:00 | 82 | Khulna | 64 | 13:00 | 148 | ShahCement | 24 | 17:00
17 | Baroaulia | 60 | 11:00 | 83 | Khulshi | 118 | 13:00 | 149 | Shahjadpur | 54 | 18:00
18 | Baroirhat | 28 | 17:00 | 84 | Kishoreganj | 102 | 18:00 | 150 | Shahjibazar | 85 | 18:00
19 | Bashundhara | 125 | 13:00 | 85 | Kodda | 279 | 12:00 | 151 | Shahmirpur | 37.5 | 00:00
20 | BashundharaCement | 12 | 12:00 | 86 | Kulaura | 30 | 18:00 | 152 | Shariatpur | 50 | 19:30
21 | Beanibazar | 42 | 18:00 | 87 | Kurigram | 45 | 07:00 | 153 | Sherpur | 96 | 18:00
22 | Benapole | 38 | 18:00 | 88 | Kushtia | 88 | 18:00 | 154 | Shikalbaha | 19 | 00:00
23 | Bhaluka | 100 | 12:00 | 89 | Lalbag | 69 | 17:00 | 155 | Shitalakhya | 64 | 12:00
24 | Bhandaria | 36 | 21:00 | 90 | Lalmonirhat | 40 | 18:00 | 156 | Sholosohor | 33 | 11:00
25 | Bhangura | 18 | 13:00 | 91 | MI_Cement | 16.4 | 08:00 | 157 | Shyampur | 154 | 12:00
26 | Bheramara(GK) | 38 | 18:00 | 92 | Madanganj | 19 | 00:00 | 158 | Siddhirganj | 102 | 09:00
27 | Bhulta | 221 | 15:00 | 93 | Madaripur | 65 | 19:00 | 159 | Sirajganj | 70 | 19:00
28 | Bog-Sherpur | 48 | 08:00 | 94 | Madartek | 49.86 | 13:00 | 160 | Sonargaon | 85 | 08:00
29 | Bogura | 112 | 18:30 | 95 | Madunaghat | 35 | 18:00 | 161 | Sreemongol | 47 | 18:00
30 | Borhanuddin | 50 | 19:30 | 96 | Magura | 45 | 18:00 | 162 | Sreepur | 70 | 18:00
31 | Brahmanbaria | 109 | 17:00 | 97 | Mahasthangarh | 48 | 18:00 | 163 | Srinagar | 28.4 | 22:00
32 | Cantonment | 88 | 13:00 | 98 | Manikganj | 98 | 18:00 | 164 | Sunamganj | 35 | 18:00
33 | Chandpur | 42 | 21:00 | 99 | Maniknagar | 52 | 12:00 | 165 | Sylhet | 28 | 13:00
34 | Chandraghona | 25 | 18:00 | 100 | Matarbari | 38 | 19:00 | 166 | Sylhet-132 | 80 | 18:00
35 | Chapai | 46 | 13:00 | 101 | Matuail | 63 | 12:00 | 167 | TK | 20 | 18:00
36 | Charsaidpur | 43 | 12:00 | 102 | Millgate | 98 | 12:00 | 168 | Tangail | 124 | 18:00
37 | Chauddagram | 42 | 18:00 | 103 | Mirpur | 105 | 18:00 | 169 | Thakurgaon | 80 | 18:30
38 | Chhatak | 20 | 20:00 | 104 | Mirsorai | 12 | 00:00 | 170 | Tongi | 115 | 11:00
39 | Chowmuhani | 134 | 18:00 | 105 | Mirzapur | 34 | 07:00 | 171 | Ullahpara | 24 | 18:00
40 | Chuadanga | 68 | 18:00 | 106 | Mithapukur | 39 | 18:00 | 172 | Ullon | 36 | 18:30
41 | Coxsbazar | 89 | 18:30 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 59 | 13:00
42 | Cumilla(N) | 102 | 18:30 | 108 | Mogbazar | 88.4 | 12:00 | 174 | UttaraNew | 40 | 12:00
43 | Cumilla(S) | 123 | 13:00 | 109 | Mongla | 38 | 08:00 | 175 | Zigatola | 78 | 12:00
44 | Daudkandi | 106 | 19:30 | 110 | Motijheel | 33 | 13:00
45 | Dhaka | 24 | 12:00 | 111 | Munshiganj | 68 | 14:00
46 | Dhamrai | 112 | 14:00 | 112 | Mymensingh | 168 | 18:00
47 | Dhanmondi | 112 | 13:00 | 113 | Naogaon | 84 | 18:00
48 | Dohazari | 65 | 18:00 | 114 | Narail | 39 | 18:00
49 | Faridpur | 102 | 18:00 | 115 | Narinda | 54 | 13:00
50 | Fatullah | 68 | 12:00 | 116 | Narshingdi | 150 | 19:30
51 | Fenchuganj | 24 | 18:00 | 117 | Natore | 96 | 18:00
52 | Feni | 73 | 19:00 | 118 | Nawabganj | 34 | 21:00
53 | GPH | 21 | 00:00 | 119 | Netrakona | 100 | 18:00
54 | Ghatail | 48 | 18:00 | 120 | New | 40 | 12:00
55 | Ghorashal | 52 | 13:00 | 121 | Niamatpur | 41 | 18:00
56 | Goalpara | 22 | 12:00 | 122 | Noapara | 30 | 18:00
57 | Gollamari | 50 | 11:00 | 123 | PHP | 7 | 02:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-11-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 412 | 03:00 | 389 | 12:00 | Kaliakoir | 384 | 04:00 | 364 | 12:00
| Ashuganj | 411 | 6:00 | 383 | 12:00 | Madunaghat | 422 | 19:00 | 403 | 11:00
| Bhulta | 405 | 05:00 | 382 | 12:00 | Meghnaghat | 412 | 03:00 | 388 | 12:00
| Bibiana | 398 | 00:00 | 387 | 12:00 | Payra | 421 | 03:00 | 410 | 12:00
| BIPTC | 402 | 03:00 | 392 | 13:00 | Rahanpur | 415 | 05:00 | 400 | 12:00
| Bogura | 413 | 05:00 | 395 | 18:00 | Rampal | 414 | 03:00 | 397 | 12:00
| Gopalganj | 417 | 06:00 | 398 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 245 | 05:00 | 226 | 13:00 | Haripur | 241 | 05:00 | 223 | 12:00
| AKSML | 241 | 02:00 | 220 | 12:00 | Hasnabad | 243 | 03:00 | 226 | 11:00
| Aminbazar | 242 | 05:00 | 227 | 13:00 | Hathazari | 245 | 04:00 | 221 | 12:00
| Ashuganj | 240 | 01:00 | 229 | 13:00 | Ishurdi | 240 | 00:00 | 231 | 12:00
| Ashuganj-400 | 240 | 1:00 | 229 | 13:00 | Jhenaidah | 238 | 03:00 | 226 | 12:00
| Baghabari | 237 | 00:00 | 230 | 12:00 | Kaliakoir | 242 | 04:00 | 228 | 12:00
| Barapukuria | 227 | 04:00 | 217 | 18:00 | Keranigonj | 243 | 05:00 | 225 | 12:00
| Barapukuria-230 | 227 | 4:00 | 217 | 18:00 | Khulna(S) | 242 | 06:00 | 230 | 12:00
| Barishal | 246 | 05:00 | 238 | 12:00 | Madunaghat | 243 | 06:00 | 219 | 12:00
| Bheramara | 238 | 05:00 | 228 | 12:00 | Madunaghat-400 | 249 | 12:00 | 219 | 13:00
| Bhulta | 240 | 05:00 | 226 | 12:00 | Maniknagar | 240 | 04:00 | 224 | 12:00
| Bibiana | 230 | 18:30 | 223 | 15:00 | Meghnaghat | 244 | 00:00 | 238 | 11:00
| BIPTC | 241 | 03:00 | 229 | 12:00 | Meghnaghat-400 | 242 | 06:00 | 229 | 12:00
| Bogura | 239 | 03:00 | 229 | 18:00 | Mirsorai | 242 | 06:00 | 221 | 13:00
| Bogura-400 | 238 | 04:00 | 227 | 18:00 | Rajshahi | 240 | 05:00 | 228 | 12:00
| Borhanuddin | 247 | 01:00 | 242 | 13:00 | Rampal | 238 | 01:00 | 227 | 12:00
| BSRM | 242 | 05:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Cumilla(N) | 238 | 05:00 | 223 | 12:00 | Rampura | 240 | 05:00 | 224 | 12:00
| Faridpur | 247 | 04:00 | 237 | 12:00 | Shikalbaha | 242 | 05:00 | 219 | 13:00
| Fenchuganj | 233 | 08:00 | 227 | 12:00 | Shyampur | 242 | 05:00 | 226 | 12:00
| Ghorashal | 240 | 22:00 | 230 | 10:00 | Siddhirganj | 240 | 01:00 | 227 | 12:00
| Ghorashal-230 | 239 | 05:00 | 224 | 12:00 | Sirajgonj | 245 | 03:00 | 237 | 13:00
| Gopalganj | 246 | 05:00 | 236 | 12:00 | Sreepur | 238 | 04:00 | 229 | 12:00
| GPH | 243 | 05:00 | 219 | 12:00 | Tongi | 238 | 03:00 | 228 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 138 | 06:00 | 126 | 12:00 | Kushtia | 140 | 01:00 | 135 | 12:00
| Agargaon | 142 | 03:00 | 131 | 12:00 | Lalbag | 140 | 06:00 | 128 | 12:00
| Agrabad | 139 | 04:00 | 124 | 12:00 | Lalmonirhat | 130 | 01:00 | 121 | 18:00
| AKS | 136 | 02:00 | 123 | 12:00 | Madanganj | 134 | 04:00 | 127 | 12:00
| Aminbazar | 143 | 02:00 | 129 | 14:00 | Madaripur | 135 | 16:00 | 132 | 12:00
| Amnura | 139 | 19:30 | 132 | 11:00 | Madartek | 136 | 04:00 | 125 | 12:00
| Ashuganj | 140 | 00:00 | 135 | 12:00 | Madunaghat | 139 | 05:00 | 126 | 12:00
| Bagerhat | 139 | 06:00 | 130 | 12:00 | Magura | 142 | 05:00 | 133 | 12:00
| Bakulia | 138 | 04:00 | 124 | 12:00 | Mahasthangarh | 137 | 05:00 | 128 | 18:00
| Banani | 137 | 05:00 | 125 | 12:00 | Manikganj | 133 | 01:00 | 121 | 16:00
| Bangabhaban | 136 | 03:00 | 126 | 12:00 | Maniknagar | 136 | 22:00 | 125 | 13:00
| Barapukuria | 137 | 04:00 | 128 | 18:00 | Matarbari | 130 | 1:00 | 115 | 14:00
| Barguna | 140 | 18:00 | 134 | 12:00 | Matuail | 135 | 1:00 | 128.5 | 12:00
| Barishal | 136 | 05:00 | 130 | 12:00 | Millgate | 136 | 06:00 | 125 | 12:00
| Barishal-230 | 137 | 02:00 | 131 | 12:00 | Mirpur | 144 | 02:00 | 127 | 14:00
| Baroaulia | 138 | 00:00 | 125 | 13:00 | Mirzapur | 131 | 05:00 | 122 | 12:00
| Baroirhat | 135 | 03:00 | 123 | 12:00 | Mithapukur | 135 | 05:00 | 123 | 18:00
| Bashundhara | 137 | 03:00 | 125 | 12:00 | MI_Cement | 139.6 | 04:00 | 129 | 12:00
| BashundharaCement | 134 | 04:00 | 125 | 15:00 | Modern | 138 | 05:00 | 124 | 12:00
| Beanibazar | 134 | 04:00 | 130 | 12:00 | Mogbazar | 138 | 04:00 | 127 | 12:00
| Benapole | 140 | 03:00 | 129 | 12:00 | Mongla | 137 | 05:00 | 129 | 12:00
| Bhaluka | 134 | 00:00 | 128 | 12:00 | Motijheel | 136 | 03:00 | 126 | 12:00
| Bhandaria | 132 | 05:00 | 129 | 19:00 | Munshiganj | 134 | 02:00 | 128 | 12:00
| Bhangura | 142 | 01:00 | 136 | 12:00 | Mymensingh | 134 | 06:00 | 125 | 12:00
| Bheramara | 139 | 03:00 | 134 | 12:00 | Naogaon | 137 | 06:00 | 128 | 12:00
| Bheramara(GK) | 139 | 03:00 | 135 | 12:00 | Narail | 141 | 04:00 | 132 | 13:00
| Bhulta | 129 | 06:00 | 120 | 12:00 | Narinda | 135 | 7:00 | 125 | 13:00
| Bog-Sherpur | 138 | 03:00 | 131 | 18:00 | Narshingdi | 134 | 01:00 | 122 | 12:00
| Bogura | 138 | 05:00 | 131 | 18:00 | Natore | 138 | 02:00 | 132 | 12:00
| Bogura-230 | 139 | 03:00 | 131 | 11:00 | Nawabganj | 139 | 05:00 | 128 | 12:00
| Brahmanbaria | 136 | 06:00 | 129 | 12:00 | Netrakona | 134 | 08:00 | 126 | 14:00
| Cantonment | 142 | 05:00 | 130 | 12:00 | New | 136 | 04:00 | 126 | 12:00
| Chandpur | 132 | 18:00 | 121 | 14:00 | Niamatpur | 140 | 01:00 | 135 | 12:00
| Chandraghona | 139 | 00:00 | 127 | 12:00 | Noapara | 139 | 03:00 | 130 | 12:00
| Chapai | 138 | 00:00 | 132 | 13:00 | Pabna | 141 | 03:00 | 135 | 12:00
| Charsaidpur | 135 | 03:00 | 128 | 12:00 | Palashbari | 131 | 00:00 | 123 | 18:00
| Chauddagram | 135 | 04:00 | 124 | 12:00 | Panchagarh | 132 | 05:00 | 118 | 20:00
| Chhatak | 134 | 05:00 | 130 | 12:00 | Patuakhali | 140 | 17:00 | 133 | 12:00
| Chowmuhani | 131 | 06:00 | 121 | 14:00 | Payra | 139 | 05:00 | 134 | 12:00
| Chuadanga | 140 | 03:00 | 129 | 13:00 | PHP | 135 | 04:00 | 122 | 12:00
| Coxsbazar | 131 | 06:00 | 113 | 14:00 | Postogola | 140 | 04:00 | 130 | 12:00
| Cumilla(N) | 139 | 05:00 | 129 | 12:00 | Purbachal | 138 | 05:00 | 124 | 12:00
| Cumilla(S) | 137 | 05:00 | 125 | 18:00 | Purbasadipur | 131 | 03:00 | 121 | 07:00
| Daudkandi | 131 | 00:00 | 123 | 12:00 | Rahanpur | 141 | 03:00 | 136 | 11:00
| Dhaka | 137 | 05:00 | 127 | 12:00 | Rahim | 135 | 04:00 | 127 | 12:00
| Dhamrai | 140 | 05:00 | 131 | 16:00 | Rajbari | 138 | 05:00 | 130 | 12:00
| Dhanmondi | 138 | 04:00 | 128 | 12:00 | Rajendrapur | 128 | 18:30 | 118 | 15:00
| Dohazari | 132 | 00:00 | 121 | 13:00 | Rajshahi | 139 | 02:00 | 132 | 12:00
| Faridpur | 138 | 05:00 | 131 | 12:00 | Rajshahi-230 | 139 | 06:00 | 129 | 12:00
| Fatullah | 138 | 03:00 | 128 | 13:00 | Ramganj | 130 | 18:30 | 121 | 13:00
| Fenchuganj | 138 | 01:00 | 135 | 11:00 | Rampur | 138 | 01:00 | 124 | 12:00
| Feni | 134 | 05:00 | 124 | 12:00 | Rampura | 137 | 03:00 | 126 | 12:00
| Ghatail | 132 | 18:30 | 122 | 14:00 | Rangamati | 139 | 03:00 | 126 | 12:00
| Ghorashal | 140 | 07:00 | 133 | 11:00 | Rangpur | 134 | 04:00 | 126 | 08:00
| Goalpara | 141 | 03:00 | 133 | 12:00 | Ruppur | 141 | 04:00 | 135 | 18:30
| Gollamari | 139 | 01:00 | 132 | 11:00 | Saidpur | 132 | 02:00 | 119 | 18:00
| Gopalganj | 138 | 01:00 | 131 | 12:00 | Satkhira | 139 | 01:00 | 131 | 12:00
| Gopalganj-400 | 139 | 06:00 | 132 | 12:00 | Satmasjid | 142 | 06:00 | 130 | 11:00
| Gulshan | 136 | 04:00 | 126 | 12:00 | Savar | 142 | 05:00 | 125 | 14:00
| Halishahar | 137 | 00:00 | 124 | 12:00 | SevenRings | 143 | 05:00 | 133 | 12:00
| Haripur | 136 | 05:00 | 128 | 12:00 | ShahCement | 135 | 03:00 | 128 | 12:00
| HaripurSBU | 136 | 05:00 | 128 | 12:00 | Shahjadpur | 144 | 00:00 | 139 | 10:00
| Hasnabad | 139 | 01:00 | 130 | 11:00 | Shahjibazar | 136 | 02:00 | 130 | 12:00
| Hathazari | 142 | 04:00 | 128 | 12:00 | Shahmirpur | 138 | 00:00 | 125 | 13:00
| Ishurdi | 141 | 03:00 | 136 | 12:00 | Shariatpur | 137 | 04:00 | 130 | 13:00
| Jaldhaka | 133 | 04:00 | 120 | 18:00 | Sherpur | 138 | 18:30 | 121 | 02:00
| Jamalpur | 140 | 18:30 | 120 | 14:00 | Shikalbaha | 128 | 03:00 | 115 | 12:00
| Jashore | 139 | 02:00 | 130 | 12:00 | Shikalbaha-230 | 140 | 04:00 | 125 | 13:00
| Jhenaidah | 140 | 00:00 | 134 | 12:00 | Shitalakhya | 139.6 | 06:00 | 129 | 12:00
| Jhenaidah-230 | 143 | 05:00 | 134 | 12:00 | Sholosohor | 139 | 02:00 | 126 | 12:00
| Joydebpur | 139 | 03:00 | 128 | 12:00 | Shyampur | 134 | 01:00 | 126 | 13:00
| Joypurhat | 136 | 01:00 | 127 | 12:00 | Shyampur-230 | 138 | 05:00 | 127 | 12:00
| Juldah | 138 | 03:00 | 125 | 12:00 | Siddhirganj | 136 | 02:00 | 128 | 12:00
| Kabirpur | 136 | 03:00 | 123 | 12:00 | Sirajganj | 138 | 00:00 | 133 | 18:00
| Kachua | 133 | 03:00 | 123 | 13:00 | Sonargaon | 135 | 05:00 | 126 | 12:00
| Kaliakoir | 141 | 03:00 | 125 | 14:00 | Sreemongol | 135 | 01:00 | 131 | 12:00
| Kallyanpur | 148 | 08:00 | 131 | 17:00 | Sreepur | 135 | 00:00 | 129 | 12:00
| Kalurghat | 139 | 00:00 | 126 | 13:00 | Srinagar | 138 | 05:00 | 128 | 12:00
| Kamrangirchar | 138 | 00:00 | 129 | 12:00 | SSM | 141 | 00:00 | 132 | 13:00
| Kaptai | 140 | 6:00 | 133 | 19:00 | Sunamganj | 133 | 03:00 | 128 | 14:00
| Kazla | 136 | 04:00 | 126 | 13:00 | Sylhet | 135 | 05:00 | 130 | 13:00
| Keranigonj | 140 | 06:00 | 128 | 12:00 | Sylhet-132 | 134 | 00:00 | 131 | 12:00
| Khagrachori | 139 | 03:00 | 125 | 13:00 | Tangail | 130 | 00:00 | 121 | 14:00
| Khulna | 138 | 00:00 | 131 | 12:00 | Thakurgaon | 132 | 05:00 | 118 | 18:00
| Khulna(S) | 141 | 05:00 | 133 | 12:00 | TK | 137 | 00:00 | 126 | 12:00
| Khulshi | 137 | 05:00 | 122 | 13:00 | Tongi | 137 | 03:00 | 128 | 11:00
| Kishoreganj | 133 | 00:00 | 128 | 12:00 | Ullahpara | 142 | 04:00 | 135 | 18:00
| Kodda | 136 | 00:00 | 118 | 12:00 | Ullon | 136 | 03:00 | 127 | 13:00
| KSRM | 139 | 00:00 | 124 | 13:00 | Uttara | 146 | 05:00 | 129 | 13:00
| Kulaura | 137 | 04:00 | 134 | 12:00 | UttaraNew | 144 | 06:00 | 127 | 13:00
| Kurigram | 131 | 05:00 | 116 | 18:00 | Zigatola | 139 | 03:00 | 128 | 12:00

## L-Curve
Date | 2024-11-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1012 | 4808 | 3879 | 8687 |  |  |  | QF-LDC-11
0:30 | 1074 | 4569 | 3816 | 8385 | Date: | 2024-11-27
1:00 | 1136 | 4330 | 3753 | 8083
1:30 | 1196 | 4202 | 3690 | 7892
2:00 | 1256 | 4074 | 3627 | 7701
2:30 | 1234 | 4021.5 | 3521 | 7542.5 | [5 empty] | Gen. at Eve. Peak | 10666 | 10666 MW (18:00 )
3:00 | 1212 | 3969 | 3415 | 7384 | [6 empty] | 18:00
3:30 | 1243 | 3902 | 3407 | 7309 | [5 empty] | Gen. at Day Peak | 9652 | 9652 MW (12:00 )
4:00 | 1274 | 3835 | 3399 | 7234 | [6 empty] | 12:00
4:30 | 1252 | 3801 | 3381.5 | 7182.5 | [5 empty] | Highest Generation | 10666
5:00 | 1230 | 3767 | 3364 | 7131 | [6 empty] | 18:00
5:30 | 1260 | 3798.5 | 3486.5 | 7285
6:00 | 1290 | 3830 | 3609 | 7439
6:30 | 1178 | 4065.5 | 3746 | 7811.5
7:00 | 1066 | 4301 | 3883 | 8184
7:30 | 1053 | 4413.5 | 4063.5 | 8477
8:00 | 1040 | 4526 | 4244 | 8770
8:30 | 1156 | 4608 | 4203.5 | 8811.5
9:00 | 1272 | 4690 | 4163 | 8853
9:30 | 1306 | 4832 | 4044 | 8876
10:00 | 1340 | 4974 | 3925 | 8899
10:30 | 1396 | 5004.5 | 4004 | 9008.5
11:00 | 1452 | 5035 | 4083 | 9118
11:30 | 1425 | 5186 | 4199 | 9385
12:00 | 1398 | 5337 | 4315 | 9652
12:30 | 1367 | 5336.5 | 4388 | 9724.5
13:00 | 1336 | 5336 | 4461 | 9797
13:30 | 1323 | 5244 | 4250.5 | 9494.5
14:00 | 1310 | 5152 | 4040 | 9192
14:30 | 1372 | 5180.5 | 3982 | 9162.5
15:00 | 1434 | 5209 | 3924 | 9133
15:30 | 1354 | 5278 | 3853.5 | 9131.5
16:00 | 1274 | 5347 | 3783 | 9130
16:30 | 1229 | 5364 | 3905.5 | 9269.5
17:00 | 1184 | 5381 | 4028 | 9409
17:30 | 1070 | 5694 | 4343.5 | 10037.5
18:00 | 956 | 6007 | 4659 | 10666
18:30 | 1028 | 5805 | 4732 | 10537
19:00 | 1100 | 5603 | 4805 | 10408
19:30 | 1110 | 5481 | 4808 | 10289
20:00 | 1102 | 5288 | 4762 | 10050 |  |  |  | Executive Engineer
20:30 | 1118 | 5208 | 4763 | 9971 |  |  |  | Network Operation Division
21:00 | 1134 | 5128 | 4764 | 9892
21:30 | 1132 | 5030 | 4649 | 9679
22:00 | 1130 | 4932 | 4534 | 9466 |  |  |  |  | Page 6 of 7
22:30 | 1108 | 4910 | 4327 | 9237
23:00 | 1086 | 4888 | 4120 | 9008
23:30 | 1049 | 4848 | 3999.5 | 8847.5
24:00 | 1012 | 4808 | 3879 | 8687
10666 MW (18:00 )
9652 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-11-27 |  |  | Energy |  | 218514537
[17 empty] | 2024-11-27 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | Nepal | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3206 | 903 | 0 | 1860 | 0 | 48 | 1939 | 96 | 0 | 0 | 56 | 570 | 0 | 9 | 0
0:30 | 3121.5 | 901.5 | 0 | 1813.5 | 0 | 44 | 1859 | 94 | 0 | 0 | 54 | 490.5 | 0 | 7 | 0 |  |  | Date: | 44161
1:00 | 3037 | 900 | 0 | 1767 | 0 | 40 | 1779 | 92 | 0 | 0 | 52 | 411 | 0 | 5 | 0
1:30 | 2991.5 | 900 | 0 | 1720 | 0 | 23 | 1698.5 | 92.5 | 0 | 0 | 50 | 412 | 0 | 4.5 | 0 | [8 empty] | Total Energy | 218.5145 | 218.5145 | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 2946 | 900 | 0 | 1673 | 0 | 6 | 1618 | 93 | 0 | 0 | 48 | 413 | 0 | 4 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2906.5 | 901.5 | 0 | 1593.5 | 0 | 3 | 1577 | 93 | 0 | 0 | 49 | 413.5 | 0 | 5.5 | 0 | [8 empty] | Energy Requirement | 218.5145 | 218.5145
3:00 | 2867 | 903 | 0 | 1514 | 0 | 0 | 1536 | 93 | 0 | 0 | 50 | 414 | 0 | 7 | 0
3:30 | 2780 | 902.5 | 0 | 1530 | 0 | 0 | 1531.5 | 93.5 | 0 | 0 | 49 | 415.5 | 0 | 7 | 0 | [7 empty] | Shortage
4:00 | 2693 | 902 | 0 | 1546 | 0 | 0 | 1527 | 94 | 0 | 0 | 48 | 417 | 0 | 7 | 0
4:30 | 2659.5 | 902 | 0 | 1529.5 | 0 | 0 | 1527 | 94.5 | 0 | 0 | 48 | 414.5 | 0 | 7.5 | 0
5:00 | 2626 | 902 | 0 | 1513 | 0 | 0 | 1527 | 95 | 0 | 0 | 48 | 412 | 0 | 8 | 0
5:30 | 2670 | 902 | 0 | 1500 | 0 | 3 | 1587 | 95.5 | 0 | 8 | 51 | 460 | 0 | 8.5 | 0
6:00 | 2714 | 902 | 0 | 1487 | 0 | 6 | 1647 | 96 | 0 | 16 | 54 | 508 | 0 | 9 | 0
6:30 | 2841 | 902 | 0 | 1631.5 | 0 | 45.5 | 1687 | 96 | 0 | 16 | 51 | 509.5 | 22 | 10 | 0 | [6 empty] | Coal
7:00 | 2968 | 902 | 0 | 1776 | 0 | 85 | 1727 | 96 | 0 | 16 | 48 | 511 | 44 | 11 | 0
7:30 | 2979.5 | 902 | 0 | 1685 | 0 | 153.5 | 1921 | 96 | 0 | 24 | 47 | 544 | 117 | 8 | 0 | [5 empty] | Oil
8:00 | 2991 | 902 | 0 | 1594 | 0 | 222 | 2115 | 96 | 0 | 32 | 46 | 577 | 190 | 5 | 0
8:30 | 2957.5 | 902 | 0 | 1571.5 | 0 | 203.5 | 2152.5 | 96 | 0 | 24 | 47 | 578 | 277 | 2.5 | 0
9:00 | 2924 | 902 | 0 | 1549 | 0 | 185 | 2190 | 96 | 0 | 16 | 48 | 579 | 364 | 0 | 0
9:30 | 2890.5 | 901.5 | 0 | 1532 | 0 | 175 | 2245 | 96 | 0 | 16 | 51 | 520.5 | 448.5 | 0 | 0
10:00 | 2857 | 901 | 0 | 1515 | 0 | 165 | 2300 | 96 | 0 | 16 | 54 | 462 | 533 | 0 | 0
10:30 | 2891 | 901.5 | 0 | 1560 | 0 | 169 | 2316.5 | 96 | 0 | 16 | 54 | 437.5 | 566.5 | 0.5 | 0
11:00 | 2925 | 902 | 0 | 1605 | 0 | 173 | 2333 | 96 | 0 | 16 | 54 | 413 | 600 | 1 | 0
11:30 | 3059 | 903 | 0 | 1652.5 | 0 | 181.5 | 2404.5 | 96 | 0 | 26.5 | 55 | 412.5 | 594 | 0.5 | 0
12:00 | 3193 | 904 | 0 | 1700 | 0 | 190 | 2476 | 96 | 0 | 37 | 56 | 412 | 588 | 0 | 0
12:30 | 3166.5 | 904.5 | 0 | 1697 | 0 | 218 | 2542 | 95 | 0 | 41.5 | 60 | 413 | 587 | 0 | 0
13:00 | 3140 | 905 | 0 | 1694 | 0 | 246 | 2608 | 94 | 0 | 46 | 64 | 414 | 586 | 0 | 0
13:30 | 3140 | 905 | 0 | 1694 | 0 | 246 | 2608 | 94 | 0 | 46 | 64 | 414 | 586 | 0 | 0
14:00 | 3140 | 905 | 0 | 1694 | 0 | 246 | 2608 | 94 | 0 | 46 | 64 | 414 | 586 | 0 | 0
14:30 | 3112 | 904 | 0 | 1697.5 | 0 | 184.5 | 2489.5 | 94 | 0 | 41 | 58.5 | 434 | 450 | 0 | 0
15:00 | 3084 | 903 | 0 | 1701 | 0 | 123 | 2371 | 94 | 0 | 36 | 53 | 454 | 314 | 0 | 0
15:30 | 3150 | 904 | 0 | 1702.5 | 0 | 137 | 2373 | 94 | 0 | 43 | 53 | 457.5 | 217.5 | 0 | 0
16:00 | 3216 | 905 | 0 | 1704 | 0 | 151 | 2375 | 94 | 0 | 50 | 53 | 461 | 121 | 0 | 0
16:30 | 3220 | 904.5 | 0 | 1679.5 | 0 | 328 | 2351.5 | 94 | 0 | 90.5 | 56 | 481.5 | 64 | 0 | 0
17:00 | 3224 | 904 | 0 | 1655 | 0 | 505 | 2328 | 94 | 0 | 131 | 59 | 502 | 7 | 0 | 0
17:30 | 3210 | 904 | 0 | 1756.5 | 0 | 771.5 | 2458.5 | 95 | 0 | 185 | 58 | 594 | 3.5 | 1.5 | 0
18:00 | 3196 | 904 | 0 | 1858 | 0 | 1038 | 2589 | 96 | 0 | 239 | 57 | 686 | 0 | 3 | 0
18:30 | 3238.5 | 904 | 0 | 1854.5 | 0 | 966 | 2517.5 | 96 | 0 | 177 | 57.5 | 721.5 | 0 | 4.5 | 0
19:00 | 3281 | 904 | 0 | 1851 | 0 | 894 | 2446 | 96 | 0 | 115 | 58 | 757 | 0 | 6 | 0
19:30 | 3247 | 904 | 0 | 1917 | 0 | 824 | 2364 | 96 | 0 | 115 | 58 | 754 | 0 | 10 | 0
20:00 | 3309 | 904 | 0 | 1939 | 0 | 569 | 2308 | 96 | 0 | 99 | 56 | 757 | 0 | 13 | 0
20:30 | 3243.5 | 904 | 0 | 2016 | 0 | 492.5 | 2311 | 96 | 0 | 83 | 56 | 757.5 | 0 | 11.5 | 0
21:00 | 3178 | 904 | 0 | 2093 | 0 | 416 | 2314 | 96 | 0 | 67 | 56 | 758 | 0 | 10 | 0
21:30 | 3150 | 904.5 | 0 | 1998 | 0 | 359 | 2310 | 96 | 0 | 41.5 | 55 | 758.5 | 0 | 6.5 | 0
22:00 | 3122 | 905 | 0 | 1903 | 0 | 302 | 2306 | 96 | 0 | 16 | 54 | 759 | 0 | 3 | 0
22:30 | 3150.5 | 904.5 | 0 | 1931.5 | 0 | 197.5 | 2131 | 95 | 0 | 16 | 53 | 751.5 | 0 | 6.5 | 0
23:00 | 3179 | 904 | 0 | 1960 | 0 | 93 | 1956 | 94 | 0 | 16 | 52 | 744 | 0 | 10 | 0
23:30 | 3192.5 | 903.5 | 0 | 1910 | 0 | 70.5 | 1947.5 | 95 | 0 | 8 | 54 | 657 | 0 | 9.5 | 0 |  |  | Max Temp. in Dhaka |  | 29.1°C
24:00 | 3206 | 903 | 0 | 1860 | 0 | 48 | 1939 | 96 | 0 | 0 | 56 | 570 | 0 | 9 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on Y13: Author:

## Generation
2024-11-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 93 | 93 | 94 | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 94 | 94 | 94 | 94 | 94 | 96 |  | 96 | 96 | 96 | 96 | 96 | 94 | 96 | 2273891
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 9 | 6 | 19 | 16 | 13 | 11 | 8 | 8 | 1 | 0 | [9 empty] | 106245
6 | Sikalbaha 225MW CCPP (Gas) | 227 | 227 | 227 | 182 | 182 | 185 | 185 | 226 | 230 | 226 | 222 | 222 | 225 | 220 | 223 | 223 | 226 | 225 |  | 226 | 228 | 226 | 226 | 227 | 227 | 228 | 5121044
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [16 empty] | 17 | 17 | [8 empty] | 33050
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 2 | 17 | [7 empty] | 0 | 35964
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [17 empty] | 16 | [8 empty] | 19472
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 140 | 81 | 81 | 81 | 80 | 140 | 180 | 140 | 140 | 80 | 80 | 80 | 201 | 180 | 184 | 128 | 115 | 96 |  | 100 | 96 | 101 | 0 |  |  | 0 | 2742000
17 | Siddhirganj 335 MW CCPP | [11 empty] | 30 | 1 | 3 | 80 | 270 | 335 | 335 |  | 335 | 335 | 335 | 335 | 300 | 300 | 335 | 2803283
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 175 | 78 | 78 | 78 | 78 | 78 | 125 | 182 | 182 | 157 | 187 | 187 | 187 | 187 | 187 | 187 | 187 | 189 |  | 177 | 177 | 177 | 178 | 192 | 197 | 199 | 3830545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 625 | 600 | 604 | 600 | 602 | 600 | 590 | 685 | 875 | 1224 | 1237 | 1240 | 1240 | 1238 | 1233 | 1240 | 1005 | 970 |  | 770 | 677 | 610 | 611 | 608 | 600 | 600 | 20329089
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 39 | 10 | 10 | 10 | 10 | 10 | 39 | 42 | 43 | 42 | 42 | 36 | 37 | 37 | 37 | 38 | 37 | 42 |  | 42 | 40 | 40 | 42 | 42 | 42 | 42 | 799128
33 | Ashuganj 225 MW CCPP | 181 | 180 | 180 | 180 | 180 | 180 | 214 | 180 | 181 | 181 | 195 | 200 | 181 | 197 | 182 | 182 | 181 | 180 |  | 198 | 181 | 187 | 181 | 180 | 211 | 180 | 4566000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 290 | 290 | 290 | 290 | 355 | 310 | 280 | 280 | 295 | 340 | 300 | 310 | 285 | 280 | 310 | 310 |  | 335 | 310 | 355 | 310 | 290 | 345 | 310 | 7581500
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1190690
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 400 | 400 | 400 | 379 | 325 | 324 | 336 | 400 | 407 | 410 | 405 | 413 | 414 | 413 | 410 | 413 | 414 | 412 |  | 412 | 410 | 412 | 412 | 401 | 378 | 400 | 9644400
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 590 | 590 | 500 | 500 | 500 | 470 | 500 | 380 | 360 | 360 | 360 | 360 | 350 | 350 | 400 | 400 | 400 | 550 |  | 480 | 480 | 480 | 590 | 590 | 583 | 550 | 11277273
40 | Meghnaghat 450 MW CCPP(MPL) | [25 empty] | 0 | 0
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 35 | 34 | 35 | 46 | 46 | 46 | 44 | 32 | 27 | 26 | 24 | 10 | 10 | 10 | 10 | 10 | 11 | 11 |  | 12 | 16 | 17 | 18 | 27 | 27 | 26 | 551040
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 15 | 29 | 39 | 46 | 35 | 48 | 29 | 27 | 9 | 0 | [9 empty] | 292380
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | [10 empty] | 497280
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 62 | 61 | 61 | 59 | 59 | 60 | 40 | 59 | 59 | 60 | 61 |  | 61 | 62 | 60 | 61 | 62 | 61 | 40 | 1275072
48 | Shahjibazar 86 MW PP (Shahjibazar) | 42 | 11 | 11 | 11 | 11 | 11 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 86 | 86 | 86 | 50 | 50 |  | 50 | 50 | 50 | 50 | 51 | 51 | 51 | 1019520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 121 | 120 | 120 | 122 | 120 | 120 | 120 | 119 | 80 | 20 | 20 | 50 | 64 | 66 |  | 66 | 72 | 73 | 96 | 102 | 111 | 171 | 3045950
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 58128
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 339168
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 285 | 290 | 290 | 285 | 295 | 310 | 295 | 285 | 280 | 300 | 295 | 290 | 285 | 290 | 285 | 295 | 275 |  | 290 | 290 | 290 | 290 | 290 | 295 | 295 | 7086500
| Bibiyana South 400 MW | 316 | 316 | 316 | 316 | 316 | 316 | 376 | 341 | 318 | 316 | 316 | 400 | 330 | 350 | 320 | 320 | 296 | 277 |  | 296 | 310 | 320 | 320 | 320 | 320 | 320 | 7788000
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 | [7 empty] | 0 | 30300
59 | Tangail Palli Power Gen 22 MW | 24 | 6 | [5 empty] | 2 | 20 | 24 | 24 | 24 | 24 | 12 | 12 | 23 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 427680
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 52 | 48 | 50 | 48 | 48 | 54 | 48 | 46 | 48 | 54 | 54 | 56 | 64 | 66 | 53 | 53 | 59 | 57 |  | 58 | 58 | 56 | 56 | 54 | 52 | 56 | 1305600
64 | Malancha, Ctg. EPZ (United) | 28 | 38 | 38 | 38 | 38 | 32 | 32 | 12 | 12 | 10 | 10 | 11 | 16 | 12 | 7 | 3 | 5 | 5 |  | 12 | 25 | 25 | 28 | 36 | 37 | 39 | 540000
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 11 | 11 | 11 | 11 | 6 | 12 | 12 | 12 | 18 | 15 | 15 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 327930
69 | Summit Ashulia | 16 | 16 | 16 | 16 | 16 | 16 | 13 | 21 | 26 | 25 | 24 | 24 | 24 | 4 | 24 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 21 | 494400
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 15 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511920
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 22 | 17 | 17 | 506880
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 31 | 30 | 30 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 769400
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0
| Chowmuhani 113 MW | [7 empty] | 0 | 8 | [7 empty] | 4 | 49 |  | 73 | 73 | 27 | 27 | 26 |  |  | 280560
| Manikgonj 162MW PP(MPGL) | [16 empty] | 19 | 72 |  | 54 | 54 | 17 | 0 |  |  | 0 | 167040
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [10 empty] | 8 | 25 | 34 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 8 | 0 |  | 0 | 202560
79 | Kodda 150 MW PP | [5 empty] | 16 | 16 | 32 | 16 | 16 | 16 | 16 | 32 | 16 | 20 | 32 | 64 | 64 |  | 64 | 64 | 48 | 16 | 16 | 16 | 0 | 507840
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 3 | 8 | [8 empty] | 14755
| Gazipur 100 MW PP | [16 empty] | 17 | 34 |  | 17 | 17 | 0 |  |  |  | 0 | 76800
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 24961
| Jodiac Power | [16 empty] | 54 | 54 |  | 54 | 54 | 54 | 54 | 35 |  | 0 | 312361
| Karnaphuli Power Ltd. | [16 empty] | 1 | 19 |  | 17 | 17 | 0 |  |  |  | 0 | 63650
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | [15 empty] | 10 | 19 | 25 |  | 37 | 90 | 112 | 152 | 126 | 157 | 135 | 696524
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 22 | 33 | 33 | [9 empty] | 0 | 206712
93 | Ashuganj 51 MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 31 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 938056
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 16 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 50 | 24 | [9 empty] | 0 | 813024
95 | Patenga 50MW PP (Baraka) | [16 empty] | 6 | 23 |  | 26 | 26 | 26 | 12 | 12 |  | 0 | 113280
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [6 empty] | 7 |  | 17 | [5 empty] | 0 | 24960
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP) | 80 | 80 | 80 | 80 | 80 | 80 | 113 | 113 | 113 | 113 | 80 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 80 | 113 | 113 | 2470827
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | [9 empty] | 12150
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 1 | 14 |  | 17 | 17 | 17 | 0 |  |  | 0 | 63720
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [5 empty] | 3 | 33 | 45 | 24 | 8 | 8 | 8 | 35 | 8 | 10 | 24 | 65 | 83 |  | 83 | 55 | 55 | 45 | 45 | 24 | 0 | 764400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 9 | 16 | 15 | 15 | 15 | 15 | 23 | 17 | 17 | 17 | 25 | 50 |  | 45 | 25 | 25 | 15 | 15 |  | 0 | 367200
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 6 | 20 |  | 12 | 12 | 12 | 0 |  |  | 0 | 67200
116 | Chandpur 200 MW (Desh energy) | [16 empty] | 11 | 17 | [7 empty] | 0 | 36000
117 | Ashuganj 150 MW PP (Midland) | [7 empty] | 2 | [8 empty] | 20 | 38 |  | 60 | 60 | 50 | 30 | 30 |  | 0 | 257600
118 | Bibiyana-III 400 MW CCPP | 336 | 336 | 312 | 238 | 225 | 225 | 225 | 280 | 310 | 310 | 311 | 386 | 386 | 386 | 386 | 386 | 342 | 342 |  | 342 | 342 | 342 | 340 | 340 | 340 | 339 | 8152000
| Jamalpur 115 MW PP (United) | 16 |  |  |  |  | 3 | 27 | 55 | 16 | 16 | 16 | 16 | 28 | 8 | 18 | 45 | 55 | 64 |  | 64 | 64 | 64 | 64 | 45 | 45 | 24 | 726000
| Anwara 300 MW PP (United) | [16 empty] | 30 | 65 |  | 65 | 65 | 30 | 30 | 0 |  | 0 | 250909
| Juldah unit-2 (Acorn) | [16 empty] | 17 | 48 |  | 12 | 12 | 12 | 0 |  |  | 0 | 99840
| Anlima Energy Ltd. | [16 empty] | 11 | 53 |  | 72 | 72 | 35 | 35 | 35 |  | 0 | 279764
| Bhairob 54.5 MW | [16 empty] | 9 | 54 |  | 28 | 17 | 17 | 0 |  |  | 0 | 119520
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 11 | 18 | 23 | 25 | 29 | 29 | 23 | 16 | 7 | 0 | [9 empty] | 172465
| Chandpur 115(Doreen) | [16 empty] | 8 | 48 |  | 16 | 16 | 16 | 0 |  |  | 0 | 131520
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 17 | 36 |  | 18 | 18 | 18 | 18 | 0 |  | 0 | 135000
| Mirsharai 150 MW (Oil) | [16 empty] | 17 | 35 | [7 empty] | 0 | 35127
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 5 | 4 | 7 | 7 | 8 | 9 | 11 | 5 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 |  | 6 | 10 | 13 | 10 | 3 | 10 | 9 | 108960
| Sonagazi 75 MW Solar Plant | [6 empty] | 5 | 8 | 51 | 66 | 67 | 68 | 64 | 36 | 39 | 14 | 1 | [9 empty] | 437000
Matarbari 2*600 MW (CPGCL)
JERA Meghnaghat Power Limited
| Sreepur 150 MW | [11 empty] | 21 | 14 | 15 | 16 | 18 | 18 | 20 | [7 empty] | 0 | 102000
120
121 | Eastern Zone Total | 4330 | 4074 | 3969 | 3835 | 3767 | 3830 | 4301 | 4526 | 4690 | 4974 | 5035 | 5337 | 5336 | 5152 | 5209 | 5347 | 5381 | 6007 |  | 5603 | 5481 | 5288 | 5128 | 4932 | 4888 | 4808 | 118453007
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | [26 empty] | 0
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 8 | 28 | 27 | 64 | 77 | 70 | 72 | 32 | 20 | 12 | 2 | [9 empty] | 428400
132 | Rampal 1320 MW (BIFPCL) | 407 | 368 | 369 | 370 | 370 | 409 | 410 | 513 | 422 | 372 | 373 | 426 | 458 | 418 | 408 | 411 | 500 | 618 |  | 619 | 617 | 618 | 620 | 618 | 506 | 409 | 11134550
133 | United Payra Power Ltd. | [15 empty] | 2 | 54 | 72 |  | 54 | 54 | 54 | 54 | 35 |  | 0 | 319200
| Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 180 | 180 | 180 | 180 | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 |  | 220 | 220 | 220 | 220 | 110 | 55 | 40 | 4790310
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 200 | 150 | 150 | 150 | 150 | 200 | 200 | 250 | 238 | 150 | 150 | 218 | 250 | 188 | 180 | 180 | 230 | 307 |  | 307 | 307 | 307 | 307 | 307 | 200 | 250 | 5302000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2960
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 134 | 134 | 134 | 80 | 100 | 100 | 100 | 100 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 2610000
141 | Bhola 33 MW PP (Venture) | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 4 | 3 | 3 | 4 | 2 | 6 | 5 | 4 | 4 | 5 | 6 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 128782
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP | [26 empty] | 0
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
| Bheramara HVDC | 900 | 900 | 903 | 902 | 902 | 902 | 902 | 902 | 902 | 901 | 902 | 904 | 905 | 905 | 903 | 905 | 904 | 904 |  | 904 | 904 | 904 | 904 | 905 | 904 | 903 | 21728727
147 | Nepal
148 | Bheramara 410 MW CCPP | 295 | 294 | 295 | 250 | 250 | 277 | 294 | 250 | 250 | 250 | 250 | 286 | 274 | 270 | 267 | 259 | 258 | 244 |  | 244 | 241 | 240 | 236 | 236 | 232 | 232 | 6418944
149 | Payra 1320 MW | 390 | 340 | 250 | 250 | 250 | 280 | 370 | 510 | 500 | 400 | 420 | 440 | 510 | 490 | 400 | 390 | 440 | 540 |  | 600 | 610 | 622 | 622 | 622 | 500 | 530 | 11255273
150
151 | Barapukuria TPP Unit-1
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 157 | 160 | 163 | 157 | 155 | 158 | 157 | 157 | 155 | 154 | 153 | 152 | 150 | 151 | 150 | 154 | 153 | 154 |  | 150 | 153 | 151 | 154 | 151 | 150 | 150 | 3781000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [8 empty] | 2 | 4 | 5 | 5 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 29100
157 | Sirajganj 68 MW Solar Park | [6 empty] | 6 | 14 | 38 | 51 | 57 | 61 | 56 | 44 | 31 | 10 | 0 | [9 empty] | 366000
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 165 | 165 | 140 | 140 | 140 | 140 | 140 | 156 | 135 | 135 | 135 | 135 | 147 | 170 | 150 | 150 | 156 | 159 |  | 151 | 144 | 141 | 141 | 142 | 138 | 138 | 3789100
Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 172 | 172 | 140 | 140 | 140 | 140 | 140 | 162 | 130 | 130 | 130 | 130 | 146 | 154 | 153 | 141 | 140 | 141 |  | 132 | 131 | 131 | 131 | 130 | 128 | 128 | 3672073
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 341 | 350 | 316 | 348 | 320 | 320 | 414 | 350 | 324 | 322 | 354 | 414 | 414 | 300 | 350 | 352 | 350 | 414 |  | 414 | 414 | 414 | 414 | 370 | 414 | 380 | 8952436
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 190224
166 | Amnura 50 MW PP(Sinha)
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP | [17 empty] | 14 | [8 empty] | 19547
169 | Santahar 50 MW Peaking PP | [16 empty] | 15 | 22 | [8 empty] | 35793
170 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
171 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 51 |  | 51 | 51 | 51 | 51 | 0 |  |  | 221840
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
173 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [25 empty] | 0 | 0
178 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 3 | 3 | 0 | 0 | [9 empty] | 34593
| Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 30 | 36 |  | 50 | 56 | 0 |  |  |  | 0 | 134784
| Intraco Solar 30 MW | [6 empty] | 2 | 10 | 19 | 28 | 33 | 34 | 32 | 23 | 17 | 7 | 0 | [9 empty] | 204113
178 | Adani Power Jharkhanda Ltd | 411 | 413 | 414 | 417 | 412 | 508 | 511 | 577 | 579 | 462 | 413 | 412 | 414 | 414 | 454 | 461 | 502 | 686 |  | 757 | 754 | 757 | 758 | 759 | 744 | 570 | 12790909
| Teesta Solar Limited | [6 empty] | 10 | 58 | 107 | 147 | 170 | 176 | 163 | 135 | 95 | 36 | 3 | [9 empty] | 1097310
179 | Pabna Solar 100 MW | [6 empty] | 5 | 33 | 60 | 82 | 93 | 86 | 96 | 70 | 52 | 24 | 1 | [9 empty] | 623562
| Western Zone Total | 3753 | 3627 | 3415 | 3399 | 3364 | 3609 | 3883 | 4244 | 4163 | 3925 | 4083 | 4315 | 4461 | 4040 | 3924 | 3783 | 4028 | 4659 |  | 4805 | 4808 | 4762 | 4764 | 4534 | 4120 | 3879 | 100061530
[27 empty] | Total | 218514537