## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-12-01 | Sunday
|  | Date (day): | 2024-12-01 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13305.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14080 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-11-30 | 2024-12-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 409 | 421 | 405 | 412
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 124 | 135 | 150 | 185 |  | GT-2 S/D
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 0 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 2 | 35 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 55 | 82 | 32 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 7 | 8 | 42 | 45 |  | 35 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 17 | 17 |  | 16 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 26 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 34 | 34 | 25 | 25 |  |  | Fuel Shortage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 53 | 52 | 149
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 35 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 5 | 0 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 108 | 50 | 162 | 0
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 14 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 36 | 36 | 36 | 19 |  | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 350 | 530 | 583 | 583
| JERA Meghnaghat Power Limited |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1430 | 1849 | 2310 | 2745 | 1762 | 1336
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 17 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 22 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 49 | 94 | 50 | 50 | 180 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 220 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 85 | 105
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 64 |  | 34 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 65 |  | 37 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 25 | 100 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 4 | 2 | 10
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 50 | 50 | 58 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 50 | 100 | 200 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 16 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 25 | 100 | 100
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 10 | 35 | 53 | 63 |  | Fuel shortage
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 35 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 885 | 1156 | 1224 | 1224
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 3 | 15 | 15 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 0 | 102 | 575 | 575 | 575 |  | Coal shortage
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1173 | 1742 | 2881 | 3135 | 1256 | 401
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 211 | 182 | 200 | 200 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 310 | 310 | 320 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 41 | 40 | 42 | 42
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 184 | 183 | 180 | 190
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 45 | 140 | 140 |  | 10 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 30 | 45 |  | 7 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 68 | 200 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 42 | 64 | 66 | 82
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 12 | 15 | 15 |  | 10 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 86 | 95 | 95 |  | 18 | Engine problem
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 72 | 16 | 51 | 64 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 69 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 1003 | 1222 | 1631 | 1647 | 232 | 805
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 11 | 10 | 20 | 20 | 182 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 10 | 93 | 96 | 96 | 104 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 35 | 55 | 55 | 55 | 60 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 24 | 24
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 8 | 17 | 53
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 0 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 115 | 190 | 263.6 | 248 | 182 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 113 | 113 |  | 50 | ST under maint
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 56 | 60 | 60
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 42 | 42 | 42 | 42 | 44 |  | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 174 | 168 | 170 | 170 |  | 61 | Machine problem
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 13 | 13 |  | 12 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 110 | 300 | 310 | 31
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 313 | 310 | 310 | 310 | 90 |  | Gas shortage
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 356 | 317 | 330 | 330 | 53 |  | Gas shortage
| Sylhet Area Total |  |  |  |  | 2411 | 2366 | 1432 | 1186 | 1345 | 1355 | 283 | 622
100 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 900 | 899 | 482 | 482
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 35 |  | 19 | Engine problem
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 60 |  | 49 | Engine problem
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 274 | 227 | 225 | 225 | 185 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
106 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 31 | 0 | 100 | 0
108 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
109 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 400 | 624 | 500 | 622 | 612 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
** | Nepal |  | 0 | Imported power | 40 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1605 | 1750 | 1357 | 1424 | 1253 | 68
110 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 | 110 |  | Fuel shortage
111 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 3 | 7 | 10 | 10
112 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 134 | 130 | 134 | 134 |  | 60 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
113 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 480 | 580 | 622 | 622 |  | 622 | Unit-2 S/D.
114 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maint
115 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 100 | 54 | 150
116 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 248 | 307 | 307 | 307
117 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 865 | 1124 | 1127 | 1223 | 110 | 902
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 26 | 32 |  | 18 | Engine problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 172 | 154 | 160 | 160 | 50 |  | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 167 | 151 | 150 | 150 | 70 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 370 | 414 | 414
127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
128 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5
129 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 40 | 53 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 8 | 95 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113
133 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 554 | 754 | 700 | 748
134 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 58 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 47 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1418 | 1517 | 1828 | 1925 | 563 | 105
135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 159 | 160 | 150 | 150 |  | 124 | Machine problem
137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 90 | 113
140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
141 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 72 | 115 | 115
142 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
143 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 182 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 383 | 232 | 563 | 378 | 40 | 294 | .
| Total |  |  |  |  | 27740 | 27035 | 9424 | 10812 | 13305.6 | 14080 | 5681 | 4533
A. |  | 2024-11-30 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 10812 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7064 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10812 | MW
3 | Day peak Generation : |  |  | 9424 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10601.33 | MW
4 | Evening peak Generation : |  |  | 10812 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 213.102 | MKWHr | By Solar | 3.167 | MKWHr
| By Gas : | 113.3184 | MKWHr |  | By Oil: | 5.7126 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 53.5757 | MKWHr |  | By Hydro: | 1.3682 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 14.3265 | MKWHr |  | By Wind: | 0.08544 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5681 | MW | Dhaka | 4053.03 | 4053.03 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4533 | MW | Chittagong | 1171 | 1171 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10214 | MW | Khulna | 1145.5 | 1145.5 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 822.43 | MMCFD | **Import Adani: | Taka | 94698343.47 | Rajshahi | 952.8 | 952.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : |  | 308354428.412 | ii) Oil : | Taka | 105741401.83 | Comilla | 952 | 952 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 377796669.8 | Total | Taka | 886590843.512 | Mymensingh | 859 | 859 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 9556.8 | MKWHr. | Sylhet | 415 | 415 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 876 | MW (W to E) at | 18:00 | hrs | Barisal | 313 | 313 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 562 | MW at | 8:00 | hrs | Rangpur | 740 | 740 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.7°C |  |  | Total | 10601.33 | 10601.33 |  | 0
B. |  | 2024-12-01 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 30.7°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14080 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9900 | MW
4 | Reserve(Generation end) |  |  |  | 3180 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 214.8365 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7244 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector(India) : |  |  |  |  | i) Energy | 20.376 | MKWHr. | ii) HVDC Flow at Peak Time |  | 899 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.1722 | MKWHr. | iii) Maximum HVDC Flow : |  | 910 | MW at | 1:00 | hrs.
* Import Through HVDC C/B Interconnector(Nepal) : |  |  |  |  | i) Energy | 0 | MKWHr.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.17 |  | (b) Today: | 96.12 |  | (c) Rule Curve: |  | 106.1
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-11-30 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | JERA Meghnaghat Power Limited | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | Nepal | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Nepal | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 0 | 150 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 17 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 0 | 183 | 197 | 50 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 40 | 42 | 0 | 171 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 3 | 0 | 0 | 583 | 0 | 0 | 0 |  | 910 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 153 | 0 | 0 | 155 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 497 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4531 | 3463 | 7994 | 3146 | 910 | 0 | 1790 | 0 | 0 | 1558 | 40 | 0 | 0 | 50 | 497 | 0 | 3 | 0 | 96.18
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 |  | 0 | 0 | 149 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 17 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 0 | 184 | 88 | 50 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 48 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 40 | 11 | 0 | 171 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 0 | 0 | 0 | 583 | 0 | 0 | 0 |  | 909 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 151 | 0 | 0 | 156 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 418 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4215 | 3306 | 7521 | 3016 | 909 | 0 | 1562 | 0 | 0 | 1528 | 40 | 0 | 0 | 48 | 418 | 0 | 0 | 0 | 96.18
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 |  | 0 | 0 | 142 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 17 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 0 | 182 | 16 | 50 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 48 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 40 | 11 | 0 | 171 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 565 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 909 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 152 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 419 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4032 | 3296 | 7328 | 2994 | 909 | 0 | 1441 | 0 | 0 | 1477 | 40 | 0 | 0 | 48 | 419 | 0 | 0 | 0 | 96.17
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 |  | 0 | 0 | 124 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 181 | 8 | 50 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 46 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 56 | 11 | 0 | 171 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563 | 1 | 0 | 0 | 350 | 0 | 0 | 0 |  | 718 | 0 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 152 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 150 | 419 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4017 | 3047 | 7064 | 3063 | 718 | 0 | 1293 | 0 | 0 | 1476 | 48 | 0 | 0 | 46 | 419 | 0 | 1 | 0 | 96.17
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 |  | 0 | 0 | 120 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 17 | 33 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 0 | 185 | 8 | 50 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 46 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 56 | 11 | 0 | 172 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 350 | 0 | 0 | 0 |  | 718 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 154 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 150 | 419 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4071 | 3050 | 7121 | 3069 | 718 | 0 | 1335 | 0 | 0 | 1486 | 48 | 0 | 0 | 46 | 419 | 0 | 0 | 0 | 96.17
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 |  | 0 | 0 | 118 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 17 | 33 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 0 | 182 | 45 | 50 | 25 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 40 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 56 | 42 | 0 | 174 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566 | 0 | 0 | 0 | 350 | 0 | 0 | 0 |  | 717 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 130 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 188 | 419 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4203 | 3164 | 7367 | 3143 | 717 | 0 | 1451 | 0 | 2 | 1546 | 49 | 0 | 0 | 40 | 419 | 0 | 0 | 0 | 96.17
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 0 | 151 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 17 | 33 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 355 | 0 | 210 | 46 | 50 | 39 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 44 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 56 | 42 | 0 | 176 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 0 | 313 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 654 | 0 | 0 | 0 | 350 | 7 | 0 | 0 |  | 718 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 120 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 451 | 2 | 200 | 521 | 10 | 0 | 0 | 1 | 2 | 0 |  | 4548 | 3432 | 7980 | 3292 | 718 | 0 | 1494 | 0 | 41 | 1775 | 50 | 0 | 16 | 44 | 521 | 29 | 0 | 0 | 96.16
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 146 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 23 | 17 | 33 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 285 | 0 | 181 | 92 | 51 | 38 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 42 | 45 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 120 | 0 | 40 | 42 | 0 | 176 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 4 | 10 | 0 | 0 | 0 | 313 | 45 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 17 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 705 | 0 | 0 | 0 | 350 | 30 | 0 | 0 |  | 864 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 123 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 440 | 0 | 0 | 0 | 2 | 19 | 0 | 0 | 0 | 464 | 12 | 224 | 662 | 67 | 0 | 0 | 19 | 30 | 0 |  | 4566 | 3971 | 8537 | 3143 | 864 | 0 | 1448 | 0 | 118 | 1956 | 50 | 0 | 32 | 42 | 662 | 222 | 0 | 0 | 96.16
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 0 | 141 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 181 | 92 | 50 | 38 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 36 | 28 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 120 | 0 | 40 | 42 | 0 | 175 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 14 | 0 | 0 | 0 | 313 | 24 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 33 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 0 | 0 | 350 | 49 | 0 | 0 |  | 900 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 430 | 0 | 0 | 0 | 4 | 16 | 0 | 0 | 0 | 408 | 25 | 200 | 714 | 119 | 0 | 0 | 20 | 28 | 0 |  | 4401 | 3952 | 8353 | 2934 | 900 | 0 | 1403 | 0 | 89 | 1861 | 50 | 0 | 32 | 36 | 714 | 334 | 0 | 0 | 96.16
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 0 | 150 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 201 | 92 | 50 | 37 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 42 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 40 | 42 | 0 | 176 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 18 | 0 | 0 | 0 | 310 | 24 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 350 | 65 | 0 | 0 |  | 900 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 430 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 379 | 28 | 150 | 609 | 158 | 0 | 0 | 50 | 41 | 0 |  | 4464 | 3864 | 8328 | 3010 | 900 | 0 | 1427 | 0 | 73 | 1735 | 50 | 0 | 32 | 42 | 609 | 450 | 0 | 0 | 96.16
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 0 | 146 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 0 | 50 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 325 | 0 | 196 | 178 | 50 | 38 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 44 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 54 | 42 | 0 | 174 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 18 | 0 | 0 | 0 | 310 | 24 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 47 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 705 | 0 | 0 | 0 | 350 | 51 | 0 | 0 |  | 901 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 165 | 0 | 0 | 142 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 430 | 0 | 0 | 0 | 2 | 21 | 0 | 0 | 0 | 378 | 35 | 150 | 563 | 179 | 0 | 0 | 41 | 55 | 0 |  | 4774 | 3991 | 8765 | 3117 | 901 | 0 | 1646 | 0 | 99 | 1828 | 50 | 0 | 46 | 44 | 563 | 471 | 0 | 0 | 96.15
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 0 | 152 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 25 | 24 | 34 | 0 | 49 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 350 | 0 | 211 | 184 | 50 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 42 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 163 | 0 | 54 | 42 | 0 | 174 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 10 | 0 | 35 | 17 | 0 | 0 | 0 | 313 | 35 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 35 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 885 | 0 | 0 | 0 | 350 | 69 | 0 | 0 |  | 900 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 159 | 0 | 0 | 172 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 480 | 0 | 0 | 0 | 4 | 31 | 0 | 0 | 0 | 400 | 36 | 248 | 554 | 182 | 0 | 0 | 58 | 47 | 0 |  | 5153 | 4271 | 9424 | 3343 | 900 | 0 | 1668 | 0 | 138 | 2172 | 49 | 0 | 55 | 42 | 554 | 503 | 0 | 0 | 96.15
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 0 | 149 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 25 | 24 | 34 | 0 | 47 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 355 | 0 | 200 | 175 | 50 | 40 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 52 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 163 | 0 | 54 | 42 | 0 | 170 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 18 | 0 | 0 | 0 | 312 | 35 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 3 | 0 | 331 | 0 | 45 | 0 | 0 | 0 | 0 | 10 | 9 | 0 | 0 | 0 | 0 | 935 | 0 | 0 | 0 | 350 | 31 | 0 | 0 |  | 900 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 155 | 0 | 0 | 173 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 600 | 0 | 0 | 0 | 4 | 16 | 0 | 0 | 0 | 561 | 32 | 307 | 558 | 168 | 0 | 0 | 56 | 37 | 0 |  | 5189 | 4554 | 9743 | 3289 | 900 | 0 | 1661 | 0 | 190 | 2558 | 47 | 0 | 64 | 52 | 558 | 424 | 0 | 0 | 96.15
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 0 | 127 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 25 | 30 | 34 | 0 | 45 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 182 | 172 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 44 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 169 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 52 | 0 | 0 | 0 | 0 | 312 | 35 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 17 | 0 | 331 | 0 | 37 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 954 | 0 | 0 | 0 | 420 | 22 | 0 | 0 |  | 900 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 163 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 622 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 531 | 24 | 295 | 531 | 138 | 0 | 0 | 43 | 29 | 0 |  | 5031 | 4306 | 9337 | 3096 | 900 | 0 | 1548 | 0 | 213 | 2565 | 45 | 0 | 64 | 44 | 531 | 331 | 0 | 0 | 96.15
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 |  | 0 | 0 | 135 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 25 | 28 | 34 | 0 | 46 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 183 | 172 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 58 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 169 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 53 | 9 | 0 | 0 | 0 | 312 | 35 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 17 | 0 | 331 | 0 | 22 | 0 | 0 | 0 | 0 | 3 | 16 | 0 | 0 | 0 | 0 | 950 | 9 | 0 | 0 | 470 | 12 | 0 | 0 |  | 900 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 550 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 0 | 511 | 17 | 270 | 517 | 97 | 0 | 0 | 20 | 19 | 0 |  | 5000 | 4078 | 9078 | 2986 | 900 | 0 | 1621 | 0 | 214 | 2441 | 46 | 0 | 64 | 58 | 517 | 222 | 9 | 0 | 96.14
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 |  | 0 | 0 | 156 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 25 | 28 | 34 | 0 | 47 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 340 | 0 | 212 | 172 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 52 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 170 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 53 | 3 | 0 | 0 | 0 | 311 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 331 | 0 | 6 | 0 | 0 | 0 | 0 | 1 | 16 | 0 | 0 | 0 | 0 | 950 | 6 | 0 | 0 | 480 | 2 | 0 | 0 |  | 899 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 530 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 516 | 7 | 270 | 570 | 37 | 0 | 0 | 14 | 7 | 0 |  | 5045 | 3956 | 9001 | 2992 | 899 | 0 | 1652 | 0 | 214 | 2422 | 47 | 0 | 64 | 52 | 570 | 83 | 6 | 0 | 96.14
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 |  | 0 | 0 | 142 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 0 | 25 | 28 | 34 | 0 | 47 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 6 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 182 | 182 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 7 | 0 | 0 | 0 | 13 | 58 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 163 | 0 | 40 | 42 | 0 | 168 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 74 | 0 | 53 | 0 | 0 | 8 | 13 | 311 | 40 | 17 | 0 | 0 | 0 | 0 | 0 | 36 | 49 | 0 | 331 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 43 | 30 | 0 | 0 | 0 | 994 | 9 | 0 | 0 | 480 | 0 | 0 | 0 |  | 900 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 162 | 0 | 0 | 152 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 10 | 0 | 0 | 33 | 0 | 0 | 511 | 0 | 270 | 702 | 1 | 0 | 0 | 1 | 1 | 0 |  | 5343 | 4154 | 9497 | 2996 | 900 | 0 | 1696 | 0 | 520 | 2487 | 47 | 0 | 79 | 58 | 702 | 3 | 9 | 0 | 96.14
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 |  | 0 | 0 | 124 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 2 | 0 | 17 | 0 | 8 | 0 | 25 | 26 | 34 | 0 | 94 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 22 | 0 | 4 | 0 | 0 | 0 | 310 | 0 | 182 | 183 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 0 | 12 | 64 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 163 | 0 | 56 | 42 | 0 | 168 | 0 | 0 | 0 | 110 | 13 | 2 | 0 | 0 | 0 | 0 | 93 | 0 | 53 | 0 | 25 | 68 | 45 | 310 | 55 | 35 | 0 | 0 | 30 | 16 | 0 | 34 | 86 | 25 | 317 | 5 | 0 | 108 | 10 | 0 | 8 | 0 | 72 | 36 | 0 | 35 | 0 | 1156 | 3 | 102 | 0 | 530 | 0 | 0 | 0 |  | 899 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 154 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 35 | 580 | 0 | 0 | 100 | 0 | 0 | 72 | 0 | 0 | 624 | 0 | 307 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6189 | 4623 | 10812 | 3172 | 899 | 0 | 1589 | 0 | 1151 | 2929 | 94 | 0 | 157 | 64 | 754 | 0 | 3 | 0 | 96.14
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 |  | 0 | 0 | 131 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 12 | 25 | 26 | 34 | 0 | 94 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 26 | 0 | 7 | 0 | 0 | 0 | 285 | 0 | 183 | 185 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 15 | 58 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 163 | 0 | 40 | 42 | 0 | 167 | 0 | 0 | 0 | 55 | 13 | 2 | 0 | 0 | 0 | 0 | 94 | 0 | 53 | 0 | 0 | 34 | 20 | 310 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 331 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 51 | 17 | 0 | 0 | 0 | 1220 | 0 | 150 | 0 | 590 | 0 | 0 | 0 |  | 898 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 138 | 0 | 0 | 150 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 0 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 623 | 0 | 307 | 755 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5791 | 4436 | 10227 | 3101 | 898 | 0 | 1606 | 0 | 573 | 3060 | 94 | 0 | 82 | 58 | 755 | 0 | 0 | 0 | 96.13
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 |  | 0 | 0 | 148 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 25 | 26 | 34 | 0 | 94 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 6 | 0 | 7 | 0 | 0 | 0 | 285 | 0 | 189 | 185 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 15 | 56 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 167 | 0 | 0 | 0 | 250 | 13 | 2 | 0 | 0 | 0 | 0 | 94 | 0 | 53 | 0 | 0 | 17 | 0 | 310 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 1221 | 0 | 154 | 0 | 595 | 0 | 0 | 0 |  | 902 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 125 | 0 | 0 | 148 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624 | 0 | 307 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5785 | 4351 | 10136 | 3110 | 902 | 0 | 1824 | 0 | 341 | 2991 | 94 | 0 | 64 | 56 | 754 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 0 |  | 0 | 0 | 139 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 25 | 26 | 8 | 0 | 94 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 285 | 0 | 181 | 185 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 54 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 167 | 0 | 0 | 0 | 215 | 13 | 2 | 0 | 0 | 0 | 0 | 94 | 0 | 37 | 0 | 0 | 17 | 0 | 310 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 1 | 153 | 0 | 595 | 0 | 0 | 0 |  | 884 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 125 | 0 | 0 | 148 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 0 | 307 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5615 | 4330 | 9945 | 3104 | 884 | 0 | 1788 | 0 | 211 | 2991 | 94 | 0 | 64 | 54 | 754 | 0 | 1 | 0 | 96.13
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 |  | 0 | 0 | 127 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 25 | 26 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 285 | 0 | 181 | 185 | 50 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 54 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 0 | 56 | 42 | 0 | 167 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 94 | 0 | 36 | 0 | 0 | 0 | 0 | 310 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 6 | 247 | 0 | 595 | 0 | 0 | 0 |  | 764 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 163 | 0 | 0 | 145 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557 | 0 | 307 | 758 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5699 | 4173 | 9872 | 3169 | 764 | 0 | 1856 | 0 | 185 | 2937 | 95 | 0 | 48 | 54 | 758 | 0 | 6 | 0 | 96.13
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 |  | 0 | 0 | 123 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 25 | 26 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 285 | 0 | 181 | 185 | 50 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 56 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 120 | 0 | 56 | 42 | 0 | 167 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 93 | 0 | 35 | 0 | 0 | 0 | 0 | 310 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 19 | 421 | 0 | 250 | 0 | 0 | 0 |  | 669 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 157 | 0 | 0 | 145 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 559 | 0 | 307 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5499 | 4058 | 9557 | 3129 | 669 | 0 | 1507 | 0 | 183 | 3097 | 95 | 0 | 48 | 56 | 754 | 0 | 19 | 0 | 96.13
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 0 | 148 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 23 | 26 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 305 | 0 | 189 | 187 | 50 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 52 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25 | 0 | 40 | 42 | 0 | 167 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 19 | 0 | 0 | 0 | 0 | 311 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 17 | 400 | 0 | 250 | 0 | 0 | 0 |  | 669 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 122 | 0 | 0 | 144 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511 | 0 | 250 | 687 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5186 | 3785 | 8971 | 3126 | 669 | 0 | 1387 | 0 | 119 | 2833 | 49 | 0 | 32 | 52 | 687 | 0 | 17 | 0 | 96.12
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 0 | 137 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 17 | 26 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 285 | 0 | 181 | 187 | 50 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 56 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25 | 0 | 40 | 42 | 0 | 177 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 947 | 22 | 397 | 0 | 250 | 0 | 0 | 0 |  | 575 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 120 | 0 | 0 | 144 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 250 | 662 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5078 | 3570 | 8648 | 3109 | 575 | 0 | 1387 | 0 | 90 | 2684 | 47 | 0 | 16 | 56 | 662 | 0 | 22 | 0 | 96.12
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9489600 | 0 |  | 0 | 0 | 3360844 | 0 | 0 | 0 | 7451167 | 0 | 0 | 0 | 22176 | 894720 | 0 | 0 | 0 | 0 | 14400 | 0 | 34560 | 0 | 123000 | 274320 | 520160 | 661700 | 304800 | 0 | 1368180 | 0 | 0 | 0 | 0 | 4909231 | 0 | 0 | 0 |  | 335280 | 0 | 0 | 0 | 0 | 66720 | 0 | 440640 | 0 | 0 | 0 | 7553900 | 0 | 4625000 | 3278545 | 1193530 | 840024 | 0 | 0 | 912576 | 0 | 0 | 51706 | 0 | 0 | 0 | 296290 | 1172160 | 489600 | 0 | 0 | 1750 | 0 | 0 | 0 | 94104 | 2916818 | 0 | 1098816 | 833280 | 0 | 3567750 | 0 | 0 | 0 | 6651390 | 354384 | 56784 | 0 | 0 | 0 | 0 | 883200 | 0 | 609120 | 105030 | 48960 | 146400 | 105382 | 7816000 | 750000 | 51427 | 0 | 22559 | 30109 | 51432 | 0 | 49020 | 330960 | 15360 | 7730300 | 10176 | 281810 | 128160 | 41400 | 0 | 33480 | 114076 | 264000 | 97920 | 0 | 8364 | 0 | 20198180 | 85440 | 1621818 | 0 | 10184545 | 348555 | 0 | 0 |  | 20376000 | 0 | 5879520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3156000 | 129063 | 0 | 0 | 0 | 0 | 0 | 0 | 60592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66456 | 0 | 0 | 3597000 | 0 | 0 | 3579636 | 0 | 3621945 | 0 | 0 | 0 | 0 | 0 | 9161527 | 0 | 0 | 19200 | 0 | 0 | 0 | 37163 | 10080 | 11344000 | 0 | 0 | 139200 | 26700 | 185760 | 104256 | 0 | 0 | 11272730 | 216335 | 5542000 | 14326527 | 1148940 | 0 | 1731 | 337500 | 339050 | 0 |  | 118423088 | 94678911 | 213101999 | 75355113 | 20376000 | 0 | 37963332 | 0 | 4748884 | 53575728 | 1368180 | 0 | 963676 | 1172160 | 14326527 | 3166959 | 85440 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27330048 | 0 |  | 0 | 0 | 11494086.48 | 0 | 0 | 0 | 22726059.35 | 0 | 0 | 0 | 398059.2 | 17375462.4 | 0 | 0 | 0 | 0 | 262944 | 0 | 632102.4 | 0 | 92250 | 0 | 0 | 0 | 5458968 | 0 | 0 | 0 | 0 | 0 | 0 | 15660446.89 | 0 | 0 | 0 |  | 5897575.2 | 0 | 0 | 0 | 0 | 1098211.2 | 0 | 0 | 0 | 0 | 0 | 21075381 | 0 | 15355000 | 10983125.75 | 3855101.9 | 2830880.88 | 0 | 0 | 3659429.76 | 0 | 0 | 933810.36 | 0 | 0 | 0 | 222217.5 | 7689369.6 | 1522656 | 0 | 0 | 0 | 0 | 0 | 0 | 428173.2 | 9975517.56 | 0 | 6098428.8 | 4349721.6 | 0 | 9954022.5 | 0 | 0 | 0 | 20552795.1 | 265788 | 43155.84 | 0 | 0 | 0 | 0 | 16966272 | 0 | 10726603.2 | 0 | 871977.6 | 2540040 | 1747233.56 | 20712400 | 14295000 | 964770.52 | 0 | 0 | 492282.15 | 999838.08 | 0 | 936772.2 | 6423933.6 | 273561.6 | 20562598 | 173704.32 | 0 | 2344046.4 | 694692 | 0 | 598287.6 | 0 | 4757280 | 1658764.8 | 0 | 117765.12 | 0 | 140781314.6 | 0 | 9568726.2 | 0 | 0 | 0 | 0 | 0 |  | 57256560 | 0 | 17344584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9972960 | 611758.62 | 0 | 0 | 0 | 0 | 0 | 0 | 1018551.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50307.192 | 0 | 0 | 30358680 | 0 | 0 | 11812798.8 | 0 | 12061076.85 | 0 | 0 | 0 | 0 | 0 | 26751658.84 | 0 | 0 | 380544 | 0 | 0 | 0 | 0 | 199987.2 | 73509120 | 0 | 0 | 2693520 | 0 | 0 | 1808841.6 | 0 | 0 | 82290929 | 0 | 41287900 | 94698343.47 | 0 | 0 | 0 | 0 | 0 | 0 |  | 487428652.02 | 464108121.092 | 951536773.112 | 219548161.502 | 57256560 | 0 | 88806266.91 | 0 | 87229622.79 | 377796669.8 | 0 | 0 | 18511779.04 | 7689369.6 | 94698343.47 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 0 | 152 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 25 | 24 | 34 | 0 | 49 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 350 | 0 | 211 | 184 | 50 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 42 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 163 | 0 | 54 | 42 | 0 | 174 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 10 | 0 | 35 | 17 | 0 | 0 | 0 | 313 | 35 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 35 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 885 | 0 | 0 | 0 | 350 | 69 | 0 | 0 |  | 900 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 159 | 0 | 0 | 172 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 480 | 0 | 0 | 0 | 4 | 31 | 0 | 0 | 0 | 400 | 36 | 248 | 554 | 182 | 0 | 0 | 58 | 47 | 0 |  | 9424 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 |  | 0 | 0 | 124 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 2 | 0 | 17 | 0 | 8 | 0 | 25 | 26 | 34 | 0 | 94 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 22 | 0 | 4 | 0 | 0 | 0 | 310 | 0 | 182 | 183 | 50 | 40 | 0 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 0 | 12 | 64 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 163 | 0 | 56 | 42 | 0 | 168 | 0 | 0 | 0 | 110 | 13 | 2 | 0 | 0 | 0 | 0 | 93 | 0 | 53 | 0 | 25 | 68 | 45 | 310 | 55 | 35 | 0 | 0 | 30 | 16 | 0 | 34 | 86 | 25 | 317 | 5 | 0 | 108 | 10 | 0 | 8 | 0 | 72 | 36 | 0 | 35 | 0 | 1156 | 3 | 102 | 0 | 530 | 0 | 0 | 0 |  | 899 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 154 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 35 | 580 | 0 | 0 | 100 | 0 | 0 | 72 | 0 | 0 | 624 | 0 | 307 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10812 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 0 | 150 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 22 | 23 | 17 | 33 | 25 | 0 | 50 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 24 | 64 | 65 | 0 | 50 | 50 | 0 | 10 | 0 | 0 |  | 320 | 0 | 200 | 190 | 50 | 42 | 0 | 0 | 51 | 0 | 45 | 52 | 0 | 0 |  | 15 | 82 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 113 | 0 | 60 | 42 | 0 | 170 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 300 | 0 | 0 | 96 | 0 | 149 | 0 | 100 | 200 | 140 | 310 | 55 | 105 | 105 | 0 | 100 | 54 | 110 | 114 | 95 | 100 | 330 | 17 | 0 | 162 | 53 | 0 | 53 | 0 | 51 | 36 | 0 | 160 | 0 | 1224 | 15 | 575 | 0 | 583 |  |  |  |  | 482 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 40 | 25 | 95 | 0 | 0 | 32 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 307 | 748 | 0 | 0 |  |  |  | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 |  | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 20 | 22 | 17 | 33 | 25 | 0 | 50 | 0 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 24 | 56 | 50 | 0 | 50 | 50 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 200 | 180 | 50 | 42 | 0 | 0 | 51 | 0 | 30 | 52 | 0 | 0 |  | 15 | 66 | 20 | 0 | 0 | 1.6 | 0 | 0 | 0 | 5 | 113 | 0 | 60 | 42 | 0 | 170 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 300 | 0 | 0 | 96 | 0 | 52 | 20 | 100 | 200 | 140 | 310 | 55 | 50 | 85 | 5 | 50 | 54 | 110 | 114 | 95 | 100 | 330 | 0 | 50 | 50 | 35 | 0 | 17 | 35 | 16 | 36 | 0 | 17 | 0 | 1224 | 15 | 575 | 0 | 583 | 70 |  |  |  | 482 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 0 | 134 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 26 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 95 | 0 | 90 | 0 | 8 | 113 | 622 | 0 |  | 54 | 6 | 100 | 115 | 0 | 0 | 500 | 30 | 307 | 700 | 170 | 0 |  | 29 | 47 | 0 |  |  |  |  | gas | hvdc |  | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 15 | 17 | 30 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 200 | 185 | 41 | 38 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 48 | 28 | 0 | 0 | 1 | 0 | 0 | 0 | 5 | 113 | 0 | 40 | 42 | 0 | 169 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 9 | 0 | 0 | 0 | 312 | 45 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 14 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 558 | 0 | 583 | 15 | 0 | 0 | 0 | 435 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 150 | 0 | 0 | 155 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 490 | 0 | 0 | 0 | 1 | 10 | 0 | 0 | 0 | 458 | 12 | 250 | 415 | 64 | 0 | 0 | 14 | 30 | 0 | 0 |  |  |  | 113318445 | 20376000 |  | 0 | 53575728 | 5712560 | 1172160 | 3166959 | 85440 | 1368180 |  |  |  | 198775472
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [10 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 |  | 299798 | [7 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [14 empty] | 499227 |  | 499229 |  |  | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [11 empty] | 113.3184 | 20.376 |  | 0 | 53.5757 | 5.7126 | 1.1722 | 3.167 | 0.08544 | 1.3682
| Minimum Generation |  | 7064 | 4:00
| Highest Generation |  | 10812 | 18:00 | [129 empty] | 0 | [77 empty] | 198.7755
| Day Peak Generation |  | 9424 | 12:00
| Evening Peak Generation |  | 10812 | 18:00 | [207 empty] | 202699852
| HVDC Max Flow |  | 910 | 1:00 | [207 empty] | 202.6999
| HVDC EvPeak Flow |  | 899 | 18:00
| Load factor L.F |  | 82.12% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-12-01
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-11-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9424 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 7244
Evening Peak Generation : |  |  | 10812 | MW Hour : | 18:00 | Available Max Generation : |  | 14080
E.P. Demand (at gen end) : |  |  | 10812 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10900
Maximum Generation : |  |  | 10812 | MW Hour : | 18:00 | Reserve(Generation end) |  | 3180
Total Gen. (MKWH) : |  |  | 213.102 | System Load Factor : | 82.12% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 562 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-12-01
Actual : |  | 96.12 | Ft.(MSL) , | Rule curve : | 106.1 | Ft.( MSL )
Gas Consumed : |  | Total = | 822.43 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 308354428.412 | Adani : | 94698343.47
|  |  | Coal : | 377796669.8 | Oil: | 105741401.83 | Total: | 886590843.512
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3725.7237 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1018.712 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1425.4791 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1237.5835 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1019.0346 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 757.155 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 425.2106 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 353.6298 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 691.6548 |  |  | 0 | 0%
Total |  | 0 |  | 10654.1832 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:12 | 16:11 | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) LT Scheduled S/D Due to
Annual maintenance.
08:13 | 16:09 | Rajshahi 230/132/33kV S/S 132/33 kV T-01 (406T) HT Scheduled S/D Due to
Annual Maintenance.
08:15 | 16:50 | Barishal-Barishal(N) 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due
to Annual maintenance.
08:23 | 18:08 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Scheduled S/D from Gopalganj 132/33kV end Due to Annual
maintenance and from Gopalganj 400/132kV end.
08:23 | 15:50 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end
Due to Sreemongal S/S Works.
08:24 | 17:17 | Hathazari-Madunaghat 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end
Due to Annual Maintenance.
08:29 | 13:19 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to A/M ten delta test.
08:29 | 12:53 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to A/M ten delta test.
08:31 | 15:59 | Sylhet (South) S/S Trafo-1 LT Scheduled S/D Due to For PBS Maintenance. | [5 empty] | 6 MW load interrup.
08:31 | 15:58 | Sylhet (South) S/S Trafo-1 HT Scheduled S/D Due to For PBS maintenance.
08:46 | 16:42 | Sylhet 132/33kV S/S T2 LT Scheduled S/D Due to Due to Yearly Maintenance.
08:47 | 16:42 | Sylhet 132/33kV S/S T2 HT Scheduled S/D Due to Due to Yearly Maintenance.
08:50 | 16:40 | Barapukuria-Rangpur 132 kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to Annual maintenance and
from Barapukuria 230/132/33kV end Due to Annual Maintenance work.
08:51 | 09:02 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Inst.E/F, inst. O/C relays Due to WZPDCL | [5 empty] | 27 MW load interrup.
33kV Polashpur feeder Fault.
08:51 | 09:02 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Inst.E/F, inst. O/C relays Due to WZPDCL | [5 empty] | 42 MW load interrup.
33kV Palashpur Feeder Fault.
08:53 |  | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to Maintenance work will be
done by Tongi S/S and from Tongi 230/132/33kV end Due to Annual maintenance work.
08:58 | 12:52 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) HT Scheduled S/D.
08:58 | 12:52 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) LT Scheduled S/D.
09:06 | 15:14 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D
Due to Annual maintenance.
09:06 | 15:13 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D
Due to Annual maintenance.
09:10 | 17:04 | Naogaon 132/33kV S/S Nao-SPPP Ckt-1 Scheduled S/D Due to Annual maintenance.
09:11 | 16:09 | Maniknagar-Siddhirganj 230kV Ckt-1 Scheduled S/D from Maniknagar 230/132kV end.
09:23 | 16:02 | Fenchuganj 230/132/33kV S/S TR-02 HT Scheduled S/D Due to Annual Maintenance.
09:26 | 14:37 | Natore-Rajshahi 132kV Ckt-1 Scheduled S/D from Natore 132/33kV end Due to D/S status signal
rectification work and from Rajshahi 132/33kV end Due to annual maintenance.
09:27 | 13:34 | Bheramara-HVDC Bheramara 230 kV Ckt-1 Scheduled S/D from BIPTC end Due to Annual Maintenance
and from Bheramara 230/132kV end Due to Annual Maintenance.
09:29 | 16:31 | Joydebpur 132/33kV S/S GT-2 HT Scheduled S/D Due to Annual Maintenance. | [5 empty] | 5 MW load interrup.
09:31 | 16:12 | Bhulta 400/230kV S/S 230kV Bus-02 Scheduled S/D Due to Annual maintenance work
by Bhulta 400kV team.
09:55 |  | Maniknagar-Siddhirganj 230kV Ckt-1 Scheduled S/D from Siddhirganj 230/132kV end Due
to Annual Maintenance work.
10:01 | 11:09 | New Tongi-Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to
New tongi side shutdown.
10:10 | 15:25 | Haripur 230/132kV S/S Bus-1 Scheduled S/D Due to 230 KV Bus-1 Shuttdown for
Annual Maintanance.
10:17 | 16:08 | Sreepur 230/132/33kV S/S 230 kV BUS-2 Scheduled S/D Due to Annual Maintenance.
10:27 |  | Fenchuganj-Sreemangal 132kV Ckt-1 Forced S/D from Sreemongol 132/33kV end Due
to Lightning Arrester Installation.
10:33 | 12:45 | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end
Due to Scheduled shutdown.
10:48 | 13:32 | Aminbazar 400/230/132kV S/S 230 kv Bus 01 Scheduled S/D Due to Scheduled shutdown.
10:51 | 17:35 | Sylhet (South) S/S Trafo-2 LT Scheduled S/D Due to For PBS Maintenance. | [5 empty] | 6 MW load interrup.
10:51 | 17:32 | Sylhet (South) S/S Trafo-2 HT Scheduled S/D Due to For PBS Maintenance.
10:54 | 12:23 | Bogura 230/132kV S/S Bogura (W) CKT-1 Scheduled S/D
10:54 | 12:23 | Bogura 230/132kV S/S Bogura (W) CKT-2 Scheduled S/D
10:58 | 13:28 | Aminbazar-Keraniganj 230kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to Annual
maintenance at Aminbazar end. and from Aminbazar 400/230/132kV end Due to Scheduled shutdown.
11:07 | 14:36 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to Annual maintenance.
12:30 | 12:51 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Forced S/D Due to Auxiliary transformer -2
fuse connecting work.
12:30 | 12:52 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Forced S/D Due to Auxiliary transformer -2 | [5 empty] | 20 MW load interrup.
fuse connecting work.
13:35 | 23:37 | Madanganj 132/33kV S/S GT-2 LT Forced S/D Due to 33 KV GT-2 Y phase PT voltage low.
13:36 | 23:34 | Madanganj 132/33kV S/S GT-2 HT Forced S/D Due to 33 KV GT-2 PT Y phase voltage low.
14:30 | 16:25 | Aminbazar 400/230/132kV S/S ATR-01 HT Forced S/D Due to Earth fault.
14:42 | 16:24 | Gopalganj 132/33kV S/S Gopalganj 100 MW PS Scheduled S/D Due to SAS Maintenance.
14:51 | 15:51 | Natore-Rajshahi 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end Due to None and from Rajshahi
132/33kV end Due to Maintenance work at Natore end.
15:30 |  | Aminbazar 400/230/132kV S/S ATR-01 LT Forced S/D Due to Earth fault.
15:33 | 16:48 | Barishal 132/33kV S/S 132 kv Summit power Scheduled S/D Due to SF6 Gas leakage repair.
17:07 |  | Summit Bibiyana -2 CCPP ST tripped due to problem with excitation system.
| 17:59 | Bakulia-MSML 132 kV Ckt-2 is restored.
| 18:54 | Summit Bibiyana -2 ST was synchronized.
| 19:38 | Cumilla(N) 230/132/33kV S/S 230KV ATR-03 HT is restored.
| 19:42 | Cumilla(N) 230/132/33kV S/S 230KV ATR-03 LT is restored.
07:22 |  | Shahjadpur 132/33kV S/S T-4(435T) LT Scheduled S/D Due to Annual Maintenance.
07:22 |  | Shahjadpur 132/33kV S/S T-4(435T) HT Scheduled S/D Due to Annual Maintenance.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-11-30
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 421 | 9489600
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 124 | 3360844 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7451167
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 22176 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 2 | 14400 | Low demand
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 894720 | Low demand
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 34560 | Low demand
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 8 | 397320 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 520160 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 26 | 661700
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 34 | 304800
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 53 | 609120 | Low demand
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 35 | 51427 | Low demand
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 5 | 10176 | Low demand
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 128160 | Fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 114076
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 97920
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 530 | 10184545
| JERA Meghnaghat Power Limited |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 1849 | 34346871
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 105030
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 22 | 66720 | Low demand
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 94 | 1368180 | Low water level
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 220 | 4909231
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 0 | 0 | Reserve
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 48960 | Low demand
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 4 | 440640
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22559
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 30109 | Low demand
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 16 | 51432 | Low demand
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Reserve
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 15360
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 10 | 41400 | Low demand
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 35 | 8364 | Low demand
55 | SS Power I |  | IPP | 2*612 | 1224 | 1156 | 20198180
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 3 | 85440
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 102 | 1621818 | Coal shortage
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1742 | 29013423
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4625000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7553900 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 840024 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 183 | 3278545
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 912576
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 45 | 105382 | Low demand
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1193530 | ST under Maint
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 68 | 146400 | Low demand
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 64 | 1172160
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 51706 | Low demand
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 296290 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 49020 | Low demand
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 86 | 330960 | Engine problem
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 264000
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 348555
| Cumilla Area Total |  |  |  | 2917 | 1222 | 21168048
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 10 | 489600 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 1750
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 93 | 883200 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 55 | 750000 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 281810
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 335280
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 8 | 33480 | Low demand
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  | 646 | 190 | 2775120
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 2916818
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 0 | 0 | 0 | Contact expired
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 94104 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 56784 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1098816 | Gas shortage
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 42 | 833280 | Gas shortage
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 168 | 3567750 | Machine problem.
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 354384
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 110 | 6651390 | ST tripped at 17:07
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 310 | 7816000 | Gas shortage
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 317 | 7730300 | Gas shortage
| Sylhet Area Total |  |  |  | 2366 | 1186 | 31119626
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 899 | 20376000
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 227 | 5879520 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 185760
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 624 | 11272730 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Nepal |  | Imported power | 40 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1750 | 37714010
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 7 | 129063 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 3156000
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 580 | 11344000 | Unit-2 under overhauling
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 139200 | Low demand
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 5542000
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 1731
| Barisal Area Total |  |  |  | 2236 | 1124 | 20311994
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | NENP
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 154 | 3579636 | Gas shortage
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 151 | 3621945
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 370 | 9161527
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 66456 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 40 | 60592 | Low demand
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 8 | 19200 | Low demand
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 10080 | Low demand
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26700
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 754 | 14326527
135 | Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 337500
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 339050
| Rajshahi Area Total |  |  |  | 3449 | 1517 | 31549213
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3597000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | Reserve
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37163
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 104256 | Low demand
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 216335
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 1148940
| Rangpur Area Total |  |  |  | 950 | 232 | 5103694
| Total |  |  |  | 27035 | 10812 | 213101999
| Eastern Grid Total |  |  |  | 16701 | 6189 | 118423088
| Western Grid Total |  |  |  | 10334 | 4623 | 94678911
| National Grid Total |  |  |  | 27035 | 10812 | 213101999
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-11-30
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6296.99 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 2732.2 | MW
i) Dhaka area |  |  | 3324.39 |  | MW | i) Khulna area |  |  |  | 1035 | MW
ii) Chattogram area |  |  | 1047.6 |  | MW | ii) Barishal area |  |  |  | 281.8 | MW
iii) Cumilla area |  |  | 827 |  | MW | iii) Rajshahi area |  |  |  | 840.4 | MW
iv) Mymensingh area |  |  | 738 |  | MW | iv) Rangpur area |  |  |  | 575 | MW
v) Sylhet area |  |  | 360 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9029.19 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 21 | 06:00 | 67 | Jashore | 91 | 18:00 | 133 | Rajbari | 52 | 18:00
2 | AKSML | 93 | 13:00 | 68 | Jhenaidah | 83 | 18:00 | 134 | Rajendrapur | 90 | 13:00
3 | Aftabnagar | 28 | 13:00 | 69 | Joydebpur | 126 | 08:00 | 135 | Rajshahi | 88 | 18:00
4 | Agargaon | 77 | 13:00 | 70 | Joypurhat | 42 | 08:00 | 136 | Rajshahi-230 | 36 | 13:00
5 | Agrabad | 80 | 18:30 | 71 | Juldah | 12 | 16:00 | 137 | Ramganj | 64 | 18:00
6 | Amnura | 35 | 18:30 | 72 | KSRM | 32 | 16:00 | 138 | Rampur | 33 | 18:00
7 | Ashuganj | 66 | 13:00 | 73 | Kabirpur | 230 | 10:00 | 139 | Rangamati | 13 | 18:00
8 | BSRM | 133 | 03:00 | 74 | Kachua | 46 | 18:00 | 140 | Rangpur | 108 | 18:00
9 | Bagerhat | 71 | 18:00 | 75 | Kallyanpur | 75 | 13:00 | 141 | Ruppur | 3.6 | 13:00
10 | Bakulia | 85 | 18:00 | 76 | Kalurghat | 32 | 17:00 | 142 | SSM | 0 | 00:00
11 | Banani | 42 | 13:00 | 77 | Kamrangirchar | 56.35 | 13:00 | 143 | Saidpur | 92 | 18:00
12 | Bangabhaban | 5 | 10:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 84 | 18:00
13 | Barapukuria | 46 | 18:00 | 79 | Kazla | 91 | 12:00 | 145 | Satmasjid | 80 | 13:00
14 | Barguna | 14 | 21:00 | 80 | Keranigonj | 60 | 13:00 | 146 | Savar | 170 | 17:00
15 | Barishal | 77 | 18:00 | 81 | Khagrachori | 22 | 18:00 | 147 | SevenRings | 13.82 | 09:00
16 | Barishal-230 | 62 | 20:00 | 82 | Khulna | 58 | 13:00 | 148 | ShahCement | 35 | 00:00
17 | Baroaulia | 69 | 07:00 | 83 | Khulshi | 121 | 20:00 | 149 | Shahjadpur | 50 | 18:00
18 | Baroirhat | 41 | 18:00 | 84 | Kishoreganj | 112 | 18:00 | 150 | Shahjibazar | 75 | 18:00
19 | Bashundhara | 165 | 13:00 | 85 | Kodda | 266 | 15:00 | 151 | Shahmirpur | 43 | 16:00
20 | BashundharaCement | 6 | 10:00 | 86 | Kulaura | 36 | 17:00 | 152 | Shariatpur | 53 | 20:00
21 | Beanibazar | 48 | 18:00 | 87 | Kurigram | 48 | 18:00 | 153 | Sherpur | 96 | 18:00
22 | Benapole | 37 | 18:00 | 88 | Kushtia | 93 | 18:00 | 154 | Shikalbaha | 20 | 00:00
23 | Bhaluka | 108 | 12:00 | 89 | Lalbag | 68 | 13:00 | 155 | Shitalakhya | 63.6 | 13:00
24 | Bhandaria | 35 | 18:00 | 90 | Lalmonirhat | 42 | 18:00 | 156 | Sholosohor | 40 | 18:00
25 | Bhangura | 22 | 18:00 | 91 | MI_Cement | 17.7 | 10:00 | 157 | Shyampur | 152 | 08:00
26 | Bheramara(GK) | 37 | 18:00 | 92 | Madanganj | 24 | 12:00 | 158 | Siddhirganj | 108 | 14:00
27 | Bhulta | 207 | 21:00 | 93 | Madaripur | 63 | 19:00 | 159 | Sirajganj | 64 | 18:00
28 | Bog-Sherpur | 52 | 18:00 | 94 | Madartek | 62.83 | 13:00 | 160 | Sonargaon | 76 | 23:00
29 | Bogura | 113 | 18:30 | 95 | Madunaghat | 44 | 18:30 | 161 | Sreemongol | 52 | 18:00
30 | Borhanuddin | 53 | 21:00 | 96 | Magura | 42 | 18:00 | 162 | Sreepur | 70 | 12:00
31 | Brahmanbaria | 118 | 18:00 | 97 | Mahasthangarh | 46 | 18:00 | 163 | Srinagar | 30.4 | 13:00
32 | Cantonment | 90 | 13:00 | 98 | Manikganj | 92 | 18:00 | 164 | Sunamganj | 36 | 19:00
33 | Chandpur | 48 | 17:00 | 99 | Maniknagar | 56 | 13:00 | 165 | Sylhet | 24 | 00:00
34 | Chandraghona | 30 | 18:00 | 100 | Matarbari | 39 | 18:00 | 166 | Sylhet-132 | 117 | 18:00
35 | Chapai | 44 | 13:00 | 101 | Matuail | 49 | 10:00 | 167 | TK | 24 | 18:30
36 | Charsaidpur | 41 | 13:00 | 102 | Millgate | 101 | 12:00 | 168 | Tangail | 134 | 19:30
37 | Chauddagram | 47 | 18:00 | 103 | Mirpur | 105 | 13:00 | 169 | Thakurgaon | 78 | 18:00
38 | Chhatak | 23 | 18:00 | 104 | Mirsorai | 13 | 18:00 | 170 | Tongi | 94 | 11:00
39 | Chowmuhani | 157 | 18:00 | 105 | Mirzapur | 36 | 18:00 | 171 | Ullahpara | 28 | 18:00
40 | Chuadanga | 71 | 18:00 | 106 | Mithapukur | 44 | 18:00 | 172 | Ullon | 32 | 13:00
41 | Coxsbazar | 100 | 21:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 69 | 13:00
42 | Cumilla(N) | 110 | 13:00 | 108 | Mogbazar | 87.4 | 12:00 | 174 | UttaraNew | 38 | 12:00
43 | Cumilla(S) | 129 | 18:00 | 109 | Mongla | 27 | 12:00 | 175 | Zigatola | 82 | 13:00
44 | Daudkandi | 102 | 18:00 | 110 | Motijheel | 34 | 13:00
45 | Dhaka | 24 | 11:00 | 111 | Munshiganj | 76 | 13:00
46 | Dhamrai | 108 | 13:00 | 112 | Mymensingh | 168 | 18:00
47 | Dhanmondi | 105 | 13:00 | 113 | Naogaon | 86 | 18:00
48 | Dohazari | 80 | 18:00 | 114 | Narail | 40 | 18:00
49 | Faridpur | 100 | 18:00 | 115 | Narinda | 55 | 13:00
50 | Fatullah | 85 | 12:00 | 116 | Narshingdi | 153 | 19:00
51 | Fenchuganj | 32 | 13:00 | 117 | Natore | 93 | 18:00
52 | Feni | 82 | 18:00 | 118 | Nawabganj | 27.2 | 18:30
53 | GPH | 3 | 00:00 | 119 | Netrakona | 98 | 18:00
54 | Ghatail | 44 | 18:00 | 120 | New | 37.3 | 18:00
55 | Ghorashal | 47 | 17:00 | 121 | Niamatpur | 40 | 18:30
56 | Goalpara | 22 | 18:30 | 122 | Noapara | 32 | 18:00
57 | Gollamari | 56 | 13:00 | 123 | PHP | 5 | 02:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-11-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 415 | 03:00 | 394 | 13:00 | Kaliakoir | 381 | 04:00 | 361 | 12:00
| Ashuganj | 410 | 0:00 | 377 | 12:00 | Madunaghat | 412 | 02:00 | 401 | 13:00
| Bhulta | 404 | 02:00 | 377 | 12:00 | Meghnaghat | 410 | 05:00 | 387 | 11:00
| Bibiana | 400 | 05:00 | 386 | 12:00 | Payra | 421 | 02:00 | 406 | 13:00
| BIPTC | 409 | 04:00 | 394 | 09:00 | Rahanpur | 416 | 04:00 | 403 | 18:30
| Bogura | 413 | 04:00 | 398 | 18:00 | Rampal | 413 | 01:00 | 396 | 13:00
| Gopalganj | 417 | 04:00 | 397 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 02:00 | 221 | 12:00 | Haripur | 242 | 03:00 | 224 | 12:00
| AKSML | 239 | 00:00 | 227 | 13:00 | Hasnabad | 240 | 04:00 | 223 | 12:00
| Aminbazar | 237 | 01:00 | 225 | 11:00 | Hathazari | 238 | 06:00 | 229 | 16:00
| Ashuganj | 240 | 01:00 | 228 | 12:00 | Ishurdi | 241 | 01:00 | 231 | 12:00
| Ashuganj-400 | 244 | 1:00 | 225 | 13:00 | Jhenaidah | 238 | 04:00 | 226 | 13:00
| Baghabari | 239 | 01:00 | 232 | 12:00 | Kaliakoir | 238 | 02:00 | 223 | 12:00
| Barapukuria | 227 | 06:00 | 218 | 19:30 | Keranigonj | 238 | 02:00 | 222 | 12:00
| Barapukuria-230 | 227 | 06:00 | 218 | 19:30 | Khulna(S) | 240 | 03:00 | 228 | 13:00
| Barishal | 246 | 01:00 | 235 | 12:00 | Madunaghat | 235 | 04:00 | 228 | 12:00
| Bheramara | 240 | 04:00 | 228 | 12:00 | Madunaghat-400 | 235 | 03:00 | 228 | 13:00
| Bhulta | 241 | 02:00 | 224 | 12:00 | Maniknagar | 240 | 02:00 | 224 | 12:00
| Bibiana | 230 | 05:00 | 223 | 12:00 | Meghnaghat | 247 | 02:00 | 236 | 11:00
| BIPTC | 242 | 04:00 | 229 | 12:00 | Meghnaghat-400 | 244 | 05:00 | 228 | 11:00
| Bogura | 240 | 04:00 | 231 | 19:30 | Mirsorai | 235 | 01:00 | 225 | 13:00
| Bogura-400 | 239 | 04:00 | 230 | 18:00 | Rajshahi | 240 | 04:00 | 228 | 12:00
| Borhanuddin | 246 | 03:00 | 239 | 12:00 | Rampal | 238 | 04:00 | 226 | 13:00
| BSRM | 235 | 04:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Cumilla(N) | 236 | 06:00 | 226 | 12:00 | Rampura | 240 | 02:00 | 223 | 12:00
| Faridpur | 247 | 03:00 | 224 | 18:00 | Shikalbaha | 234 | 05:00 | 227 | 13:00
| Fenchuganj | 233 | 04:00 | 224 | 21:00 | Shyampur | 240 | 01:00 | 224 | 13:00
| Ghorashal | 242 | 01:00 | 240 | 00:00 | Siddhirganj | 241 | 00:00 | 225 | 12:00
| Ghorashal-230 | 238 | 01:00 | 223 | 12:00 | Sirajgonj | 245 | 01:00 | 239 | 12:00
| Gopalganj | 246 | 02:00 | 234 | 12:00 | Sreepur | 239 | 01:00 | 229 | 12:00
| GPH | 235 | 03:00 | 227 | 12:00 | Tongi | 238 | 04:00 | 225 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 137 | 03:00 | 126 | 12:00 | Kushtia | 140 | 03:00 | 134 | 12:00
| Agargaon | 138 | 01:00 | 127 | 12:00 | Lalbag | 137 | 03:00 | 125 | 13:00
| Agrabad | 133 | 02:00 | 127 | 12:00 | Lalmonirhat | 132 | 04:00 | 124 | 19:30
| AKS | 132 | 04:00 | 127 | 13:00 | Madanganj | 135 | 04:00 | 125 | 12:00
| Aminbazar | 137 | 01:00 | 128 | 13:00 | Madaripur | 138 | 06:00 | 131 | 13:00
| Amnura | 139 | 04:00 | 133 | 08:00 | Madartek | 136 | 02:00 | 126 | 12:00
| Ashuganj | 140 | 00:00 | 136 | 12:00 | Madunaghat | 135 | 06:00 | 130 | 12:00
| Bagerhat | 138 | 05:00 | 129 | 18:00 | Magura | 142 | 06:00 | 133 | 12:00
| Bakulia | 135 | 00:00 | 128 | 16:00 | Mahasthangarh | 137 | 02:00 | 130 | 18:30
| Banani | 137 | 00:00 | 126 | 12:00 | Manikganj | 132 | 01:00 | 121 | 12:00
| Bangabhaban | 138 | 04:00 | 122 | 12:00 | Maniknagar | 138 | 03:00 | 122 | 12:00
| Barapukuria | 136 | 01:00 | 129 | 19:30 | Matarbari | 123 | 08:00 | 117 | 12:00
| Barguna | 142 | 18:00 | 132 | 13:00 | Matuail | 136 | 01:00 | 127 | 12:00
| Barishal | 136 | 04:00 | 130 | 12:00 | Millgate | 136 | 02:00 | 124 | 12:00
| Barishal-230 | 137 | 01:00 | 129 | 13:00 | Mirpur | 137 | 02:00 | 124 | 12:00
| Baroaulia | 134 | 02:00 | 132 | 15:00 | Mirzapur | 129 | 04:00 | 121 | 12:00
| Baroirhat | 132 | 06:00 | 125 | 12:00 | Mithapukur | 135 | 04:00 | 127 | 08:00
| Bashundhara | 137 | 02:00 | 120 | 18:30 | MI_Cement | 136 | 01:00 | 126 | 12:00
| BashundharaCement | 135 | 04:00 | 125 | 12:00 | Modern | 134 | 07:00 | 128 | 12:00
| Beanibazar | 134 | 05:00 | 130 | 12:00 | Mogbazar | 139 | 03:00 | 127 | 12:00
| Benapole | 138 | 06:00 | 128 | 12:00 | Mongla | 136 | 04:00 | 129 | 18:00
| Bhaluka | 134 | 22:00 | 125 | 12:00 | Motijheel | 138 | 05:00 | 122 | 12:00
| Bhandaria | 135 | 09:00 | 129 | 12:00 | Munshiganj | 136 | 05:00 | 126 | 12:00
| Bhangura | 143 | 02:00 | 124 | 07:00 | Mymensingh | 135 | 22:00 | 120 | 00:00
| Bheramara | 140 | 04:00 | 134 | 12:00 | Naogaon | 137 | 05:00 | 130 | 08:00
| Bheramara(GK) | 140 | 04:00 | 135 | 12:00 | Narail | 142 | 05:00 | 133 | 12:00
| Bhulta | 140 | 17:00 | 120 | 12:00 | Narinda | 138 | 03:00 | 122 | 12:00
| Bog-Sherpur | 138 | 02:00 | 132 | 17:00 | Narshingdi | 134 | 01:00 | 121 | 12:00
| Bogura | 137 | 00:00 | 133 | 08:00 | Natore | 138 | 02:00 | 132 | 12:00
| Bogura-230 | 138 | 03:00 | 129 | 20:00 | Nawabganj | 137 | 01:00 | 127 | 12:00
| Brahmanbaria | 135 | 06:00 | 128 | 12:00 | Netrakona | 135 | 09:00 | 122 | 00:00
| Cantonment | 138 | 03:00 | 127 | 12:00 | New | 137 | 01:00 | 126 | 12:00
| Chandpur | 135 | 17:00 | 122 | 12:00 | Niamatpur | 141 | 02:00 | 135 | 13:00
| Chandraghona | 136 | 03:00 | 131 | 12:00 | Noapara | 139 | 04:00 | 130 | 12:00
| Chapai | 139 | 02:00 | 135 | 08:00 | Pabna | 141 | 02:00 | 134 | 12:00
| Charsaidpur | 136 | 03:00 | 126 | 12:00 | Palashbari | 135 | 04:00 | 124 | 18:00
| Chauddagram | 134 | 18:00 | 124 | 12:00 | Panchagarh | 131 | 03:00 | 119 | 12:00
| Chhatak | 134 | 05:00 | 120 | 16:00 | Patuakhali | 142 | 18:00 | 134 | 00:00
| Chowmuhani | 133 | 18:00 | 121 | 15:00 | Payra | 139 | 18:00 | 134 | 13:00
| Chuadanga | 140 | 05:00 | 130 | 12:00 | PHP | 132 | 17:00 | 123 | 13:00
| Coxsbazar | 122 | 02:00 | 116 | 00:00 | Postogola | 138 | 04:00 | 127 | 12:00
| Cumilla(N) | 137 | 04:00 | 128 | 12:00 | Purbachal | 137 | 01:00 | 125 | 12:00
| Cumilla(S) | 136 | 17:00 | 126 | 12:00 | Purbasadipur | 131 | 04:00 | 121 | 08:00
| Daudkandi | 133 | 01:00 | 120 | 12:00 | Rahanpur | 141 | 02:00 | 137 | 08:00
| Dhaka | 137 | 01:00 | 126 | 12:00 | Rahim | 135 | 00:00 | 123 | 22:00
| Dhamrai | 138 | 03:00 | 126 | 12:00 | Rajbari | 137 | 02:00 | 129 | 13:00
| Dhanmondi | 137 | 05:00 | 127 | 12:00 | Rajendrapur | 128 | 19:30 | 117 | 12:00
| Dohazari | 129 | 06:00 | 125 | 12:00 | Rajshahi | 140 | 06:00 | 131 | 12:00
| Faridpur | 136 | 00:00 | 130 | 13:00 | Rajshahi-230 | 139 | 04:00 | 131 | 13:00
| Fatullah | 137 | 03:00 | 127 | 12:00 | Ramganj | 134 | 18:30 | 121 | 12:00
| Fenchuganj | 137 | 04:00 | 134 | 16:00 | Rampur | 133 | 02:00 | 127 | 16:00
| Feni | 133 | 18:00 | 124 | 12:00 | Rampura | 137 | 03:00 | 126 | 12:00
| Ghatail | 131 | 08:00 | 121 | 00:00 | Rangamati | 135 | 06:00 | 130 | 12:00
| Ghorashal | 141 | 00:00 | 134 | 12:00 | Rangpur | 133 | 02:00 | 123 | 18:30
| Goalpara | 141 | 04:00 | 132 | 12:00 | Ruppur | 141 | 05:00 | 136 | 12:00
| Gollamari | 140 | 05:00 | 132 | 12:00 | Saidpur | 134 | 05:00 | 122 | 19:30
| Gopalganj | 138 | 03:00 | 131 | 12:00 | Satkhira | 138 | 03:00 | 130 | 18:00
| Gopalganj-400 | 138 | 02:00 | 131 | 12:00 | Satmasjid | 137 | 19:30 | 126 | 13:00
| Gulshan | 135 | 00:00 | 125 | 13:00 | Savar | 136 | 04:00 | 123 | 12:00
| Halishahar | 134 | 06:00 | 127 | 12:00 | SevenRings | 142 | 01:00 | 133 | 13:00
| Haripur | 136 | 02:00 | 127 | 12:00 | ShahCement | 136 | 03:00 | 126 | 12:00
| HaripurSBU | 136 | 02:00 | 128 | 13:00 | Shahjadpur | 145 | 02:00 | 139 | 12:00
| Hasnabad | 137 | 00:00 | 128 | 12:00 | Shahjibazar | 135 | 04:00 | 129 | 12:00
| Hathazari | 138 | 09:00 | 132 | 15:00 | Shahmirpur | 134 | 01:00 | 130 | 12:00
| Ishurdi | 141 | 03:00 | 135 | 12:00 | Shariatpur | 137 | 04:00 | 130 | 12:00
| Jaldhaka | 132 | 03:00 | 122 | 08:00 | Sherpur | 138 | 22:00 | 118 | 00:00
| Jamalpur | 139 | 22:00 | 121 | 00:00 | Shikalbaha | 123 | 06:00 | 118 | 11:00
| Jashore | 138 | 06:00 | 129 | 12:00 | Shikalbaha-230 | 135 | 07:00 | 130 | 13:00
| Jhenaidah | 142 | 04:00 | 134 | 12:00 | Shitalakhya | 136 | 01:00 | 126 | 12:00
| Jhenaidah-230 | 143 | 03:00 | 134 | 13:00 | Sholosohor | 135 | 06:00 | 130 | 12:00
| Joydebpur | 140 | 00:00 | 133 | 12:00 | Shyampur | 134 | 15:00 | 131 | 17:00
| Joypurhat | 137 | 02:00 | 129 | 12:00 | Shyampur-230 | 135 | 00:00 | 126 | 12:00
| Juldah | 133 | 04:00 | 128 | 16:00 | Siddhirganj | 137 | 04:00 | 127 | 12:00
| Kabirpur | 135 | 01:00 | 121 | 12:00 | Sirajganj | 141 | 03:00 | 134 | 12:00
| Kachua | 137 | 18:00 | 126 | 14:00 | Sonargaon | 135 | 02:00 | 124 | 12:00
| Kaliakoir | 139 | 01:00 | 125 | 12:00 | Sreemongol | 135 | 03:00 | 130 | 12:00
| Kallyanpur | 136 | 03:00 | 127 | 12:00 | Sreepur | 136 | 00:00 | 129 | 12:00
| Kalurghat | 135 | 03:00 | 130 | 12:00 | Srinagar | 136 | 04:00 | 126 | 12:00
| Kamrangirchar | 136 | 01:00 | 125 | 12:00 | SSM | 139 | 06:00 | 136 | 10:00
| Kaptai | 135 | 1:00 | 129 | 12:00 | Sunamganj | 132 | 04:00 | 128 | 12:00
| Kazla | 138 | 03:00 | 120 | 13:00 | Sylhet | 135 | 05:00 | 131 | 10:00
| Keranigonj | 137 | 03:00 | 126 | 13:00 | Sylhet-132 | 134 | 06:00 | 131 | 12:00
| Khagrachori | 137 | 00:00 | 129 | 16:00 | Tangail | 129 | 08:00 | 122 | 12:00
| Khulna | 137 | 00:00 | 130 | 13:00 | Thakurgaon | 132 | 05:00 | 118 | 19:30
| Khulna(S) | 140 | 03:00 | 132 | 12:00 | TK | 135 | 07:00 | 130 | 13:00
| Khulshi | 133 | 06:00 | 126 | 12:00 | Tongi | 139 | 04:00 | 129 | 11:00
| Kishoreganj | 134 | 01:00 | 127 | 12:00 | Ullahpara | 142 | 04:00 | 124 | 00:00
| Kodda | 138 | 19:00 | 119 | 10:00 | Ullon | 136 | 01:00 | 125 | 13:00
| KSRM | 136 | 06:00 | 129 | 12:00 | Uttara | 137 | 03:00 | 125 | 13:00
| Kulaura | 137 | 03:00 | 134 | 11:00 | UttaraNew | 137 | 07:00 | 125 | 12:00
| Kurigram | 132 | 05:00 | 122 | 07:00 | Zigatola | 137 | 03:00 | 126 | 12:00

## L-Curve
Date | 2024-11-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1214 | 5078 | 3570 | 8648 |  |  |  | QF-LDC-11
0:30 | 1115 | 4804.5 | 3516.5 | 8321 | Date: | 2024-11-30
1:00 | 1016 | 4531 | 3463 | 7994
1:30 | 1021 | 4373 | 3384.5 | 7757.5
2:00 | 1026 | 4215 | 3306 | 7521
2:30 | 958 | 4123.5 | 3301 | 7424.5 | [5 empty] | Gen. at Eve. Peak | 10812 | 10812 MW (18:00 )
3:00 | 890 | 4032 | 3296 | 7328 | [6 empty] | 18:00
3:30 | 921 | 4024.5 | 3171.5 | 7196 | [5 empty] | Gen. at Day Peak | 9424 | 9424 MW (12:00 )
4:00 | 952 | 4017 | 3047 | 7064 | [6 empty] | 12:00
4:30 | 960 | 4044 | 3048.5 | 7092.5 | [5 empty] | Highest Generation | 10812
5:00 | 968 | 4071 | 3050 | 7121 | [6 empty] | 18:00
5:30 | 934 | 4137 | 3107 | 7244
6:00 | 900 | 4203 | 3164 | 7367
6:30 | 806 | 4375.5 | 3298 | 7673.5
7:00 | 712 | 4548 | 3432 | 7980
7:30 | 637 | 4557 | 3701.5 | 8258.5
8:00 | 562 | 4566 | 3971 | 8537
8:30 | 696 | 4483.5 | 3961.5 | 8445
9:00 | 830 | 4401 | 3952 | 8353
9:30 | 928 | 4432.5 | 3908 | 8340.5
10:00 | 1026 | 4464 | 3864 | 8328
10:30 | 1158 | 4619 | 3927.5 | 8546.5
11:00 | 1290 | 4774 | 3991 | 8765
11:30 | 1349 | 4963.5 | 4131 | 9094.5
12:00 | 1408 | 5153 | 4271 | 9424
12:30 | 1341 | 5171 | 4412.5 | 9583.5
13:00 | 1274 | 5189 | 4554 | 9743
13:30 | 1330 | 5110 | 4430 | 9540
14:00 | 1386 | 5031 | 4306 | 9337
14:30 | 1290 | 5015.5 | 4192 | 9207.5
15:00 | 1194 | 5000 | 4078 | 9078
15:30 | 1137 | 5022.5 | 4017 | 9039.5
16:00 | 1080 | 5045 | 3956 | 9001
16:30 | 1095 | 5194 | 4055 | 9249
17:00 | 1110 | 5343 | 4154 | 9497
17:30 | 993 | 5766 | 4388.5 | 10154.5
18:00 | 876 | 6189 | 4623 | 10812
18:30 | 956 | 5990 | 4529.5 | 10519.5
19:00 | 1036 | 5791 | 4436 | 10227
19:30 | 1082 | 5785 | 4351 | 10136
20:00 | 1120 | 5615 | 4330 | 9945 |  |  |  | Executive Engineer
20:30 | 1116 | 5657 | 4251.5 | 9908.5 |  |  |  | Network Operation Division
21:00 | 1112 | 5699 | 4173 | 9872
21:30 | 1155 | 5599 | 4115.5 | 9714.5
22:00 | 1198 | 5499 | 4058 | 9557 |  |  |  |  | Page 6 of 7
22:30 | 1204 | 5342.5 | 3921.5 | 9264
23:00 | 1210 | 5186 | 3785 | 8971
23:30 | 1212 | 5132 | 3677.5 | 8809.5
24:00 | 1214 | 5078 | 3570 | 8648
10812 MW (18:00 )
9424 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-11-30 |  |  | Energy |  | 213101999
[17 empty] | 2024-11-30 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | Nepal | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3109 | 575 | 0 | 1387 | 0 | 90 | 2684 | 47 | 0 | 16 | 56 | 662 | 0 | 22 | 0
0:30 | 3127.5 | 742.5 | 0 | 1588.5 | 0 | 45 | 2121 | 43.5 | 0 | 8 | 53 | 579.5 | 0 | 12.5 | 0 |  |  | Date: | 44164
1:00 | 3146 | 910 | 0 | 1790 | 0 | 0 | 1558 | 40 | 0 | 0 | 50 | 497 | 0 | 3 | 0
1:30 | 3081 | 909.5 | 0 | 1676 | 0 | 0 | 1543 | 40 | 0 | 0 | 49 | 457.5 | 0 | 1.5 | 0 | [8 empty] | Total Energy | 213.102 | 213.102 | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr | Total Energy Gen 213.102 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 213.102 MKWHr
2:00 | 3016 | 909 | 0 | 1562 | 0 | 0 | 1528 | 40 | 0 | 0 | 48 | 418 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 3005 | 909 | 0 | 1501.5 | 0 | 0 | 1502.5 | 40 | 0 | 0 | 48 | 418.5 | 0 | 0 | 0 | [8 empty] | Energy Requirement | 213.102 | 213.102
3:00 | 2994 | 909 | 0 | 1441 | 0 | 0 | 1477 | 40 | 0 | 0 | 48 | 419 | 0 | 0 | 0
3:30 | 3028.5 | 813.5 | 0 | 1367 | 0 | 0 | 1476.5 | 44 | 0 | 0 | 47 | 419 | 0 | 0.5 | 0 | [7 empty] | Shortage
4:00 | 3063 | 718 | 0 | 1293 | 0 | 0 | 1476 | 48 | 0 | 0 | 46 | 419 | 0 | 1 | 0
4:30 | 3066 | 718 | 0 | 1314 | 0 | 0 | 1481 | 48 | 0 | 0 | 46 | 419 | 0 | 0.5 | 0
5:00 | 3069 | 718 | 0 | 1335 | 0 | 0 | 1486 | 48 | 0 | 0 | 46 | 419 | 0 | 0 | 0
5:30 | 3106 | 717.5 | 0 | 1393 | 0 | 1 | 1516 | 48.5 | 0 | 0 | 43 | 419 | 0 | 0 | 0
6:00 | 3143 | 717 | 0 | 1451 | 0 | 2 | 1546 | 49 | 0 | 0 | 40 | 419 | 0 | 0 | 0
6:30 | 3217.5 | 717.5 | 0 | 1472.5 | 0 | 21.5 | 1660.5 | 49.5 | 0 | 8 | 42 | 470 | 14.5 | 0 | 0 | [6 empty] | Coal
7:00 | 3292 | 718 | 0 | 1494 | 0 | 41 | 1775 | 50 | 0 | 16 | 44 | 521 | 29 | 0 | 0
7:30 | 3217.5 | 791 | 0 | 1471 | 0 | 79.5 | 1865.5 | 50 | 0 | 24 | 43 | 591.5 | 125.5 | 0 | 0 | [5 empty] | Oil
8:00 | 3143 | 864 | 0 | 1448 | 0 | 118 | 1956 | 50 | 0 | 32 | 42 | 662 | 222 | 0 | 0
8:30 | 3038.5 | 882 | 0 | 1425.5 | 0 | 103.5 | 1908.5 | 50 | 0 | 32 | 39 | 688 | 278 | 0 | 0
9:00 | 2934 | 900 | 0 | 1403 | 0 | 89 | 1861 | 50 | 0 | 32 | 36 | 714 | 334 | 0 | 0
9:30 | 2972 | 900 | 0 | 1415 | 0 | 81 | 1798 | 50 | 0 | 32 | 39 | 661.5 | 392 | 0 | 0
10:00 | 3010 | 900 | 0 | 1427 | 0 | 73 | 1735 | 50 | 0 | 32 | 42 | 609 | 450 | 0 | 0
10:30 | 3063.5 | 900.5 | 0 | 1536.5 | 0 | 86 | 1781.5 | 50 | 0 | 39 | 43 | 586 | 460.5 | 0 | 0
11:00 | 3117 | 901 | 0 | 1646 | 0 | 99 | 1828 | 50 | 0 | 46 | 44 | 563 | 471 | 0 | 0
11:30 | 3230 | 900.5 | 0 | 1657 | 0 | 118.5 | 2000 | 49.5 | 0 | 50.5 | 43 | 558.5 | 487 | 0 | 0
12:00 | 3343 | 900 | 0 | 1668 | 0 | 138 | 2172 | 49 | 0 | 55 | 42 | 554 | 503 | 0 | 0
12:30 | 3316 | 900 | 0 | 1664.5 | 0 | 164 | 2365 | 48 | 0 | 59.5 | 47 | 556 | 463.5 | 0 | 0
13:00 | 3289 | 900 | 0 | 1661 | 0 | 190 | 2558 | 47 | 0 | 64 | 52 | 558 | 424 | 0 | 0
13:30 | 3289 | 900 | 0 | 1661 | 0 | 190 | 2558 | 47 | 0 | 64 | 52 | 558 | 424 | 0 | 0
14:00 | 3289 | 900 | 0 | 1661 | 0 | 190 | 2558 | 47 | 0 | 64 | 52 | 558 | 424 | 0 | 0
14:30 | 3137.5 | 900 | 0 | 1641 | 0 | 202 | 2499.5 | 46.5 | 0 | 64 | 55 | 537.5 | 323 | 4.5 | 0
15:00 | 2986 | 900 | 0 | 1621 | 0 | 214 | 2441 | 46 | 0 | 64 | 58 | 517 | 222 | 9 | 0
15:30 | 2989 | 899.5 | 0 | 1636.5 | 0 | 214 | 2431.5 | 46.5 | 0 | 64 | 55 | 543.5 | 152.5 | 7.5 | 0
16:00 | 2992 | 899 | 0 | 1652 | 0 | 214 | 2422 | 47 | 0 | 64 | 52 | 570 | 83 | 6 | 0
16:30 | 2994 | 899.5 | 0 | 1674 | 0 | 367 | 2454.5 | 47 | 0 | 71.5 | 55 | 636 | 43 | 7.5 | 0
17:00 | 2996 | 900 | 0 | 1696 | 0 | 520 | 2487 | 47 | 0 | 79 | 58 | 702 | 3 | 9 | 0
17:30 | 3084 | 899.5 | 0 | 1642.5 | 0 | 835.5 | 2708 | 70.5 | 0 | 118 | 61 | 728 | 1.5 | 6 | 0
18:00 | 3172 | 899 | 0 | 1589 | 0 | 1151 | 2929 | 94 | 0 | 157 | 64 | 754 | 0 | 3 | 0
18:30 | 3136.5 | 898.5 | 0 | 1597.5 | 0 | 862 | 2994.5 | 94 | 0 | 119.5 | 61 | 754.5 | 0 | 1.5 | 0
19:00 | 3101 | 898 | 0 | 1606 | 0 | 573 | 3060 | 94 | 0 | 82 | 58 | 755 | 0 | 0 | 0
19:30 | 3110 | 902 | 0 | 1824 | 0 | 341 | 2991 | 94 | 0 | 64 | 56 | 754 | 0 | 0 | 0
20:00 | 3104 | 884 | 0 | 1788 | 0 | 211 | 2991 | 94 | 0 | 64 | 54 | 754 | 0 | 1 | 0
20:30 | 3136.5 | 824 | 0 | 1822 | 0 | 198 | 2964 | 94.5 | 0 | 56 | 54 | 756 | 0 | 3.5 | 0
21:00 | 3169 | 764 | 0 | 1856 | 0 | 185 | 2937 | 95 | 0 | 48 | 54 | 758 | 0 | 6 | 0
21:30 | 3149 | 716.5 | 0 | 1681.5 | 0 | 184 | 3017 | 95 | 0 | 48 | 55 | 756 | 0 | 12.5 | 0
22:00 | 3129 | 669 | 0 | 1507 | 0 | 183 | 3097 | 95 | 0 | 48 | 56 | 754 | 0 | 19 | 0
22:30 | 3127.5 | 669 | 0 | 1447 | 0 | 151 | 2965 | 72 | 0 | 40 | 54 | 720.5 | 0 | 18 | 0
23:00 | 3126 | 669 | 0 | 1387 | 0 | 119 | 2833 | 49 | 0 | 32 | 52 | 687 | 0 | 17 | 0
23:30 | 3117.5 | 622 | 0 | 1387 | 0 | 104.5 | 2758.5 | 48 | 0 | 24 | 54 | 674.5 | 0 | 19.5 | 0 |  |  | Max Temp. in Dhaka |  | 30.7°C
24:00 | 3109 | 575 | 0 | 1387 | 0 | 90 | 2684 | 47 | 0 | 16 | 56 | 662 | 0 | 22 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 213.102 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 213.102 MKWHr
Note on Y13: Author:

## Generation
2024-11-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 48 | 48 | 49 | 50 | 50 | 50 | 50 | 50 | 49 | 47 | 45 | 46 | 47 | 47 | 94 |  | 94 | 94 | 94 | 95 | 95 | 49 | 47 | 1368180
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 10 | 14 | 18 | 18 | 17 | 18 |  | 9 | 3 | [10 empty] | 105030
6 | Sikalbaha 225MW CCPP (Gas) | 227 | 186 | 187 | 188 | 187 | 187 | 226 | 226 | 182 | 183 | 212 | 216 | 218 | 218 | 216 | 216 | 215 | 220 |  | 225 | 223 | 224 | 223 | 224 | 221 | 221 | 4909231
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [25 empty] | 0 | 0
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [25 empty] | 0 | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 290 | 280 | 335 | 335 | 335 | 335 | 290 | 290 | 290 | 290 | 325 | 323 | 290 | 250 | 250 | 250 | 335 |  | 280 | 280 | 280 | 335 | 335 | 335 | 335 | 7451167
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 197 | 88 | 16 | 8 | 8 | 45 | 46 | 92 | 92 | 92 | 178 | 184 | 175 | 172 | 172 | 172 | 182 | 183 |  | 185 | 185 | 185 | 185 | 185 | 187 | 187 | 3278545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 595 | 602 | 565 | 563 | 570 | 566 | 654 | 705 | 700 | 650 | 705 | 885 | 935 | 954 | 950 | 950 | 994 | 1156 |  | 1220 | 1221 | 1224 | 1103 | 1103 | 1000 | 947 | 20198180
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 41 | 10 | 10 | 10 | 10 | 25 | 39 | 38 | 38 | 37 | 38 | 41 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 41 | 41 | 41 | 41 | 840024
33 | Ashuganj 225 MW CCPP | 183 | 184 | 182 | 181 | 185 | 182 | 210 | 181 | 181 | 201 | 196 | 211 | 200 | 182 | 183 | 212 | 182 | 182 |  | 183 | 189 | 181 | 181 | 181 | 189 | 181 | 4625000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 290 | 280 | 280 | 310 | 280 | 310 | 355 | 285 | 285 | 315 | 325 | 350 | 355 | 285 | 280 | 340 | 285 | 310 |  | 285 | 285 | 285 | 285 | 285 | 305 | 285 | 7553900
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1193530
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 401 | 392 | 358 | 362 | 384 | 392 | 408 | 400 | 373 | 373 | 402 | 409 | 405 | 407 | 353 | 323 | 361 | 421 |  | 415 | 417 | 419 | 425 | 387 | 380 | 380 | 9489600
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 583 | 583 | 500 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 420 | 470 | 480 | 480 | 530 |  | 590 | 595 | 595 | 595 | 250 | 250 | 250 | 10184545
40 | Meghnaghat 450 MW CCPP(MPL) | [25 empty] | 0 | 0
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 16 | 16 | 35 | 35 | 50 | 51 | 47 | 45 | 28 | 28 | 27 | 11 | 10 | 14 | 10 | 10 | 10 | 10 |  | 10 | 16 | 16 | 18 | 17 | 18 | 27 | 489600
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 17 | 33 | 42 | 47 | 35 | 45 | 37 | 22 | 6 | 0 | [9 empty] | 281810
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 56 | 56 | 56 | 56 | 40 | 40 | 40 | 54 | 54 | 54 | 40 | 40 | 40 | 40 | 56 |  | 40 | 40 | 40 | 56 | 56 | 40 | 40 | 1098816
48 | Shahjibazar 86 MW PP (Shahjibazar) | 42 | 11 | 11 | 11 | 11 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 833280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 171 | 171 | 171 | 171 | 172 | 174 | 176 | 176 | 175 | 176 | 174 | 174 | 170 | 169 | 169 | 170 | 168 | 168 |  | 167 | 167 | 167 | 167 | 167 | 167 | 177 | 3567750
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 56784
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 354384
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 280 | 290 | 300 | 295 | 300 | 290 | 285 | 280 | 295 | 305 | 310 | 310 | 275 | 290 | 290 | 295 | 110 |  | 55 | 250 | 215 | 295 | 285 | 290 | 300 | 6651390
| Bibiyana South 400 MW | 305 | 305 | 306 | 309 | 305 | 305 | 307 | 305 | 305 | 335 | 316 | 356 | 331 | 331 | 331 | 331 | 331 | 317 |  | 331 | 331 | 331 | 331 | 331 | 330 | 330 | 7730300
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 5 | 17 | [7 empty] | 0 | 34560
59 | Tangail Palli Power Gen 22 MW | [6 empty] | 7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 |  |  |  |  | 0 | 335280
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 50 | 48 | 48 | 46 | 46 | 40 | 44 | 42 | 36 | 42 | 44 | 42 | 52 | 44 | 58 | 52 | 58 | 64 |  | 58 | 56 | 54 | 54 | 56 | 52 | 56 | 1172160
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 34 | 6 | 2 | 2 | 2 | 2 | 6 | 2 | 2 | 2 | 2 | 4 |  | 7 | 7 | 15 | 15 | 25 | 32 | 33 | 440640
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 3 | 10 | 13 | 13 | 13 | 13 | 13 | 13 | 12 |  | 15 | 15 | 15 | 15 | 15 | 13 | 13 | 296290
69 | Summit Ashulia | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 7 | 7 | 7 | 9 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 123000
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0 | 0 | 0 |  | 0 | [6 empty] | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 274320
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 23 | 17 | 520160
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  |  | 24 | 24 | 24 | 30 | 28 | 28 | 28 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 661700
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [16 empty] | 36 | 34 | [7 empty] | 0 | 49020
| Chowmuhani 113 MW | [12 empty] | 3 | 17 | 17 | 17 | 49 | 86 |  | 63 | 34 | [5 empty] | 330960
| Manikgonj 162MW PP(MPGL) | [16 empty] | 30 | 108 |  | 17 | [5 empty] | 0 | 128160
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [10 empty] | 25 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 8 |  |  |  | 0 | 304800
79 | Kodda 150 MW PP | [6 empty] | 16 | 32 | 32 | 32 | 46 | 55 | 64 | 64 | 64 | 64 | 64 | 82 |  | 82 | 64 | 64 | 48 | 48 | 32 | 16 | 894720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 7 | 25 |  | 8 | 8 | [5 empty] | 51706
| Gazipur 100 MW PP | [16 empty] | 17 | 35 |  | 17 | [5 empty] | 0 | 51427
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 3 | 4 | 4 | 2 | 3 | 2 | 0 | [10 empty] | 22559
| Jodiac Power | [17 empty] | 16 | [7 empty] | 0 | 51432
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 150 | 149 | 142 | 124 | 120 | 118 | 151 | 146 | 141 | 150 | 146 | 152 | 149 | 127 | 135 | 156 | 142 | 124 |  | 131 | 148 | 139 | 127 | 123 | 148 | 137 | 3360844
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [17 empty] | 5 | [7 empty] | 0 | 10176
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | [11 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 94104
93 | Ashuganj 51 MW PP (Midland) | 51 | 5 | 5 | 5 | 5 | 5 | 33 | 42 | 43 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 912576
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 8 | 8 |  | 8 | [5 empty] | 0 | 22176
95 | Patenga 50MW PP (Baraka) | [16 empty] | 6 | 22 |  | 26 | 6 |  |  |  |  | 0 | 66720
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP) | 20 | 28 | 60 | 98 | 148 | 163 | 163 | 120 | 120 | 120 | 163 | 163 | 163 | 120 | 120 | 120 | 163 | 163 |  | 163 | 120 | 120 | 120 | 120 | 25 | 25 | 2916818
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | [6 empty] | 0 | [10 empty] | 1750
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 2 | [7 empty] | 0 | 14400
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [6 empty] | 10 | 45 | 24 | 8 | 8 | 10 | 35 | 35 | 35 | 35 | 74 | 93 |  | 94 | 94 | 94 | 94 | 93 | 45 | 35 | 883200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 4 | 17 | 17 | 18 | 35 | 50 | 52 | 53 | 53 | 53 | 53 |  | 53 | 53 | 37 | 36 | 35 | 19 | 0 | 609120
115 | Juldah 100 MW PP Unit-3 (Acorn) | [17 empty] | 25 | [7 empty] | 0 | 48960
116 | Chandpur 200 MW (Desh energy) | [16 empty] | 8 | 68 |  | 34 | 17 | 17 |  |  |  | 0 | 146400
117 | Ashuganj 150 MW PP (Midland) | [16 empty] | 13 | 45 |  | 20 | [5 empty] | 0 | 105382
118 | Bibiyana-III 400 MW CCPP | 311 | 312 | 313 | 313 | 313 | 313 | 313 | 313 | 313 | 310 | 310 | 313 | 312 | 312 | 312 | 311 | 311 | 310 |  | 310 | 310 | 310 | 310 | 310 | 311 | 312 | 7816000
| Jamalpur 115 MW PP (United) | [5 empty] | 2 | 24 | 45 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35 | 40 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 750000
| Anwara 300 MW PP (United) | [17 empty] | 30 | [7 empty] | 0 | 30109
| Juldah unit-2 (Acorn) | [17 empty] | 25 | [7 empty] | 0 | 15360
| Anlima Energy Ltd. | [17 empty] | 10 | [7 empty] | 0 | 41400
| Bhairob 54.5 MW | [17 empty] | 8 | [7 empty] | 0 | 33480
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 12 | 18 | 14 | 13 | 14 | 10 | 7 | 3 | 1 | [10 empty] | 114076
| Chandpur 115(Doreen) | [12 empty] | 9 | 16 | 16 | 16 | 43 | 72 |  | 51 | 16 |  |  |  |  | 0 | 264000
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 30 | 36 |  | 17 | [5 empty] | 0 | 97920
| Mirsharai 150 MW (Oil) | [17 empty] | 35 | [7 empty] | 0 | 8364
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 9 | 3 |  | 0 | 0 | 1 | 6 | 19 | 17 | 22 | 85440
| Sonagazi 75 MW Solar Plant | [6 empty] | 7 | 30 | 49 | 65 | 51 | 69 | 31 | 22 | 12 | 2 | 0 | [9 empty] | 348555
| Matarbari 2*600 MW (CPGCL) | [16 empty] | 0 | 102 |  | 150 | 154 | 153 | 247 | 421 | 400 | 397 | 1621818
JERA Meghnaghat Power Limited
| Sreepur 150 MW | [25 empty] | 0 | 0
120
121 | Eastern Zone Total | 4531 | 4215 | 4032 | 4017 | 4071 | 4203 | 4548 | 4566 | 4401 | 4464 | 4774 | 5153 | 5189 | 5031 | 5000 | 5045 | 5343 | 6189 |  | 5791 | 5785 | 5615 | 5699 | 5499 | 5186 | 5078 | 118423088
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 19 | 16 | 26 | 21 | 31 | 16 | 24 | 17 | 4 | 0 | [9 empty] | 185760
132 | Rampal 1320 MW (BIFPCL) | 360 | 360 | 360 | 361 | 362 | 402 | 451 | 464 | 408 | 379 | 378 | 400 | 561 | 531 | 511 | 516 | 511 | 624 |  | 623 | 624 | 622 | 557 | 559 | 511 | 410 | 11272730
133 | United Payra Power Ltd. | [16 empty] | 10 | 100 |  | 17 | [5 empty] | 0 | 139200
Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 188 | 200 | 224 | 200 | 150 | 150 | 248 | 307 | 295 | 270 | 270 | 270 | 307 |  | 307 | 307 | 307 | 307 | 307 | 250 | 250 | 5542000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 1731
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 130 | 130 | 130 | 130 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 3156000
141 | Bhola 33 MW PP (Venture) | 6 | 6 | 5 | 5 | 6 | 6 | 5 | 5 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 129063
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
| Bheramara HVDC | 910 | 909 | 909 | 718 | 718 | 717 | 718 | 864 | 900 | 900 | 901 | 900 | 900 | 900 | 900 | 899 | 900 | 899 |  | 898 | 902 | 884 | 764 | 669 | 669 | 575 | 20376000
147 | Nepal
148 | Bheramara 410 MW CCPP | 232 | 235 | 235 | 241 | 240 | 261 | 268 | 278 | 230 | 230 | 230 | 274 | 264 | 252 | 252 | 200 | 228 | 227 |  | 227 | 227 | 227 | 224 | 224 | 224 | 224 | 5879520
149 | Payra 1320 MW | 300 | 265 | 250 | 250 | 250 | 260 | 350 | 440 | 430 | 430 | 430 | 480 | 600 | 622 | 550 | 530 | 550 | 580 |  | 622 | 560 | 560 | 560 | 550 | 550 | 560 | 11344000
150
151 | Barapukuria TPP Unit-1
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 153 | 151 | 152 | 152 | 154 | 130 | 120 | 123 | 123 | 126 | 165 | 159 | 155 | 163 | 160 | 156 | 162 | 160 |  | 138 | 125 | 125 | 163 | 157 | 122 | 120 | 3597000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 4 | 0 | 2 | 4 | 4 | 0 | 1 | 1 | 0 | [9 empty] | 26700
157 | Sirajganj 68 MW Solar Park | [6 empty] | 1 | 19 | 20 | 50 | 41 | 58 | 56 | 43 | 20 | 14 | 1 | [9 empty] | 337500
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 155 | 156 | 160 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 142 | 172 | 173 | 140 | 140 | 140 | 152 | 154 |  | 150 | 148 | 148 | 145 | 145 | 144 | 144 | 3579636
Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 150 | 150 | 150 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 141 | 167 | 164 | 140 | 140 | 140 | 152 | 151 |  | 148 | 144 | 143 | 135 | 133 | 132 | 132 | 3621945
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 414 | 370 | 370 | 350 | 350 | 380 | 380 | 360 | 330 | 330 | 414 | 414 | 414 | 330 | 330 | 330 | 330 | 370 |  | 370 | 414 | 414 | 414 | 414 | 350 | 350 | 9161527
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 |  |  | 2 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 66456
166 | Amnura 50 MW PP(Sinha)
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP
169 | Santahar 50 MW Peaking PP | [26 empty] | 0
170 | Natore 52 MW PP (Rajlanka)
171 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 15 | 40 | [7 empty] | 0 | 60592
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [17 empty] | 8 | [7 empty] | 0 | 19200
173 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 35 | [7 empty] | 0 | 10080
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [25 empty] | 0 | 0
178 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 5 | 5 | 6 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 37163
| Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 33 | 72 |  | 35 | [5 empty] | 0 | 104256
| Intraco Solar 30 MW | [6 empty] | 2 | 12 | 25 | 28 | 35 | 36 | 32 | 24 | 17 | 7 | 0 | [9 empty] | 216335
178 | Adani Power Jharkhanda Ltd | 497 | 418 | 419 | 419 | 419 | 419 | 521 | 662 | 714 | 609 | 563 | 554 | 558 | 531 | 517 | 570 | 702 | 754 |  | 755 | 754 | 754 | 758 | 754 | 687 | 662 | 14326527
| Teesta Solar Limited | [6 empty] | 10 | 67 | 119 | 158 | 179 | 182 | 168 | 138 | 97 | 37 | 1 | [9 empty] | 1148940
179 | Pabna Solar 100 MW | [6 empty] | 2 | 30 | 28 | 41 | 55 | 47 | 37 | 29 | 19 | 7 | 1 | [9 empty] | 339050
| Western Zone Total | 3463 | 3306 | 3296 | 3047 | 3050 | 3164 | 3432 | 3971 | 3952 | 3864 | 3991 | 4271 | 4554 | 4306 | 4078 | 3956 | 4154 | 4623 |  | 4436 | 4351 | 4330 | 4173 | 4058 | 3785 | 3570 | 94678911
[27 empty] | Total | 213101999