## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-12-13 | Friday
|  | Date (day): | 2024-12-13 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12721.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13521 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-12-12 | 2024-12-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 367 | 431 | 400 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 2024-12-24
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Gas shortage
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 106 | 106 | 104 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 0 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 34 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 30 | 150 | 149 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 55 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 15 | 35 | 48 | 48 |  | 32 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 30 | 25 | 25 |  | 8 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 26 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 34 | 34 | 34 | 52
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 81 | 58 | 149 | 149
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 7 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 72 | 162 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 3 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 36 | 36 | 36 | 19 |  | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| JERA Meghnaghat Power Limited |  | Gas | IPP | 718 | 0 | 0 | 743 | 690 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1653 | 1931 | 1733 | 2144 | 2389 | 1325
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 190 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Filter Change
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 85 | 105
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 74 |  | 24 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 51 |  | 51 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 5 | 10 | 30
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 18 | 20 | 50 | 58 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 32 | 50 | 120 | 180 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 50 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 47 | 50 | 108
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 17 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 663 | 660 | 660 | 660 | 564 |  | Coal shortage
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 12 | 15 | 38 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 504 | 575 | 515 | 515 |  | 635 | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1214 | 1533 | 2015 | 2390 | 992 | 1445
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 198 | 180 | 200 | 200 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 310 | 350 | 350
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 41 | 40 | 40 |  |  | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 5 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 192 | 195 | 195 | 195 | 55
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 17 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 58 | 140 | 140 |  | 10 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 30 | 45 |  | 7 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 35 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 56 | 62 | 66 | 70
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 16 | 15 | 15 |  | 10 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 26 | 95 | 100 |  | 13 | Engine problem
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 50 | 92 | 23 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 65 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 954 | 990 | 1718 | 1714 | 196 | 800
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 7 | 5 | 12 | 16 | 186 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 24 | 50 | 96 | 95 | 105 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 57 | 55 | 55 | 60 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 40 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 24 | 24 | 24
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 53
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 37 | 0 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 161 | 153 | 255.6 | 243 | 186 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 29 | 30 | 30 | 30 |  | 40 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 34 | 5 | 34 | 34 | 16 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 57 | 58 | 60 | 60 | 6
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 65 | 42 | 86 | 86
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 135 | 135 | 135 | 135 |  | 96
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 22 | 22 |  | 3 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 330 | 330
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 80 | 359 | 360 | 360 |  | 40 | Machine problem
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 346 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2411 | 2366 | 1255 | 1473 | 1652 | 1652 | 22 | 578
100 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 441 | 484 | 450 | 499
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 35 |  | 19 | Engine problem
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 34 | 60 |  | 49 | Engine problem
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 248 | 229 | 250 | 250 | 160 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
106 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 100 | 0
108 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
109 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 464 | 583 | 620 | 620 | 614 |  | GT-1 S/D
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
** | Nepal |  | 0 | Imported power | 40 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1227 | 1296 | 1474 | 1464 | 1230 | 68
110 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 | 110 |  | Fuel shortage
111 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 4 | 6 | 5 | 7
112 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 134 | 135 | 135 |  | 59 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
113 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 490 | 470 | 622 | 622 |  | 622 | Unit-2 S/D.
114 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 217 | 220 | 220 | 220
115 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 54 | 150
116 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 240 | 285 | 307 | 307
117 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1031 | 1169 | 1343 | 1441 | 110 | 681
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 26 | 32 |  | 18 | Engine problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 150 | 185 | 185 | 185 |  |  | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 163 | 170 | 170 | 50 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 340 | 414 | 414 | 414 |  |  | FGMO
127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 24 |  | 26 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
128 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
129 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 25 | 52
130 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 42 | 53 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 95 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
133 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 664 | 741 | 700 | 750
134 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 38 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 12 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1352 | 1550 | 1892 | 2018 | 441 | 117
135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 71 | 70 | 71 | 71 |  | 14 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 153 | 155 | 155 | 156 |  | 118 | Machine problem
137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 90 | 113
140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
141 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 34 | 115 | 115
142 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 30 | 0
143 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 106 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 360 | 259 | 639 | 455 | 40 | 217 | .
| Total |  |  |  |  | 27740 | 27035 | 9207 | 10354 | 12721.6 | 13521 | 5606 | 5231
A. |  | 2024-12-12 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 10354 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6734 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10354 | MW
3 | Day peak Generation : |  |  | 9207 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10062.79 | MW
4 | Evening peak Generation : |  |  | 10354 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 209.5939 | MKWHr | By Solar | 2.1331 | MKWHr
| By Gas : | 113.2477 | MKWHr |  | By Oil: | 6.3919 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 60.7931 | MKWHr |  | By Hydro: | 0.9627 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 13.8047 | MKWHr |  | By Wind: | 0.5088 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5606 | MW | Dhaka | 3902.69 | 3902.69 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 5231 | MW | Chittagong | 974 | 974 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10837 | MW | Khulna | 1159.8 | 1159.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 861.17 | MMCFD | **Import Adani: | Taka | 91249245.47 | Rajshahi | 954.6 | 954.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : |  | 290215388.278 | ii) Oil : | Taka | 110175433.15 | Comilla | 900 | 900 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 423670629.13 | Total | Taka | 915310696.028 | Mymensingh | 823 | 823 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3585.45 | MKWHr. | Sylhet | 362 | 362 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 428 | MW (W to E) at | 18:00 | hrs | Barisal | 291.7 | 291.7 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 396 | MW at | 8:00 | hrs | Rangpur | 695 | 695 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 21.2°C |  |  | Total | 10062.79 | 10062.79 |  | 0
B. |  | 2024-12-13 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 21.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13521 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
4 | Reserve(Generation end) |  |  |  | 3521 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 202.4279 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6590 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector(India) : |  |  |  |  | i) Energy | 10.5047 | MKWHr. | ii) HVDC Flow at Peak Time |  | 484 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.247 | MKWHr. | iii) Maximum HVDC Flow : |  | 486 | MW at | 21:00 | hrs.
* Import Through HVDC C/B Interconnector(Nepal) : |  |  |  |  | i) Energy | 0 | MKWHr.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.28 |  | (b) Today: | 95.22 |  | (c) Rule Curve: |  | 104.9
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-12-12 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | JERA Meghnaghat Power Limited | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | Nepal | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Nepal | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 17 | 31 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 33 | 0 | 0 | 0 | 20 | 0 | 181 | 128 | 36 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 16 | 0 | 0 | 0 | 30 | 30 | 0 | 37 | 163 | 0 | 40 | 86 | 0 | 135 | 15 | 0 | 0 | 60 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 29 | 0 | 0 | 0 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 665 | 50 | 495 | 0 | 0 | 0 | 702 | 0 |  | 431 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71 | 0 | 156 | 0 | 0 | 175 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454 | 0 | 150 | 659 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4307 | 3407 | 7714 | 2327 | 431 | 0 | 1661 | 0 | 59 | 2391 | 40 | 0 | 48 | 48 | 659 | 0 | 50 | 0 | 95.29
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 17 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 40 | 0 | 181 | 128 | 36 | 37 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 16 | 0 | 0 | 0 | 30 | 30 | 0 | 37 | 163 | 0 | 40 | 62 | 0 | 135 | 15 | 0 | 0 | 140 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 665 | 56 | 500 | 0 | 0 | 0 | 716 | 0 |  | 436 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71 | 0 | 158 | 0 | 0 | 175 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 150 | 531 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4322 | 3142 | 7464 | 2319 | 436 | 0 | 1716 | 0 | 17 | 2269 | 40 | 0 | 32 | 48 | 531 | 0 | 56 | 0 | 95.29
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 17 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 40 | 0 | 181 | 78 | 40 | 37 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 17 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 163 | 0 | 40 | 31 | 0 | 136 | 15 | 0 | 0 | 240 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 665 | 44 | 406 | 0 | 0 | 0 | 662 | 0 |  | 436 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71 | 0 | 157 | 0 | 0 | 140 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 150 | 417 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4087 | 2896 | 6983 | 2265 | 436 | 0 | 1615 | 0 | 16 | 2068 | 40 | 0 | 32 | 50 | 417 | 0 | 44 | 0 | 95.28
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 17 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 145 | 0 | 181 | 35 | 40 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 52 | 19 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 120 | 0 | 40 | 8 | 0 | 136 | 15 | 0 | 0 | 250 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 665 | 41 | 405 | 0 | 0 | 0 | 699 | 0 |  | 436 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72 | 0 | 156 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 150 | 419 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3979 | 2847 | 6826 | 2166 | 436 | 0 | 1546 | 0 | 17 | 2077 | 40 | 0 | 32 | 52 | 419 | 0 | 41 | 0 | 95.28
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 17 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 150 | 0 | 197 | 8 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 20 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 120 | 0 | 12 | 8 | 0 | 136 | 0 | 0 | 0 | 255 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 48 | 405 | 0 | 0 | 0 | 727 | 0 |  | 436 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73 | 0 | 156 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 150 | 416 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3913 | 2821 | 6734 | 2126 | 436 | 0 | 1554 | 0 | 17 | 2015 | 40 | 0 | 32 | 50 | 416 | 0 | 48 | 0 | 95.28
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 17 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 354 | 0 | 155 | 31 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 21 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 163 | 0 | 12 | 8 | 0 | 136 | 0 | 0 | 0 | 255 | 13 | 2 | 0 | 0 | 0 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 0 | 67 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603 | 41 | 405 | 0 | 0 | 0 | 718 | 0 |  | 436 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73 | 0 | 158 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 150 | 416 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4254 | 2914 | 7168 | 2447 | 436 | 0 | 1670 | 0 | 23 | 2013 | 40 | 0 | 32 | 50 | 416 | 0 | 41 | 0 | 95.28
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 357 | 0 | 142 | 185 | 50 | 34 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 48 | 18 | 0 | 0 | 0 | 29 | 30 | 0 | 25 | 130 | 0 | 40 | 42 | 0 | 136 | 0 | 0 | 0 | 250 | 13 | 2 | 0 | 0 | 0 | 0 | 10 | 0 | 24 | 2 | 0 | 0 | 0 | 67 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 41 | 405 | 0 | 0 | 2 | 718 | 0 |  | 436 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72 | 0 | 158 | 0 | 0 | 141 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 90 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 374 | 0 | 250 | 465 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4561 | 3175 | 7736 | 2596 | 436 | 0 | 1875 | 0 | 61 | 2151 | 40 | 0 | 16 | 48 | 465 | 7 | 41 | 0 | 95.27
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 147 | 185 | 50 | 34 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 52 | 16 | 0 | 0 | 0 | 29 | 30 | 0 | 37 | 130 | 0 | 40 | 86 | 0 | 136 | 0 | 0 | 0 | 255 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 56 | 8 | 0 | 0 | 0 | 67 | 45 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 662 | 23 | 575 | 0 | 0 | 7 | 718 | 0 |  | 435 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72 | 0 | 155 | 0 | 0 | 150 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 109 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 455 | 1 | 250 | 522 | 8 | 0 | 0 | 1 | 6 | 0 |  | 4908 | 3539 | 8447 | 2612 | 435 | 0 | 1965 | 0 | 145 | 2579 | 40 | 0 | 16 | 52 | 522 | 58 | 23 | 0 | 95.27
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 33 | 16 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 280 | 0 | 188 | 185 | 40 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 52 | 14 | 0 | 0 | 0 | 30 | 30 | 0 | 37 | 120 | 0 | 58 | 86 | 0 | 136 | 0 | 0 | 0 | 255 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 61 | 0 | 0 | 0 | 0 | 72 | 45 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 6 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 662 | 6 | 554 | 0 | 0 | 19 | 718 | 0 |  | 435 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 155 | 0 | 0 | 150 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 490 | 126 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 513 | 3 | 307 | 610 | 17 | 0 | 0 | 2 | 8 | 0 |  | 4873 | 3883 | 8756 | 2663 | 435 | 0 | 1904 | 0 | 170 | 2751 | 40 | 0 | 16 | 52 | 610 | 109 | 6 | 0 | 95.27
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 15 | 20 | 17 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 285 | 0 | 222 | 185 | 40 | 38 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 10 | 0 | 0 | 1 | 30 | 30 | 0 | 37 | 120 | 0 | 58 | 65 | 0 | 136 | 0 | 0 | 0 | 260 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 68 | 0 | 0 | 0 | 0 | 68 | 45 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 660 | 4 | 500 | 0 | 0 | 42 | 718 | 0 |  | 436 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 159 | 0 | 0 | 150 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 550 | 122 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 451 | 6 | 240 | 661 | 31 | 0 | 0 | 3 | 16 | 0 |  | 4869 | 3868 | 8737 | 2639 | 436 | 0 | 1887 | 0 | 194 | 2630 | 40 | 0 | 16 | 50 | 661 | 180 | 4 | 0 | 95.27
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 25 | 17 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 320 | 0 | 196 | 187 | 40 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 54 | 8 | 0 | 0 | 1 | 30 | 30 | 0 | 34 | 120 | 0 | 57 | 65 | 0 | 136 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 0 | 0 | 0 | 70 | 45 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 18 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 660 | 3 | 504 | 0 | 0 | 58 | 742 | 37 |  | 441 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71 | 0 | 152 | 0 | 0 | 149 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 500 | 141 | 0 | 0 | 1 | 69 | 0 | 0 | 0 | 464 | 11 | 240 | 664 | 49 | 0 | 0 | 14 | 16 | 0 |  | 5018 | 3802 | 8820 | 2589 | 441 | 0 | 1916 | 0 | 206 | 2591 | 40 | 0 | 67 | 54 | 664 | 249 | 3 | 0 | 95.26
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 0 | 28 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 325 | 0 | 198 | 192 | 45 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 56 | 7 | 0 | 0 | 2 | 29 | 30 | 0 | 34 | 120 | 0 | 57 | 65 | 0 | 135 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 81 | 0 | 0 | 0 | 0 | 80 | 45 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 40 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 663 | 0 | 504 | 0 | 0 | 65 | 743 | 37 |  | 441 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71 | 0 | 153 | 0 | 0 | 150 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 490 | 217 | 0 | 0 | 3 | 74 | 0 | 0 | 0 | 464 | 25 | 240 | 664 | 106 | 0 | 0 | 38 | 12 | 0 |  | 5237 | 3970 | 9207 | 2745 | 441 | 0 | 2025 | 0 | 207 | 2585 | 40 | 0 | 67 | 56 | 664 | 377 | 0 | 0 | 95.26
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 15 | 0 | 28 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 310 | 0 | 180 | 195 | 40 | 41 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 56 | 7 | 0 | 0 | 2 | 30 | 30 | 0 | 34 | 163 | 0 | 57 | 86 | 0 | 135 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 0 | 0 | 0 | 130 | 45 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 34 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 575 | 0 | 0 | 59 | 720 | 45 |  | 441 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71 | 0 | 154 | 0 | 0 | 169 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 490 | 220 | 0 | 0 | 4 | 68 | 0 | 0 | 0 | 511 | 24 | 280 | 664 | 133 | 0 | 0 | 42 | 19 | 0 |  | 5389 | 4256 | 9645 | 2848 | 441 | 0 | 2174 | 0 | 206 | 2741 | 40 | 0 | 76 | 56 | 664 | 399 | 0 | 0 | 95.26
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 15 | 0 | 26 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 0 | 180 | 195 | 40 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 6 | 0 | 0 | 2 | 30 | 30 | 0 | 34 | 120 | 0 | 57 | 84 | 0 | 135 | 0 | 0 | 0 | 265 | 13 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 80 | 0 | 0 | 0 | 0 | 215 | 45 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 30 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 575 | 0 | 0 | 50 | 744 | 64 |  | 441 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 155 | 0 | 0 | 140 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 450 | 180 | 0 | 0 | 3 | 58 | 0 | 0 | 0 | 506 | 20 | 200 | 540 | 112 | 0 | 0 | 37 | 18 | 0 |  | 5360 | 3903 | 9263 | 2843 | 441 | 0 | 2099 | 0 | 192 | 2616 | 40 | 0 | 94 | 50 | 540 | 348 | 0 | 0 | 95.26
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 26 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 180 | 128 | 38 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 52 | 6 | 0 | 0 | 1 | 30 | 30 | 0 | 5 | 120 | 0 | 57 | 42 | 0 | 133 | 0 | 0 | 0 | 270 | 13 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 80 | 0 | 0 | 0 | 0 | 380 | 45 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 20 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 662 | 3 | 500 | 0 | 0 | 31 | 744 | 73 |  | 441 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 155 | 0 | 0 | 140 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 400 | 180 | 0 | 0 | 1 | 36 | 0 | 0 | 0 | 454 | 13 | 150 | 462 | 72 | 0 | 0 | 22 | 13 | 0 |  | 5283 | 3499 | 8782 | 2991 | 441 | 0 | 1896 | 0 | 175 | 2391 | 40 | 0 | 103 | 52 | 462 | 228 | 3 | 0 | 95.25
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 12 | 26 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 182 | 88 | 38 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 60 | 6 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 120 | 0 | 56 | 42 | 0 | 133 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 80 | 0 | 0 | 0 | 0 | 380 | 45 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 7 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 663 | 7 | 452 | 0 | 0 | 15 | 603 | 74 |  | 441 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 158 | 0 | 0 | 144 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 220 | 0 | 2 | 0 | 15 | 0 | 0 | 0 | 412 | 5 | 150 | 484 | 28 | 0 | 0 | 8 | 18 | 0 |  | 5158 | 3439 | 8597 | 3112 | 441 | 0 | 1774 | 0 | 169 | 2305 | 40 | 0 | 105 | 60 | 484 | 100 | 7 | 0 | 95.25
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 15 | 17 | 21 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9 | 0 | 0 | 0 | 1 | 11 | 0 | 7 | 0 | 0 | 0 | 310 | 0 | 182 | 168 | 38 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 58 | 5 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 163 | 0 | 57 | 42 | 0 | 133 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 80 | 0 | 12 | 0 | 11 | 375 | 57 | 10 | 9 | 0 | 32 | 14 | 9 | 0 | 2 | 12 | 346 | 0 | 0 | 35 | 11 | 0 | 14 | 0 | 5 | 12 | 0 | 17 | 0 | 660 | 10 | 453 | 0 | 0 | 1 | 492 | 55 |  | 485 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 158 | 0 | 0 | 176 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 220 | 0 | 32 | 0 | 2 | 34 | 0 | 0 | 410 | 0 | 150 | 514 | 2 | 0 | 0 | 0 | 1 | 0 |  | 5492 | 3583 | 9075 | 3121 | 485 | 0 | 1803 | 0 | 508 | 2301 | 40 | 0 | 229 | 58 | 514 | 6 | 10 | 0 | 95.25
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 15 | 30 | 26 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 18 | 19 | 0 | 5 | 0 | 0 | 0 | 310 | 0 | 180 | 195 | 35 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 62 | 5 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 163 | 0 | 58 | 42 | 0 | 135 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 50 | 0 | 58 | 0 | 12 | 0 | 58 | 359 | 57 | 17 | 17 | 0 | 32 | 50 | 17 | 0 | 26 | 12 | 346 | 0 | 0 | 72 | 47 | 0 | 17 | 0 | 16 | 36 | 0 | 17 | 0 | 660 | 12 | 575 | 0 | 0 | 0 | 690 | 0 |  | 484 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 155 | 0 | 0 | 185 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 220 | 0 | 54 | 0 | 0 | 34 | 0 | 0 | 583 | 0 | 285 | 741 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6080 | 4274 | 10354 | 3133 | 484 | 0 | 2081 | 0 | 794 | 2798 | 40 | 0 | 209 | 62 | 741 | 0 | 12 | 0 | 95.25
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 30 | 24 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 19 | 0 | 10 | 0 | 0 | 0 | 285 | 0 | 185 | 197 | 31 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 52 | 5 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 163 | 0 | 58 | 42 | 0 | 136 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 22 | 0 | 0 | 0 | 50 | 303 | 57 | 0 | 0 | 0 | 85 | 34 | 0 | 0 | 26 | 0 | 316 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 660 | 14 | 576 | 0 | 0 | 0 | 740 | 0 |  | 484 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 154 | 0 | 0 | 185 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 220 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 630 | 0 | 307 | 760 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5726 | 4357 | 10083 | 3021 | 484 | 0 | 2133 | 0 | 494 | 2987 | 40 | 0 | 98 | 52 | 760 | 0 | 14 | 0 | 95.24
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 30 | 24 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 19 | 0 | 20 | 0 | 0 | 0 | 290 | 0 | 191 | 197 | 31 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 52 | 6 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 163 | 0 | 57 | 42 | 0 | 136 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 0 | 0 | 0 | 315 | 57 | 0 | 0 | 0 | 50 | 17 | 0 | 0 | 26 | 0 | 320 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 660 | 20 | 575 | 0 | 0 | 0 | 741 | 0 |  | 484 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 157 | 0 | 0 | 185 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 307 | 756 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5648 | 4371 | 10019 | 3050 | 484 | 0 | 2165 | 0 | 343 | 3011 | 40 | 0 | 98 | 52 | 756 | 0 | 20 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 30 | 24 | 26 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 19 | 0 | 23 | 0 | 0 | 0 | 280 | 0 | 180 | 197 | 32 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 52 | 6 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 163 | 0 | 58 | 42 | 0 | 136 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 0 | 0 | 0 | 303 | 57 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 26 | 0 | 316 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 660 | 18 | 575 | 0 | 0 | 0 | 742 | 0 |  | 485 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 158 | 0 | 0 | 185 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 0 | 307 | 755 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5552 | 4378 | 9930 | 3015 | 485 | 0 | 2159 | 0 | 308 | 3018 | 40 | 0 | 80 | 52 | 755 | 0 | 18 | 0 | 95.24
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 25 | 24 | 26 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 285 | 0 | 180 | 199 | 36 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 54 | 8 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 163 | 0 | 58 | 42 | 0 | 136 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 0 | 0 | 0 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 15 | 575 | 0 | 0 | 0 | 743 | 0 |  | 486 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 157 | 0 | 0 | 184 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 628 | 0 | 307 | 755 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5342 | 4380 | 9722 | 3002 | 486 | 0 | 2155 | 0 | 115 | 3020 | 40 | 0 | 80 | 54 | 755 | 0 | 15 | 0 | 95.24
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 25 | 24 | 26 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 285 | 0 | 181 | 199 | 34 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 9 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 163 | 0 | 58 | 42 | 0 | 136 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 0 | 0 | 0 | 0 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 7 | 522 | 0 | 0 | 0 | 743 | 0 |  | 485 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 69 | 0 | 157 | 0 | 0 | 181 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 215 | 657 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5235 | 4002 | 9237 | 2982 | 485 | 0 | 2158 | 0 | 103 | 2691 | 40 | 0 | 64 | 50 | 657 | 0 | 7 | 0 | 95.24
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 17 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 285 | 0 | 187 | 199 | 35 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 50 | 9 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 120 | 0 | 58 | 42 | 0 | 136 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 0 | 0 | 303 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 14 | 503 | 0 | 0 | 0 | 718 | 0 |  | 486 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 39 | 0 | 157 | 0 | 0 | 181 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 200 | 580 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5073 | 3709 | 8782 | 2979 | 486 | 0 | 2081 | 0 | 45 | 2459 | 40 | 0 | 48 | 50 | 580 | 0 | 14 | 0 | 95.23
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 17 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 285 | 0 | 181 | 158 | 35 | 39 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 54 | 7 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 120 | 0 | 58 | 42 | 0 | 137 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 27 | 441 | 0 | 0 | 0 | 718 | 0 |  | 485 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 153 | 0 | 0 | 181 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 200 | 460 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4914 | 3445 | 8359 | 2927 | 485 | 0 | 2035 | 0 | 29 | 2254 | 40 | 0 | 48 | 54 | 460 | 0 | 27 | 0 | 95.23
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9187200 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 7429631 | 0 | 0 | 0 | 5040 | 1189440 | 0 | 0 | 0 | 0 | 41760 | 76763 | 0 | 0 | 411000 | 356400 | 358200 | 670400 | 450720 | 0 | 962700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 250800 | 0 | 0 | 0 | 23040 | 81600 | 0 | 477600 | 0 | 0 | 0 | 6311800 | 0 | 4398000 | 3680000 | 949670 | 833976 | 0 | 0 | 906428 | 0 | 0 | 0 | 0 | 0 | 0 | 364930 | 1247040 | 243840 | 0 | 0 | 6950 | 708000 | 707520 | 0 | 451512 | 3682718 | 0 | 1169568 | 1202880 | 0 | 3247710 | 67000 | 0 | 0 | 6311500 | 343968 | 58176 | 0 | 0 | 0 | 0 | 537600 | 0 | 1071504 | 6800 | 27840 | 0 | 120436 | 4586000 | 786000 | 27840 | 40145 | 23043 | 185673 | 144067 | 39309 | 0 | 131880 | 23040 | 7433300 | 0 | 171810 | 131040 | 146782 | 0 | 41400 | 52341 | 35520 | 109080 | 0 | 26764 | 0 | 15769089 | 508800 | 12189090 | 0 | 0 | 351691 | 16878590 | 378000 |  | 10504727 | 0 | 5668416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3071000 | 132985 | 0 | 0 | 0 | 0 | 0 | 0 | 76048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147744 | 1565672 | 0 | 3806000 | 0 | 0 | 3910000 | 0 | 3899318 | 0 | 0 | 0 | 0 | 0 | 9502763 | 0 | 0 | 0 | 0 | 0 | 0 | 28421 | 0 | 10757818 | 3487970 | 0 | 111600 | 14940 | 458640 | 81216 | 0 | 0 | 11425450 | 112610 | 5280000 | 13804727 | 583920 | 0 | 3324 | 184496 | 134117 | 0 |  | 120839954 | 88753922 | 209593876 | 66532767 | 10504727 | 0 | 46714946 | 0 | 4721695 | 60793119 | 962700 | 0 | 1670252 | 1247040 | 13804727 | 2133103 | 508800 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26459136 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22660374.55 | 0 | 0 | 0 | 90468 | 23098924.8 | 0 | 0 | 0 | 0 | 762537.6 | 1209784.88 | 0 | 0 | 308250 | 0 | 0 | 0 | 8072395.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4411572 | 0 | 0 | 0 | 450892.8 | 1343136 | 0 | 0 | 0 | 0 | 0 | 17609922 | 0 | 14601360 | 12328000 | 3067434.1 | 2810499.12 | 0 | 0 | 3634776.28 | 0 | 0 | 0 | 0 | 0 | 0 | 273697.5 | 8180582.4 | 758342.4 | 0 | 0 | 0 | 2761200 | 2639049.6 | 0 | 2054379.6 | 12594895.56 | 0 | 6491102.4 | 6279033.6 | 0 | 9061110.9 | 440860 | 0 | 0 | 19502535 | 257976 | 44213.76 | 0 | 0 | 0 | 0 | 10327296 | 0 | 18869185.44 | 0 | 495830.4 | 0 | 1996828.88 | 12152900 | 14981160 | 522278.4 | 720201.3 | 0 | 3035753.55 | 2800662.48 | 705203.46 | 0 | 2559790.8 | 410342.4 | 19772578 | 0 | 0 | 2396721.6 | 2463001.96 | 0 | 739818 | 0 | 640070.4 | 1847815.2 | 0 | 376837.12 | 0 | 109910550.33 | 0 | 71915631 | 0 | 0 | 0 | 0 | 0 |  | 29518282.87 | 0 | 16721827.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9704360 | 630348.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1278366.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111842.208 | 17269362.16 | 0 | 32122640 | 0 | 0 | 12903000 | 0 | 12984728.94 | 0 | 0 | 0 | 0 | 0 | 27748067.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69710660.64 | 10847586.7 | 0 | 2159460 | 0 | 0 | 1409097.6 | 0 | 0 | 83405785 | 0 | 39336000 | 91249245.47 | 0 | 0 | 0 | 0 | 0 | 0 |  | 493898898.77 | 459110662.528 | 953009561.298 | 194595764.678 | 29518282.87 | 0 | 95619623.6 | 0 | 85421304.35 | 423670629.13 | 0 | 0 | 24754128.8 | 8180582.4 | 91249245.47 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 0 | 28 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 325 | 0 | 198 | 192 | 45 | 40 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 56 | 7 | 0 | 0 | 2 | 29 | 30 | 0 | 34 | 120 | 0 | 57 | 65 | 0 | 135 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 81 | 0 | 0 | 0 | 0 | 80 | 45 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 40 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 663 | 0 | 504 | 0 | 0 | 65 | 743 | 37 |  | 441 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71 | 0 | 153 | 0 | 0 | 150 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 490 | 217 | 0 | 0 | 3 | 74 | 0 | 0 | 0 | 464 | 25 | 240 | 664 | 106 | 0 | 0 | 38 | 12 | 0 |  | 9207 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 15 | 30 | 26 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 18 | 19 | 0 | 5 | 0 | 0 | 0 | 310 | 0 | 180 | 195 | 35 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 62 | 5 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 163 | 0 | 58 | 42 | 0 | 135 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 50 | 0 | 58 | 0 | 12 | 0 | 58 | 359 | 57 | 17 | 17 | 0 | 32 | 50 | 17 | 0 | 26 | 12 | 346 | 0 | 0 | 72 | 47 | 0 | 17 | 0 | 16 | 36 | 0 | 17 | 0 | 660 | 12 | 575 | 0 | 0 | 0 | 690 | 0 |  | 484 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 155 | 0 | 0 | 185 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 220 | 0 | 54 | 0 | 0 | 34 | 0 | 0 | 583 | 0 | 285 | 741 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10354 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 55 | 335 | 0 | 106 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 23 | 25 | 33 | 52 | 0 | 40 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 74 | 51 | 0 | 50 | 50 | 0 | 30 | 0 | 0 |  | 350 | 0 | 200 | 195 | 50 | 40 | 0 | 0 | 51 | 0 | 45 | 52 | 0 | 0 |  | 15 | 70 | 16 | 0 | 0 | 0 | 30 | 30 | 0 | 34 | 163 | 0 | 60 | 86 | 0 | 135 | 0 | 0 | 0 | 330 | 22 | 2 | 0 | 300 | 0 | 0 | 95 | 0 | 149 | 0 | 100 | 200 | 140 | 360 | 55 | 105 | 105 | 0 | 120 | 54 | 110 | 114 | 100 | 100 | 400 | 17 | 0 | 162 | 108 | 0 | 53 | 0 | 92 | 36 | 0 | 160 | 0 | 660 | 38 | 515 | 0 | 0 |  | 0 |  |  | 499 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 135 | 7 | 0 | 0 | 0 | 0 | 40 | 25 | 95 | 0 | 0 | 32 | 52 | 24 | 0 | 0 | 5 | 71 | 0 | 156 | 0 | 0 | 185 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 307 | 750 | 0 | 0 |  |  |  | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 |  | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 106 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 34 | 55 | 55 | 0 | 25 | 23 | 25 | 33 | 34 | 0 | 40 | 0 | 0 | 0 | 8 | 0 |  | 0 | 0 | 0 | 24 | 56 | 50 | 0 | 20 | 50 | 0 | 10 | 0 | 0 | 0 | 350 | 0 | 200 | 195 | 50 | 40 | 0 | 0 | 51 | 0 | 30 | 52 | 0 | 0 |  | 15 | 66 | 12 | 0 | 0 | 1.6 | 30 | 30 | 0 | 34 | 163 | 0 | 60 | 86 | 0 | 135 | 0 | 0 | 0 | 330 | 22 | 2 | 0 | 300 | 0 | 0 | 96 | 0 | 149 | 20 | 100 | 200 | 140 | 360 | 55 | 50 | 85 | 5 | 50 | 54 | 110 | 114 | 95 | 100 | 400 | 7 | 50 | 162 | 50 | 0 | 17 | 35 | 50 | 36 | 0 | 17 | 0 | 660 | 15 | 515 | 0 | 0 | 70 | 0 |  |  | 450 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 135 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 26 | 25 | 24 | 0 | 0 | 5 | 71 | 0 | 155 | 0 | 0 | 185 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 95 | 0 | 90 | 0 | 8 | 113 | 622 | 220 |  | 54 | 6 | 100 | 115 | 0 | 0 | 620 | 30 | 307 | 700 | 170 | 0 |  | 29 | 47 | 0 |  |  |  |  | gas | hvdc |  | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 17 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 360 | 0 | 165 | 199 | 45 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 36 | 11 | 0 | 0 | 0 | 30 | 30 | 0 | 5 | 163 | 0 | 58 | 42 | 0 | 137 | 0 | 0 | 0 | 75 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 1 | 0 | 0 | 0 | 360 | 35 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 2 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 663 | 14 | 523 | 0 | 0 | 6 | 0 | 0 | 0 | 485 | 0 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 153 | 0 | 0 | 180 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 440 | 220 | 0 | 0 | 1 | 21 | 0 | 0 | 0 | 459 | 4 | 250 | 516 | 28 | 0 | 0 | 10 | 12 | 0 | 0 |  |  |  | 113247713 | 10504727 |  | 0 | 60793119 | 6391947 | 1247040 | 2133103 | 508800 | 962700 |  |  |  | 195789149
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [9 empty] | 399427 | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 |  | 299798 | [7 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [14 empty] | 499227 |  | 499229 |  |  | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [11 empty] | 113.2477 | 10.5047 |  | 0 | 60.7931 | 6.3919 | 1.247 | 2.1331 | 0.5088 | 0.9627
| Minimum Generation |  | 6734 | 5:00
| Highest Generation |  | 10354 | 18:00 | [129 empty] | 0 | [77 empty] | 195.7891
| Day Peak Generation |  | 9207 | 12:00
| Evening Peak Generation |  | 10354 | 18:00 | [207 empty] | 202699852
| HVDC Max Flow |  | 486 | 21:00 | [207 empty] | 202.6999
| HVDC EvPeak Flow |  | 484 | 18:00
| Load factor L.F |  | 84.34% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-12-13
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-12-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9207 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6590
Evening Peak Generation : |  |  | 10354 | MW Hour : | 18:00 | Available Max Generation : |  | 13521
E.P. Demand (at gen end) : |  |  | 10354 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10000
Maximum Generation : |  |  | 10354 | MW Hour : | 18:00 | Reserve(Generation end) |  | 3521
Total Gen. (MKWH) : |  |  | 209.5939 | System Load Factor : | 84.34% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 396 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-12-13
Actual : |  | 95.22 | Ft.(MSL) , | Rule curve : | 104.9 | Ft.( MSL )
Gas Consumed : |  | Total = | 861.17 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 290215388.278 | Adani : | 91249245.47
|  |  | Coal : | 423670629.13 | Oil: | 110175433.15 | Total: | 915310696.028
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3499.4504 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 955.1576 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1336.0395 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1159.4645 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 954.9506 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 709.2906 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 398.5972 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 331.2534 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 647.895 |  |  | 0 | 0%
Total |  | 0 |  | 9992.0988 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:01 | 19:05 | Feni 132/33kV S/S T-2(415T) HT Scheduled S/D Due to For annual maintenance
08:01 | 19:05 | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to For annual maintenance
08:02 | 13:44 | Mirsorai 230/33kV S/S TR-2, 728T HT Scheduled S/D Due to Annual Maintenance
08:02 | 14:55 | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to Annual Dead
Line Checking
08:02 |  | Mirsorai 230/33kV S/S TR-2, 728T LT Scheduled S/D Due to Annual Maintanence
08:03 | 16:59 | Daudkandi 132/33kV S/S Transformer-3 LT Scheduled S/D Due to annual maintenance
08:04 | 16:59 | Daudkandi 132/33kV S/S Transformer-3 HT Scheduled S/D Due to annual maintenance
08:06 | 16:29 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end Due to
Annual maintenance
08:07 | 16:30 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance
08:14 | 15:18 | Bogura-Natore 132 kV Ckt-2 Scheduled S/D from Natore 132/33kV end Due to Yearly
maintenance and from Bogura 132/33kV end Due to Annual maintenance (Dead line inspection)
08:17 | 15:18 | Khulna(C )-Noapara 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to annual
maintenance and from Noapara 132/33kV end Due to Annual Maintenance
08:17 | 15:09 | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Naogaon 132/33kV end Due to Annual
maintenance.
08:20 | 14:33 | Gallamari- Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to
Annual Maintenance Work. and from Gollamari 132/33kV end Due to Annual maintenance
08:23 | 15:46 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to For 33 kv Bus-02 Annual Maintenance | [5 empty] | 8.0MW load interrup.
by PBS
08:24 | 15:42 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to For 33 kv Bus-02 Annual Maintenance | [5 empty] | 8.0MW load interrup.
by PBS
08:26 | 16:30 | Gopalganj(N)-Madaripur 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end.
08:27 | 16:29 | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Gopalganj 400/132kV end.
08:30 | 16:28 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Annual
maintenance (deadline checking)
08:35 | 15:26 | Jhenaidah-Magura 132 kV Ckt-1 Scheduled S/D from Jhenaidah 132/33kV end Due to Annual
Maintenance. and from Magura 132/33kV end Due to Annual maintenance.
08:37 | 17:13 | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual Maintenance work and from Bogura 400/230kV end Due to annual Maintenance.
08:39 | 16:25 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT Scheduled S/D Due to Annual
Maintenance.
08:39 | 16:25 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT Scheduled S/D Due to Annual
Maintenance
| 08:47 | Sylhet 132/33kV S/S T1 HT is restored.
| 08:48 | Sylhet 132/33kV S/S T1 LT is restored.
08:55 | 16:49 | Haripur-Sonargaon 132kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to Annual
maintenance work. and from Haripur 230/132kVend.
09:07 | 14:20 | Sunamganj 132/33kV S/S Tr-2 LT Scheduled S/D
09:08 | 14:16 | Sunamganj 132/33kV S/S Tr-2 HT Scheduled S/D
09:15 | 13:26 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Annual maintenance
09:15 | 13:26 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenance
09:20 | 13:40 | Savar 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance
09:24 | 16:08 | Rangpur 132/33kV S/S T-3 (424T) HT Scheduled S/D Due to Annual maintenance.
09:24 | 16:08 | Rangpur 132/33kV S/S T-3 (424T) LT Scheduled S/D Due to Annual maintenance.
09:25 | 14:52 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
dead line checking
09:27 | 15:05 | Mymensingh RPCL-Tangail 132kV Ckt-2 Scheduled S/D from Ghatail 132/33kV end Due to
Annual Maintenance
10:34 | 14:42 | Rampur 230/132/33 S/S Halishahar-1 Scheduled S/D Due to Relay Test By SPMD(CTG)
10:47 | 16:20 | Sylhet (South) S/S Trafo-2 LT Scheduled S/D Due to Coling fan maintenance work
10:48 | 16:19 | Sylhet (South) S/S Trafo-2 HT Scheduled S/D Due to Coling fan maintenance work by siemens
10:56 | 17:23 | HVDC Bheramera-Ishwardi 230kV Ckt-4 Scheduled S/D from Ishurdi 230/132kV end Due to
Relay Softwar updating by spmd, bay maintenance.
11:14 | 17:06 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance
11:17 | 17:23 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Scheduled S/D from BIPTC end Due to For annual
maintenance
11:30 | 19:50 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Scheduled S/D Due to CT & isolator changing Pdb
33 kv feeder Incoming -1.
11:54 |  | Bogura 400---Parbotipur 400KV Ckt-1 charged [Charged by 230 KV] (1st Charged from bogura
End to Dead End Tower Parbotipur S/S)
11:57 |  | Bogura 400---Parbotipur 400KV Ckt-2 charged [Charged by 230 KV] (1st Charged from bogura
End to Dead End Tower Parbotipur S/S)
12:00 |  | Day peak generation 9207MW
12:00 |  | Day peak Generation is 9207 MW
12:02 | 18:15 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Tripped showing MCGG82 relays Due to
33KV Underground cable fault.
12:14 |  | Bogura 400---Naogaon 230 KV ckt-1 charged (1st Charged from bogura End to 5 Towers
Naogaon S/S)
12:15 |  | Bogura 400---Naogaon 230 KV ckt-2 charged (1st Charged from bogura End to 5 Towers
Naogaon S/S)
12:38 |  | Rampal 400/230kV S/S Generator Transformer-1 (GT-1) HT Project Work S/D Due to
Maintenance purpose.
| 13:04 | Hasnabad-Keraniganj 230kV Ckt-2 is restored.
15:23 | 16:01 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing Master Trip, 86 relays Due to
Matuail Trip
15:23 | 22:33 | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing Distances | [5 empty] | 40.0MW load interrup. Matuail
|  | Relay & Lockout Relay, Zone-2, Ph- B & Y relays Due to Trip and from Matuail 132/33kV end | [5 empty] | 132/33kV end
Due to 132Kv Matuail to Siddhirgonj ckt tripped on siddhirgonj end.
15:35 | 15:49 | Maniknagar-Matuail 132kV Ckt-1 Forced S/D from Matuail 132/33kV end Due to 132Kv
Matuail to Siddhirgonj ckt tripped on siddhirgonj end.
16:09 | 22:28 | Matuail-Siddhirganj 132kV Ckt-1 Forced S/D from Siddhirganj 132/33kV end Due to Trip DS
Finger Damage
| 17:02 | Narshingdi 132/33kV S/S T-3 HT is restored.
| 17:03 | Narshingdi 132/33kV S/S T-3 LT is restored.
18:00 |  | Evening Peak Generation: 10354 MW.
| 18:35 | Aminbazar-Airport(Old) 230kV Ckt-1 is restored.
| 19:50 | Kalurghat 132/33kV S/S TRFO-02(516T) LT is restored.
| 22:02 | Kulaura 132/33kV S/S TR-2 HT is restored.
| 22:03 | Kulaura 132/33kV S/S TR-2 LT is restored.
22:34 | 22:36 | Maniknagar-Matuail 132kV Ckt-1 Forced S/D from Matuail 132/33kV end Due to load shift | [5 empty] | 34.0MW load interrup. Matuail
|  | from maniknagar to siddhirgong. | [5 empty] | 132/33kV end
23:15 |  | Barapukuria-1 was shut down.
02:45 |  | Bangabhaban 132/11 kv T-1 Tripped showing Buchholz Relay. | [5 empty] | 4MW load interrup.
03:52 |  | Khulna (C) S/S KPCL-2 Tripped showing (E/F, O/C) Y phase relays Due to Cable pot blast
(Y Phase)
03:52 | 05:02 | Khulna(C )-Khulna (S) 132kV Ckt-1 Tripped from Khulna (C) end showing differential RYB
relays Due to Cable pot bust on kpcl -2 Y PHASE and from Khulna(S) 230/132kV end
showing Differential Relay relays Due to KPCL ckt Y phase LA blust from khulna central ss
04:01 |  | JERA (Reliance) Meghnaghat Power Ltd 718 MW CCPP tripped as gas booster got tripped.
04:25 |  | Bangabhaban 132/11 kv T-1 was switched on.
05:00 |  | Min. Gen. 6591 MW
05:57 |  | Siddirganj CCPP 335MW was shut down for air filter cleaning
06:58 |  | Hathazari-Madunaghat 132kV Ckt-2 Forced S/D from Madunaghat 132/33kV end Due to
Operation By NLDC
06:58 |  | Baroirhat-Hathazari 132 kV Ckt-1 Forced S/D from Baroirhat 132/33kV end.
07:00 |  | Hathazari-Madunaghat 132kV Ckt-1 Forced S/D from Madunaghat 132/33kV end.
07:00 |  | Baroirhat-Hathazari 132 kV Ckt-2 Forced S/D from Baroirhat 132/33kV end.
07:05 |  | Hathazari 230/132/33kV S/S 132KV MAIN BUS-01 Scheduled S/D Due to annual maintenance work
07:05 |  | Hathazari 132 kv bus-1 was shut down due to annual maintenance.
07:09 |  | Siddhirganj GT-2 was sync.
07:22 |  | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Scheduled S/D from Barguna
132/33kV end Due to Barishal - Patuakhali line Bakergonj poin re-jumppering. and from
Patuakhali 132/33kV end Due to Jumper tightening
07:30 |  | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT Scheduled S/D Due to Annual
Maintenance
07:30 |  | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT Scheduled S/D Due to Annual
Maintenance
07:41 |  | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Project Work S/D from Barishal
132/33kV end Due to Power restoring of Bakergonj Patuakhali and Barguna 132 kV line.
07:41 |  | Summit Bibiyana -2 was shut down due to problem with GBC of Bibiyana Gas Plant.
07:46 |  | Keranigonj 230/132/33kV S/S 132 kV Lalbagh Ckt. 3 Scheduled S/D Due to Annual maintenance
work.
08:00 |  | Jhenaidah-Kushtia 132kV Ckt-2 Project Work S/D from Kushtia 132/33kV end Due to
Ruppur-gopalgonge 400 kv line project work
08:00 |  | Jhenaidah-Kushtia 132kV Ckt-1 Project Work S/D from Kushtia 132/33kV end Due to
Ruppur-gopalgonge 400 kv line project work

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-12-12
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 431 | 9187200
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | GT-2 shutdown for gas shortage
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7429631
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 5040 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 41760 | Low demand
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1189440
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 76763 | Reserve
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 767400 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 358200 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 26 | 670400 | Engine problem
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 34 | 450720 | Low demand
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 58 | 1071504 | Low demand
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 27840 | Low demand
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | Reserve
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 131040 | Low demand
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 52341
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 109080 | Fuel shortage
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 718 | 0 | 690 | 16878590 | On test.
| Dhaka area Total |  |  |  | 5915 | 1931 | 38446949
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 6800
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 81600 | High Voltage
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 962700 | Low water level
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 0 | 0 | Under maint.
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 40145 | Low demand
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 27840 | Low demand
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 5 | 477600
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 18 | 23040 | Low demand
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23043
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 185673 | Machine problem.
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 50 | 144067
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 39309 | Low demand
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 23040 | Low demand
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 47 | 146782 | Low demand
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 26764 | Reserve
55 | SS Power I |  | IPP | 2*612 | 1224 | 660 | 15769089 | Coal shortage
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 12 | 508800
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 575 | 12189090 | Machine problem.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1533 | 30675382
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 180 | 4398000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 6311800 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 833976 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 195 | 3680000
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 906428
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 58 | 120436 | Low demand
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 949670 | Machine problem.
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | Reserve
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 62 | 1247040
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 16 | 364930 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 131880 | Low demand
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 35520 | Low demand
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 351691
| Cumilla Area Total |  |  |  | 2917 | 990 | 19331371
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 5 | 243840 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6950
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 50 | 537600 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 57 | 786000 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 171810
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 250800
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 41400 | Low demand
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 0 | 378000
| Mymensingh Area Total |  |  |  | 646 | 153 | 2416400
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 708000 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 707520 | Machine problem.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3682718
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 0 | 0 | 0 | Contact expired
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 451512 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 58176 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 58 | 1169568 | Gas shortage
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 42 | 1202880 | Gas shortage
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 135 | 3247710 | Machine problem.
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 67000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 343968 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6311500 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 359 | 4586000 | FGMO
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 346 | 7433300 | FGMO
| Sylhet Area Total |  |  |  | 2366 | 1473 | 29969852
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 484 | 10504727
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 229 | 5668416 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 458640
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 583 | 11425450 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Nepal |  | Imported power | 40 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1296 | 28057233
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 6 | 132985 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 134 | 3071000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 470 | 10757818 | Unit-2 under overhauling
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 3487970
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 111600 | Low demand
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 285 | 5280000
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3324
| Barisal Area Total |  |  |  | 2236 | 1169 | 22844697
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | NENP
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 185 | 3910000 | Gas shortage
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 163 | 3899318
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 9502763 | FGMO
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 147744 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 76048 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Low demand
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Low demand
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 14940
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 741 | 13804727
135 | Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 184496
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 134117
| Rajshahi Area Total |  |  |  | 3449 | 1550 | 31674153
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 70 | 1565672
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 155 | 3806000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | Reserve
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28421
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 34 | 81216 | Low demand
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 112610
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 583920
| Rangpur Area Total |  |  |  | 950 | 259 | 6177839
| Total |  |  |  | 27035 | 10354 | 209593876
| Eastern Grid Total |  |  |  | 16701 | 6080 | 120839954
| Western Grid Total |  |  |  | 10334 | 4274 | 88753922
| National Grid Total |  |  |  | 27035 | 10354 | 209593876
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-12-12
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6869.82 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3166 | MW
i) Dhaka area |  |  | 3885.82 |  | MW | i) Khulna area |  |  |  | 1157 | MW
ii) Chattogram area |  |  | 965 |  | MW | ii) Barishal area |  |  |  | 297 | MW
iii) Cumilla area |  |  | 847 |  | MW | iii) Rajshahi area |  |  |  | 983 | MW
iv) Mymensingh area |  |  | 825 |  | MW | iv) Rangpur area |  |  |  | 729 | MW
v) Sylhet area |  |  | 347 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10035.82 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jashore | 91 | 13:00 | 133 | Rajbari | 54 | 18:00
2 | AKSML | 113.4 | 04:00 | 68 | Jhenaidah | 91 | 18:00 | 134 | Rajendrapur | 94 | 18:30
3 | Aftabnagar | 24 | 13:00 | 69 | Joydebpur | 119 | 18:00 | 135 | Rajshahi | 90 | 13:00
4 | Agargaon | 71 | 13:00 | 70 | Joypurhat | 40 | 20:00 | 136 | Rajshahi-230 | 36 | 12:00
5 | Agrabad | 64 | 18:00 | 71 | Juldah | 9 | 17:00 | 137 | Ramganj | 74 | 18:00
6 | Amnura | 39 | 12:00 | 72 | KSRM | 32 | 13:00 | 138 | Rampur | 25 | 14:00
7 | Ashuganj | 60 | 12:00 | 73 | Kabirpur | 232 | 18:00 | 139 | Rangamati | 12 | 18:00
8 | BSRM | 142 | 14:00 | 74 | Kachua | 49 | 18:00 | 140 | Rangpur | 94 | 18:30
9 | Bagerhat | 61 | 18:00 | 75 | Kallyanpur | 66 | 18:00 | 141 | Ruppur | 4.6 | 10:00
10 | Bakulia | 75 | 18:00 | 76 | Kalurghat | 20 | 10:00 | 142 | SSM | 12 | 01:00
11 | Banani | 51 | 13:00 | 77 | Kamrangirchar | 50.7 | 13:00 | 143 | Saidpur | 86 | 18:30
12 | Bangabhaban | 9 | 11:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 81 | 18:00
13 | Barapukuria | 49 | 18:00 | 79 | Kazla | 84 | 14:00 | 145 | Satmasjid | 74 | 13:00
14 | Barguna | 14 | 20:00 | 80 | Keranigonj | 56 | 13:00 | 146 | Savar | 170 | 09:00
15 | Barishal | 87 | 13:00 | 81 | Khagrachori | 22 | 18:00 | 147 | SevenRings | 17.62 | 13:00
16 | Barishal-230 | 58 | 18:00 | 82 | Khulna | 63 | 12:00 | 148 | ShahCement | 21 | 22:00
17 | Baroaulia | 55 | 08:00 | 83 | Khulshi | 134 | 12:00 | 149 | Shahjadpur | 50 | 12:00
18 | Baroirhat | 38 | 18:00 | 84 | Kishoreganj | 98 | 19:30 | 150 | Shahjibazar | 72 | 18:00
19 | Bashundhara | 116 | 18:00 | 85 | Kodda | 252 | 18:00 | 151 | Shahmirpur | 32 | 18:00
20 | BashundharaCement | 11 | 00:00 | 86 | Kulaura | 28 | 18:00 | 152 | Shariatpur | 52 | 19:30
21 | Beanibazar | 40 | 18:00 | 87 | Kurigram | 44 | 08:00 | 153 | Sherpur | 86 | 18:00
22 | Benapole | 40 | 18:30 | 88 | Kushtia | 105 | 18:00 | 154 | Shikalbaha | 20 | 12:00
23 | Bhaluka | 108 | 19:00 | 89 | Lalbag | 92 | 17:00 | 155 | Shitalakhya | 59.6 | 11:00
24 | Bhandaria | 34.5 | 19:30 | 90 | Lalmonirhat | 41 | 18:00 | 156 | Sholosohor | 32 | 16:00
25 | Bhangura | 22 | 18:00 | 91 | MI_Cement | 17.6 | 10:00 | 157 | Shyampur | 164 | 10:00
26 | Bheramara(GK) | 39 | 18:00 | 92 | Madanganj | 23 | 00:00 | 158 | Siddhirganj | 89 | 18:00
27 | Bhulta | 225 | 18:30 | 93 | Madaripur | 60 | 20:00 | 159 | Sirajganj | 62 | 18:00
28 | Bog-Sherpur | 58 | 18:00 | 94 | Madartek | 57.4 | 13:00 | 160 | Sonargaon | 76 | 00:00
29 | Bogura | 108 | 18:30 | 95 | Madunaghat | 35 | 18:00 | 161 | Sreemongol | 45 | 12:00
30 | Borhanuddin | 54 | 20:00 | 96 | Magura | 43 | 18:30 | 162 | Sreepur | 59 | 11:00
31 | Brahmanbaria | 101 | 18:00 | 97 | Mahasthangarh | 44 | 18:00 | 163 | Srinagar | 30 | 17:00
32 | Cantonment | 68 | 13:00 | 98 | Manikganj | 93 | 20:00 | 164 | Sunamganj | 36 | 18:00
33 | Chandpur | 43 | 18:00 | 99 | Maniknagar | 46 | 13:00 | 165 | Sylhet | 27 | 13:00
34 | Chandraghona | 25 | 18:00 | 100 | Matarbari | 42 | 18:00 | 166 | Sylhet-132 | 74 | 18:00
35 | Chapai | 45 | 08:00 | 101 | Matuail | 48 | 10:00 | 167 | TK | 20.5 | 19:30
36 | Charsaidpur | 35 | 18:30 | 102 | Millgate | 81 | 10:00 | 168 | Tangail | 122 | 20:00
37 | Chauddagram | 43 | 13:00 | 103 | Mirpur | 87 | 12:00 | 169 | Thakurgaon | 73 | 18:00
38 | Chhatak | 21 | 18:30 | 104 | Mirsorai | 8 | 18:00 | 170 | Tongi | 98 | 11:00
39 | Chowmuhani | 136 | 18:00 | 105 | Mirzapur | 30 | 04:00 | 171 | Ullahpara | 30 | 19:00
40 | Chuadanga | 70 | 13:00 | 106 | Mithapukur | 44 | 18:00 | 172 | Ullon | 36 | 13:00
41 | Coxsbazar | 91 | 18:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 50 | 12:00
42 | Cumilla(N) | 102 | 18:00 | 108 | Mogbazar | 78.3 | 14:00 | 174 | UttaraNew | 34 | 18:00
43 | Cumilla(S) | 118 | 18:00 | 109 | Mongla | 34 | 12:00 | 175 | Zigatola | 65 | 13:00
44 | Daudkandi | 120 | 18:00 | 110 | Motijheel | 22 | 13:00
45 | Dhaka | 28 | 13:00 | 111 | Munshiganj | 64 | 19:30
46 | Dhamrai | 130 | 17:00 | 112 | Mymensingh | 159 | 18:00
47 | Dhanmondi | 76 | 13:00 | 113 | Naogaon | 87 | 18:30
48 | Dohazari | 63 | 18:00 | 114 | Narail | 39 | 18:00
49 | Faridpur | 107 | 18:00 | 115 | Narinda | 48 | 13:00
50 | Fatullah | 76 | 11:00 | 116 | Narshingdi | 141 | 22:00
51 | Fenchuganj | 24 | 19:00 | 117 | Natore | 100 | 18:00
52 | Feni | 66 | 18:00 | 118 | Nawabganj | 27.6 | 20:00
53 | GPH | 26 | 14:00 | 119 | Netrakona | 108 | 18:00
54 | Ghatail | 48 | 18:00 | 120 | New | 56 | 12:00
55 | Ghorashal | 49 | 00:00 | 121 | Niamatpur | 42 | 18:00
56 | Goalpara | 16 | 18:00 | 122 | Noapara | 34 | 18:00
57 | Gollamari | 56 | 13:00 | 123 | PHP | 3 | 22:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-12-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 413 | 04:00 | 398 | 12:00 | Kaliakoir | 383 | 04:00 | 233 | 19:00
| Ashuganj | 411 | 3:00 | 390 | 12:00 | Madunaghat | 413 | 04:00 | 402 | 13:00
| Bhulta | 411 | 06:00 | 397 | 12:00 | Meghnaghat | 405 | 06:00 | 393 | 12:00
| Bibiana | 396 | 15:00 | 390 | 00:00 | Payra | 422 | 04:00 | 413 | 12:00
| BIPTC | 409 | 23:00 | 396 | 11:00 | Rahanpur | 414 | 04:00 | 403 | 19:00
| Bogura | 409 | 04:00 | 395 | 08:00 | Rampal | 413 | 04:00 | 402 | 12:00
| Gopalganj | 416 | 04:00 | 404 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 239 | 04:00 | 228 | 12:00 | Haripur | 239 | 03:00 | 231 | 12:00
| AKSML | 239 | 02:00 | 227 | 12:00 | Hasnabad | 240 | 03:00 | 231 | 12:00
| Aminbazar | 237 | 03:00 | 228 | 13:00 | Hathazari | 238 | 18:00 | 231 | 12:00
| Ashuganj | 244 | 07:00 | 236 | 12:00 | Ishurdi | 241 | 22:00 | 233 | 11:00
| Ashuganj-400 | 244 | 7:00 | 236 | 12:00 | Jhenaidah | 238 | 04:00 | 228 | 13:00
| Baghabari | 240 | 23:00 | 233 | 12:00 | Kaliakoir | 239 | 02:00 | 229 | 05:00
| Barapukuria | 226 | 04:00 | 218 | 08:00 | Keranigonj | 239 | 04:00 | 228 | 12:00
| Barapukuria-230 | 226 | 4:00 | 218 | 8:00 | Khulna(S) | 241 | 03:00 | 231 | 13:00
| Barishal | 247 | 03:00 | 238 | 13:00 | Madunaghat | 238 | 03:00 | 230 | 11:00
| Bheramara | 239 | 23:00 | 231 | 08:00 | Madunaghat-400 | 237 | 04:00 | 230 | 01:00
| Bhulta | 243 | 04:00 | 232 | 12:00 | Maniknagar | 241 | 07:00 | 230 | 12:00
| Bibiana | 232 | 05:00 | 226 | 13:00 | Meghnaghat | 245 | 03:00 | 240 | 17:00
| BIPTC | 240 | 23:00 | 229 | 12:00 | Meghnaghat-400 | 243 | 03:00 | 234 | 12:00
| Bogura | 237 | 04:00 | 231 | 09:00 | Mirsorai | 237 | 02:00 | 224 | 09:00
| Bogura-400 | 237 | 03:00 | 229 | 08:00 | Rajshahi | 239 | 04:00 | 230 | 08:00
| Borhanuddin | 248 | 03:00 | 244 | 16:00 | Rampal | 239 | 04:00 | 229 | 12:00
| BSRM | 239 | 07:00 | 228 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Cumilla(N) | 238 | 04:00 | 231 | 12:00 | Rampura | 242 | 07:00 | 232 | 12:00
| Faridpur | 247 | 03:00 | 239 | 12:00 | Shikalbaha | 237 | 02:00 | 227 | 12:00
| Fenchuganj | 236 | 00:00 | 231 | 09:00 | Shyampur | 241 | 04:00 | 231 | 12:00
| Ghorashal | 240 | 01:00 | 235 | 00:00 | Siddhirganj | 241 | 04:00 | 233 | 12:00
| Ghorashal-230 | 240 | 04:00 | 231 | 10:00 | Sirajgonj | 246 | 04:00 | 240 | 13:00
| Gopalganj | 247 | 04:00 | 239 | 13:00 | Sreepur | 240 | 02:00 | 235 | 09:00
| GPH | 238 | 06:00 | 229 | 12:00 | Tongi | 238 | 01:00 | 231 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 137 | 03:00 | 131 | 13:00 | Kushtia | 140 | 22:00 | 135 | 08:00
| Agargaon | 140 | 04:00 | 132 | 12:00 | Lalbag | 137 | 04:00 | 130 | 12:00
| Agrabad | 137 | 02:00 | 129 | 12:00 | Lalmonirhat | 130 | 01:00 | 122 | 22:00
| AKS | 135 | 03:00 | 130 | 14:00 | Madanganj | 134 | 02:00 | 129 | 11:00
| Aminbazar | 137 | 00:00 | 130 | 12:00 | Madaripur | 136 | 00:00 | 134 | 08:00
| Amnura | 139 | 17:00 | 133 | 11:00 | Madartek | 136 | 03:00 | 130 | 13:00
| Ashuganj | 143 | 07:00 | 140 | 00:00 | Madunaghat | 137 | 04:00 | 132 | 12:00
| Bagerhat | 139 | 04:00 | 131 | 18:00 | Magura | 142 | 03:00 | 134 | 13:00
| Bakulia | 136 | 04:00 | 130 | 12:00 | Mahasthangarh | 136 | 02:00 | 129 | 08:00
| Banani | 137 | 02:00 | 129 | 12:00 | Manikganj | 133 | 02:00 | 127 | 13:00
| Bangabhaban | 138 | 04:00 | 127 | 12:00 | Maniknagar | 139 | 03:00 | 127 | 12:00
| Barapukuria | 136 | 03:00 | 129 | 08:00 | Matarbari | 135 | 08:00 | 108 | 12:00
| Barguna | 140 | 17:00 | 134 | 19:00 | Matuail | 136.6 | 04:00 | 129 | 16:00
| Barishal | 137 | 04:00 | 132 | 12:00 | Millgate | 138 | 02:00 | 130 | 12:00
| Barishal-230 | 137 | 01:00 | 132 | 12:00 | Mirpur | 138 | 04:00 | 131 | 12:00
| Baroaulia | 137 | 03:00 | 132 | 12:00 | Mirzapur | 130 | 02:00 | 126 | 07:00
| Baroirhat | 135 | 07:00 | 129 | 12:00 | Mithapukur | 135 | 03:00 | 127 | 08:00
| Bashundhara | 138 | 03:00 | 128 | 15:00 | MI_Cement | 135.5 | 05:00 | 129 | 12:00
| BashundharaCement | 134 | 02:00 | 129 | 11:00 | Modern | 137 | 02:00 | 128 | 12:00
| Beanibazar | 136 | 00:00 | 133 | 11:00 | Mogbazar | 138 | 03:00 | 132 | 15:00
| Benapole | 141 | 03:00 | 131 | 13:00 | Mongla | 137 | 06:00 | 131 | 12:00
| Bhaluka | 132 | 00:00 | 127 | 08:00 | Motijheel | 138 | 03:00 | 128 | 11:00
| Bhandaria | 135 | 06:00 | 130 | 12:00 | Munshiganj | 134 | 01:00 | 127 | 12:00
| Bhangura | 142 | 22:00 | 138 | 10:00 | Mymensingh | 134 | 10:00 | 115 | 01:00
| Bheramara | 139 | 22:00 | 135 | 09:00 | Naogaon | 137 | 03:00 | 130 | 08:00
| Bheramara(GK) | 140 | 23:00 | 135 | 08:00 | Narail | 141 | 03:00 | 134 | 12:00
| Bhulta | 125 | 01:00 | 118 | 12:00 | Narinda | 138 | 6:00 | 127 | 13:00
| Bog-Sherpur | 138 | 04:00 | 131 | 09:00 | Narshingdi | 131 | 04:00 | 123 | 12:00
| Bogura | 138 | 04:00 | 132 | 09:00 | Natore | 138 | 23:00 | 133 | 08:00
| Bogura-230 | 137 | 03:00 | 132 | 09:00 | Nawabganj | 137 | 04:00 | 130 | 13:00
| Brahmanbaria | 138 | 00:00 | 135 | 12:00 | Netrakona | 136 | 10:00 | 123 | 08:00
| Cantonment | 139 | 03:00 | 132 | 12:00 | New | 137 | 03:00 | 131 | 11:00
| Chandpur | 132 | 02:00 | 126 | 21:00 | Niamatpur | 139 | 15:00 | 136 | 07:00
| Chandraghona | 138 | 07:00 | 131 | 12:00 | Noapara | 139 | 00:00 | 133 | 11:00
| Chapai | 139 | 03:00 | 134 | 09:00 | Pabna | 141 | 04:00 | 136 | 08:00
| Charsaidpur | 136 | 06:00 | 129 | 13:00 | Palashbari | 132 | 02:00 | 125 | 08:00
| Chauddagram | 136 | 02:00 | 130 | 12:00 | Panchagarh | 139 | 04:00 | 124 | 09:00
| Chhatak | 136 | 04:00 | 132 | 12:00 | Patuakhali | 139 | 18:30 | 134 | 20:00
| Chowmuhani | 130 | 01:00 | 125 | 13:00 | Payra | 139 | 04:00 | 135 | 13:00
| Chuadanga | 140 | 02:00 | 131 | 13:00 | PHP | 135 | 04:00 | 127 | 13:00
| Coxsbazar | 129 | 00:00 | 113 | 12:00 | Postogola | 138 | 04:00 | 131 | 12:00
| Cumilla(N) | 139 | 04:00 | 134 | 12:00 | Purbachal | 138 | 03:00 | 130 | 12:00
| Cumilla(S) | 138 | 03:00 | 129 | 09:00 | Purbasadipur | 132 | 04:00 | 123 | 18:30
| Daudkandi | 136 | 06:00 | 128 | 19:00 | Rahanpur | 141 | 04:00 | 137 | 08:00
| Dhaka | 136 | 04:00 | 131 | 12:00 | Rahim | 135 | 04:00 | 128 | 13:00
| Dhamrai | 139 | 03:00 | 131 | 11:00 | Rajbari | 137 | 02:00 | 132 | 12:00
| Dhanmondi | 138 | 06:00 | 130 | 13:00 | Rajendrapur | 131 | 01:00 | 125 | 09:00
| Dohazari | 135 | 05:00 | 127 | 12:00 | Rajshahi | 137 | 17:00 | 133 | 09:00
| Faridpur | 136 | 01:00 | 133 | 12:00 | Rajshahi-230 | 138 | 03:00 | 131 | 08:00
| Fatullah | 136 | 02:00 | 130 | 12:00 | Ramganj | 129 | 07:00 | 124 | 13:00
| Fenchuganj | 140 | 02:00 | 137 | 13:00 | Rampur | 137 | 04:00 | 127 | 12:00
| Feni | 132 | 03:00 | 130 | 00:00 | Rampura | 137 | 07:00 | 130 | 12:00
| Ghatail | 129 | 07:00 | 120 | 08:00 | Rangamati | 137 | 03:00 | 132 | 11:00
| Ghorashal | 142 | 01:00 | 138 | 12:00 | Rangpur | 131 | 14:00 | 122 | 09:00
| Goalpara | 141 | 03:00 | 132 | 18:00 | Ruppur | 141 | 22:00 | 136 | 08:00
| Gollamari | 140 | 04:00 | 134 | 12:00 | Saidpur | 134 | 06:00 | 123 | 09:00
| Gopalganj | 139 | 04:00 | 133 | 18:30 | Satkhira | 139 | 04:00 | 131 | 18:00
| Gopalganj-400 | 139 | 04:00 | 134 | 12:00 | Satmasjid | 139 | 04:00 | 132 | 12:00
| Gulshan | 137 | 05:00 | 130 | 12:00 | Savar | 135 | 00:00 | 130 | 09:00
| Halishahar | 136 | 01:00 | 128 | 12:00 | SevenRings | 143 | 4:00 | 138 | 16:00
| Haripur | 134 | 02:00 | 129 | 12:00 | ShahCement | 136 | 06:00 | 129 | 13:00
| HaripurSBU | 134 | 03:00 | 129 | 12:00 | Shahjadpur | 145 | 03:00 | 140 | 09:00
| Hasnabad | 137 | 02:00 | 131 | 13:00 | Shahjibazar | 138 | 00:00 | 135 | 16:00
| Hathazari | 138 | 18:00 | 133 | 12:00 | Shahmirpur | 135 | 00:00 | 130 | 12:00
| Ishurdi | 141 | 04:00 | 136 | 13:00 | Shariatpur | 138 | 04:00 | 133 | 12:00
| Jaldhaka | 132 | 03:00 | 120 | 09:00 | Sherpur | 135 | 10:00 | 112 | 02:00
| Jamalpur | 136 | 10:00 | 115 | 02:00 | Shikalbaha | 125 | 01:00 | 119 | 12:00
| Jashore | 139 | 03:00 | 131 | 07:00 | Shikalbaha-230 | 138 | 02:00 | 131 | 12:00
| Jhenaidah | 140 | 4:00 | 135 | 13:00 | Shitalakhya | 135.5 | 05:00 | 129 | 12:00
| Jhenaidah-230 | 142 | 03:00 | 135 | 13:00 | Sholosohor | 137 | 03:00 | 130 | 13:00
| Joydebpur | 140 | 17:00 | 133 | 12:00 | Shyampur | 134 | 22:00 | 129 | 12:00
| Joypurhat | 137 | 02:00 | 125 | 00:00 | Shyampur-230 | 137 | 04:00 | 130 | 12:00
| Juldah | 136 | 04:00 | 129 | 12:00 | Siddhirganj | 136 | 03:00 | 130 | 12:00
| Kabirpur | 137 | 03:00 | 127 | 08:00 | Sirajganj | 140 | 01:00 | 134 | 10:00
| Kachua | 134 | 03:00 | 129 | 13:00 | Sonargaon | 134 | 08:00 | 128 | 12:00
| Kaliakoir | 140 | 02:00 | 128 | 16:00 | Sreemongol | 138 | 00:00 | 136 | 11:00
| Kallyanpur | 135 | 01:00 | 131 | 11:00 | Sreepur | 134 | 02:00 | 130 | 09:00
| Kalurghat | 137 | 05:00 | 131 | 13:00 | Srinagar | 136 | 03:00 | 131 | 12:00
| Kamrangirchar | 136 | 01:00 | 129 | 12:00 | SSM | 140 | 00:00 | 136 | 11:00
| Kaptai | 138 | 8:00 | 135 | 15:00 | Sunamganj | 135 | 01:00 | 131 | 18:00
| Kazla | 138 | 03:00 | 126 | 13:00 | Sylhet | 137 | 02:00 | 134 | 11:00
| Keranigonj | 137 | 03:00 | 130 | 13:00 | Sylhet-132 | 136 | 00:00 | 133 | 16:00
| Khagrachori | 137 | 04:00 | 130 | 12:00 | Tangail | 128 | 01:00 | 121 | 16:00
| Khulna | 139 | 03:00 | 133 | 12:00 | Thakurgaon | 136 | 04:00 | 121 | 09:00
| Khulna(S) | 140 | 02:00 | 134 | 12:00 | TK | 137 | 08:00 | 131 | 12:00
| Khulshi | 136 | 04:00 | 128 | 12:00 | Tongi | 137 | 01:00 | 132 | 11:00
| Kishoreganj | 134 | 00:00 | 128 | 18:00 | Ullahpara | 140 | 00:00 | 137 | 09:00
| Kodda | 138 | 05:00 | 125 | 16:00 | Ullon | 136 | 02:00 | 131 | 12:00
| KSRM | 137 | 01:00 | 130 | 12:00 | Uttara | 138 | 03:00 | 130 | 12:00
| Kulaura | 139 | 00:00 | 136 | 16:00 | UttaraNew | 138 | 03:00 | 131 | 12:00
| Kurigram | 131 | 03:00 | 120 | 08:00 | Zigatola | 137 | 03:00 | 130 | 13:00

## L-Curve
Date | 2024-12-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 505 | 4914 | 3445 | 8359 |  |  |  | QF-LDC-11
0:30 | 632 | 4610.5 | 3426 | 8036.5 | Date: | 2024-12-12
1:00 | 759 | 4307 | 3407 | 7714
1:30 | 711.5 | 4314.5 | 3274.5 | 7589
2:00 | 664 | 4322 | 3142 | 7464
2:30 | 657.5 | 4204.5 | 3019 | 7223.5 | [5 empty] | Gen. at Eve. Peak | 10354 | 10354 MW (18:00 )
3:00 | 651 | 4087 | 2896 | 6983 | [6 empty] | 18:00
3:30 | 655.5 | 4033 | 2871.5 | 6904.5 | [5 empty] | Gen. at Day Peak | 9207 | 9207 MW (12:00 )
4:00 | 660 | 3979 | 2847 | 6826 | [6 empty] | 12:00
4:30 | 677 | 3946 | 2834 | 6780 | [5 empty] | Highest Generation | 10354
5:00 | 694 | 3913 | 2821 | 6734 | [6 empty] | 18:00
5:30 | 653 | 4083.5 | 2867.5 | 6951
6:00 | 612 | 4254 | 2914 | 7168
6:30 | 548 | 4407.5 | 3044.5 | 7452
7:00 | 484 | 4561 | 3175 | 7736
7:30 | 440 | 4734.5 | 3357 | 8091.5
8:00 | 396 | 4908 | 3539 | 8447
8:30 | 501 | 4890.5 | 3711 | 8601.5
9:00 | 606 | 4873 | 3883 | 8756
9:30 | 646 | 4871 | 3875.5 | 8746.5
10:00 | 686 | 4869 | 3868 | 8737
10:30 | 696.5 | 4943.5 | 3835 | 8778.5
11:00 | 707 | 5018 | 3802 | 8820
11:30 | 703.5 | 5127.5 | 3886 | 9013.5
12:00 | 700 | 5237 | 3970 | 9207
12:30 | 729 | 5313 | 4113 | 9426
13:00 | 758 | 5389 | 4256 | 9645
13:30 | 727 | 5374.5 | 4079.5 | 9454
14:00 | 696 | 5360 | 3903 | 9263
14:30 | 691.5 | 5321.5 | 3701 | 9022.5
15:00 | 687 | 5283 | 3499 | 8782
15:30 | 667 | 5220.5 | 3469 | 8689.5
16:00 | 647 | 5158 | 3439 | 8597
16:30 | 617.5 | 5325 | 3511 | 8836
17:00 | 588 | 5492 | 3583 | 9075
17:30 | 508 | 5786 | 3928.5 | 9714.5
18:00 | 428 | 6080 | 4274 | 10354
18:30 | 472.5 | 5903 | 4315.5 | 10218.5
19:00 | 517 | 5726 | 4357 | 10083
19:30 | 526 | 5648 | 4371 | 10019
20:00 | 537 | 5552 | 4378 | 9930 |  |  |  | Executive Engineer
20:30 | 573.5 | 5447 | 4379 | 9826 |  |  |  | Network Operation Division
21:00 | 610 | 5342 | 4380 | 9722
21:30 | 590.5 | 5288.5 | 4191 | 9479.5
22:00 | 571 | 5235 | 4002 | 9237 |  |  |  |  | Page 6 of 7
22:30 | 551.5 | 5154 | 3855.5 | 9009.5
23:00 | 532 | 5073 | 3709 | 8782
23:30 | 518.5 | 4993.5 | 3577 | 8570.5
24:00 | 505 | 4914 | 3445 | 8359
10354 MW (18:00 )
9207 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-12-12 |  |  | Energy |  | 209593876
[17 empty] | 2024-12-12 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | Nepal | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 2927 | 485 | 0 | 2035 | 0 | 29 | 2254 | 40 | 0 | 48 | 54 | 460 | 0 | 27 | 0
0:30 | 2627 | 458 | 0 | 1848 | 0 | 44 | 2322.5 | 40 | 0 | 48 | 51 | 559.5 | 0 | 38.5 | 0 |  |  | Date: | 44176
1:00 | 2327 | 431 | 0 | 1661 | 0 | 59 | 2391 | 40 | 0 | 48 | 48 | 659 | 0 | 50 | 0
1:30 | 2323 | 433.5 | 0 | 1688.5 | 0 | 38 | 2330 | 40 | 0 | 40 | 48 | 595 | 0 | 53 | 0 | [8 empty] | Total Energy | 209.5939 | 209.5939 | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 2319 | 436 | 0 | 1716 | 0 | 17 | 2269 | 40 | 0 | 32 | 48 | 531 | 0 | 56 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2292 | 436 | 0 | 1665.5 | 0 | 16.5 | 2168.5 | 40 | 0 | 32 | 49 | 474 | 0 | 50 | 0 | [8 empty] | Energy Requirement | 209.5939 | 209.5939
3:00 | 2265 | 436 | 0 | 1615 | 0 | 16 | 2068 | 40 | 0 | 32 | 50 | 417 | 0 | 44 | 0
3:30 | 2215.5 | 436 | 0 | 1580.5 | 0 | 16.5 | 2072.5 | 40 | 0 | 32 | 51 | 418 | 0 | 42.5 | 0 | [7 empty] | Shortage
4:00 | 2166 | 436 | 0 | 1546 | 0 | 17 | 2077 | 40 | 0 | 32 | 52 | 419 | 0 | 41 | 0
4:30 | 2146 | 436 | 0 | 1550 | 0 | 17 | 2046 | 40 | 0 | 32 | 51 | 417.5 | 0 | 44.5 | 0
5:00 | 2126 | 436 | 0 | 1554 | 0 | 17 | 2015 | 40 | 0 | 32 | 50 | 416 | 0 | 48 | 0
5:30 | 2286.5 | 436 | 0 | 1612 | 0 | 20 | 2014 | 40 | 0 | 32 | 50 | 416 | 0 | 44.5 | 0
6:00 | 2447 | 436 | 0 | 1670 | 0 | 23 | 2013 | 40 | 0 | 32 | 50 | 416 | 0 | 41 | 0
6:30 | 2521.5 | 436 | 0 | 1772.5 | 0 | 42 | 2082 | 40 | 0 | 24 | 49 | 440.5 | 3.5 | 41 | 0 | [6 empty] | Coal
7:00 | 2596 | 436 | 0 | 1875 | 0 | 61 | 2151 | 40 | 0 | 16 | 48 | 465 | 7 | 41 | 0
7:30 | 2604 | 435.5 | 0 | 1920 | 0 | 103 | 2365 | 40 | 0 | 16 | 50 | 493.5 | 32.5 | 32 | 0 | [5 empty] | Oil
8:00 | 2612 | 435 | 0 | 1965 | 0 | 145 | 2579 | 40 | 0 | 16 | 52 | 522 | 58 | 23 | 0
8:30 | 2637.5 | 435 | 0 | 1934.5 | 0 | 157.5 | 2665 | 40 | 0 | 16 | 52 | 566 | 83.5 | 14.5 | 0
9:00 | 2663 | 435 | 0 | 1904 | 0 | 170 | 2751 | 40 | 0 | 16 | 52 | 610 | 109 | 6 | 0
9:30 | 2651 | 435.5 | 0 | 1895.5 | 0 | 182 | 2690.5 | 40 | 0 | 16 | 51 | 635.5 | 144.5 | 5 | 0
10:00 | 2639 | 436 | 0 | 1887 | 0 | 194 | 2630 | 40 | 0 | 16 | 50 | 661 | 180 | 4 | 0
10:30 | 2614 | 438.5 | 0 | 1901.5 | 0 | 200 | 2610.5 | 40 | 0 | 41.5 | 52 | 662.5 | 214.5 | 3.5 | 0
11:00 | 2589 | 441 | 0 | 1916 | 0 | 206 | 2591 | 40 | 0 | 67 | 54 | 664 | 249 | 3 | 0
11:30 | 2667 | 441 | 0 | 1970.5 | 0 | 206.5 | 2588 | 40 | 0 | 67 | 55 | 664 | 313 | 1.5 | 0
12:00 | 2745 | 441 | 0 | 2025 | 0 | 207 | 2585 | 40 | 0 | 67 | 56 | 664 | 377 | 0 | 0
12:30 | 2796.5 | 441 | 0 | 2099.5 | 0 | 206.5 | 2663 | 40 | 0 | 71.5 | 56 | 664 | 388 | 0 | 0
13:00 | 2848 | 441 | 0 | 2174 | 0 | 206 | 2741 | 40 | 0 | 76 | 56 | 664 | 399 | 0 | 0
13:30 | 2848 | 441 | 0 | 2174 | 0 | 206 | 2741 | 40 | 0 | 76 | 56 | 664 | 399 | 0 | 0
14:00 | 2848 | 441 | 0 | 2174 | 0 | 206 | 2741 | 40 | 0 | 76 | 56 | 664 | 399 | 0 | 0
14:30 | 2919.5 | 441 | 0 | 2035 | 0 | 190.5 | 2566 | 40 | 0 | 89.5 | 54 | 563 | 313.5 | 1.5 | 0
15:00 | 2991 | 441 | 0 | 1896 | 0 | 175 | 2391 | 40 | 0 | 103 | 52 | 462 | 228 | 3 | 0
15:30 | 3051.5 | 441 | 0 | 1835 | 0 | 172 | 2348 | 40 | 0 | 104 | 56 | 473 | 164 | 5 | 0
16:00 | 3112 | 441 | 0 | 1774 | 0 | 169 | 2305 | 40 | 0 | 105 | 60 | 484 | 100 | 7 | 0
16:30 | 3116.5 | 463 | 0 | 1788.5 | 0 | 338.5 | 2303 | 40 | 0 | 167 | 59 | 499 | 53 | 8.5 | 0
17:00 | 3121 | 485 | 0 | 1803 | 0 | 508 | 2301 | 40 | 0 | 229 | 58 | 514 | 6 | 10 | 0
17:30 | 3127 | 484.5 | 0 | 1942 | 0 | 651 | 2549.5 | 40 | 0 | 219 | 60 | 627.5 | 3 | 11 | 0
18:00 | 3133 | 484 | 0 | 2081 | 0 | 794 | 2798 | 40 | 0 | 209 | 62 | 741 | 0 | 12 | 0
18:30 | 3077 | 484 | 0 | 2107 | 0 | 644 | 2892.5 | 40 | 0 | 153.5 | 57 | 750.5 | 0 | 13 | 0
19:00 | 3021 | 484 | 0 | 2133 | 0 | 494 | 2987 | 40 | 0 | 98 | 52 | 760 | 0 | 14 | 0
19:30 | 3050 | 484 | 0 | 2165 | 0 | 343 | 3011 | 40 | 0 | 98 | 52 | 756 | 0 | 20 | 0
20:00 | 3015 | 485 | 0 | 2159 | 0 | 308 | 3018 | 40 | 0 | 80 | 52 | 755 | 0 | 18 | 0
20:30 | 3008.5 | 485.5 | 0 | 2157 | 0 | 211.5 | 3019 | 40 | 0 | 80 | 53 | 755 | 0 | 16.5 | 0
21:00 | 3002 | 486 | 0 | 2155 | 0 | 115 | 3020 | 40 | 0 | 80 | 54 | 755 | 0 | 15 | 0
21:30 | 2992 | 485.5 | 0 | 2156.5 | 0 | 109 | 2855.5 | 40 | 0 | 72 | 52 | 706 | 0 | 11 | 0
22:00 | 2982 | 485 | 0 | 2158 | 0 | 103 | 2691 | 40 | 0 | 64 | 50 | 657 | 0 | 7 | 0
22:30 | 2980.5 | 485.5 | 0 | 2119.5 | 0 | 74 | 2575 | 40 | 0 | 56 | 50 | 618.5 | 0 | 10.5 | 0
23:00 | 2979 | 486 | 0 | 2081 | 0 | 45 | 2459 | 40 | 0 | 48 | 50 | 580 | 0 | 14 | 0
23:30 | 2953 | 485.5 | 0 | 2058 | 0 | 37 | 2356.5 | 40 | 0 | 48 | 52 | 520 | 0 | 20.5 | 0 |  |  | Max Temp. in Dhaka |  | 21.2°C
24:00 | 2927 | 485 | 0 | 2035 | 0 | 29 | 2254 | 40 | 0 | 48 | 54 | 460 | 0 | 27 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Note on Y13: Author:

## Generation
2024-12-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 962700
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 8 | [18 empty] | 6800
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [26 empty] | 0
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 9 | 17 | [8 empty] | 40145
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [26 empty] | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 270 | 270 | 270 | 220 | 220 | 280 | 309 | 309 | 305 | 280 | 280 | 335 | 335 | 335 | 335 | 335 | 335 | 335 |  | 335 | 335 | 335 | 335 | 335 | 335 | 315 | 7429631
18 | Kodda 300 MW PP Unit-2 (Summit) | [26 empty] | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 128 | 128 | 78 | 35 | 8 | 31 | 185 | 185 | 185 | 185 | 187 | 192 | 195 | 195 | 128 | 88 | 168 | 195 |  | 197 | 197 | 197 | 199 | 199 | 199 | 158 | 3680000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 665 | 665 | 665 | 665 | 607 | 603 | 602 | 662 | 662 | 660 | 660 | 663 | 660 | 660 | 662 | 663 | 660 | 660 |  | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 15769089
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 41 | 37 | 37 | 10 |  |  | 34 | 34 | 36 | 38 | 36 | 40 | 41 | 41 | 41 | 41 | 41 | 41 |  | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 833976
33 | Ashuganj 225 MW CCPP | 181 | 181 | 181 | 181 | 197 | 155 | 142 | 147 | 188 | 222 | 196 | 198 | 180 | 180 | 180 | 182 | 182 | 180 |  | 185 | 191 | 180 | 180 | 181 | 187 | 181 | 4398000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 20 | 40 | 40 | 145 | 150 | 354 | 357 | 310 | 280 | 285 | 320 | 325 | 310 | 280 | 280 | 315 | 310 | 310 |  | 285 | 290 | 280 | 285 | 285 | 285 | 285 | 6311800
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 36 | 36 | 40 | 40 | 50 | 50 | 50 | 50 | 40 | 40 | 40 | 45 | 40 | 40 | 38 | 38 | 38 | 35 |  | 31 | 31 | 32 | 36 | 34 | 35 | 35 | 949670
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 330 | 320 | 294 | 281 | 281 | 347 | 386 | 387 | 377 | 352 | 350 | 367 | 400 | 400 | 410 | 427 | 427 | 431 |  | 431 | 433 | 433 | 418 | 401 | 401 | 380 | 9187200
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | [26 empty] | 0
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 16 | 16 | 17 | 19 | 20 | 21 | 18 | 16 | 14 | 10 | 8 | 7 | 7 | 6 | 6 | 6 | 5 | 5 |  | 5 | 6 | 6 | 8 | 9 | 9 | 7 | 243840
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 3 | 6 | 10 | 18 | 40 | 34 | 30 | 20 | 7 | 0 | [9 empty] | 171810
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 30 | 30 | 30 | 29 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 708000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 707520
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 12 | 12 | 40 | 40 | 58 | 58 | 57 | 57 | 57 | 57 | 57 | 56 | 57 | 58 |  | 58 | 57 | 58 | 58 | 58 | 58 | 58 | 1169568
48 | Shahjibazar 86 MW PP (Shahjibazar) | 86 | 62 | 31 | 8 | 8 | 8 | 42 | 86 | 86 | 65 | 65 | 65 | 86 | 84 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1202880
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 135 | 135 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 135 | 135 | 135 | 133 | 133 | 133 | 135 |  | 136 | 136 | 136 | 136 | 136 | 136 | 137 | 3247710
51 | Sylhet 20 MW GTPP | 15 | 15 | 15 | 15 | [22 empty] | 67000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 58176
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 343968
57 | Bibiana-II 341 MW CCPP (Summit) | 60 | 140 | 240 | 250 | 255 | 255 | 250 | 255 | 255 | 260 | 280 | 290 | 290 | 265 | 270 | 290 | 300 | 290 |  | 285 | 305 | 295 | 285 | 285 | 280 | 275 | 6311500
| Bibiyana South 400 MW | 306 | 306 | 306 | 256 | 256 | 256 | 256 | 256 | 282 | 313 | 330 | 400 | 346 | 310 | 305 | 360 | 346 | 346 |  | 316 | 320 | 316 | 316 | 316 | 316 | 316 | 7433300
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Tangail Palli Power Gen 22 MW | [6 empty] | 2 | 20 | 24 | 6 | 6 | 6 | 6 |  |  |  | 9 | 24 |  | 24 | 24 | 24 | 24 | 12 | 12 | 12 | 250800
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 48 | 48 | 50 | 52 | 50 | 50 | 48 | 52 | 52 | 50 | 54 | 56 | 56 | 50 | 52 | 60 | 58 | 62 |  | 52 | 52 | 52 | 54 | 50 | 50 | 54 | 1247040
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 33 | 33 | 35 | 35 | 32 | 10 | 3 | 3 | 3 | 3 | 10 | 8 | 2 | 2 | 7 | 5 |  | 10 | 20 | 23 | 26 | 29 | 25 | 25 | 477600
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 12 | 12 | 12 | 9 | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 364930
69 | Summit Ashulia | 18 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 |  |  | 21 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 411000
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 356400
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 20 | 25 |  |  |  |  | 12 | 17 | 30 |  | 30 | 30 | 30 | 25 | 25 | 17 | 17 | 358200
72 | Rupganj 33 MW PP(Summit) | 31 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 28 | 28 | 26 | 26 | 26 | 21 | 26 |  | 24 | 24 | 24 | 24 | 24 | 26 | 26 | 670400
73 | Ghorashal 108 MW PP (Regent)
Feni Lanka Power
| Chowmuhani 113 MW | [16 empty] | 2 | 26 |  | 26 | 26 | 26 |  |  |  |  | 131880
| Manikgonj 162MW PP(MPGL) | [16 empty] | 35 | 72 | [8 empty] | 131040
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [8 empty] | 16 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 26 | 26 | 26 |  |  | 450720
79 | Kodda 150 MW PP | 48 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 30 | 30 | 31 | 30 | 30 | 31 | 115 | 150 |  | 98 | 98 | 80 | 80 | 64 | 48 | 48 | 1189440
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [16 empty] | 10 | 17 | [8 empty] | 27840
| Kaptai 7 MW Solar PP | [7 empty] | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 23043
| Jodiac Power | [16 empty] | 14 | 50 |  | 34 | 17 | 17 |  |  |  |  | 144067
| Karnaphuli Power Ltd. | [16 empty] | 9 | 17 | [8 empty] | 39309
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 37 | 37 | 5 |  |  |  | 25 | 37 | 37 | 37 | 34 | 34 | 34 | 34 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 451512
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 7 |  |  |  | 17 | 51 | 0 | 3 | 0 | 17 | 37 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 906428
94 | Gagnagar 102 MW PP (Digital Power) | [21 empty] | 8 |  |  |  |  | 5040
95 | Patenga 50MW PP (Baraka) | 6 | [15 empty] | 11 | 19 |  | 19 | 19 | 19 |  |  |  |  | 81600
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 1 | 18 | [8 empty] | 23040
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [26 empty] | 0
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 17 | 17 | 17 | 17 | [12 empty] | 76763
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 120 | 120 | 163 | 130 | 130 | 120 | 120 | 120 | 120 | 163 | 120 | 120 | 120 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 3682718
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 6950
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 17 | [8 empty] | 41760
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 8 |  |  |  |  | 3 | 10 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 8 | 45 | 50 |  | 65 | 65 | 65 | 24 | 24 | 8 |  | 537600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 29 | 17 | 16 | 17 | 17 | 17 | 24 | 56 | 61 | 68 | 80 | 81 | 80 | 80 | 80 | 80 | 80 | 58 |  | 22 | 17 | 17 | 17 | 17 | 17 | 17 | 1071504
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 12 | 12 | [8 empty] | 27840
116 | Chandpur 200 MW (Desh energy)
117 | Ashuganj 150 MW PP (Midland) | [16 empty] | 11 | 58 |  | 50 | [6 empty] | 120436
118 | Bibiyana-III 400 MW CCPP | 80 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 72 | 68 | 70 | 80 | 130 | 215 | 380 | 380 | 375 | 359 |  | 303 | 315 | 303 | 300 | 300 | 303 | 303 | 4586000
| Jamalpur 115 MW PP (United) | 16 |  |  |  |  | 3 | 25 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 57 | 57 |  | 57 | 57 | 57 | 24 | 24 | 8 |  | 786000
| Anwara 300 MW PP (United) | [16 empty] | 32 | 32 |  | 85 | 50 | 15 |  |  |  |  | 185673
| Juldah unit-2 (Acorn) | [16 empty] | 12 | 12 | [8 empty] | 23040
| Anlima Energy Ltd. | [16 empty] | 11 | 47 |  | 53 | 17 | 17 |  |  |  |  | 146782
| Bhairob 54.5 MW | [16 empty] | 14 | 17 | [8 empty] | 41400
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 1 | 2 | 3 | 4 | 3 | 6 | 12 | 15 | 3 | 0 | [9 empty] | 52341
| Chandpur 115(Doreen) | [16 empty] | 5 | 16 | [8 empty] | 35520
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 12 | 36 |  | 17 | 17 | 17 |  |  |  |  | 109080
| Mirsharai 150 MW (Oil) | [16 empty] | 17 | 17 | [8 empty] | 26764
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 50 | 56 | 44 | 41 | 48 | 41 | 41 | 23 | 6 | 4 | 3 | 0 | 0 | 0 | 3 | 7 | 10 | 12 |  | 14 | 20 | 18 | 15 | 7 | 14 | 27 | 508800
| Sonagazi 75 MW Solar Plant | [6 empty] | 2 | 7 | 19 | 42 | 58 | 65 | 59 | 50 | 31 | 15 | 1 | [9 empty] | 351691
| Matarbari 2*600 MW (CPGCL) | 495 | 500 | 406 | 405 | 405 | 405 | 405 | 575 | 554 | 500 | 504 | 504 | 575 | 575 | 500 | 452 | 453 | 575 |  | 576 | 575 | 575 | 575 | 522 | 503 | 441 | 12189090
| JERA Meghnaghat Power Limited | 702 | 716 | 662 | 699 | 727 | 718 | 718 | 718 | 718 | 718 | 742 | 743 | 720 | 744 | 744 | 603 | 492 | 690 |  | 740 | 741 | 742 | 743 | 743 | 718 | 718 | 16878590
| Sreepur 150 MW | [10 empty] | 37 | 37 | 45 | 64 | 73 | 74 | 55 | [9 empty] | 378000
120
121 | Eastern Zone Total | 4307 | 4322 | 4087 | 3979 | 3913 | 4254 | 4561 | 4908 | 4873 | 4869 | 5018 | 5237 | 5389 | 5360 | 5283 | 5158 | 5492 | 6080 |  | 5726 | 5648 | 5552 | 5342 | 5235 | 5073 | 4914 | 120839954
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [26 empty] | 0
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 22 | 47 | 61 | 69 | 74 | 68 | 58 | 36 | 15 | 2 | [9 empty] | 458640
132 | Rampal 1320 MW (BIFPCL) | 454 | 425 | 369 | 379 | 374 | 374 | 374 | 455 | 513 | 451 | 464 | 464 | 511 | 506 | 454 | 412 | 410 | 583 |  | 630 | 620 | 626 | 628 | 508 | 450 | 400 | 11425450
133 | United Payra Power Ltd. | [15 empty] | 2 | 32 | 54 |  | 8 | [6 empty] | 111600
| Bhola Nutan Biddut BD LTD (GAS) | 15 |  | 10 | 25 | 25 | 40 | 90 | 109 | 126 | 122 | 141 | 217 | 220 | 180 | 180 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 3487970
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 250 | 250 | 307 | 240 | 240 | 240 | 280 | 200 | 150 | 150 | 150 | 285 |  | 307 | 307 | 307 | 307 | 215 | 200 | 200 | 5280000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3324
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 138 | 138 | 138 | 100 | 100 | 100 | 138 | 138 | 138 | 136 | 80 | 80 | 134 | 134 | 134 | 134 | 134 | 134 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 3071000
141 | Bhola 33 MW PP (Venture) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 3 | 5 | 6 |  | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 132985
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
| Bheramara HVDC | 431 | 436 | 436 | 436 | 436 | 436 | 436 | 435 | 435 | 436 | 441 | 441 | 441 | 441 | 441 | 441 | 485 | 484 |  | 484 | 484 | 485 | 486 | 485 | 486 | 485 | 10504727
147 | Nepal
148 | Bheramara 410 MW CCPP | 214 | 214 | 214 | 219 | 200 | 232 | 237 | 260 | 256 | 253 | 247 | 248 | 243 | 243 | 229 | 229 | 230 | 229 |  | 228 | 229 | 229 | 229 | 229 | 225 | 225 | 5668416
149 | Payra 1320 MW | 400 | 300 | 250 | 250 | 250 | 250 | 290 | 410 | 490 | 550 | 500 | 490 | 490 | 450 | 400 | 400 | 400 | 470 |  | 590 | 622 | 622 | 622 | 560 | 450 | 400 | 10757818
150
151 | Barapukuria TPP Unit-1 | 71 | 71 | 71 | 72 | 73 | 73 | 72 | 72 | 70 | 70 | 71 | 71 | 71 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 71 | 69 | 39 |  | 1565672
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 156 | 158 | 157 | 156 | 156 | 158 | 158 | 155 | 155 | 159 | 152 | 153 | 154 | 155 | 155 | 158 | 158 | 155 |  | 154 | 157 | 158 | 157 | 157 | 157 | 153 | 3806000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 0 | 1 | 3 | 4 | 3 | 1 | 0 | 0 | [9 empty] | 14940
157 | Sirajganj 68 MW Solar Park | [7 empty] | 1 | 2 | 3 | 14 | 38 | 42 | 37 | 22 | 8 | 0 | [9 empty] | 184496
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 175 | 175 | 140 | 130 | 130 | 130 | 141 | 150 | 150 | 150 | 149 | 150 | 169 | 140 | 140 | 144 | 176 | 185 |  | 185 | 185 | 185 | 184 | 181 | 181 | 181 | 3910000
Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 153 | 153 | 153 | 130 | 130 | 130 | 130 | 156 | 174 | 140 | 140 | 140 | 161 | 170 | 166 | 163 | 163 | 163 |  | 159 | 158 | 158 | 158 | 158 | 158 | 158 | 3899318
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 380 | 380 | 380 | 370 | 370 | 414 | 380 | 380 | 370 | 370 | 340 | 340 | 414 | 414 | 350 | 350 | 350 | 414 |  | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 9502763
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 147744
166 | Amnura 50 MW PP(Sinha)
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP
169 | Santahar 50 MW Peaking PP | [26 empty] | 0
170 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
171 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 42 | 42 | [8 empty] | 76048
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
173 | Confidence Power Bogura Unit-1 113 MW | [26 empty] | 0
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [26 empty] | 0
178 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 3 | 4 | 4 | 5 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 28421
| Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 34 | 34 | [8 empty] | 81216
| Intraco Solar 30 MW | [6 empty] | 0 | 1 | 3 | 6 | 11 | 25 | 24 | 20 | 13 | 5 | 0 | [9 empty] | 112610
178 | Adani Power Jharkhanda Ltd | 659 | 531 | 417 | 419 | 416 | 416 | 465 | 522 | 610 | 661 | 664 | 664 | 664 | 540 | 462 | 484 | 514 | 741 |  | 760 | 756 | 755 | 755 | 657 | 580 | 460 | 13804727
| Teesta Solar Limited | [7 empty] | 8 | 17 | 31 | 49 | 106 | 133 | 112 | 72 | 28 | 2 | [9 empty] | 583920
179 | Pabna Solar 100 MW | [6 empty] | 0 | 6 | 8 | 16 | 16 | 12 | 19 | 18 | 13 | 18 | 1 | [9 empty] | 134117
| Western Zone Total | 3407 | 3142 | 2896 | 2847 | 2821 | 2914 | 3175 | 3539 | 3883 | 3868 | 3802 | 3970 | 4256 | 3903 | 3499 | 3439 | 3583 | 4274 |  | 4357 | 4371 | 4378 | 4380 | 4002 | 3709 | 3445 | 88753922
[27 empty] | Total | 209593876