## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-12-15 | Sunday
|  | Date (day): | 2024-12-15 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13410.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13833 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-12-14 | 2024-12-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 360 | 384 | 400 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 2024-12-24
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | under maint
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 335 | 335 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 34 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 48 | 149 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 21 | 30 | 48 | 48 |  | 32 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 25 | 25 |  | 8 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 28 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 26 | 34 | 52
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 15 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 35 | 149 | 149
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 7 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 35 | 162 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 28 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 36 | 36 | 19 |  | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 392 | 394 | 400 | 400 | 184 |  | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| JERA Meghnaghat Power Limited |  | Gas | IPP | 718 | 0 | 0 | 306 | 357 | 330 | 330 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1454 | 1737 | 2692 | 2768 | 2095 | 1325
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 25 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 190 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 230 | 230 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 85 | 105
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 74 |  | 24 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 51 |  | 51 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 8 | 3 | 20
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 20 | 50 | 58 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 50 | 120 | 180 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 35 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 50 | 108
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 660 | 660 | 660 | 660 | 564 |  | Coal shortage
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 6 | 20 | 15 | 38 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 575 | 576 | 575 | 575 |  | 575 | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1540 | 1650 | 2293 | 2665 | 992 | 1160
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 222 | 201 | 200 | 200 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 345 | 300 | 315 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 41 | 43 | 42 | 42 |  |  | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 3 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 185 | 184 | 185 | 185 | 55 |  | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 20 | 140 | 140 |  | 10 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 30 | 45 |  | 7 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 42 | 40 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 56 | 58 | 66 | 70
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 8 | 15 | 15 |  | 10 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 44 | 95 | 100 |  | 13 | Engine problem
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 34 | 50 | 92 | 23 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 73 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 950 | 1028 | 1660 | 1671 | 194 | 800
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 16 | 12 | 20 | 20 | 182 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 64 | 64 | 96 | 95 | 105 |  | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 55 | 55 | 55 | 60 |  | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 14 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 24 | 24
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 53
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 37 | 16 | 0 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 180 | 176 | 263.6 | 247 | 182 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 2 | 2 |  | 9 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 57 | 60 | 60 | 6
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 42 | 42 | 86 | 86
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 136 | 133 | 135 | 135 |  | 96 | machine problem
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 22 | 22 |  | 3 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Gas problem
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 345 | 367 | 360 | 360 |  | 40
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 316 | 372 | 383 | 383
| Sylhet Area Total |  |  |  |  | 2411 | 2366 | 1047 | 1182 | 1246 | 1246 | 51 | 949
100 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 477 | 479 | 477 | 477
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 35 |  | 19 | Engine problem
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 34 | 60 |  | 49 | Engine problem
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 308 | 327 | 355 | 355 | 55 |  | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
106 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 100 | 0
108 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
109 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 499 | 833 | 617 | 617 | 617 |  | Unit-2 S/D
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
** | Nepal |  | 0 | Imported power | 40 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1358 | 1639 | 1603 | 1544 | 1128 | 68
110 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 | 110 |  | Fuel shortage
111 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 3 | 7 | 5 | 7
112 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 134 | 134 | 135 | 135 |  | 59 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
113 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 470 | 540 | 622 | 622 |  | 622 | Unit-2 S/D.
114 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 54 | 150
116 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 288 | 307 | 307 | 307
117 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1115 | 1225 | 1343 | 1441 | 110 | 681
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 26 | 32 |  | 18 | Engine problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 214 | 214 | 214
124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 162 | 180 | 180 | 40 |  | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 5 | 154 | 216 | 216 | 4
126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | under maint |  | 2025-01-31
127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 24 |  | 26 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
128 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
129 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 25 | 52
130 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 53 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 95 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
133 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 601 | 747 | 700 | 750
134 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 52 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 87 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1012 | 1282 | 1733 | 1859 | 215 | 531
135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 147 | 158 | 164 | 164 |  | 110 | Machine problem
137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 90 | 113
140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
141 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 46 | 115 | 115
142 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0
143 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 141 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 320 | 204 | 577 | 392 | 40 | 280 | .
| Total |  |  |  |  | 27740 | 27035 | 8976 | 10123 | 13410.6 | 13833 | 5007 | 5794
A. |  | 2024-12-14 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 10123 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6258 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10123 | MW
3 | Day peak Generation : |  |  | 8976 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9871.12 | MW
4 | Evening peak Generation : |  |  | 10123 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 203.4762 | MKWHr | By Solar | 3.1756 | MKWHr
| By Gas : | 107.5296 | MKWHr |  | By Oil: | 4.8248 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 60.2803 | MKWHr |  | By Hydro: | 0.9609 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 13.6763 | MKWHr |  | By Wind: | 0.46608 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5007 | MW | Dhaka | 3813.22 | 3813.22 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 5794 | MW | Chittagong | 977.4 | 977.4 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10801 | MW | Khulna | 1081 | 1081 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 827.84 | MMCFD | **Import Adani: | Taka | 90400164.53 | Rajshahi | 946 | 946 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : |  | 277635688.128 | ii) Oil : | Taka | 83048966.75 | Comilla | 847 | 847 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 414300494.78 | Total | Taka | 865385314.188 | Mymensingh | 807 | 807 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3016.2 | MKWHr. | Sylhet | 367 | 367 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 408 | MW (W to E) at | 18:00 | hrs | Barisal | 295.5 | 295.5 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 172 | MW at | 8:00 | hrs | Rangpur | 737 | 737 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 24.8°C |  |  | Total | 9871.12 | 9871.12 |  | 0
B. |  | 2024-12-15 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 24.8°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13833 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
4 | Reserve(Generation end) |  |  |  | 3633 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 205.0239 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6617 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector(India) : |  |  |  |  | i) Energy | 11.4836 | MKWHr. | ii) HVDC Flow at Peak Time |  | 479 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.079 | MKWHr. | iii) Maximum HVDC Flow : |  | 479 | MW at | 16:00 | hrs.
* Import Through HVDC C/B Interconnector(Nepal) : |  |  |  |  | i) Energy | 0 | MKWHr.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.16 |  | (b) Today: | 95.1 |  | (c) Rule Curve: |  | 101.4
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-12-14 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | JERA Meghnaghat Power Limited | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | Nepal | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Nepal | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 16 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 0 | 162 | 78 | 45 | 42 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 38 | 20 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 40 | 5 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 31 | 372 | 130 | 0 | 0 | 329 | 0 |  | 477 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 145 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 415 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4144 | 3181 | 7325 | 3108 | 477 | 0 | 1268 | 0 | 17 | 1915 | 40 | 0 | 16 | 38 | 415 | 0 | 31 | 0 | 95.17
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 16 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 0 | 150 | 16 | 45 | 20 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 36 | 22 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 40 | 5 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 38 | 372 | 135 | 0 | 0 | 320 | 0 |  | 477 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 150 | 417 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3942 | 2916 | 6858 | 2753 | 477 | 0 | 1175 | 0 | 0 | 1906 | 40 | 0 | 16 | 36 | 417 | 0 | 38 | 0 | 95.17
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 16 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 290 | 0 | 147 | 8 | 50 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 34 | 23 | 0 | 0 | 0 | 15 | 0 | 0 | 5 | 120 | 0 | 40 | 5 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 26 | 373 | 140 | 0 | 0 | 306 | 0 |  | 476 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 150 | 417 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3814 | 2751 | 6565 | 2657 | 476 | 0 | 1003 | 0 | 0 | 1896 | 40 | 0 | 16 | 34 | 417 | 0 | 26 | 0 | 95.16
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 16 | 33 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 290 | 0 | 144 | 8 | 50 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 28 | 23 | 0 | 0 | 0 | 15 | 0 | 0 | 5 | 120 | 0 | 25 | 5 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 20 | 373 | 140 | 0 | 0 | 290 | 0 |  | 476 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 150 | 416 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3655 | 2670 | 6325 | 2528 | 476 | 0 | 904 | 0 | 0 | 1897 | 40 | 0 | 16 | 28 | 416 | 0 | 20 | 0 | 95.16
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 16 | 28 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 0 | 140 | 8 | 50 | 10 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 32 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 25 | 5 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 16 | 374 | 140 | 0 | 0 | 300 | 0 |  | 477 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 150 | 417 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3687 | 2571 | 6258 | 2541 | 477 | 0 | 809 | 0 | 0 | 1910 | 40 | 0 | 16 | 32 | 417 | 0 | 16 | 0 | 95.16
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 15 | 16 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 0 | 135 | 45 | 50 | 40 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 34 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 58 | 42 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 17 | 371 | 270 | 0 | 0 | 295 | 0 |  | 476 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 417 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4120 | 2604 | 6724 | 2768 | 476 | 0 | 1017 | 0 | 0 | 1939 | 40 | 0 | 16 | 34 | 417 | 0 | 17 | 0 | 95.16
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 16 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 355 | 0 | 131 | 45 | 50 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 30 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 58 | 42 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 665 | 19 | 420 | 310 | 0 | 1 | 305 | 0 |  | 477 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 140 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 220 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 406 | 1 | 150 | 527 | 4 | 0 | 0 | 1 | 2 | 0 |  | 4429 | 2960 | 7389 | 3009 | 477 | 0 | 1135 | 0 | 12 | 2106 | 40 | 0 | 21 | 30 | 527 | 13 | 19 | 0 | 95.15
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 385 | 0 | 126 | 75 | 50 | 42 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 57 | 42 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 3 | 0 | 0 | 0 | 350 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 4 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 660 | 10 | 522 | 355 | 0 | 5 | 304 | 0 |  | 477 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 152 | 0 | 0 | 190 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 430 | 220 | 0 | 0 | 1 | 19 | 0 | 0 | 0 | 482 | 6 | 240 | 578 | 34 | 0 | 0 | 10 | 20 | 0 |  | 4806 | 3477 | 8283 | 3242 | 477 | 0 | 1222 | 0 | 46 | 2486 | 40 | 0 | 32 | 40 | 578 | 110 | 10 | 0 | 95.15
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 126 | 102 | 50 | 37 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 44 | 22 | 0 | 0 | 1 | 30 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 91 | 0 | 27 | 12 | 0 | 0 | 0 | 349 | 55 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 9 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 660 | 9 | 576 | 360 | 0 | 11 | 304 | 0 |  | 476 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 152 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 450 | 180 | 0 | 0 | 1 | 41 | 0 | 0 | 0 | 479 | 13 | 235 | 610 | 85 | 0 | 0 | 27 | 47 | 0 |  | 4915 | 3460 | 8375 | 2987 | 476 | 0 | 1170 | 0 | 173 | 2552 | 40 | 0 | 48 | 44 | 610 | 266 | 9 | 0 | 95.15
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 8 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 171 | 102 | 50 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 48 | 20 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 30 | 17 | 0 | 0 | 0 | 349 | 45 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 11 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 660 | 8 | 575 | 370 | 0 | 24 | 305 | 0 |  | 477 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 400 | 180 | 0 | 0 | 2 | 58 | 0 | 0 | 0 | 413 | 19 | 200 | 519 | 119 | 0 | 0 | 41 | 66 | 0 |  | 4936 | 3309 | 8245 | 3022 | 477 | 0 | 1172 | 0 | 139 | 2398 | 40 | 0 | 32 | 48 | 519 | 390 | 8 | 0 | 95.15
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 296 | 0 | 207 | 102 | 45 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 44 | 19 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 17 | 20 | 0 | 0 | 0 | 360 | 45 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 10 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 660 | 8 | 578 | 390 | 0 | 67 | 305 | 10 |  | 476 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 400 | 180 | 0 | 0 | 2 | 71 | 0 | 0 | 0 | 421 | 24 | 200 | 509 | 140 | 0 | 0 | 49 | 82 | 0 |  | 5039 | 3321 | 8360 | 3010 | 476 | 0 | 1193 | 0 | 126 | 2411 | 40 | 0 | 42 | 44 | 509 | 501 | 8 | 0 | 95.14
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 28 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 280 | 0 | 222 | 185 | 42 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 16 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 17 | 20 | 0 | 0 | 0 | 345 | 47 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 14 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 660 | 6 | 575 | 392 | 0 | 73 | 306 | 37 |  | 477 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 147 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 470 | 220 | 0 | 0 | 2 | 74 | 0 | 0 | 0 | 499 | 28 | 288 | 601 | 141 | 0 | 0 | 52 | 87 | 0 |  | 5171 | 3805 | 8976 | 3110 | 477 | 0 | 1321 | 0 | 128 | 2639 | 40 | 0 | 69 | 56 | 601 | 529 | 6 | 0 | 95.14
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 28 | 2 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 280 | 0 | 181 | 184 | 42 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 16 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 163 | 0 | 56 | 42 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 31 | 20 | 0 | 0 | 0 | 345 | 45 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 35 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 660 | 6 | 577 | 392 | 0 | 68 | 304 | 45 |  | 477 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 147 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 540 | 220 | 0 | 0 | 3 | 71 | 0 | 0 | 0 | 560 | 24 | 306 | 614 | 131 | 0 | 0 | 43 | 85 | 0 |  | 5420 | 3962 | 9382 | 3292 | 477 | 0 | 1366 | 0 | 142 | 2790 | 40 | 0 | 77 | 62 | 614 | 516 | 6 | 0 | 95.14
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 28 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 0 | 182 | 127 | 42 | 44 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 11 | 0 | 0 | 1 | 30 | 0 | 0 | 5 | 163 | 0 | 56 | 42 | 0 | 133 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 36 | 16 | 0 | 0 | 0 | 350 | 45 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 34 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 660 | 5 | 500 | 392 | 0 | 57 | 310 | 53 |  | 477 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 540 | 220 | 0 | 0 | 2 | 56 | 0 | 0 | 0 | 518 | 16 | 250 | 611 | 67 | 0 | 0 | 35 | 67 | 0 |  | 5202 | 3797 | 8999 | 3238 | 477 | 0 | 1322 | 0 | 162 | 2620 | 40 | 0 | 85 | 60 | 611 | 379 | 5 | 0 | 95.14
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 28 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 182 | 128 | 40 | 44 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 54 | 11 | 0 | 0 | 1 | 30 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 133 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 34 | 11 | 0 | 0 | 0 | 350 | 45 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 23 | 0 | 0 | 0 | 0 | 14 | 9 | 0 | 0 | 0 | 0 | 660 | 0 | 455 | 394 | 0 | 40 | 300 | 58 |  | 477 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 153 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 450 | 180 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 510 | 14 | 200 | 608 | 91 | 0 | 0 | 22 | 38 | 0 |  | 4997 | 3593 | 8590 | 3201 | 477 | 0 | 1225 | 0 | 169 | 2428 | 40 | 0 | 90 | 54 | 608 | 298 | 0 | 0 | 95.13
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 28 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 345 | 0 | 204 | 88 | 40 | 36 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 44 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 133 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 36 | 6 | 0 | 0 | 1 | 372 | 45 | 0 | 0 | 1 | 15 | 1 | 0 | 0 | 8 | 0 | 372 | 0 | 9 | 0 | 0 | 0 | 0 | 6 | 16 | 1 | 0 | 0 | 0 | 660 | 0 | 456 | 350 | 0 | 17 | 307 | 82 |  | 479 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 153 | 0 | 0 | 138 | 0 | 130 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 440 | 180 | 0 | 2 | 0 | 17 | 0 | 0 | 0 | 461 | 3 | 200 | 547 | 31 | 0 | 0 | 8 | 16 | 0 |  | 5031 | 3339 | 8370 | 3307 | 479 | 0 | 1148 | 0 | 206 | 2370 | 40 | 0 | 114 | 44 | 547 | 115 | 0 | 0 | 95.13
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 12 | 28 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 0 | 0 | 285 | 0 | 182 | 145 | 40 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 54 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 57 | 42 | 0 | 133 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 10 | 0 | 0 | 64 | 0 | 35 | 0 | 3 | 0 | 16 | 345 | 55 | 0 | 0 | 0 | 15 | 18 | 0 | 0 | 16 | 0 | 342 | 0 | 0 | 31 | 12 | 0 | 8 | 1 | 23 | 17 | 0 | 0 | 0 | 660 | 3 | 575 | 350 | 0 | 1 | 294 | 80 |  | 479 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 157 | 0 | 0 | 210 | 0 | 130 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 220 | 0 | 17 | 0 | 2 | 34 | 0 | 0 | 640 | 0 | 200 | 585 | 3 | 0 | 0 | 0 | 1 | 0 |  | 5254 | 3714 | 8968 | 3336 | 479 | 0 | 1236 | 0 | 397 | 2712 | 40 | 0 | 118 | 54 | 585 | 8 | 3 | 0 | 95.13
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 7 | 33 | 28 | 26 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 345 | 0 | 201 | 184 | 40 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 58 | 12 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 57 | 42 | 0 | 133 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 15 | 0 | 0 | 64 | 0 | 35 | 0 | 12 | 0 | 20 | 367 | 55 | 0 | 0 | 0 | 15 | 35 | 0 | 0 | 44 | 12 | 372 | 0 | 0 | 35 | 17 | 0 | 17 | 0 | 34 | 17 | 0 | 0 | 0 | 660 | 20 | 576 | 394 | 0 | 0 | 357 | 16 |  | 479 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 214 | 0 | 162 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 220 | 0 | 17 | 0 | 0 | 46 | 0 | 0 | 833 | 0 | 307 | 747 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5773 | 4350 | 10123 | 3657 | 479 | 0 | 1431 | 0 | 553 | 3074 | 40 | 0 | 64 | 58 | 747 | 0 | 20 | 0 | 95.13
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 431 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 25 | 28 | 26 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 26 | 0 | 15 | 0 | 0 | 0 | 310 | 0 | 182 | 185 | 40 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 52 | 16 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 58 | 42 | 0 | 135 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 64 | 0 | 35 | 0 | 0 | 0 | 20 | 336 | 55 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 342 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 33 | 17 | 0 | 0 | 0 | 660 | 36 | 575 | 394 | 0 | 0 | 314 | 0 |  | 478 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 156 | 0 | 0 | 214 | 0 | 218 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 220 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 855 | 0 | 307 | 757 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5516 | 4527 | 10043 | 3670 | 478 | 0 | 1353 | 0 | 446 | 3163 | 40 | 0 | 48 | 52 | 757 | 0 | 36 | 0 | 95.12
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 7 | 25 | 28 | 26 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 335 | 0 | 196 | 185 | 40 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 52 | 16 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 57 | 42 | 0 | 135 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 0 | 0 | 0 | 5 | 342 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 660 | 38 | 577 | 394 | 0 | 0 | 314 | 0 |  | 478 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 154 | 0 | 0 | 214 | 0 | 220 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 875 | 0 | 307 | 756 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5344 | 4589 | 9933 | 3663 | 478 | 0 | 1358 | 0 | 305 | 3195 | 40 | 0 | 48 | 52 | 756 | 0 | 38 | 0 | 95.12
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 7 | 17 | 28 | 26 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 40 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 52 | 17 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 57 | 42 | 0 | 135 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 0 | 0 | 0 | 0 | 357 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 660 | 44 | 575 | 393 | 0 | 0 | 316 | 0 |  | 478 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 157 | 0 | 0 | 214 | 0 | 220 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 870 | 0 | 307 | 756 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5304 | 4571 | 9875 | 3622 | 478 | 0 | 1361 | 0 | 283 | 3191 | 40 | 0 | 48 | 52 | 756 | 0 | 44 | 0 | 95.12
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 15 | 17 | 28 | 26 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 310 | 0 | 181 | 185 | 40 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 52 | 17 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 57 | 42 | 0 | 135 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 34 | 0 | 0 | 0 | 0 | 332 | 45 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 660 | 37 | 576 | 394 | 0 | 0 | 305 | 0 |  | 479 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 214 | 0 | 220 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 854 | 0 | 307 | 756 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5179 | 4417 | 9596 | 3590 | 479 | 0 | 1307 | 0 | 175 | 3112 | 40 | 0 | 48 | 52 | 756 | 0 | 37 | 0 | 95.12
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 15 | 17 | 26 | 26 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 310 | 0 | 183 | 185 | 40 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 18 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 135 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 24 | 0 | 34 | 0 | 0 | 0 | 0 | 332 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 660 | 44 | 577 | 393 | 0 | 0 | 318 | 0 |  | 478 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 214 | 0 | 197 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 0 | 250 | 672 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5147 | 3993 | 9140 | 3549 | 478 | 0 | 1319 | 0 | 142 | 2798 | 40 | 0 | 48 | 50 | 672 | 0 | 44 | 0 | 95.12
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 15 | 17 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 285 | 0 | 181 | 190 | 36 | 43 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 19 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 130 | 0 | 40 | 42 | 0 | 135 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 0 | 0 | 0 | 286 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 42 | 577 | 394 | 0 | 0 | 318 | 0 |  | 478 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 154 | 0 | 0 | 175 | 0 | 161 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 200 | 626 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4951 | 3698 | 8649 | 3342 | 478 | 0 | 1319 | 0 | 71 | 2649 | 40 | 0 | 32 | 50 | 626 | 0 | 42 | 0 | 95.11
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 15 | 17 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 295 | 0 | 223 | 190 | 36 | 43 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 44 | 17 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 130 | 0 | 40 | 42 | 0 | 135 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 16 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 46 | 575 | 400 | 0 | 0 | 318 | 0 |  | 479 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 157 | 0 | 0 | 154 | 0 | 156 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 150 | 446 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4985 | 3298 | 8283 | 3329 | 479 | 0 | 1333 | 0 | 58 | 2492 | 40 | 0 | 16 | 44 | 446 | 0 | 46 | 0 | 95.11
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8679600 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 6650139 | 0 | 28000 | 0 | 0 | 789120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493800 | 178200 | 277200 | 706000 | 211680 | 0 | 960900 | 0 | 0 | 0 | 0 | 5199915 | 0 | 0 | 0 |  | 62400 | 0 | 0 | 0 | 0 | 63840 | 0 | 480000 | 0 | 0 | 0 | 7613000 | 0 | 4224000 | 2676364 | 1050620 | 893952 | 0 | 0 | 829423 | 0 | 0 | 0 | 0 | 0 | 0 | 215040 | 1079040 | 433920 | 0 | 0 | 11100 | 685000 | 0 | 0 | 201312 | 3464427 | 0 | 1096992 | 796800 | 0 | 3244430 | 0 | 0 | 0 | 0 | 344400 | 33504 | 0 | 27600 | 0 | 0 | 856800 | 0 | 530496 | 125145 | 20160 | 0 | 81963 | 8517000 | 724800 | 102720 | 0 | 21844 | 42655 | 88897 | 0 | 0 | 164640 | 20160 | 7191600 | 0 | 153250 | 99360 | 45164 | 0 | 47160 | 166616 | 148800 | 117720 | 0 | 0 | 0 | 15616362 | 466080 | 12029090 | 7493636 | 0 | 368627 | 7389910 | 360000 |  | 11483636 | 0 | 6956352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2650000 | 128679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128304 | 0 | 0 | 3793000 | 0 | 0 | 4140000 | 0 | 4155173 | 0 | 0 | 0 | 1952000 | 0 | 1232800 | 0 | 0 | 0 | 0 | 0 | 0 | 29626 | 0 | 10805818 | 5098130 | 0 | 46800 | 19980 | 451440 | 171840 | 0 | 0 | 12800000 | 150129 | 5236000 | 13676273 | 855360 | 0 | 3011 | 296248 | 523200 | 0 |  | 116692373 | 86783799 | 203476172 | 77738141 | 11483636 | 0 | 29791481 | 0 | 3675655 | 60280270 | 960900 | 0 | 1149120 | 1079040 | 13676273 | 3175576 | 466080 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24997248 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20282923.95 | 0 | 149800 | 0 | 0 | 15324710.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370350 | 0 | 0 | 0 | 3791188.8 | 0 | 0 | 0 | 0 | 0 | 0 | 16587728.85 | 0 | 0 | 0 |  | 1097616 | 0 | 0 | 0 | 0 | 1050806.4 | 0 | 0 | 0 | 0 | 0 | 21240270 | 0 | 14023680 | 8965819.4 | 3393502.6 | 3012618.24 | 0 | 0 | 3325986.23 | 0 | 0 | 0 | 0 | 0 | 0 | 161280 | 7078502.4 | 1349491.2 | 0 | 0 | 0 | 2671500 | 0 | 0 | 915969.6 | 11848340.34 | 0 | 6088305.6 | 4159296 | 0 | 9051959.7 | 0 | 0 | 0 | 0 | 258300 | 25463.04 | 0 | 563040 | 0 | 0 | 16459128 | 0 | 9342034.56 | 0 | 359049.6 | 0 | 1358946.54 | 22570050 | 13814688 | 1927027.2 | 0 | 0 | 697409.25 | 1728157.68 | 0 | 0 | 3195662.4 | 359049.6 | 19129656 | 0 | 0 | 1817294.4 | 757851.92 | 0 | 842749.2 | 0 | 2681376 | 1994176.8 | 0 | 0 | 0 | 108846043.14 | 0 | 70971631 | 0 | 0 | 0 | 0 | 0 |  | 32269017.16 | 0 | 20521238.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8374000 | 609938.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97126.128 | 0 | 0 | 32012920 | 0 | 0 | 13662000 | 0 | 13836726.09 | 0 | 0 | 0 | 6500160 | 0 | 3599776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70021700.64 | 15855184.3 | 0 | 905580 | 0 | 0 | 2981424 | 0 | 0 | 93440000 | 0 | 39008200 | 90400164.53 | 0 | 0 | 0 | 0 | 0 | 0 |  | 460637678.04 | 444095155.708 | 904732833.748 | 228355377.798 | 32269017.16 | 0 | 49280310.33 | 0 | 67724256.35 | 414300494.78 | 0 | 0 | 15324710.4 | 7078502.4 | 90400164.53 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 28 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 280 | 0 | 222 | 185 | 42 | 41 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 16 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 40 | 42 | 0 | 136 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 17 | 20 | 0 | 0 | 0 | 345 | 47 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 14 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 660 | 6 | 575 | 392 | 0 | 73 | 306 | 37 |  | 477 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 147 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 470 | 220 | 0 | 0 | 2 | 74 | 0 | 0 | 0 | 499 | 28 | 288 | 601 | 141 | 0 | 0 | 52 | 87 | 0 |  | 8976 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 7 | 33 | 28 | 26 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 345 | 0 | 201 | 184 | 40 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 58 | 12 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 57 | 42 | 0 | 133 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 15 | 0 | 0 | 64 | 0 | 35 | 0 | 12 | 0 | 20 | 367 | 55 | 0 | 0 | 0 | 15 | 35 | 0 | 0 | 44 | 12 | 372 | 0 | 0 | 35 | 17 | 0 | 17 | 0 | 34 | 17 | 0 | 0 | 0 | 660 | 20 | 576 | 394 | 0 | 0 | 357 | 16 |  | 479 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 214 | 0 | 162 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 220 | 0 | 17 | 0 | 0 | 46 | 0 | 0 | 833 | 0 | 307 | 747 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10123 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 23 | 25 | 33 | 52 | 0 | 40 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 24 | 74 | 51 | 0 | 50 | 50 | 0 | 20 | 0 | 0 |  | 315 | 0 | 200 | 185 | 50 | 42 | 0 | 0 | 51 | 0 | 45 | 52 | 0 | 0 |  | 15 | 70 | 20 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 60 | 86 | 0 | 135 | 0 | 0 | 0 | 0 | 22 | 2 | 0 | 300 | 0 | 0 | 95 | 0 | 149 | 0 | 100 | 200 | 140 | 360 | 55 | 105 | 105 | 0 | 120 | 54 | 110 | 114 | 100 | 100 | 383 | 17 | 0 | 162 | 108 | 0 | 53 | 0 | 92 | 36 | 0 | 160 | 0 | 660 | 38 | 575 | 400 | 0 |  | 330 |  |  | 477 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 135 | 7 | 0 | 0 | 0 | 0 | 40 | 25 | 95 | 0 | 0 | 32 | 52 | 24 | 0 | 0 | 5 | 0 | 0 | 164 | 0 | 0 | 214 | 0 | 180 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 617 | 0 | 307 | 750 | 0 | 0 |  |  |  | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 |  | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 34 | 55 | 55 | 0 | 25 | 23 | 25 | 33 | 34 | 0 | 40 | 0 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 24 | 56 | 50 | 0 | 20 | 50 | 0 | 3 | 0 | 0 | 0 | 300 | 0 | 200 | 185 | 50 | 42 | 0 | 0 | 51 | 0 | 30 | 52 | 0 | 0 |  | 15 | 66 | 20 | 0 | 0 | 1.6 | 30 | 0 | 0 | 5 | 163 | 0 | 60 | 86 | 0 | 135 | 0 | 0 | 0 | 0 | 22 | 2 | 0 | 300 | 0 | 0 | 96 | 0 | 149 | 20 | 100 | 200 | 140 | 360 | 55 | 50 | 85 | 5 | 50 | 54 | 110 | 114 | 95 | 100 | 383 | 7 | 50 | 162 | 50 | 0 | 17 | 35 | 50 | 36 | 0 | 17 | 0 | 660 | 15 | 575 | 400 | 0 | 70 | 330 |  |  | 477 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 135 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 26 | 25 | 24 | 0 | 0 | 5 | 0 | 0 | 164 | 0 | 0 | 214 | 0 | 180 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 95 | 0 | 90 | 0 | 8 | 113 | 622 | 220 |  | 54 | 6 | 100 | 115 | 0 | 0 | 617 | 30 | 307 | 700 | 170 | 0 |  | 29 | 47 | 0 |  |  |  |  | gas | hvdc |  | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 17 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 310 | 0 | 143 | 185 | 45 | 41 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 58 | 42 | 0 | 135 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 9 | 0 | 0 | 0 | 346 | 35 | 20 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 4 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 606 | 4 | 577 | 400 | 0 | 28 | 318 | 0 | 0 | 478 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 164 | 0 | 0 | 153 | 0 | 163 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 340 | 220 | 0 | 0 | 1 | 19 | 0 | 0 | 0 | 464 | 8 | 200 | 459 | 40 | 0 | 0 | 11 | 21 | 0 | 0 |  |  |  | 107529622 | 11483636 |  | 0 | 60280270 | 4824775 | 1079040 | 3175576 | 466080 | 960900 |  |  |  | 189799899
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [9 empty] | 399427 | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 |  | 299798 | [7 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [14 empty] | 499227 |  | 499229 |  |  | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [11 empty] | 107.5296 | 11.4836 |  | 0 | 60.2803 | 4.8248 | 1.079 | 3.1756 | 0.46608 | 0.9609
| Minimum Generation |  | 6258 | 5:00
| Highest Generation |  | 10123 | 18:00 | [129 empty] | 0 | [77 empty] | 189.7999
| Day Peak Generation |  | 8976 | 12:00
| Evening Peak Generation |  | 10123 | 18:00 | [207 empty] | 202699852
| HVDC Max Flow |  | 479 | 16:00 | [207 empty] | 202.6999
| HVDC EvPeak Flow |  | 479 | 18:00
| Load factor L.F |  | 83.75% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-12-15
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-12-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8976 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6617
Evening Peak Generation : |  |  | 10123 | MW Hour : | 18:00 | Available Max Generation : |  | 13833
E.P. Demand (at gen end) : |  |  | 10123 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10200
Maximum Generation : |  |  | 10123 | MW Hour : | 18:00 | Reserve(Generation end) |  | 3633
Total Gen. (MKWH) : |  |  | 203.4762 | System Load Factor : | 83.75% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 172 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-12-15
Actual : |  | 95.1 | Ft.(MSL) , | Rule curve : | 101.4 | Ft.( MSL )
Gas Consumed : |  | Total = | 827.84 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 277635688.128 | Adani : | 90400164.53
|  |  | Coal : | 414300494.78 | Oil: | 83048966.75 | Total: | 865385314.188
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3499.4504 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 955.1576 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1336.0395 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1159.4645 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 954.9506 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 709.2906 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 398.5972 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 331.2534 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 647.895 |  |  | 0 | 0%
Total |  | 0 |  | 9992.0988 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:14 | 14:59 | Gallamari- Khulna (S) 132kV Ckt-2 Scheduled S/D from Gollamari 132/33kV end Due to
Annual Maintenance. and from Khulna(S) 230/132kV end Due to Annual Maintenance.
08:20 | 16:59 | Madaripur-Shariatpur 132kV Ckt-1 Scheduled S/D from Shariatpur 132/33kV end Due to
Annual Maintenance
08:29 | 10:23 | Haripur-Sonargaon 132kV Ckt-2 Scheduled S/D from Sonargaon 132/33kV end Due to Annual
maintenance and from Haripur 230/132kV end Due to Shuttdown taken by Sonargaon Side by
NLDC.
08:30 | 18:59 | Cumilla(S) 132/33kV S/S TR-4 LT Scheduled S/D Due to Annual Maintenance
08:30 | 18:59 | Cumilla(S) 132/33kV S/S TR-4 HT Scheduled S/D Due to Annual Maintenance
08:31 | 16:57 | Madaripur-Shariatpur 132kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end Due to Annual
Maintenance
08:34 |  | Bheramara-GK 132kV Ckt-1 Scheduled S/D from Bheramara 230/132kV end Due to A/M and from
Bheramara(GK) 132/33kV end Due to Annual Maintenance
08:40 | 17:40 | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Annual maintenance and from Bogura 400/230kV end Due to Annual Maintenance
08:50 | 16:35 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due
to Annual maintenance by sherpur grid
08:50 | 16:53 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-01 Scheduled S/D Due to A/M
08:51 | 17:19 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to AM
08:57 | 16:12 | Bogura-Natore 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to Annual
maintenance and from Natore 132/33kV end Due to Yearly maintenance
09:02 | 15:15 | Saidpur 132/33kV S/S TR-5 (434T) HT Scheduled S/D Due to Annual Maintenance work.
09:03 | 15:16 | Saidpur 132/33kV S/S TR-5 (434T) LT Scheduled S/D Due to Annual Maintenance work.
09:05 | 16:10 | Jamalpur United (20MW)- Sherpur 132kV Ckt-2 Scheduled S/D from Sherpur 132/33kV end Due
to Annual Maintanance
09:06 | 15:32 | Mymensingh RPCL-Tangail 132kV Ckt-2 Scheduled S/D from Ghatail 132/33kV end Due to
Annual Maintenance
09:07 | 15:30 | Tangail 132/33kV S/S RPCL-2 Scheduled S/D Due to Annual Maintenance
09:10 | 16:49 | Barishal(N)-Madaripur 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end Due to
Annual Maintenance and from Madaripur 132/33kV end Due to Annual maintenance
09:32 | 15:07 | Narshingdi 132/33kV S/S T-3 LT Scheduled S/D Due to Annul Maintenance purpose.
09:33 | 15:02 | Narshingdi 132/33kV S/S T-3 HT Scheduled S/D Due to Annul Maintenance purpose.
09:45 | 17:03 | Fenchuganj 230/132/33kV S/S AT-01 HT Scheduled S/D Due to Annual Maintenance
09:45 | 17:03 | Fenchuganj 230/132/33kV S/S AT-01 LT Scheduled S/D Due to Annual Maintenance.
09:45 | 17:23 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to AM
10:02 | 15:54 | Khulna (C) S/S North-WestCkt-1 Scheduled S/D Due to Due to annual maintenance work.
10:45 | 15:00 | Shikalbaha 230/132kV S/S Interconnection-1 Scheduled S/D Due to Annual Maintenance
10:45 | 15:00 | Shikalbaha 230/132kV S/S Interconnection-1 Scheduled S/D
10:45 | 15:00 | Shikalbaha 230/132kV S/S Interconnection-1 Scheduled S/D
11:25 | 12:07 | Mogbazar 132/33kV S/S GT-2 LT Forced S/D Due to Oil Filling
12:00 |  | Day Peak Generation = 8,979MW
12:06 | 12:06 | Mogbazar 132/33kV S/S GT-2 HT Forced S/D Due to Oil filling
12:42 | 16:03 | Sylhet (South) S/S Trafo-2 HT Forced S/D Due to Cooling fan maintenance work by siemens
12:42 | 16:03 | Sylhet (South) S/S Trafo-2 LT Forced S/D Due to Cooling fan maintenance work by siemens
| 15:10 | Bakulia 132/33kV S/S T-1 (402T) HT is restored.
15:23 | 19:59 | Munshiganj 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual Maintenance
15:24 | 19:58 | Munshiganj 132/33kV S/S Transformer-2 HT Scheduled S/D Due to None
| 16:35 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-2 is restored.
16:45 |  | Rampal Unit-1 synch
18:00 |  | Peak generation 10123 MW
19:31 | 19:42 | Daudkandi-Sonargaon 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing Dist Trip
C-phase, zone-1, Dist 24.05km. relays.
| 19:54 | Ghorasal-Tongi 230kV Ckt-2 is restored.
05:00 |  | Minimum Generation is 6617 MW
07:01 |  | Sirajgonj 230 S/S SNWPCL (Unit-04) Scheduled S/D Due to Due to maintenance of SNWPCL
(Unit-4) end.
07:46 |  | Narshingdi 132/33kV S/S T-2 HT Scheduled S/D Due to 132kV Tr-2 and Related Equipment.
07:46 |  | Narshingdi 132/33kV S/S T-2 LT Scheduled S/D Due to 132kV Tr-2 and Related Equipment.
07:50 |  | Bogura-Natore 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to Annual
Maintenance and from Natore 132/33kVend.
|  | Sub-Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
|  | Network Operation Division |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-12-14
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 384 | 8679600 | Gas shortage
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | GT-2 shutdown for gas shortage
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 28000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6650139
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 789120 | Low demand
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 672000 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 277200 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 706000 | Engine problem
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 26 | 211680 | Low demand
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 27600 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 530496 | Low demand
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 102720 | Reserve
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | Reserve
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 99360 | Low demand
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 166616
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 117720 | Low demand
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 394 | 7493636 | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 718 | 0 | 357 | 7389910 | On test.
| Dhaka area Total |  |  |  | 5915 | 1737 | 33941797
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 125145
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 63840 | Low demand
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 960900 | Low water level
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 230 | 5199915
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 0 | 0 | Reserve
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 20160 | Low demand
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 8 | 480000
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21844
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 42655 | Low demand
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 88897 | Low demand
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Reserve
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 20160 | Low demand
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 45164 | Low demand
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Reserve
55 | SS Power I |  | IPP | 2*612 | 1224 | 660 | 15616362 | Coal shortage
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 20 | 466080
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 576 | 12029090 | Machine problem.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1650 | 35180212
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 201 | 4224000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7613000 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 43 | 893952 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 0 | 0 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 184 | 2676364
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 829423
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 20 | 81963 | Low demand
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 1050620 | Machine problem.
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | Reserve
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 58 | 1079040
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 8 | 215040 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 44 | 164640 | Low demand
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 148800 | Low demand
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 368627
| Cumilla Area Total |  |  |  | 2917 | 1028 | 19345469
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 12 | 433920 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11100
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 64 | 856800 | Fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 55 | 724800 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 153250
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 62400
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 47160 | Low demand
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 16 | 360000
| Mymensingh Area Total |  |  |  | 646 | 176 | 2649430
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 685000 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3464427
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 0 | 0 | 0 | Contact expired
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 201312 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 33504 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 57 | 1096992 | Gas shortage
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 42 | 796800 | Gas shortage
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 133 | 3244430 | Machine problem.
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 344400 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8517000 | FGMO
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 372 | 7191600 | FGMO
| Sylhet Area Total |  |  |  | 2366 | 1182 | 25575465
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 479 | 11483636
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 327 | 6956352 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 451440
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 833 | 12800000 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Nepal |  | Imported power | 40 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1639 | 31691428
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 7 | 128679 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 134 | 2650000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 540 | 10805818 | Unit-2 under overhauling
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5098130
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 46800 | Low demand
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 5236000
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3011
| Barisal Area Total |  |  |  | 2236 | 1225 | 23968438
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | NENP
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 4140000
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 162 | 4155173
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 154 | 1952000 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 0 | 1232800 | Under maint.
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 128304 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 19980
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 747 | 13676273
135 | Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 296248
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 523200
| Rajshahi Area Total |  |  |  | 3449 | 1282 | 26123978
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3793000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | Reserve
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29626
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 46 | 171840 | Low demand
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 150129
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 855360
| Rangpur Area Total |  |  |  | 950 | 204 | 4999955
| Total |  |  |  | 27035 | 10123 | 203476172
| Eastern Grid Total |  |  |  | 16701 | 5773 | 116692373
| Western Grid Total |  |  |  | 10334 | 4350 | 86783799
| National Grid Total |  |  |  | 27035 | 10123 | 203476172
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-12-2024
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6811.62 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3059.5 | MW
i) Dhaka area |  |  | 3813.22 |  | MW | i) Khulna area |  |  |  | 1081 | MW
ii) Chattogram area |  |  | 977.4 |  | MW | ii) Barishal area |  |  |  | 295.5 | MW
iii) Cumilla area |  |  | 847 |  | MW | iii) Rajshahi area |  |  |  | 946 | MW
iv) Mymensingh area |  |  | 807 |  | MW | iv) Rangpur area |  |  |  | 737 | MW
v) Sylhet area |  |  | 367 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9871.12 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jashore | 95 | 13:00 | 133 | Rajbari | 56 | 18:00
2 | AKSML | 101 | 06:00 | 68 | Jhenaidah | 89 | 18:30 | 134 | Rajendrapur | 86 | 18:30
3 | Aftabnagar | 22 | 12:00 | 69 | Joydebpur | 120 | 18:00 | 135 | Rajshahi | 92 | 13:00
4 | Agargaon | 71 | 13:00 | 70 | Joypurhat | 42 | 18:00 | 136 | Rajshahi-230 | 40 | 13:00
5 | Agrabad | 58 | 18:30 | 71 | Juldah | 8 | 07:00 | 137 | Ramganj | 78 | 20:00
6 | Amnura | 47 | 12:00 | 72 | KSRM | 23 | 01:00 | 138 | Rampur | 24 | 18:30
7 | Ashuganj | 59 | 13:00 | 73 | Kabirpur | 219 | 17:00 | 139 | Rangamati | 12 | 18:00
8 | BSRM | 134 | 01:00 | 74 | Kachua | 46 | 20:00 | 140 | Rangpur | 106 | 18:00
9 | Bagerhat | 61 | 18:00 | 75 | Kallyanpur | 66 | 12:00 | 141 | Ruppur | 3.4 | 15:00
10 | Bakulia | 72 | 19:00 | 76 | Kalurghat | 18 | 15:00 | 142 | SSM | 8 | 23:00
11 | Banani | 38.6 | 13:00 | 77 | Kamrangirchar | 55.71 | 13:00 | 143 | Saidpur | 88 | 18:00
12 | Bangabhaban | 4 | 11:00 | 78 | Kaptai | N/A | N/A | 144 | Satkhira | 81 | 18:30
13 | Barapukuria | 49 | 18:30 | 79 | Kazla | 83 | 13:00 | 145 | Satmasjid | 73 | 14:00
14 | Barguna | 14 | 21:00 | 80 | Keranigonj | 68 | 13:00 | 146 | Savar | 146 | 10:00
15 | Barishal | 80 | 13:00 | 81 | Khagrachori | 24 | 18:00 | 147 | SevenRings | 14.12 | 16:00
16 | Barishal-230 | 64 | 18:00 | 82 | Khulna | 53 | 18:30 | 148 | ShahCement | 25 | 00:00
17 | Baroaulia | 56 | 15:00 | 83 | Khulshi | 137 | 13:00 | 149 | Shahjadpur | 47 | 19:00
18 | Baroirhat | 40 | 13:00 | 84 | Kishoreganj | 100 | 19:00 | 150 | Shahjibazar | 69 | 18:30
19 | Bashundhara | 110 | 18:00 | 85 | Kodda | 227 | 18:00 | 151 | Shahmirpur | 25 | 08:00
20 | BashundharaCement | 12 | 13:00 | 86 | Kulaura | 28 | 18:00 | 152 | Shariatpur | 50 | 19:30
21 | Beanibazar | 42 | 18:00 | 87 | Kurigram | 44 | 08:00 | 153 | Sherpur | 100 | 18:00
22 | Benapole | 40 | 18:00 | 88 | Kushtia | 98 | 18:30 | 154 | Shikalbaha | 20 | 11:00
23 | Bhaluka | 114 | 18:00 | 89 | Lalbag | 65 | 20:00 | 155 | Shitalakhya | 58.2 | 13:00
24 | Bhandaria | 35 | 21:00 | 90 | Lalmonirhat | 40 | 18:00 | 156 | Sholosohor | 31 | 18:00
25 | Bhangura | 21 | 18:00 | 91 | MI_Cement | 11.7 | 19:00 | 157 | Shyampur | 144 | 10:00
26 | Bheramara(GK) | 41 | 18:00 | 92 | Madanganj | 29 | 12:00 | 158 | Siddhirganj | 94 | 12:00
27 | Bhulta | 217 | 23:00 | 93 | Madaripur | 63 | 20:00 | 159 | Sirajganj | 64 | 18:30
28 | Bog-Sherpur | 56 | 09:00 | 94 | Madartek | 58 | 13:00 | 160 | Sonargaon | 67 | 12:00
29 | Bogura | 109 | 18:00 | 95 | Madunaghat | 35 | 13:00 | 161 | Sreemongol | 50 | 18:00
30 | Borhanuddin | 52 | 20:00 | 96 | Magura | 50 | 18:30 | 162 | Sreepur | 63 | 16:00
31 | Brahmanbaria | 105 | 18:00 | 97 | Mahasthangarh | 54 | 18:00 | 163 | Srinagar | 29.2 | 21:00
32 | Cantonment | 70 | 13:00 | 98 | Manikganj | 91 | 18:00 | 164 | Sunamganj | 38 | 18:00
33 | Chandpur | 40 | 21:00 | 99 | Maniknagar | 42 | 13:00 | 165 | Sylhet | 48 | 15:00
34 | Chandraghona | 25 | 18:00 | 100 | Matarbari | 33 | 18:00 | 166 | Sylhet-132 | 76 | 17:00
35 | Chapai | 51 | 13:00 | 101 | Matuail | 44 | 11:00 | 167 | TK | 22.4 | 19:00
36 | Charsaidpur | 35 | 09:00 | 102 | Millgate | 83 | 13:00 | 168 | Tangail | 124 | 13:00
37 | Chauddagram | 40 | 18:30 | 103 | Mirpur | 87 | 14:00 | 169 | Thakurgaon | 79 | 18:00
38 | Chhatak | 20 | 19:00 | 104 | Mirsorai | 8 | 20:00 | 170 | Tongi | 98 | 12:00
39 | Chowmuhani | 135 | 18:00 | 105 | Mirzapur | 34 | 12:00 | 171 | Ullahpara | 26 | 18:00
40 | Chuadanga | 68 | 13:00 | 106 | Mithapukur | 46 | 18:00 | 172 | Ullon | 35 | 13:00
41 | Coxsbazar | 95 | 18:00 | 107 | Modern | 0 | 00:00 | 173 | Uttara | 52 | 14:00
42 | Cumilla(N) | 92 | 20:00 | 108 | Mogbazar | 76.8 | 18:00 | 174 | UttaraNew | 36 | 13:00
43 | Cumilla(S) | 115 | 18:00 | 109 | Mongla | 27 | 09:00 | 175 | Zigatola | 66 | 13:00
44 | Daudkandi | 98 | 20:00 | 110 | Motijheel | 24 | 13:00
45 | Dhaka | 26 | 13:00 | 111 | Munshiganj | 66 | 01:00
46 | Dhamrai | 92 | 17:00 | 112 | Mymensingh | 164 | 18:00
47 | Dhanmondi | 85.4 | 13:00 | 113 | Naogaon | 88 | 18:30
48 | Dohazari | 67 | 18:30 | 114 | Narail | 39 | 18:00
49 | Faridpur | 102 | 19:00 | 115 | Narinda | 44 | 13:00
50 | Fatullah | 75 | 12:00 | 116 | Narshingdi | 154 | 18:30
51 | Fenchuganj | 24 | 18:00 | 117 | Natore | 96 | 18:30
52 | Feni | 62 | 13:00 | 118 | Nawabganj | 27.2 | 13:00
53 | GPH | 78 | 17:00 | 119 | Netrakona | 96 | 18:00
54 | Ghatail | 46 | 17:00 | 120 | New | 48.9 | 15:00
55 | Ghorashal | 50 | 18:00 | 121 | Niamatpur | 45 | 08:00
56 | Goalpara | 22 | 13:00 | 122 | Noapara | 34 | 18:30
57 | Gollamari | 54 | 14:00 | 123 | PHP | 8 | 15:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-12-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 417 | 06:00 | 401 | 13:00 | Kaliakoir | 388 | 04:00 | 361 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Madunaghat | 412 | 04:00 | 403 | 13:00
| Bhulta | 412 | 04:00 | 396 | 11:00 | Meghnaghat | 410 | 04:00 | 398 | 12:00
| Bibiana | 400 | 03:00 | 389 | 12:00 | Payra | 422 | 01:00 | 412 | 13:00
| BIPTC | 409 | 03:00 | 397 | 10:00 | Rahanpur | 415 | 02:00 | 398 | 18:00
| Bogura | 412 | 06:00 | 389 | 18:00 | Rampal | 416 | 03:00 | 402 | 13:00
| Gopalganj | 419 | 06:00 | 402 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 241 | 06:00 | 228 | 13:00 | Haripur | 240 | 07:00 | 232 | 12:00
| AKSML | 238 | 02:00 | 229 | 12:00 | Hasnabad | 242 | 03:00 | 231 | 12:00
| Aminbazar | 239 | 02:00 | 229 | 13:00 | Hathazari | 237 | 02:00 | 230 | 13:00
| Ashuganj | 243 | 05:00 | 234 | 09:00 | Ishurdi | 246 | 06:00 | 235 | 19:00
| Ashuganj-400 | 243 | 05:00 | 234 | 09:00 | Jhenaidah | 242 | 03:00 | 230 | 13:00
| Baghabari | 243 | 04:00 | 234 | 18:00 | Kaliakoir | 243 | 04:00 | 227 | 12:00
| Barapukuria | 228 | 05:00 | 214 | 18:00 | Keranigonj | 241 | 06:00 | 229 | 12:00
| Barapukuria-230 | 228 | 05:00 | 214 | 18:00 | Khulna(S) | 242 | 02:00 | 232 | 13:00
| Barishal | 248 | 04:00 | 240 | 12:00 | Madunaghat | 237 | 04:00 | 230 | 13:00
| Bheramara | 244 | 06:00 | 233 | 18:00 | Madunaghat-400 | 237 | 06:00 | 231 | 13:00
| Bhulta | 245 | 04:00 | 233 | 12:00 | Maniknagar | 243 | 04:00 | 232 | 11:00
| Bibiana | 233 | 06:00 | 226 | 12:00 | Meghnaghat | 250 | 04:00 | 241 | 14:00
| BIPTC | 245 | 06:00 | 232 | 18:00 | Meghnaghat-400 | 245 | 04:00 | 235 | 12:00
| Bogura | 241 | 04:00 | 227 | 18:00 | Mirsorai | 238 | 06:00 | 230 | 13:00
| Bogura-400 | 240 | 06:00 | 226 | 18:00 | Rajshahi | 243 | 02:00 | 232 | 18:00
| Borhanuddin | 249 | 02:00 | 244 | 11:00 | Rampal | 241 | 03:00 | 229 | 18:00
| BSRM | 237 | 04:00 | 230 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Cumilla(N) | 238 | 06:00 | 230 | 12:00 | Rampura | 243 | 04:00 | 233 | 12:00
| Faridpur | 249 | 06:00 | 239 | 13:00 | Shikalbaha | 235 | 04:00 | 228 | 12:00
| Fenchuganj | 235 | 02:00 | 230 | 12:00 | Shyampur | 243 | 06:00 | 231 | 12:00
| Ghorashal | 240 | 00:00 | 240 | 00:00 | Siddhirganj | 246 | 06:00 | 234 | 12:00
| Ghorashal-230 | 243 | 05:00 | 231 | 12:00 | Sirajgonj | 247 | 02:00 | 239 | 18:30
| Gopalganj | 247 | 01:00 | 238 | 13:00 | Sreepur | 242 | 02:00 | 234 | 10:00
| GPH | 236 | 02:00 | 229 | 13:00 | Tongi | 240 | 04:00 | 227 | 12:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 138 | 02:00 | 130 | 12:00 | Kushtia | 143 | 06:00 | 138 | 19:00
| Agargaon | 141 | 06:00 | 133 | 12:00 | Lalbag | 139 | 06:00 | 130 | 13:00
| Agrabad | 136 | 04:00 | 130 | 13:00 | Lalmonirhat | 133 | 05:00 | 121 | 18:00
| AKS | 134 | 06:00 | 129 | 12:00 | Madanganj | 135 | 00:00 | 129 | 12:00
| Aminbazar | 138 | 00:00 | 131 | 13:00 | Madaripur | 137 | 05:00 | 134 | 13:00
| Amnura | 141 | 02:00 | 132 | 13:00 | Madartek | 138 | 03:00 | 130 | 13:00
| Ashuganj | 145 | 04:00 | 140 | 12:00 | Madunaghat | 136 | 02:00 | 132 | 12:00
| Bagerhat | 139 | 03:00 | 132 | 13:00 | Magura | 144 | 05:00 | 134 | 13:00
| Bakulia | 134 | 00:00 | 131 | 13:00 | Mahasthangarh | 138 | 03:00 | 127 | 18:00
| Banani | 139 | 03:00 | 131 | 12:00 | Manikganj | 135 | 05:00 | 127 | 12:00
| Bangabhaban | 140 | 04:00 | 132 | 12:00 | Maniknagar | 140 | 06:00 | 132 | 11:00
| Barapukuria | 137 | 04:00 | 126 | 18:00 | Matarbari | 130 | 09:00 | 123 | 18:00
| Barguna | 139 | 02:00 | 135 | 12:00 | Matuail | 137.6 | 04:00 | 131 | 18:00
| Barishal | 137 | 04:00 | 132 | 12:00 | Millgate | 139 | 02:00 | 127 | 13:00
| Barishal-230 | 138 | 01:00 | 133 | 12:00 | Mirpur | 137 | 00:00 | 131 | 12:00
| Baroaulia | 137 | 02:00 | 132 | 13:00 | Mirzapur | 132 | 06:00 | 123 | 12:00
| Baroirhat | 134 | 03:00 | 127 | 13:00 | Mithapukur | 136 | 04:00 | 124 | 18:00
| Bashundhara | 138 | 01:00 | 128 | 16:00 | MI_Cement | 137.2 | 05:00 | 130 | 12:00
| BashundharaCement | 135 | 00:00 | 129 | 12:00 | Modern | 136 | 06:00 | 131 | 14:00
| Beanibazar | 136 | 03:00 | 131 | 16:00 | Mogbazar | 139 | 03:00 | 132 | 12:00
| Benapole | 142 | 05:00 | 133 | 12:00 | Mongla | 138 | 01:00 | 131 | 18:00
| Bhaluka | 134 | 05:00 | 128 | 10:00 | Motijheel | 140 | 04:00 | 130 | 07:00
| Bhandaria | 135 | 06:00 | 130 | 00:00 | Munshiganj | 136 | 02:00 | 130 | 12:00
| Bhangura | 144 | 01:00 | 134 | 18:00 | Mymensingh | 136 | 09:00 | 122 | 00:00
| Bheramara | 141 | 01:00 | 136 | 18:00 | Naogaon | 138 | 04:00 | 128 | 12:00
| Bheramara(GK) | 142 | 05:00 | 137 | 12:00 | Narail | 145 | 03:00 | 135 | 13:00
| Bhulta | 128 | 08:00 | 121 | 18:00 | Narinda | 140 | 06:00 | 132 | 11:00
| Bog-Sherpur | 140 | 04:00 | 132 | 18:30 | Narshingdi | 130 | 01:00 | 124 | 18:30
| Bogura | 139 | 03:00 | 131 | 13:00 | Natore | 141 | 06:00 | 133 | 13:00
| Bogura-230 | 139 | 03:00 | 130 | 18:00 | Nawabganj | 139 | 04:00 | 130 | 12:00
| Brahmanbaria | 139 | 00:00 | 135 | 11:00 | Netrakona | 135 | 09:00 | 122 | 07:00
| Cantonment | 140 | 02:00 | 133 | 12:00 | New | 138 | 04:00 | 129 | 12:00
| Chandpur | 133 | 04:00 | 123 | 13:00 | Niamatpur | 140 | 00:00 | 133 | 18:00
| Chandraghona | 137 | 02:00 | 133 | 11:00 | Noapara | 142 | 04:00 | 132 | 16:00
| Chapai | 139 | 03:00 | 133 | 11:00 | Pabna | 143 | 02:00 | 135 | 18:00
| Charsaidpur | 136 | 00:00 | 130 | 12:00 | Palashbari | 134 | 04:00 | 122 | 18:00
| Chauddagram | 136 | 02:00 | 128 | 12:00 | Panchagarh | 138 | 03:00 | 122 | 09:00
| Chhatak | 136 | 04:00 | 131 | 22:00 | Patuakhali | 138 | 05:00 | 133 | 22:00
| Chowmuhani | 128 | 00:00 | 125 | 13:00 | Payra | 139 | 01:00 | 135 | 19:30
| Chuadanga | 143 | 03:00 | 132 | 13:00 | PHP | 136 | 04:00 | 125 | 13:00
| Coxsbazar | 129 | 06:00 | 123 | 18:00 | Postogola | 139 | 00:00 | 133 | 11:00
| Cumilla(N) | 139 | 01:00 | 132 | 12:00 | Purbachal | 138 | 01:00 | 128 | 12:00
| Cumilla(S) | 139 | 04:00 | 128 | 17:00 | Purbasadipur | 134 | 04:00 | 120 | 09:00
| Daudkandi | 136 | 01:00 | 128 | 13:00 | Rahanpur | 140 | 00:00 | 135 | 18:00
| Dhaka | 138 | 01:00 | 131 | 13:00 | Rahim | 135 | 04:00 | 130 | 12:00
| Dhamrai | 140 | 03:00 | 131 | 12:00 | Rajbari | 138 | 06:00 | 132 | 12:00
| Dhanmondi | 137 | 00:00 | 132 | 12:00 | Rajendrapur | 131 | 03:00 | 121 | 13:00
| Dohazari | 134 | 00:00 | 129 | 13:00 | Rajshahi | 140 | 04:00 | 134 | 13:00
| Faridpur | 138 | 06:00 | 133 | 11:00 | Rajshahi-230 | 141 | 03:00 | 129 | 13:00
| Fatullah | 139 | 05:00 | 131 | 12:00 | Ramganj | 131 | 04:00 | 122 | 14:00
| Fenchuganj | 141 | 06:00 | 136 | 11:00 | Rampur | 137 | 05:00 | 132 | 12:00
| Feni | 134 | 06:00 | 126 | 14:00 | Rampura | 138 | 02:00 | 131 | 12:00
| Ghatail | 132 | 09:00 | 122 | 00:00 | Rangamati | 137 | 05:00 | 132 | 12:00
| Ghorashal | 143 | 03:00 | 137 | 11:00 | Rangpur | 133 | 02:00 | 119 | 18:00
| Goalpara | 143 | 04:00 | 135 | 13:00 | Ruppur | 142 | 02:00 | 137 | 13:00
| Gollamari | 142 | 04:00 | 134 | 13:00 | Saidpur | 134 | 05:00 | 122 | 09:00
| Gopalganj | 139 | 02:00 | 133 | 13:00 | Satkhira | 141 | 06:00 | 132 | 18:00
| Gopalganj-400 | 139 | 01:00 | 133 | 13:00 | Satmasjid | 140 | 02:00 | 131 | 13:00
| Gulshan | 137 | 01:00 | 130 | 12:00 | Savar | 138 | 02:00 | 130 | 12:00
| Halishahar | 137 | 05:00 | 131 | 13:00 | SevenRings | 145 | 06:00 | 137 | 12:00
| Haripur | 137 | 01:00 | 130 | 12:00 | ShahCement | 136 | 00:00 | 130 | 12:00
| HaripurSBU | 137 | 01:00 | 125 | 19:30 | Shahjadpur | 144 | 00:00 | 139 | 12:00
| Hasnabad | 138 | 01:00 | 133 | 12:00 | Shahjibazar | 139 | 05:00 | 135 | 11:00
| Hathazari | 139 | 02:00 | 133 | 13:00 | Shahmirpur | 135 | 04:00 | 131 | 14:00
| Ishurdi | 144 | 06:00 | 137 | 18:00 | Shariatpur | 139 | 05:00 | 132 | 13:00
| Jaldhaka | 133 | 04:00 | 119 | 09:00 | Sherpur | 137 | 09:00 | 118 | 23:00
| Jamalpur | 140 | 09:00 | 121 | 23:00 | Shikalbaha | 126 | 03:00 | 120 | 14:00
| Jashore | 140 | 00:00 | 132 | 13:00 | Shikalbaha-230 | 137 | 03:00 | 131 | 12:00
| Jhenaidah | 144 | 02:00 | 136 | 13:00 | Shitalakhya | 137.2 | 05:00 | 130 | 12:00
| Jhenaidah-230 | 145 | 06:00 | 137 | 12:00 | Sholosohor | 136 | 02:00 | 131 | 13:00
| Joydebpur | 143 | 00:00 | 132 | 16:00 | Shyampur | 136 | 01:00 | 130 | 12:00
| Joypurhat | 137 | 01:00 | 127 | 13:00 | Shyampur-230 | 138 | 03:00 | 130 | 13:00
| Juldah | 135 | 00:00 | 132 | 10:00 | Siddhirganj | 137 | 00:00 | 131 | 12:00
| Kabirpur | 139 | 03:00 | 126 | 11:00 | Sirajganj | 141 | 01:00 | 131 | 18:00
| Kachua | 135 | 04:00 | 125 | 13:00 | Sonargaon | 135 | 00:00 | 129 | 11:00
| Kaliakoir | 142 | 04:00 | 126 | 12:00 | Sreemongol | 138 | 00:00 | 134 | 11:00
| Kallyanpur | 138 | 03:00 | 129 | 13:00 | Sreepur | 135 | 17:00 | 130 | 11:00
| Kalurghat | 136 | 00:00 | 132 | 13:00 | Srinagar | 139 | 06:00 | 131 | 12:00
| Kamrangirchar | 139 | 02:00 | 129 | 12:00 | SSM | 140 | 01:00 | 136 | 00:00
| Kaptai | 139 | 4:00 | 135 | 15:00 | Sunamganj | 135 | 02:00 | 130 | 16:00
| Kazla | 140 | 06:00 | 131 | 13:00 | Sylhet | 137 | 03:00 | 133 | 12:00
| Keranigonj | 139 | 06:00 | 131 | 12:00 | Sylhet-132 | 136 | 02:00 | 133 | 10:00
| Khagrachori | 136 | 03:00 | 130 | 13:00 | Tangail | 130 | 09:00 | 123 | 08:00
| Khulna | 139 | 00:00 | 131 | 18:30 | Thakurgaon | 136 | 04:00 | 120 | 09:00
| Khulna(S) | 142 | 06:00 | 134 | 13:00 | TK | 136 | 04:00 | 132 | 13:00
| Khulshi | 135 | 04:00 | 130 | 13:00 | Tongi | 140 | 04:00 | 130 | 15:00
| Kishoreganj | 134 | 15:00 | 130 | 10:00 | Ullahpara | 141 | 00:00 | 134 | 18:00
| Kodda | 139 | 01:00 | 123 | 12:00 | Ullon | 139 | 06:00 | 130 | 13:00
| KSRM | 139 | 00:00 | 132 | 14:00 | Uttara | 139 | 04:00 | 128 | 13:00
| Kulaura | 139 | 02:00 | 134 | 12:00 | UttaraNew | 139 | 02:00 | 131 | 12:00
| Kurigram | 131 | 00:00 | 118 | 18:00 | Zigatola | 138 | 00:00 | 131 | 13:00

## L-Curve
Date | 2024-12-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 375 | 4985 | 3298 | 8283 |  |  |  | QF-LDC-11
0:30 | 496.5 | 4564.5 | 3239.5 | 7804 | Date: | 2024-12-14
1:00 | 618 | 4144 | 3181 | 7325
1:30 | 595 | 4043 | 3048.5 | 7091.5
2:00 | 572 | 3942 | 2916 | 6858
2:30 | 539 | 3878 | 2833.5 | 6711.5 | [5 empty] | Gen. at Eve. Peak | 10123 | 10123 MW (18:00 )
3:00 | 506 | 3814 | 2751 | 6565 | [6 empty] | 18:00
3:30 | 490 | 3734.5 | 2710.5 | 6445 | [5 empty] | Gen. at Day Peak | 8976 | 8976 MW (12:00 )
4:00 | 474 | 3655 | 2670 | 6325 | [6 empty] | 12:00
4:30 | 430 | 3671 | 2620.5 | 6291.5 | [5 empty] | Highest Generation | 10123
5:00 | 386 | 3687 | 2571 | 6258 | [6 empty] | 18:00
5:30 | 320 | 3903.5 | 2587.5 | 6491
6:00 | 254 | 4120 | 2604 | 6724
6:30 | 266 | 4274.5 | 2782 | 7056.5
7:00 | 278 | 4429 | 2960 | 7389
7:30 | 225 | 4617.5 | 3218.5 | 7836
8:00 | 172 | 4806 | 3477 | 8283
8:30 | 242.5 | 4860.5 | 3468.5 | 8329
9:00 | 313 | 4915 | 3460 | 8375
9:30 | 372.5 | 4925.5 | 3384.5 | 8310
10:00 | 432 | 4936 | 3309 | 8245
10:30 | 431 | 4987.5 | 3315 | 8302.5
11:00 | 430 | 5039 | 3321 | 8360
11:30 | 436 | 5105 | 3563 | 8668
12:00 | 442 | 5171 | 3805 | 8976
12:30 | 401 | 5295.5 | 3883.5 | 9179
13:00 | 360 | 5420 | 3962 | 9382
13:30 | 415.5 | 5311 | 3879.5 | 9190.5
14:00 | 471 | 5202 | 3797 | 8999
14:30 | 541 | 5099.5 | 3695 | 8794.5
15:00 | 611 | 4997 | 3593 | 8590
15:30 | 545.5 | 5014 | 3466 | 8480
16:00 | 480 | 5031 | 3339 | 8370
16:30 | 509 | 5142.5 | 3526.5 | 8669
17:00 | 538 | 5254 | 3714 | 8968
17:30 | 473 | 5513.5 | 4032 | 9545.5
18:00 | 408 | 5773 | 4350 | 10123
18:30 | 447 | 5644.5 | 4438.5 | 10083
19:00 | 486 | 5516 | 4527 | 10043
19:30 | 520 | 5344 | 4589 | 9933
20:00 | 571 | 5304 | 4571 | 9875 |  |  |  | Executive Engineer
20:30 | 586.5 | 5241.5 | 4494 | 9735.5 |  |  |  | Network Operation Division
21:00 | 602 | 5179 | 4417 | 9596
21:30 | 587.5 | 5163 | 4205 | 9368
22:00 | 573 | 5147 | 3993 | 9140 |  |  |  |  | Page 6 of 7
22:30 | 539.5 | 5049 | 3845.5 | 8894.5
23:00 | 506 | 4951 | 3698 | 8649
23:30 | 440.5 | 4968 | 3498 | 8466
24:00 | 375 | 4985 | 3298 | 8283
10123 MW (18:00 )
8976 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-12-14 |  |  | Energy |  | 203476172
[17 empty] | 2024-12-14 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | Nepal | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 3329 | 479 | 0 | 1333 | 0 | 58 | 2492 | 40 | 0 | 16 | 44 | 446 | 0 | 46 | 0
0:30 | 3218.5 | 478 | 0 | 1300.5 | 0 | 37.5 | 2203.5 | 40 | 0 | 16 | 41 | 430.5 | 0 | 38.5 | 0 |  |  | Date: | 44178
1:00 | 3108 | 477 | 0 | 1268 | 0 | 17 | 1915 | 40 | 0 | 16 | 38 | 415 | 0 | 31 | 0
1:30 | 2930.5 | 477 | 0 | 1221.5 | 0 | 8.5 | 1910.5 | 40 | 0 | 16 | 37 | 416 | 0 | 34.5 | 0 | [8 empty] | Total Energy | 203.4762 | 203.4762 | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr | Total Energy Gen 203.476 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 203.476 MKWHr
2:00 | 2753 | 477 | 0 | 1175 | 0 | 0 | 1906 | 40 | 0 | 16 | 36 | 417 | 0 | 38 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2705 | 476.5 | 0 | 1089 | 0 | 0 | 1901 | 40 | 0 | 16 | 35 | 417 | 0 | 32 | 0 | [8 empty] | Energy Requirement | 203.4762 | 203.4762
3:00 | 2657 | 476 | 0 | 1003 | 0 | 0 | 1896 | 40 | 0 | 16 | 34 | 417 | 0 | 26 | 0
3:30 | 2592.5 | 476 | 0 | 953.5 | 0 | 0 | 1896.5 | 40 | 0 | 16 | 31 | 416.5 | 0 | 23 | 0 | [7 empty] | Shortage
4:00 | 2528 | 476 | 0 | 904 | 0 | 0 | 1897 | 40 | 0 | 16 | 28 | 416 | 0 | 20 | 0
4:30 | 2534.5 | 476.5 | 0 | 856.5 | 0 | 0 | 1903.5 | 40 | 0 | 16 | 30 | 416.5 | 0 | 18 | 0
5:00 | 2541 | 477 | 0 | 809 | 0 | 0 | 1910 | 40 | 0 | 16 | 32 | 417 | 0 | 16 | 0
5:30 | 2654.5 | 476.5 | 0 | 913 | 0 | 0 | 1924.5 | 40 | 0 | 16 | 33 | 417 | 0 | 16.5 | 0
6:00 | 2768 | 476 | 0 | 1017 | 0 | 0 | 1939 | 40 | 0 | 16 | 34 | 417 | 0 | 17 | 0
6:30 | 2888.5 | 476.5 | 0 | 1076 | 0 | 6 | 2022.5 | 40 | 0 | 18.5 | 32 | 472 | 6.5 | 18 | 0 | [6 empty] | Coal
7:00 | 3009 | 477 | 0 | 1135 | 0 | 12 | 2106 | 40 | 0 | 21 | 30 | 527 | 13 | 19 | 0
7:30 | 3125.5 | 477 | 0 | 1178.5 | 0 | 29 | 2296 | 40 | 0 | 26.5 | 35 | 552.5 | 61.5 | 14.5 | 0 | [5 empty] | Oil
8:00 | 3242 | 477 | 0 | 1222 | 0 | 46 | 2486 | 40 | 0 | 32 | 40 | 578 | 110 | 10 | 0
8:30 | 3114.5 | 476.5 | 0 | 1196 | 0 | 109.5 | 2519 | 40 | 0 | 40 | 42 | 594 | 188 | 9.5 | 0
9:00 | 2987 | 476 | 0 | 1170 | 0 | 173 | 2552 | 40 | 0 | 48 | 44 | 610 | 266 | 9 | 0
9:30 | 3004.5 | 476.5 | 0 | 1171 | 0 | 156 | 2475 | 40 | 0 | 40 | 46 | 564.5 | 328 | 8.5 | 0
10:00 | 3022 | 477 | 0 | 1172 | 0 | 139 | 2398 | 40 | 0 | 32 | 48 | 519 | 390 | 8 | 0
10:30 | 3016 | 476.5 | 0 | 1182.5 | 0 | 132.5 | 2404.5 | 40 | 0 | 37 | 46 | 514 | 445.5 | 8 | 0
11:00 | 3010 | 476 | 0 | 1193 | 0 | 126 | 2411 | 40 | 0 | 42 | 44 | 509 | 501 | 8 | 0
11:30 | 3060 | 476.5 | 0 | 1257 | 0 | 127 | 2525 | 40 | 0 | 55.5 | 50 | 555 | 515 | 7 | 0
12:00 | 3110 | 477 | 0 | 1321 | 0 | 128 | 2639 | 40 | 0 | 69 | 56 | 601 | 529 | 6 | 0
12:30 | 3201 | 477 | 0 | 1343.5 | 0 | 135 | 2714.5 | 40 | 0 | 73 | 59 | 607.5 | 522.5 | 6 | 0
13:00 | 3292 | 477 | 0 | 1366 | 0 | 142 | 2790 | 40 | 0 | 77 | 62 | 614 | 516 | 6 | 0
13:30 | 3292 | 477 | 0 | 1366 | 0 | 142 | 2790 | 40 | 0 | 77 | 62 | 614 | 516 | 6 | 0
14:00 | 3292 | 477 | 0 | 1366 | 0 | 142 | 2790 | 40 | 0 | 77 | 62 | 614 | 516 | 6 | 0
14:30 | 3246.5 | 477 | 0 | 1295.5 | 0 | 155.5 | 2609 | 40 | 0 | 83.5 | 58 | 611 | 407 | 3 | 0
15:00 | 3201 | 477 | 0 | 1225 | 0 | 169 | 2428 | 40 | 0 | 90 | 54 | 608 | 298 | 0 | 0
15:30 | 3254 | 478 | 0 | 1186.5 | 0 | 187.5 | 2399 | 40 | 0 | 102 | 49 | 577.5 | 206.5 | 0 | 0
16:00 | 3307 | 479 | 0 | 1148 | 0 | 206 | 2370 | 40 | 0 | 114 | 44 | 547 | 115 | 0 | 0
16:30 | 3321.5 | 479 | 0 | 1192 | 0 | 301.5 | 2541 | 40 | 0 | 116 | 49 | 566 | 61.5 | 1.5 | 0
17:00 | 3336 | 479 | 0 | 1236 | 0 | 397 | 2712 | 40 | 0 | 118 | 54 | 585 | 8 | 3 | 0
17:30 | 3496.5 | 479 | 0 | 1333.5 | 0 | 475 | 2893 | 40 | 0 | 91 | 56 | 666 | 4 | 11.5 | 0
18:00 | 3657 | 479 | 0 | 1431 | 0 | 553 | 3074 | 40 | 0 | 64 | 58 | 747 | 0 | 20 | 0
18:30 | 3663.5 | 478.5 | 0 | 1392 | 0 | 499.5 | 3118.5 | 40 | 0 | 56 | 55 | 752 | 0 | 28 | 0
19:00 | 3670 | 478 | 0 | 1353 | 0 | 446 | 3163 | 40 | 0 | 48 | 52 | 757 | 0 | 36 | 0
19:30 | 3663 | 478 | 0 | 1358 | 0 | 305 | 3195 | 40 | 0 | 48 | 52 | 756 | 0 | 38 | 0
20:00 | 3622 | 478 | 0 | 1361 | 0 | 283 | 3191 | 40 | 0 | 48 | 52 | 756 | 0 | 44 | 0
20:30 | 3606 | 478.5 | 0 | 1334 | 0 | 229 | 3151.5 | 40 | 0 | 48 | 52 | 756 | 0 | 40.5 | 0
21:00 | 3590 | 479 | 0 | 1307 | 0 | 175 | 3112 | 40 | 0 | 48 | 52 | 756 | 0 | 37 | 0
21:30 | 3569.5 | 478.5 | 0 | 1313 | 0 | 158.5 | 2955 | 40 | 0 | 48 | 51 | 714 | 0 | 40.5 | 0
22:00 | 3549 | 478 | 0 | 1319 | 0 | 142 | 2798 | 40 | 0 | 48 | 50 | 672 | 0 | 44 | 0
22:30 | 3445.5 | 478 | 0 | 1319 | 0 | 106.5 | 2723.5 | 40 | 0 | 40 | 50 | 649 | 0 | 43 | 0
23:00 | 3342 | 478 | 0 | 1319 | 0 | 71 | 2649 | 40 | 0 | 32 | 50 | 626 | 0 | 42 | 0
23:30 | 3335.5 | 478.5 | 0 | 1326 | 0 | 64.5 | 2570.5 | 40 | 0 | 24 | 47 | 536 | 0 | 44 | 0 |  |  | Max Temp. in Dhaka |  | 24.8°C
24:00 | 3329 | 479 | 0 | 1333 | 0 | 58 | 2492 | 40 | 0 | 16 | 44 | 446 | 0 | 46 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 203.476 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 203.476 MKWHr
Note on Y13: Author:

## Generation
2024-12-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960900
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 3 | 12 | 17 | 20 | 20 | 20 | 16 | 11 | 6 | 0 | [9 empty] | 125145
6 | Sikalbaha 225MW CCPP (Gas) | 227 | 206 | 187 | 187 | 187 | 229 | 229 | 229 | 228 | 228 | 229 | 230 | 229 | 229 | 229 | 229 | 229 | 230 |  | 228 | 229 | 229 | 228 | 229 | 228 | 228 | 5199915
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [25 empty] | 0
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [25 empty] | 0 | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [25 empty] | 0 | 28000
17 | Siddhirganj 335 MW CCPP | 280 | 240 | 240 | 180 | 180 | 250 | 250 | 315 | 335 | 270 | 270 | 270 | 335 | 335 | 280 | 240 | 280 | 335 |  | 335 | 290 | 280 | 280 | 280 | 280 | 280 | 6650139
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 10 | 15 | [7 empty] | 0 | 27600
19 | Ashuganj 195 MW PP (APSCL-United) | 78 | 16 | 8 | 8 | 8 | 45 | 45 | 75 | 102 | 102 | 102 | 185 | 184 | 127 | 128 | 88 | 145 | 184 |  | 185 | 185 | 185 | 185 | 185 | 190 | 190 | 2676364
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 608 | 608 | 608 | 606 | 608 | 608 | 665 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 |  | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 15616362
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 42 | 20 | 10 | 10 | 10 | 40 | 42 | 42 | 37 | 41 | 41 | 41 | 41 | 44 | 44 | 36 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 893952
33 | Ashuganj 225 MW CCPP | 162 | 150 | 147 | 144 | 140 | 135 | 131 | 126 | 126 | 171 | 207 | 222 | 181 | 182 | 182 | 204 | 182 | 201 |  | 182 | 196 | 181 | 181 | 183 | 181 | 223 | 4224000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 290 | 290 | 280 | 280 | 355 | 385 | 280 | 310 | 296 | 280 | 280 | 280 | 285 | 345 | 285 | 345 |  | 310 | 335 | 310 | 310 | 310 | 285 | 295 | 7613000
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 45 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 42 | 42 | 42 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 36 | 36 | 1050620
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 380 | 352 | 301 | 293 | 290 | 290 | 301 | 366 | 379 | 326 | 321 | 360 | 400 | 387 | 383 | 384 | 382 | 384 |  | 431 | 366 | 382 | 367 | 362 | 361 | 361 | 8679600
| Meghnaghat Unique power | 130 | 135 | 140 | 140 | 140 | 270 | 310 | 355 | 360 | 370 | 390 | 392 | 392 | 392 | 394 | 350 | 350 | 394 |  | 394 | 394 | 393 | 394 | 393 | 394 | 400 | 7493636
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | [25 empty] | 0 | 0
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 20 | 22 | 23 | 23 | 32 | 32 | 32 | 30 | 22 | 20 | 19 | 16 | 16 | 11 | 11 | 11 | 11 | 12 |  | 16 | 16 | 17 | 17 | 18 | 19 | 17 | 433920
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 4 | 9 | 11 | 10 | 14 | 35 | 34 | 23 | 9 | 0 | [9 empty] | 153250
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 685000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 25 | 25 | 58 | 58 | 57 | 40 | 40 | 40 | 40 | 56 | 56 | 40 | 40 | 57 | 57 |  | 58 | 57 | 57 | 57 | 40 | 40 | 40 | 1096992
48 | Shahjibazar 86 MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 796800
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 133 | 133 | 133 | 133 | 133 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3244430
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 33504
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 344400
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 240 | 240 | 240 | 236 | 230 | 230 | 230 | 235 | 235 | 338 | 336 | 316 | 400 | 316 | 316 | 372 | 342 | 372 |  | 342 | 360 | 342 | 342 | 345 | 316 | 316 | 7191600
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Tangail Palli Power Gen 22 MW | [7 empty] | 1 | [8 empty] | 0 | 12 |  | 12 | 12 | 12 | 12 |  |  | 0 | 62400
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 38 | 36 | 34 | 28 | 32 | 34 | 30 | 40 | 44 | 48 | 44 | 56 | 62 | 60 | 54 | 44 | 54 | 58 |  | 52 | 52 | 52 | 52 | 50 | 50 | 44 | 1079040
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 36 | 36 | 42 | 42 | 32 | 3 | 2 | 2 | 3 | 5 | 9 | 8 | 2 | 2 | 5 | 8 |  | 15 | 20 | 22 | 18 | 18 | 27 | 35 | 480000
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 215040
69 | Summit Ashulia | 11 | 12 | 13 | 14 | 14 | 14 | 17 | 17 | 27 | 26 | 27 | 21 | 19 | 16 | 24 | 24 | 24 | 23 |  | 23 | 23 | 23 | 24 | 24 | 24 | 23 | 493800
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [10 empty] | 7 |  |  | 7 | 7 | 15 | 15 | 15 | 15 | 178200
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 0 |  | 0 |  |  |  | 12 | 33 |  | 25 | 25 | 17 | 17 | 17 | 17 | 17 | 277200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 28 | 32 | 32 | 32 | 32 | 8 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 26 | 26 | 26 | 706000
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0
| Chowmuhani 113 MW | [15 empty] | 8 | 16 | 44 |  | 44 | 26 | 26 |  |  |  | 0 | 164640
| Manikgonj 162MW PP(MPGL) | [16 empty] | 31 | 35 |  | 35 | [5 empty] | 0 | 99360
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [12 empty] | 2 | 17 | 17 | 17 | 17 | 26 |  | 26 | 26 | 26 | 26 | 26 |  |  | 211680
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 32 | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 38 | 48 |  | 48 | 48 | 48 | 48 | 48 | 32 | 16 | 789120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | [19 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 34 | 102720
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 1 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 21844
| Jodiac Power | [15 empty] | 1 | 18 | 35 | [7 empty] | 0 | 88897
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 201312
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 12 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 26 | 26 | 829423
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | [15 empty] | 0 | 6 | 25 |  | 26 | [5 empty] | 0 | 63840
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 120 | 120 | 120 | 120 | 163 | 163 | 120 | 120 | 120 | 163 |  | 120 | 120 | 120 | 120 | 120 | 130 | 130 | 3464427
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [10 empty] | 11100
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [7 empty] | 24 | 91 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 64 | 45 | 45 | 24 | 24 | 16 | 8 | 856800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 0 |  |  |  |  | 12 | 17 | 27 | 30 | 17 | 17 | 31 | 36 | 34 | 36 | 35 | 35 |  | 35 | 34 | 34 | 34 | 34 | 22 | 0 | 530496
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 3 | 12 | [7 empty] | 0 | 20160
116 | Chandpur 200 MW (Desh energy)
117 | Ashuganj 150 MW PP (Midland) | [15 empty] | 1 | 16 | 20 |  | 20 | 5 |  |  |  |  | 0 | 81963
118 | Bibiyana-III 400 MW CCPP | 318 | 314 | 313 | 273 | 290 | 343 | 363 | 350 | 349 | 349 | 360 | 345 | 345 | 350 | 350 | 372 | 345 | 367 |  | 336 | 342 | 357 | 332 | 332 | 286 | 290 | 8517000
| Jamalpur 115 MW PP (United) | [7 empty] | 4 | 55 | 45 | 45 | 47 | 45 | 45 | 45 | 45 | 55 | 55 |  | 55 | 55 | 55 | 45 | 24 | 16 | 16 | 724800
| Anwara 300 MW PP (United) | [15 empty] | 15 | 15 | 15 | [7 empty] | 0 | 42655
| Juldah unit-2 (Acorn) | [17 empty] | 12 | [7 empty] | 0 | 20160
| Anlima Energy Ltd. | [16 empty] | 12 | 17 | [7 empty] | 0 | 45164
| Bhairob 54.5 MW | [16 empty] | 8 | 17 |  | 17 | [5 empty] | 0 | 47160
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 7 | 16 | 23 | 26 | 28 | 26 | 21 | 14 | 6 | 1 | [9 empty] | 166616
| Chandpur 115(Doreen) | [14 empty] | 9 | 16 | 23 | 34 |  | 33 | 16 | 16 |  |  |  | 0 | 148800
| Kanchan Purbachal Power Generation Ltd. | [15 empty] | 1 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 117720
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 31 | 38 | 26 | 20 | 16 | 17 | 19 | 10 | 9 | 8 | 8 | 6 | 6 | 5 | 0 | 0 | 3 | 20 |  | 36 | 38 | 44 | 37 | 44 | 42 | 46 | 466080
| Sonagazi 75 MW Solar Plant | [6 empty] | 1 | 5 | 11 | 24 | 67 | 73 | 68 | 57 | 40 | 17 | 1 | [9 empty] | 368627
| Matarbari 2*600 MW (CPGCL) | 372 | 372 | 373 | 373 | 374 | 371 | 420 | 522 | 576 | 575 | 578 | 575 | 577 | 500 | 455 | 456 | 575 | 576 |  | 575 | 577 | 575 | 576 | 577 | 577 | 575 | 12029090
| JERA Meghnaghat Power Limited | 329 | 320 | 306 | 290 | 300 | 295 | 305 | 304 | 304 | 305 | 305 | 306 | 304 | 310 | 300 | 307 | 294 | 357 |  | 314 | 314 | 316 | 305 | 318 | 318 | 318 | 7389910
| Sreepur 150 MW | [10 empty] | 10 | 37 | 45 | 53 | 58 | 82 | 80 | 16 | [8 empty] | 360000
120
121 | Eastern Zone Total | 4144 | 3942 | 3814 | 3655 | 3687 | 4120 | 4429 | 4806 | 4915 | 4936 | 5039 | 5171 | 5420 | 5202 | 4997 | 5031 | 5254 | 5773 |  | 5516 | 5344 | 5304 | 5179 | 5147 | 4951 | 4985 | 116692373
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
| Faridpur 50 MW Peaking PP | [26 empty] | 0
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 19 | 41 | 58 | 71 | 74 | 71 | 56 | 38 | 17 | 2 | [9 empty] | 451440
132 | Rampal 1320 MW (BIFPCL) | 360 | 358 | 355 | 358 | 358 | 360 | 406 | 482 | 479 | 413 | 421 | 499 | 560 | 518 | 510 | 461 | 640 | 833 |  | 855 | 875 | 870 | 854 | 606 | 508 | 450 | 12800000
133 | United Payra Power Ltd. | [15 empty] | 2 | 17 | 17 | [7 empty] | 0 | 46800
| Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 180 | 180 | 220 | 220 |  | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 5098130
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 240 | 235 | 200 | 200 | 288 | 306 | 250 | 200 | 200 | 200 | 307 |  | 307 | 307 | 307 | 307 | 250 | 200 | 150 | 5236000
137 | Barisal 1 MW Solar Plant | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3011
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 184 | 84 | 80 | 80 | 80 | 80 | 134 | 134 | 80 | 80 | 80 | 134 | 130 | 134 | 134 | 100 | 100 | 134 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 2650000
141 | Bhola 33 MW PP (Venture) | 6 | 6 | 6 | 5 | 4 | 6 | 5 | 4 | 4 | 3 | 3 | 3 | 4 | 4 | 3 | 3 | 4 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 128679
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
| Bheramara HVDC | 477 | 477 | 476 | 476 | 477 | 476 | 477 | 477 | 476 | 477 | 476 | 477 | 477 | 477 | 477 | 479 | 479 | 479 |  | 478 | 478 | 478 | 479 | 478 | 478 | 479 | 11483636
147 | Nepal
148 | Bheramara 410 MW CCPP | 290 | 200 | 200 | 200 | 200 | 200 | 260 | 254 | 260 | 260 | 260 | 308 | 330 | 330 | 330 | 330 | 329 | 327 |  | 325 | 325 | 326 | 326 | 330 | 300 | 300 | 6956352
149 | Payra 1320 MW | 270 | 260 | 250 | 250 | 260 | 290 | 310 | 430 | 450 | 400 | 400 | 470 | 540 | 540 | 450 | 440 | 480 | 540 |  | 610 | 622 | 622 | 560 | 550 | 550 | 500 | 10805818
150
151 | Barapukuria TPP Unit-1
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 155 | 158 | 160 | 160 | 160 | 160 | 155 | 152 | 152 | 150 | 152 | 147 | 147 | 152 | 153 | 153 | 157 | 158 |  | 156 | 154 | 157 | 155 | 155 | 154 | 157 | 3793000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 3 | 2 | 2 | 0 | 0 | [9 empty] | 19980
157 | Sirajganj 68 MW Solar Park | [6 empty] | 1 | 10 | 27 | 41 | 49 | 52 | 43 | 35 | 22 | 8 | 0 | [9 empty] | 296248
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 145 | 140 | 140 | 140 | 140 | 140 | 140 | 190 | 160 | 160 | 130 | 130 | 130 | 130 | 130 | 138 | 210 | 214 |  | 214 | 214 | 214 | 214 | 214 | 175 | 154 | 4140000
Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 176 | 140 | 140 | 140 | 140 | 140 | 160 | 220 | 150 | 150 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 162 |  | 218 | 220 | 220 | 220 | 197 | 161 | 156 | 4155173
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
| Sirajgonj 225MW CCPP Unit-3 (Gas) | [8 empty] | 3 | 3 | 3 | 5 | 8 | 49 | 76 | 95 | 118 | 154 |  | 189 | 220 | 220 | 220 | 220 | 220 | 180 | 1952000
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4 | 368 | 341 | 192 | 110 | 0 | [20 empty] | 0 | 1232800
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 |  | 5 | 5 | 128304
166 | Amnura 50 MW PP(Sinha)
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP
169 | Santahar 50 MW Peaking PP | [26 empty] | 0
170 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
171 | Chapainawabganj 100 MW Peaking PP | [25 empty] | 0 | 0
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
173 | Confidence Power Bogura Unit-1 113 MW | [26 empty] | 0
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence)
178 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 4 | 2 | 1 | 0 | [9 empty] | 29626
| Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 34 | 46 |  | 52 | 52 | 35 |  |  |  | 0 | 171840
| Intraco Solar 30 MW | [6 empty] | 1 | 6 | 13 | 19 | 24 | 28 | 24 | 16 | 14 | 3 | 0 | [9 empty] | 150129
178 | Adani Power Jharkhanda Ltd | 415 | 417 | 417 | 416 | 417 | 417 | 527 | 578 | 610 | 519 | 509 | 601 | 614 | 611 | 608 | 547 | 585 | 747 |  | 757 | 756 | 756 | 756 | 672 | 626 | 446 | 13676273
| Teesta Solar Limited | [6 empty] | 4 | 34 | 85 | 119 | 140 | 141 | 131 | 67 | 91 | 31 | 3 | [9 empty] | 855360
179 | Pabna Solar 100 MW | [6 empty] | 2 | 20 | 47 | 66 | 82 | 87 | 85 | 67 | 38 | 16 | 1 | [9 empty] | 523200
| Western Zone Total | 3181 | 2916 | 2751 | 2670 | 2571 | 2604 | 2960 | 3477 | 3460 | 3309 | 3321 | 3805 | 3962 | 3797 | 3593 | 3339 | 3714 | 4350 |  | 4527 | 4589 | 4571 | 4417 | 3993 | 3698 | 3298 | 86783799
[27 empty] | Total | 203476172