## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-12-26 | Thursday
|  | Date (day): | 2024-12-26 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13644.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14092 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-12-25 | 2024-12-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 338 | 336 | 350 | 400
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 350 | 450 | 450 | 0
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | under maint
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 260 | 252 | 270 | 335
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 34 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 16 | 149 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 39 | 40 | 42 |  | 38 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 22 | 25 | 25 |  | 8 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 22 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 34 | 34 | 34 | 34 | 18 |  | Fuel shoratage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 17 | 149 | 149
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 16 | 7 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 72 | 162 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 36 | 36 | 38 | 17 |  | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 280 | 400 | 270 | 270 |  | 314 | Machine problem
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| JERA Meghnaghat Power Limited |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1451 | 1751 | 2559 | 2736 | 1927 | 1195
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 7 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 25 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 190 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 226 | 226 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 85 | 105
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 57 | 75 |  | 23 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 50 | 50 |  | 52 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 36 | 100 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 11 | 10 | 5 | 10
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 26 | 20 | 50 | 58 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 45 | 50 | 100 | 200 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 50 | 108
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 17 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 612 | 530 | 612 | 612 | 612 |  | Unit-2 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 2 | 6 | 15 | 38 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 575 | 575 | 575 | 575 |  | 575 | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1475 | 1750 | 2248 | 2587 | 1060 | 1160
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 182 | 215 | 215 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 295 | 350 | 350 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 39 | 40 | 40
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 24 | 28 | 25 | 25 | 30 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 145 | 199 | 185 | 195
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 25 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 80 | 140 | 150
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 30 | 40 |  | 12 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 35 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 200 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 54 | 60 | 66 | 70
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 17 | 16 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 42 | 95 | 100 |  | 13 | Engine problem
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 46 | 50 | 92 | 23 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 32 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 910 | 1099 | 1749 | 1761 | 166 | 793
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 5 | 4 | 10 | 10 | 192 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 8 | 100 | 200
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 45 | 55 | 115
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 42 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 35 | 17 | 52
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 163 | 163 | 163 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 212 | 279 | 418.6 | 399 | 192 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 32 | 32 | 32 | 34 |  | Gas shortage
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 42 | 42 | 42 | 42 | 44 |  | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 138 | 138 | 138 | 138 |  | 93 | ST Under maint.
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 13 | 13 |  | 12 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 265 | 310 | 315 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 371 | 381 | 380 | 380
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 340 | 346 | 383 | 383
| Sylhet Area Total |  |  |  |  | 2411 | 2366 | 1376 | 1417 | 1498 | 1503 | 123 | 574
100 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 917 | 918 | 926 | 926
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 35 |  | 19 | Engine problem
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 34 | 60 |  | 49 | Engine problem
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
106 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 26 | 0 | 100 | 0
108 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
109 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 1228 | 1236 | 1234 | 1234
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
** | Nepal |  | 0 | Imported power | 40 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 2171 | 2154 | 2314 | 2255 | 456 | 478
110 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 | 110 |  | Fuel shortage
111 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 3 | 6 | 5 | 6 |  | 4 | Engine problem
112 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 68 | 68 |  | 126 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
113 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 0 | 0 | 0 | 0 |  |  | Gopalganj(N)-Payara 400 kV ckt-1 & 2 S/D
114 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 220 | 220 | 220
115 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 54 | 150
116 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 150 | 170 |  |  | Gopalganj(N)-Payara 400 kV ckt-1 & 2 S/D
117 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 248 | 345 | 497 | 614 | 110 | 130
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 26 | 32 |  | 18 | Engine problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 180 | 200 | 200 | 10
124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 188 | 200 | 200 | 20
125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 220 | 187 | 200 | 200 | 20
126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint |  | 2025-01-31
127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 24 |  | 26 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
128 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 5 | 5 |  | 6 | Engine problem
129 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 45 | 52
130 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 98 | 53 | 100
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 95 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
133 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 769 | 688 | 750 | 750
134 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 52 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 87 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1511 | 1349 | 1793 | 1854 | 221 | 522
135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 162 | 155 | 155 |  | 119 | Machine problem
137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 90 | 113
140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
141 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 115 | 115
142 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0
143 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 165 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 358 | 197 | 568 | 383 | 40 | 289 | .
| Total |  |  |  |  | 27740 | 27035 | 9712 | 10341 | 13644.6 | 14092 | 4295 | 5141
A. |  | 2024-12-25 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10341 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6910 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10341 | MW
3 | Day peak Generation : |  |  | 9712 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10100.99 | MW
4 | Evening peak Generation : |  |  | 10341 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 214.0442 | MKWHr | By Solar | 3.0457 | MKWHr
| By Gas : | 113.2032 | MKWHr |  | By Oil: | 8.8329 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 51.7056 | MKWHr |  | By Hydro: | 0.96822 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 13.9902 | MKWHr |  | By Wind: | 0.25296 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4295 | MW | Dhaka | 3885.89 | 3885.89 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 5141 | MW | Chittagong | 994 | 994 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9436 | MW | Khulna | 1150 | 1150 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 829.82 | MMCFD | **Import Adani: | Taka | 92475103.02 | Rajshahi | 961.4 | 961.4 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : |  | 316723927.046 | ii) Oil : | Taka | 88648714.64 | Comilla | 882 | 882 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 361454962.23 | Total | Taka | 859302706.936 | Mymensingh | 864 | 864 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 8649.3 | MKWHr. | Sylhet | 365 | 365 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 786 | MW (W to E) at | 18:00 | hrs | Barisal | 288.7 | 288.7 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 600 | MW at | 5:00 | hrs | Rangpur | 710 | 710 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26.7°C |  |  | Total | 10100.99 | 10100.99 |  | 0
B. |  | 2024-12-26 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 26.7°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14092 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9750 | MW
4 | Reserve(Generation end) |  |  |  | 3492 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 219.4051 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6950 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector(India) : |  |  |  |  | i) Energy | 20.8436 | MKWHr. | ii) HVDC Flow at Peak Time |  | 918 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.2019 | MKWHr. | iii) Maximum HVDC Flow : |  | 923 | MW at | 1:00 | hrs.
* Import Through HVDC C/B Interconnector(Nepal) : |  |  |  |  | i) Energy | 0 | MKWHr.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.38 |  | (b) Today: | 94.3 |  | (c) Rule Curve: |  | 103.6
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-12-25 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | JERA Meghnaghat Power Limited | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | Nepal | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Nepal | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 17 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 310 | 0 | 182 | 168 | 45 | 40 | 23 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 46 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 33 | 42 | 0 | 138 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 11 | 373 | 300 | 0 | 0 | 0 | 163 |  | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 140 | 0 | 177 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 0 | 0 | 479 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4819 | 3089 | 7908 | 2941 | 923 | 0 | 1552 | 0 | 17 | 1736 | 40 | 0 | 163 | 46 | 479 | 0 | 11 | 0 | 94.39
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 295 | 0 | 181 | 78 | 45 | 40 | 23 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 44 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 33 | 5 | 0 | 138 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 19 | 374 | 300 | 0 | 0 | 0 | 163 |  | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 156 | 0 | 0 | 140 | 0 | 179 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 0 | 0 | 459 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4607 | 2882 | 7489 | 2905 | 734 | 0 | 1385 | 0 | 0 | 1740 | 40 | 0 | 163 | 44 | 459 | 0 | 19 | 0 | 94.39
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 295 | 0 | 181 | 78 | 45 | 40 | 23 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 40 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 33 | 5 | 0 | 139 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 22 | 375 | 290 | 0 | 0 | 0 | 163 |  | 642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 140 | 0 | 184 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 427 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4514 | 2717 | 7231 | 2831 | 642 | 0 | 1371 | 0 | 0 | 1695 | 40 | 0 | 163 | 40 | 427 | 0 | 22 | 0 | 94.39
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 295 | 0 | 182 | 78 | 45 | 10 | 23 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 20 | 5 | 0 | 138 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 9 | 375 | 290 | 0 | 0 | 0 | 163 |  | 640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 140 | 0 | 186 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4373 | 2666 | 7039 | 2715 | 640 | 0 | 1324 | 0 | 0 | 1690 | 40 | 0 | 163 | 42 | 416 | 0 | 9 | 0 | 94.38
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 295 | 0 | 181 | 78 | 45 | 10 | 24 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 20 | 5 | 0 | 138 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 374 | 290 | 0 | 0 | 0 | 163 |  | 640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 157 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 718 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4327 | 2583 | 6910 | 2658 | 640 | 0 | 1328 | 0 | 0 | 1622 | 40 | 0 | 163 | 42 | 417 | 0 | 0 | 0 | 94.38
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 335 | 0 | 205 | 78 | 45 | 20 | 22 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 20 | 5 | 0 | 138 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 374 | 330 | 0 | 0 | 0 | 163 |  | 640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 157 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4513 | 2637 | 7150 | 2766 | 640 | 0 | 1446 | 0 | 0 | 1634 | 40 | 0 | 163 | 42 | 419 | 0 | 0 | 0 | 94.38
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 17 | 26 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 365 | 0 | 222 | 125 | 50 | 37 | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 40 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 20 | 5 | 0 | 138 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 366 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 375 | 3 | 374 | 330 | 0 | 2 | 0 | 163 |  | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 144 | 0 | 145 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 724 | 0 | 0 | 421 | 4 | 0 | 0 | 0 | 1 | 0 |  | 4926 | 2763 | 7689 | 3085 | 734 | 0 | 1524 | 0 | 19 | 1633 | 40 | 0 | 179 | 40 | 421 | 11 | 3 | 0 | 94.37
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 17 | 24 | 25 | 0 | 40 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 360 | 0 | 208 | 190 | 50 | 37 | 20 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | 9 | 0 | 0 | 1 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 385 | 0 | 34 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 7 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 464 | 8 | 500 | 330 | 0 | 12 | 0 | 163 |  | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 151 | 0 | 0 | 214 | 0 | 195 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 802 | 5 | 0 | 415 | 37 | 0 | 0 | 7 | 14 | 0 |  | 5307 | 3241 | 8548 | 3227 | 923 | 0 | 1629 | 0 | 59 | 1917 | 40 | 0 | 179 | 44 | 415 | 107 | 8 | 0 | 94.37
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 17 | 24 | 25 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 320 | 0 | 186 | 197 | 50 | 37 | 20 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 5 | 0 | 0 | 1 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 342 | 0 | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 25 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 500 | 11 | 500 | 330 | 0 | 17 | 0 | 163 |  | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 153 | 0 | 0 | 214 | 0 | 220 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 220 | 0 | 0 | 1 | 12 | 0 | 0 | 0 | 1002 | 14 | 0 | 520 | 91 | 0 | 0 | 9 | 49 | 0 |  | 5234 | 3725 | 8959 | 3135 | 923 | 0 | 1651 | 0 | 65 | 2155 | 40 | 0 | 179 | 42 | 520 | 238 | 11 | 0 | 94.37
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 22 | 24 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 330 | 0 | 193 | 108 | 45 | 39 | 22 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 44 | 5 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 20 | 42 | 0 | 138 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 342 | 0 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 35 | 0 | 0 | 0 | 0 | 9 | 0 | 11 | 0 | 0 | 0 | 502 | 2 | 504 | 280 | 0 | 24 | 0 | 163 |  | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 214 | 0 | 160 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 180 | 0 | 0 | 3 | 48 | 0 | 0 | 0 | 1010 | 21 | 0 | 513 | 128 | 0 | 0 | 43 | 68 | 0 |  | 5096 | 3767 | 8863 | 3080 | 923 | 0 | 1416 | 0 | 97 | 2174 | 40 | 0 | 179 | 44 | 513 | 395 | 2 | 0 | 94.36
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 22 | 24 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 0 | 181 | 108 | 45 | 39 | 24 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 48 | 5 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 20 | 42 | 0 | 138 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 0 | 0 | 0 | 335 | 0 | 52 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 41 | 0 | 0 | 0 | 0 | 28 | 0 | 17 | 0 | 0 | 0 | 555 | 1 | 577 | 280 | 0 | 54 | 0 | 163 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 160 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 180 | 0 | 0 | 4 | 49 | 0 | 0 | 0 | 1010 | 26 | 0 | 615 | 152 | 0 | 0 | 50 | 82 | 0 |  | 5235 | 3916 | 9151 | 3022 | 917 | 0 | 1419 | 0 | 104 | 2302 | 40 | 0 | 179 | 48 | 615 | 504 | 1 | 0 | 94.36
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 22 | 24 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 340 | 0 | 200 | 145 | 40 | 39 | 24 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 54 | 5 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 20 | 42 | 0 | 138 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 0 | 371 | 0 | 52 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 42 | 0 | 0 | 0 | 0 | 29 | 0 | 17 | 0 | 0 | 0 | 612 | 2 | 575 | 280 | 0 | 32 | 0 | 163 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 160 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 4 | 26 | 0 | 0 | 0 | 1228 | 28 | 0 | 769 | 165 | 0 | 0 | 52 | 87 | 0 |  | 5424 | 4288 | 9712 | 3125 | 917 | 0 | 1450 | 0 | 120 | 2575 | 40 | 0 | 179 | 54 | 769 | 481 | 2 | 0 | 94.36
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 22 | 24 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 11 | 0 | 0 | 0 | 310 | 0 | 183 | 194 | 42 | 39 | 21 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 64 | 5 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 163 | 0 | 30 | 42 | 0 | 138 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 0 | 0 | 0 | 358 | 8 | 52 | 0 | 2 | 15 | 17 | 0 | 0 | 4 | 0 | 340 | 0 | 37 | 10 | 5 | 0 | 0 | 28 | 0 | 28 | 0 | 0 | 0 | 612 | 1 | 575 | 330 | 0 | 30 | 0 | 163 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 200 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 220 | 0 | 0 | 4 | 59 | 0 | 0 | 0 | 1246 | 26 | 0 | 760 | 158 | 0 | 0 | 50 | 87 | 0 |  | 5628 | 4399 | 10027 | 3120 | 917 | 0 | 1653 | 0 | 191 | 2593 | 40 | 0 | 195 | 64 | 760 | 493 | 1 | 0 | 94.35
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 22 | 24 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 315 | 0 | 198 | 195 | 40 | 39 | 24 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 60 | 4 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 30 | 42 | 0 | 138 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 340 | 8 | 17 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 31 | 0 | 0 | 0 | 0 | 15 | 0 | 30 | 0 | 0 | 0 | 558 | 1 | 575 | 400 | 0 | 39 | 0 | 163 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 180 | 0 | 218 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 180 | 0 | 0 | 3 | 35 | 0 | 0 | 0 | 1060 | 21 | 0 | 756 | 131 | 0 | 0 | 40 | 69 | 0 |  | 5429 | 4027 | 9456 | 3027 | 917 | 0 | 1635 | 0 | 89 | 2353 | 40 | 0 | 179 | 60 | 756 | 399 | 1 | 0 | 94.36
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 257 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 22 | 24 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 285 | 0 | 181 | 195 | 40 | 39 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 4 | 0 | 0 | 1 | 30 | 0 | 0 | 5 | 120 | 0 | 31 | 42 | 0 | 138 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 340 | 8 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 20 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 500 | 4 | 560 | 400 | 0 | 43 | 0 | 163 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 185 | 0 | 190 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 180 | 0 | 0 | 2 | 52 | 0 | 0 | 0 | 1056 | 15 | 0 | 749 | 89 | 0 | 0 | 24 | 44 | 0 |  | 5262 | 3901 | 9163 | 2941 | 918 | 0 | 1635 | 0 | 59 | 2276 | 40 | 0 | 179 | 48 | 749 | 314 | 4 | 0 | 94.35
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 22 | 24 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 325 | 0 | 203 | 197 | 40 | 39 | 24 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 50 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 31 | 42 | 0 | 138 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 341 | 8 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 9 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 450 | 5 | 505 | 400 | 0 | 17 | 0 | 163 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 159 | 0 | 0 | 214 | 0 | 171 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 220 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 968 | 6 | 0 | 604 | 36 | 0 | 0 | 9 | 14 | 0 |  | 5309 | 3570 | 8879 | 3071 | 917 | 0 | 1733 | 0 | 76 | 2082 | 40 | 0 | 195 | 50 | 604 | 106 | 5 | 0 | 94.34
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 3 | 17 | 0 | 19 | 22 | 22 | 22 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 5 | 17 | 0 | 0 | 0 | 4 | 0 | 11 | 0 | 0 | 0 | 280 | 0 | 182 | 199 | 40 | 39 | 27 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 56 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 33 | 42 | 0 | 138 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 9 | 0 | 24 | 6 | 10 | 381 | 19 | 52 | 9 | 0 | 49 | 54 | 5 | 0 | 4 | 36 | 320 | 4 | 0 | 54 | 18 | 0 | 10 | 1 | 4 | 25 | 0 | 17 | 0 | 452 | 2 | 502 | 320 | 0 | 1 | 0 | 163 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 162 | 0 | 0 | 170 | 0 | 164 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 30 | 0 | 1 | 34 | 0 | 0 | 1063 | 1 | 0 | 579 | 4 | 0 | 0 | 1 | 2 | 0 |  | 5542 | 3547 | 9089 | 2954 | 917 | 0 | 1570 | 0 | 552 | 2179 | 40 | 0 | 229 | 56 | 579 | 11 | 2 | 0 | 94.34
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 19 | 20 | 22 | 22 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 24 | 24 | 17 | 0 | 26 | 25 | 0 | 10 | 0 | 0 | 0 | 295 | 0 | 182 | 199 | 35 | 39 | 28 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 60 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 265 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 36 | 17 | 80 | 381 | 45 | 70 | 17 | 0 | 45 | 54 | 17 | 0 | 42 | 50 | 346 | 16 | 0 | 72 | 35 | 0 | 35 | 0 | 46 | 36 | 0 | 17 | 0 | 530 | 6 | 575 | 400 | 0 | 0 | 0 | 163 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 162 | 0 | 0 | 180 | 0 | 188 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 54 | 0 | 0 | 35 | 0 | 0 | 1236 | 0 | 0 | 688 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6296 | 4045 | 10341 | 3039 | 918 | 0 | 1739 | 0 | 1013 | 2503 | 40 | 0 | 335 | 60 | 688 | 0 | 6 | 0 | 94.34
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 22 | 22 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 24 | 0 | 17 | 0 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 335 | 0 | 229 | 199 | 35 | 39 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 60 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 33 | 42 | 0 | 138 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 0 | 45 | 381 | 45 | 52 | 0 | 0 | 45 | 54 | 0 | 0 | 9 | 12 | 400 | 0 | 0 | 17 | 35 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 609 | 16 | 575 | 400 | 0 | 0 | 0 | 163 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 162 | 0 | 0 | 214 | 0 | 220 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240 | 0 | 0 | 747 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6085 | 4120 | 10205 | 3279 | 920 | 0 | 1796 | 0 | 467 | 2586 | 40 | 0 | 294 | 60 | 747 | 0 | 16 | 0 | 94.33
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 22 | 22 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 23 | 0 | 17 | 0 | 0 | 26 | 0 | 7 | 0 | 0 | 0 | 315 | 0 | 204 | 199 | 35 | 40 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 52 | 6 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 10 | 383 | 45 | 52 | 0 | 0 | 15 | 54 | 0 | 0 | 9 | 0 | 400 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 609 | 18 | 575 | 400 | 0 | 0 | 0 | 163 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 220 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5990 | 4074 | 10064 | 3233 | 921 | 0 | 1857 | 0 | 364 | 2582 | 40 | 0 | 238 | 52 | 759 | 0 | 18 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 22 | 22 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 23 | 0 | 17 | 0 | 0 | 26 | 0 | 10 | 0 | 0 | 0 | 315 | 0 | 181 | 199 | 35 | 40 | 29 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 54 | 6 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 10 | 383 | 45 | 52 | 0 | 0 | 15 | 54 | 0 | 0 | 9 | 0 | 400 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 610 | 33 | 575 | 400 | 0 | 0 | 0 | 163 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 159 | 0 | 0 | 214 | 0 | 216 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5963 | 4070 | 10033 | 3210 | 920 | 0 | 1831 | 0 | 364 | 2584 | 40 | 0 | 238 | 54 | 759 | 0 | 33 | 0 | 94.33
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 22 | 22 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 0 | 26 | 0 | 19 | 0 | 0 | 0 | 310 | 0 | 182 | 199 | 35 | 40 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 52 | 8 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 33 | 42 | 0 | 138 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 24 | 35 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 610 | 26 | 575 | 400 | 0 | 0 | 0 | 163 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 214 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 0 | 13 | 758 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5732 | 4028 | 9760 | 3143 | 921 | 0 | 1834 | 0 | 221 | 2586 | 40 | 0 | 179 | 52 | 758 | 0 | 26 | 0 | 94.33
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 22 | 24 | 16 | 0 | 40 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 280 | 0 | 180 | 199 | 35 | 40 | 29 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 56 | 9 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 33 | 42 | 0 | 138 | 0 | 0 | 0 | 260 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 24 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 559 | 28 | 523 | 350 | 0 | 0 | 0 | 163 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 155 | 0 | 0 | 214 | 0 | 220 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1094 | 0 | 55 | 731 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5373 | 3910 | 9283 | 3105 | 921 | 0 | 1762 | 0 | 75 | 2386 | 40 | 0 | 179 | 56 | 731 | 0 | 28 | 0 | 94.32
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 22 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 300 | 0 | 188 | 199 | 35 | 40 | 29 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 50 | 9 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 40 | 525 | 350 | 0 | 0 | 0 | 163 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 194 | 0 | 194 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1012 | 0 | 105 | 564 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5297 | 3648 | 8945 | 3054 | 921 | 0 | 1794 | 0 | 51 | 2252 | 40 | 0 | 179 | 50 | 564 | 0 | 40 | 0 | 94.32
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 300 | 0 | 182 | 130 | 37 | 40 | 28 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 46 | 8 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 33 | 5 | 0 | 138 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 32 | 454 | 350 | 0 | 0 | 0 | 163 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 154 | 0 | 0 | 170 | 0 | 153 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912 | 0 | 150 | 526 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4958 | 3432 | 8390 | 2932 | 920 | 0 | 1632 | 0 | 17 | 2082 | 40 | 0 | 163 | 46 | 526 | 0 | 32 | 0 | 94.32
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8067600 | 0 |  | 0 | 8278000 | 0 | 0 | 0 | 0 | 6134730 | 0 | 0 | 0 | 22608 | 331200 | 0 | 0 | 0 | 0 | 68400 | 28889 | 45660 | 0 | 462000 | 520200 | 520920 | 584000 | 515040 | 0 | 968220 | 0 | 0 | 0 | 0 | 5144901 | 0 | 0 | 0 |  | 111120 | 32046 | 49429 | 0 | 47040 | 132000 | 0 | 346560 | 0 | 0 | 0 | 7796600 | 0 | 4623000 | 3830545 | 988180 | 878328 | 588960 | 0 | 972712 | 0 | 0 | 18072 | 0 | 0 | 0 | 382940 | 1201920 | 97920 | 0 | 0 | 11100 | 715000 | 0 | 0 | 201168 | 3607445 | 0 | 692928 | 769920 | 0 | 3319660 | 0 | 0 | 0 | 7089500 | 356784 | 58032 | 0 | 0 | 0 | 0 | 24000 | 0 | 113904 | 57645 | 59520 | 32640 | 197381 | 8865000 | 259200 | 779520 | 41818 | 12602 | 173127 | 292070 | 35127 | 0 | 130200 | 92160 | 8239300 | 22080 | 254340 | 182880 | 154309 | 0 | 61920 | 145426 | 82560 | 289080 | 0 | 31782 | 0 | 11809089 | 252960 | 11818181 | 8214545 | 0 | 249445 | 0 | 3926400 |  | 20843636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1438000 | 133180 | 0 | 0 | 0 | 0 | 0 | 0 | 223728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146448 | 0 | 0 | 3875000 | 0 | 0 | 4531000 | 0 | 4701964 | 0 | 0 | 0 | 4738445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29751 | 0 | 0 | 5166760 | 0 | 152400 | 27180 | 277920 | 73564 | 0 | 0 | 24007280 | 164309 | 196000 | 13990182 | 990000 | 0 | 2019 | 306752 | 517170 | 0 |  | 127511488 | 86532688 | 214044176 | 74003880 | 20843636 | 0 | 39199295 | 0 | 4238289 | 51705550 | 968220 | 0 | 4594585 | 1201920 | 13990182 | 3045659 | 252960 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23234688 | 0 |  | 0 | 26324040 | 0 | 0 | 0 | 0 | 18710926.5 | 0 | 0 | 0 | 405813.6 | 6431904 | 0 | 0 | 0 | 0 | 1248984 | 455290.64 | 835121.4 | 0 | 346500 | 0 | 0 | 0 | 9224366.4 | 0 | 0 | 0 | 0 | 0 | 0 | 16412234.19 | 0 | 0 | 0 |  | 1954600.8 | 564330.06 | 885273.39 | 0 | 920572.8 | 2172720 | 0 | 0 | 0 | 0 | 0 | 21752514 | 0 | 15348360 | 12832325.75 | 3191821.4 | 2959965.36 | 2579644.8 | 0 | 3900575.12 | 0 | 0 | 326380.32 | 0 | 0 | 0 | 287205 | 7884595.2 | 304531.2 | 0 | 0 | 0 | 2788500 | 0 | 0 | 915314.4 | 12337461.9 | 0 | 3845750.4 | 4018982.4 | 0 | 9261851.4 | 0 | 0 | 0 | 21906555 | 267588 | 44104.32 | 0 | 0 | 0 | 0 | 461040 | 0 | 2005849.44 | 0 | 1060051.2 | 566304 | 3272576.98 | 23492250 | 4940352 | 14623795.2 | 750214.92 | 0 | 2830626.45 | 5677840.8 | 630178.38 | 0 | 2527182 | 1641369.6 | 21916538 | 376905.6 | 0 | 3344875.2 | 2589305.02 | 0 | 1106510.4 | 0 | 1487731.2 | 4897015.2 | 0 | 447490.56 | 0 | 82309350.33 | 0 | 69727267.9 | 0 | 0 | 0 | 0 | 0 |  | 58570617.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4544080 | 631273.2 | 0 | 0 | 0 | 0 | 0 | 0 | 3760867.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110861.136 | 0 | 0 | 32705000 | 0 | 0 | 14952300 | 0 | 15657540.12 | 0 | 0 | 0 | 15779021.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16068623.6 | 0 | 2948940 | 0 | 0 | 1276335.4 | 0 | 0 | 175253144 | 0 | 1460200 | 92475103.02 | 0 | 0 | 0 | 0 | 0 | 0 |  | 489564012.13 | 436193907.166 | 925757919.296 | 215209130.876 | 58570617.16 | 0 | 101514796.17 | 0 | 76558848.95 | 361454962.23 | 0 | 0 | 12089865.69 | 7884595.2 | 92475103.02 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 22 | 24 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 340 | 0 | 200 | 145 | 40 | 39 | 24 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 54 | 5 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 20 | 42 | 0 | 138 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 0 | 371 | 0 | 52 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 42 | 0 | 0 | 0 | 0 | 29 | 0 | 17 | 0 | 0 | 0 | 612 | 2 | 575 | 280 | 0 | 32 | 0 | 163 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 160 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 4 | 26 | 0 | 0 | 0 | 1228 | 28 | 0 | 769 | 165 | 0 | 0 | 52 | 87 | 0 |  | 9712 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 19 | 20 | 22 | 22 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 24 | 24 | 17 | 0 | 26 | 25 | 0 | 10 | 0 | 0 | 0 | 295 | 0 | 182 | 199 | 35 | 39 | 28 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 60 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 265 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 36 | 17 | 80 | 381 | 45 | 70 | 17 | 0 | 45 | 54 | 17 | 0 | 42 | 50 | 346 | 16 | 0 | 72 | 35 | 0 | 35 | 0 | 46 | 36 | 0 | 17 | 0 | 530 | 6 | 575 | 400 | 0 | 0 | 0 | 163 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 162 | 0 | 0 | 180 | 0 | 188 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 54 | 0 | 0 | 35 | 0 | 0 | 1236 | 0 | 0 | 688 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10341 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 22 | 25 | 33 | 34 | 0 | 40 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 22 | 75 | 50 | 0 | 50 | 50 | 0 | 10 | 0 | 0 |  | 350 | 0 | 215 | 195 | 50 | 40 | 25 | 0 | 51 | 0 | 40 | 52 | 0 | 0 |  | 17 | 70 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 150 | 380 | 115 | 105 | 105 | 0 | 100 | 54 | 110 | 114 | 100 | 100 | 383 | 17 | 0 | 162 | 108 | 0 | 52 | 0 | 92 | 38 | 0 | 160 | 0 | 612 | 38 | 575 | 270 | 0 |  | 0 |  |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 68 | 6 | 0 | 0 | 0 | 0 | 40 | 25 | 100 | 0 | 0 | 32 | 52 | 24 | 0 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 200 | 0 | 200 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 0 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 1234 | 0 | 170 | 750 | 0 | 0 |  |  |  | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 |  | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 34 | 55 | 55 | 0 | 18 | 22 | 25 | 33 | 34 | 0 | 40 | 0 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 22 | 57 | 50 | 0 | 20 | 50 | 0 | 5 | 0 | 0 | 0 | 350 | 0 | 215 | 185 | 50 | 40 | 25 | 0 | 51 | 0 | 30 | 52 | 0 | 0 |  | 16 | 66 | 10 | 0 | 0 | 1.6 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 300 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 200 | 140 | 380 | 55 | 50 | 85 | 5 | 50 | 54 | 110 | 114 | 95 | 100 | 383 | 7 | 50 | 162 | 50 | 0 | 17 | 35 | 50 | 36 | 0 | 17 | 0 | 612 | 15 | 575 | 270 | 0 | 70 | 0 | 163 |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 68 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 26 | 45 | 24 | 0 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 200 | 0 | 200 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 95 | 0 | 90 | 0 | 8 | 113 | 0 | 220 |  | 54 | 6 | 100 | 115 | 0 | 0 | 1234 | 30 | 150 | 750 | 170 | 0 |  | 29 | 47 | 0 |  |  |  |  | gas | hvdc |  | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 17 | 26 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 370 | 0 | 217 | 185 | 40 | 36 | 26 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 8 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 380 | 0 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 9 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 460 | 15 | 529 | 276 | 0 | 20 | 0 | 163 | 0 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 157 | 0 | 0 | 176 | 0 | 170 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 220 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 962 | 6 | 150 | 415 | 37 | 0 | 0 | 10 | 18 | 0 | 0 |  |  |  | 113203175 | 20843636 |  | 0 | 51705550 | 8832874 | 1201920 | 3045659 | 252960 | 968220 |  |  |  | 200053994
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [9 empty] | 399427 | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 |  | 299798 | [7 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [14 empty] | 499227 |  | 499229 |  |  | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [11 empty] | 113.2032 | 20.8436 |  | 0 | 51.7056 | 8.8329 | 1.2019 | 3.0457 | 0.25296 | 0.96822
| Minimum Generation |  | 6910 | 5:00
| Highest Generation |  | 10341 | 18:00 | [129 empty] | 0 | [77 empty] | 200.054
| Day Peak Generation |  | 9712 | 12:00
| Evening Peak Generation |  | 10341 | 18:00 | [207 empty] | 202699852
| HVDC Max Flow |  | 923 | 1:00 | [207 empty] | 202.6999
| HVDC EvPeak Flow |  | 918 | 18:00
| Load factor L.F |  | 86.24% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-12-26
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-12-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9712 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6950
Evening Peak Generation : |  |  | 10341 | MW Hour : | 18:00 | Available Max Generation : |  | 14092
E.P. Demand (at gen end) : |  |  | 10341 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10600
Maximum Generation : |  |  | 10341 | MW Hour : | 18:00 | Reserve(Generation end) |  | 3492
Total Gen. (MKWH) : |  |  | 214.0442 | System Load Factor : | 86.24% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 600 | MW at | 5:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-12-26
Actual : |  | 94.3 | Ft.(MSL) , | Rule curve : | 103.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 829.82 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 316723927.046 | Adani : | 92475103.02
|  |  | Coal : | 361454962.23 | Oil: | 88648714.64 | Total: | 859302706.936
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3596.4247 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 982.3952 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1374.3707 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1192.9441 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 982.4152 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 729.8039 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 410.003 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 340.8433 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 666.6492 |  |  | 0 | 0%
Total |  | 0 |  | 10275.8492 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:15 | 16:35 | Natore-Rajshahi 132kV Ckt-2 Scheduled S/D from Rajshahi 132/33kV end Due to Annual maintenance work
and from Natore 132/33kV end Due to ALDC.
08:16 | 13:14 | Chapai 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to SF6 gas pressure low maintenance work.
08:17 | 13:12 | Chapai 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to SF6 gas pressure low maintenance work.
08:31 | 14:34 | Bakulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Khulshi 132/33kV end Due to Annual maintenance. and from
Bakulia 132/33kV end Due to Annual Maintenance(Dead Line Checking).
08:53 |  | Bheramara HVDC - Rajshahi 230 kv L-1&2 were shut down due to Annual Maintenance.
09:10 | 18:05 | HVDC Bheramera- Rajshahi 230kV Ckt-1 Scheduled S/D from BIPTC end Due to Shutdown is taken from
Ishurdi end for annual maintenance.
| 09:16 | Ghorashal 230kV S/S TARFO-2 LT is restored.
10:10 | 14:00 | Mahasthangar-Palashbari 132kV Ckt-1 Scheduled S/D from Mahasthangarh 132/33kV end Due to Project Work
and from Palashbari 132/33kV end Due to project work.
10:11 | 18:04 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Scheduled S/D from BIPTC end Due to Shutdown is taken from
Ishurdi end for annual maintenance.
10:30 | 13:42 | Lalmonirhat 132/33kV S/S Transformer T-1 425T LT Scheduled S/D Due to T1 x-former s/d for annual maintenance.
10:30 | 13:42 | Lalmonirhat 132/33kV S/S Transformer T-1 425T HT Scheduled S/D Due to T1 x former s/d for annual maintenance.
| 11:42 | Kabirpur 132/33kV S/S Reserve bus is restored.
12:04 | 13:48 | Tongi 230/132/33kV S/S T-01 HT Forced S/D Due to Tap changer oil refills.
| 12:22 | Kabirpur 132/33kV S/S XFR, T-2 LT is restored.
| 12:22 | Kabirpur 132/33kV S/S XFR, T-2 HT is restored.
17:02 | 17:34 | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to 33kV jhalokathi feeder loop damage. | [5 empty] | 30 MW load interrup.
17:03 | 17:33 | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to 33kV Jhalokathi feeder loop damage.
| 17:38 | Rangpur-Saidpur 132kV Ckt-2 is restored.
| 18:04 | Maniknagar-Siddhirganj 230kV Ckt-1 is restored.
| 19:02 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) HT is restored.
| 19:07 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) LT is restored.
| 20:44 | Barishal Electric 307 MW PP was sync.
06:59 |  | Baroaulia-Hathazari 132 kV Ckt-2 Forced S/D from Baroaulia 132/33kV end Due to CT Change.
07:20 |  | Barishal-Barishal(N) 132 kV Ckt-2 Scheduled S/D from Barishal 230/132kV end Due to Annual Maintenance
and from Barishal 132/33kV end Due to Annual maintenance.
07:22 |  | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to Annual maintenance.
07:22 |  | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to Annual maintenance.
07:30 |  | Ramganj 132/33kV S/S Ramgonj- Desh Energy Ckt-01 Scheduled S/D Due to Ramgonj- Desh Energy Ckt -01
shutdown due to Annual Maintenance.
07:30 |  | Ramganj 132/33kV S/S Ramgonj- Desh Energy Ckt-01 Scheduled S/D Due to Ramgonj- Desh Energy Ckt -01
shutdown due to Annual Maintenance.
|  | Sub-Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
|  | Network Operation Division |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-12-25
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 336 | 8067600 | DP High
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8278000 | Frequency control
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 252 | 6134730 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 22608 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 68400 | Low demand
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 331200 | Low demand
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 28889 | Low demand
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 45660 | Low demand
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 39 | 982200 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 520920 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 584000 | Engine problem
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 34 | 515040 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 113904 | Low demand
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 779520 | Low demand
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 16 | 22080 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 182880 | Low demand
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 145426
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 289080 | Low demand
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 400 | 8214545 | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 1751 | 35326682
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 57645
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 132000 | Low demand
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 968220 | Low water level
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 226 | 5144901
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 41818 | Low demand
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 32046 | Low demand
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 49429 | Low demand
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 59520 | Low demand
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 346560
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 26 | 47040 | Low demand
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 12602
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 173127 | Low demand
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 292070
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 35127 | Low demand
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 92160 | Fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 154309 | Low demand
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 31782 | Low demand
55 | SS Power I |  | IPP | 2*612 | 1224 | 530 | 11809089 | Unit-2 Under maint
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 6 | 252960
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 575 | 11818181 | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1750 | 31550586
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4623000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7796600 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 878328
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 28 | 588960 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 199 | 3830545
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 972712
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 80 | 197381 | Low demand
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 988180 | Machine problem.
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 32640 | Low demand
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 60 | 1201920
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 18072 | Low demand
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 382940 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 42 | 130200 | Low demand
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 46 | 82560 | Low demand
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 249445
| Cumilla Area Total |  |  |  | 2917 | 1099 | 21973483
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 4 | 97920 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11100
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 8 | 24000 | Low demand
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 45 | 259200 | Low demand
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 254340
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 111120
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 61920 | Low demand
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 163 | 3926400
| Mymensingh Area Total |  |  |  | 646 | 279 | 4746000
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3607445
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 0 | 0 | 0 | Contact expired
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 201168 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 58032 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 692928 | Gas shortage
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 42 | 769920 | Gas shortage
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 138 | 3319660 | ST under maint
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 356784 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 265 | 7089500 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 381 | 8865000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 346 | 8239300 | FGMO
| Sylhet Area Total |  |  |  | 2366 | 1417 | 33914737
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 918 | 20843636
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | under maint
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 277920
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 1236 | 24007280
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Nepal |  | Imported power | 40 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 2154 | 45128836
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 6 | 133180 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1438000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 0 | 0 | Development work.
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5166760
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 152400 | Low demand
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 196000 | Development work.
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 2019
| Barisal Area Total |  |  |  | 2236 | 345 | 7088359
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | NENP
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 180 | 4531000 | Gas shortage
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4701964
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 187 | 4738445 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 146448 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 223728 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 27180
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 688 | 13990182
135 | Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 306752
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 517170
| Rajshahi Area Total |  |  |  | 3449 | 1349 | 29182869
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 162 | 3875000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | Reserve
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29751
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 73564 | Low demand
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 164309
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 990000
| Rangpur Area Total |  |  |  | 950 | 197 | 5132624
| Total |  |  |  | 27035 | 10341 | 214044176
| Eastern Grid Total |  |  |  | 16701 | 6296 | 127511488
| Western Grid Total |  |  |  | 10334 | 4045 | 86532688
| National Grid Total |  |  |  | 27035 | 10341 | 214044176
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-12-2024
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7112.47 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3160.7 | MW
i) Dhaka area |  |  | 4003.87 |  | MW | i) Khulna area |  |  |  | 1160.1 | MW
ii) Chattogram area |  |  | 1013.6 |  | MW | ii) Barishal area |  |  |  | 304 | MW
iii) Cumilla area |  |  | 855 |  | MW | iii) Rajshahi area |  |  |  | 970.6 | MW
iv) Mymensingh area |  |  | 873 |  | MW | iv) Rangpur area |  |  |  | 726 | MW
v) Sylhet area |  |  | 367 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10273.17 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 80 | 18:00 | 133 | Rahim | 47 | 12:00
2 | AKSML | 146.5 | 15:00 | 68 | Jashore | 95 | 13:00 | 134 | Rajbari | 54 | 18:00
3 | Aftabnagar | 22 | 12:00 | 69 | Jhenaidah | 90 | 18:00 | 135 | Rajendrapur | 90 | 10:00
4 | Agargaon | 67 | 13:00 | 70 | Joydebpur | 124 | 18:30 | 136 | Rajshahi | 86 | 21:00
5 | Agrabad | 62 | 18:30 | 71 | Joypurhat | 39 | 08:00 | 137 | Rajshahi-230 | 40 | 13:00
6 | Amnura | 44 | 09:00 | 72 | Juldah | 8 | 12:00 | 138 | Ramganj | 74 | 18:00
7 | Ashuganj | 75 | 18:30 | 73 | KSRM | 42.5 | 18:30 | 139 | Rampur | 25 | 18:30
8 | BSRM | 145 | 00:00 | 74 | Kabirpur | 186 | 18:00 | 140 | Rangamati | 12 | 18:00
9 | Bagerhat | 62 | 18:00 | 75 | Kachua | 46 | 20:00 | 141 | Rangpur | 104 | 18:00
10 | Bakulia | 63 | 13:00 | 76 | Kallyanpur | 78 | 12:00 | 142 | Ruppur | 4.6 | 16:00
11 | Banani | 31.6 | 13:00 | 77 | Kalurghat | 24 | 10:00 | 143 | SSM | 11 | 02:00
12 | Bangabhaban | 4 | 13:00 | 78 | Kamrangirchar | 51 | 17:00 | 144 | Saidpur | 90 | 18:30
13 | Barapukuria | 41 | 18:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 82 | 18:00
14 | Barguna | 14 | 21:00 | 80 | Kazla | 82 | 12:00 | 146 | Satmasjid | 74 | 13:00
15 | Barishal | 62 | 13:00 | 81 | Keranigonj | 67 | 13:00 | 147 | Savar | 148 | 16:00
16 | Barishal-230 | 74 | 18:00 | 82 | Khagrachori | 24 | 18:00 | 148 | SevenRings | 14.11 | 04:00
17 | Baroaulia | 54 | 10:00 | 83 | Khulna | 70 | 13:00 | 149 | ShahCement | 24 | 18:00
18 | Baroirhat | 42 | 18:00 | 84 | Khulshi | 120 | 00:00 | 150 | Shahjadpur | 46 | 19:00
19 | Bashundhara | 113 | 13:00 | 85 | Kishoreganj | 110 | 20:00 | 151 | Shahjibazar | 76 | 18:00
20 | BashundharaCement | 11 | 02:00 | 86 | Kodda | 257 | 18:00 | 152 | Shahmirpur | 32 | 18:00
21 | Beanibazar | 42 | 18:00 | 87 | Kulaura | 28 | 18:00 | 153 | Shariatpur | 50 | 19:30
22 | Benapole | 40 | 18:00 | 88 | Kurigram | 44 | 18:00 | 154 | Sherpur | 102 | 18:00
23 | Bhaluka | 116 | 18:00 | 89 | Kushtia | 88 | 18:30 | 155 | Shikalbaha | 21 | 10:00
24 | Bhandaria | 36 | 21:00 | 90 | Lalbag | 65 | 13:00 | 156 | Shitalakhya | 63.7 | 13:00
25 | Bhangura | 22 | 18:00 | 91 | Lalmonirhat | 42 | 18:00 | 157 | Sholosohor | 23 | 12:00
26 | Bheramara(GK) | 40 | 18:00 | 92 | MI_Cement | 17.9 | 00:00 | 158 | Shyampur | 148 | 13:00
27 | Bhulta | 237 | 10:00 | 93 | Madanganj | 29 | 13:00 | 159 | Siddhirganj | 91 | 13:00
28 | Bog-Sherpur | 52 | 18:00 | 94 | Madaripur | 64 | 18:00 | 160 | Sirajganj | 74 | 19:00
29 | Bogura | 111 | 18:30 | 95 | Madartek | 59.78 | 13:00 | 161 | Sonargaon | 70 | 16:00
30 | Borhanuddin | 53 | 20:00 | 96 | Madunaghat | 33 | 18:00 | 162 | Sreemongol | 43 | 18:00
31 | Brahmanbaria | 104 | 19:30 | 97 | Magura | 43 | 18:00 | 163 | Sreepur | 60 | 15:00
32 | Cantonment | 74 | 13:00 | 98 | Mahasthangarh | 52 | 18:00 | 164 | Srinagar | 28.2 | 21:00
33 | Chandpur | 44 | 18:00 | 99 | Manikganj | 95 | 19:00 | 165 | Sunamganj | 34 | 18:00
34 | Chandraghona | 25 | 18:00 | 100 | Maniknagar | 40 | 13:00 | 166 | Sylhet | 28 | 18:00
35 | Chapai | 50 | 12:00 | 101 | Matarbari | 32 | 19:00 | 167 | Sylhet-132 | 74 | 19:30
36 | Charsaidpur | 29 | 16:00 | 102 | Matuail | 46 | 10:00 | 168 | TK | 21 | 18:00
37 | Chauddagram | 42 | 13:00 | 103 | Millgate | 76 | 12:00 | 169 | Tangail | 128 | 18:00
38 | Chhatak | 20 | 18:00 | 104 | Mirpur | 84 | 13:00 | 170 | Thakurgaon | 76 | 18:00
39 | Chowmuhani | 144 | 18:00 | 105 | Mirsorai | 7 | 12:00 | 171 | Tongi | 97 | 12:00
40 | Chuadanga | 67 | 13:00 | 106 | Mirzapur | 35 | 08:00 | 172 | Ullahpara | 23 | 18:00
41 | Coxsbazar | 92 | 18:00 | 107 | Mithapukur | 42 | 18:00 | 173 | Ullon | 37 | 13:00
42 | Cumilla(N) | 100 | 20:00 | 108 | Modern | 0 | 00:00 | 174 | Uttara | 47 | 13:00
43 | Cumilla(S) | 122 | 18:00 | 109 | Mogbazar | 70.1 | 14:00 | 175 | UttaraNew | 30 | 13:00
44 | Daudkandi | 103 | 21:00 | 110 | Mongla | 26 | 09:00 | 176 | Zigatola | 68 | 13:00
45 | Dhaka | 26 | 13:00 | 111 | Motijheel | 22 | 13:00
46 | Dhamrai | 102 | 18:00 | 112 | Munshiganj | 71 | 18:30
47 | Dhanmondi | 87 | 13:00 | 113 | Mymensingh | 162 | 18:00
48 | Dohazari | 59 | 19:00 | 114 | Naogaon | 86 | 13:00
49 | Faridpur | 107 | 18:00 | 115 | Narail | 39 | 18:00
50 | Fatullah | 80 | 12:00 | 116 | Narinda | 44.5 | 13:00
51 | Fenchuganj | 24 | 18:00 | 117 | Narshingdi | 148 | 19:00
52 | Feni | 69 | 18:00 | 118 | Natore | 95 | 18:30
53 | GPH | 28 | 12:00 | 119 | Nawabganj | 27.6 | 20:00
54 | Ghatail | 40 | 08:00 | 120 | Netrakona | 102 | 18:00
55 | Ghorashal | 7 | 08:00 | 121 | New | 61.5 | 17:00
56 | Ghorashal-230 | 59 | 00:00 | 122 | Niamatpur | 52 | 09:00
57 | Goalpara | 22 | 13:00 | 123 | Noapara | 34 | 18:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-12-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 406 | 03:00 | 387 | 12:00 | Kaliakoir | 381 | 04:00 | 361 | 12:00
| Ashuganj | 407 | 4:00 | 384 | 12:00 | Madunaghat | 406 | 04:00 | 394 | 13:00
| Bhulta | 405 | 04:00 | 384 | 12:00 | Meghnaghat | 399 | 03:00 | 383 | 12:00
| Bibiana | 397 | 03:00 | 386 | 12:00 | Payra | 436 | 17:00 | 378 | 00:00
| BIPTC | 407 | 02:00 | 389 | 10:00 | Rahanpur | 414 | 03:00 | 400 | 09:00
| Bogura | 411 | 04:00 | 390 | 12:00 | Rampal | 409 | 04:00 | 394 | 12:00
| Gopalganj | 409 | 03:00 | 388 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 235 | 03:00 | 222 | 12:00 | Haripur | 234 | 00:00 | 225 | 12:00
| AKSML | 233 | 02:00 | 225 | 11:00 | Hasnabad | 235 | 02:00 | 223 | 12:00
| Aminbazar | 235 | 03:00 | 223 | 23:00 | Hathazari | 235 | 17:00 | 225 | 12:00
| Ashuganj | 239 | 01:00 | 229 | 12:00 | Ishurdi | 244 | 03:00 | 226 | 12:00
| Ashuganj-400 | 243 | 1:00 | 228 | 12:00 | Jhenaidah | 241 | 04:00 | 222 | 12:00
| Baghabari | 239 | 05:00 | 228 | 12:00 | Kaliakoir | 238 | 04:00 | 224 | 12:00
| Barapukuria | 226 | 04:00 | 215 | 18:30 | Keranigonj | 235 | 03:00 | 222 | 12:00
| Barapukuria-230 | 226 | 04:00 | 215 | 18:30 | Khulna(S) | 241 | 04:00 | 225 | 13:00
| Barishal | 245 | 04:00 | 234 | 12:00 | Madunaghat | 233 | 18:00 | 226 | 12:00
| Bheramara | 242 | 03:00 | 222 | 12:00 | Madunaghat-400 | 234 | 18:00 | 226 | 12:00
| Bhulta | 239 | 04:00 | 225 | 12:00 | Maniknagar | 236 | 02:00 | 224 | 12:00
| Bibiana | 229 | 04:00 | 223 | 12:00 | Meghnaghat | 245 | 03:00 | 235 | 15:00
| BIPTC | 243 | 03:00 | 213 | 20:00 | Meghnaghat-400 | 239 | 03:00 | 229 | 12:00
| Bogura | 238 | 04:00 | 227 | 12:00 | Mirsorai | 233 | 03:00 | 222 | 14:00
| Bogura-400 | 239 | 04:00 | 227 | 09:00 | Rajshahi | 244 | 05:00 | 227 | 08:00
| Borhanuddin | 246 | 03:00 | 241 | 20:00 | Rampal | 237 | 04:00 | 223 | 12:00
| BSRM | 234 | 03:00 | 225 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Cumilla(N) | 233 | 01:00 | 224 | 12:00 | Rampura | 238 | 03:00 | 225 | 12:00
| Faridpur | 244 | 03:00 | 232 | 13:00 | Shikalbaha | 233 | 05:00 | 225 | 12:00
| Fenchuganj | 233 | 00:00 | 228 | 12:00 | Shyampur | 236 | 03:00 | 224 | 12:00
| Ghorashal | 240 | 01:00 | 235 | 00:00 | Siddhirganj | 240 | 03:00 | 228 | 13:00
| Ghorashal-230 | 237 | 04:00 | 224 | 12:00 | Sirajgonj | 247 | 03:00 | 238 | 12:00
| Gopalganj | 243 | 03:00 | 233 | 12:00 | Sreepur | 240 | 04:00 | 227 | 12:00
| GPH | 234 | 03:00 | 224 | 13:00 | Tongi | 234 | 04:00 | 224 | 12:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 135 | 03:00 | 127 | 12:00 | Kushtia | 139 | 03:00 | 129 | 12:00
| Agargaon | 137 | 03:00 | 129 | 12:00 | Lalbag | 135 | 03:00 | 126 | 12:00
| Agrabad | 135 | 03:00 | 128 | 12:00 | Lalmonirhat | 137 | 15:00 | 120 | 13:00
| AKS | 133 | 18:00 | 127 | 12:00 | Madanganj | 132 | 03:00 | 125 | 12:00
| Aminbazar | 136 | 03:00 | 125 | 12:00 | Madaripur | 133 | 23:00 | 130 | 12:00
| Amnura | 140 | 04:00 | 125 | 12:00 | Madartek | 134 | 03:00 | 126 | 12:00
| Ashuganj | 140 | 00:00 | 136 | 12:00 | Madunaghat | 136 | 18:00 | 129 | 13:00
| Bagerhat | 136 | 01:00 | 125 | 14:00 | Magura | 139 | 02:00 | 127 | 12:00
| Bakulia | 134 | 03:00 | 130 | 12:00 | Mahasthangarh | 136 | 03:00 | 127 | 12:00
| Banani | 135 | 02:00 | 126 | 12:00 | Manikganj | 130 | 07:00 | 121 | 12:00
| Bangabhaban | 134 | 03:00 | 123 | 12:00 | Maniknagar | 134 | 00:00 | 124 | 12:00
| Barapukuria | 135 | 03:00 | 127 | 18:30 | Matarbari | 129 | 03:00 | 123 | 12:00
| Barguna | 138 | 17:00 | 127 | 12:00 | Matuail | 134 | 05:00 | 119 | 14:00
| Barishal | 135 | 17:00 | 128 | 12:00 | Millgate | 133 | 02:00 | 125 | 12:00
| Barishal-230 | 136 | 04:00 | 129 | 12:00 | Mirpur | 134 | 04:00 | 126 | 12:00
| Baroaulia | 134 | 17:00 | 128 | 12:00 | Mirzapur | 129 | 03:00 | 122 | 12:00
| Baroirhat | 133 | 03:00 | 125 | 14:00 | Mithapukur | 135 | 04:00 | 125 | 09:00
| Bashundhara | 135 | 04:00 | 123 | 12:00 | MI_Cement | 134 | 03:00 | 126 | 12:00
| BashundharaCement | 132 | 03:00 | 125 | 12:00 | Modern | 135 | 06:00 | 128 | 12:00
| Beanibazar | 136 | 02:00 | 132 | 11:00 | Mogbazar | 135 | 01:00 | 128 | 12:00
| Benapole | 139 | 03:00 | 125 | 12:00 | Mongla | 136 | 16:00 | 126 | 12:00
| Bhaluka | 131 | 02:00 | 125 | 12:00 | Motijheel | 134 | 03:00 | 123 | 12:00
| Bhandaria | 134 | 17:00 | 126 | 12:00 | Munshiganj | 133 | 03:00 | 125 | 12:00
| Bhangura | 140 | 04:00 | 131 | 12:00 | Mymensingh | 130 | 17:00 | 122 | 12:00
| Bheramara | 140 | 03:00 | 128 | 12:00 | Naogaon | 137 | 02:00 | 126 | 12:00
| Bheramara(GK) | 138 | 05:00 | 129 | 12:00 | Narail | 140 | 05:00 | 127 | 12:00
| Bhulta | 125 | 03:00 | 119 | 12:00 | Narinda | 134 | 00:00 | 124 | 12:00
| Bog-Sherpur | 138 | 03:00 | 129 | 12:00 | Narshingdi | 126 | 05:00 | 118 | 12:00
| Bogura | 138 | 06:00 | 130 | 08:00 | Natore | 136 | 01:00 | 127 | 12:00
| Bogura-230 | 138 | 04:00 | 129 | 12:00 | Nawabganj | 135 | 03:00 | 126 | 12:00
| Brahmanbaria | 138 | 01:00 | 131 | 12:00 | Netrakona | 132 | 05:00 | 123 | 12:00
| Cantonment | 136 | 03:00 | 128 | 12:00 | New | 134 | 04:00 | 124 | 12:00
| Chandpur | 131 | 02:00 | 123 | 13:00 | Niamatpur | 140 | 02:00 | 133 | 12:00
| Chandraghona | 135 | 02:00 | 130 | 12:00 | Noapara | 140 | 04:00 | 127 | 13:00
| Chapai | 139 | 03:00 | 131 | 12:00 | Pabna | 141 | 03:00 | 130 | 12:00
| Charsaidpur | 134 | 03:00 | 126 | 12:00 | Palashbari | 132 | 03:00 | 123 | 08:00
| Chauddagram | 134 | 03:00 | 126 | 12:00 | Panchagarh | 136 | 03:00 | 117 | 09:00
| Chhatak | 135 | 01:00 | 132 | 11:00 | Patuakhali | 143 | 17:00 | 125 | 12:00
| Chowmuhani | 129 | 18:00 | 122 | 22:00 | Payra | 142 | 17:00 | 126 | 12:00
| Chuadanga | 140 | 05:00 | 124 | 12:00 | PHP | 132 | 03:00 | 123 | 13:00
| Coxsbazar | 127 | 02:00 | 123 | 19:00 | Postogola | 136 | 04:00 | 128 | 12:00
| Cumilla(N) | 136 | 01:00 | 130 | 12:00 | Purbachal | 136 | 04:00 | 126 | 12:00
| Cumilla(S) | 134 | 04:00 | 128 | 09:00 | Purbasadipur | 130 | 17:00 | 117 | 09:00
| Daudkandi | 132 | 03:00 | 126 | 12:00 | Rahanpur | 140 | 05:00 | 138 | 01:00
| Dhaka | 135 | 03:00 | 126 | 12:00 | Rahanpur-400 | 140 | 01:00 | 134 | 12:00
| Dhamrai | 137 | 03:00 | 128 | 12:00 | Rahim | 133 | 04:00 | 125 | 12:00
| Dhanmondi | 135 | 03:00 | 127 | 12:00 | Rajbari | 135 | 04:00 | 128 | 12:00
| Dohazari | 132 | 03:00 | 127 | 12:00 | Rajendrapur | 135 | 08:00 | 128 | 13:00
| Faridpur | 134 | 03:00 | 130 | 12:00 | Rajshahi | 139 | 04:00 | 124 | 12:00
| Fatullah | 135 | 04:00 | 126 | 12:00 | Rajshahi-230 | 141 | 04:00 | 123 | 13:00
| Fenchuganj | 139 | 00:00 | 135 | 12:00 | Ramganj | 129 | 18:00 | 121 | 13:00
| Feni | 130 | 02:00 | 125 | 12:00 | Rampur | 135 | 18:00 | 129 | 12:00
| Ghatail | 130 | 03:00 | 122 | 12:00 | Rampura | 135 | 03:00 | 126 | 12:00
| Ghorashal | 140 | 00:00 | 135 | 12:00 | Rangamati | 135 | 03:00 | 129 | 12:00
| Goalpara | 141 | 03:00 | 128 | 12:00 | Rangpur | 133 | 03:00 | 120 | 18:30
| Gollamari | 139 | 03:00 | 129 | 13:00 | Ruppur | 141 | 03:00 | 131 | 11:00
| Gopalganj | 137 | 03:00 | 129 | 12:00 | Saidpur | 132 | 04:00 | 120 | 13:00
| Gopalganj-400 | 136 | 02:00 | 130 | 12:00 | Satkhira | 138 | 04:00 | 127 | 13:00
| Gulshan | 134 | 05:00 | 126 | 12:00 | Satmasjid | 136 | 03:00 | 128 | 12:00
| Halishahar | 135 | 18:00 | 128 | 12:00 | Savar | 133 | 03:00 | 125 | 12:00
| Haripur | 133 | 04:00 | 126 | 12:00 | SevenRings | 141 | 03:00 | 135 | 12:00
| HaripurSBU | 133 | 04:00 | 128 | 11:00 | ShahCement | 134 | 03:00 | 126 | 12:00
| Hasnabad | 135 | 01:00 | 128 | 12:00 | Shahjadpur | 140 | 00:00 | 135 | 11:00
| Hathazari | 136 | 18:00 | 132 | 12:00 | Shahjibazar | 136 | 00:00 | 131 | 12:00
| Ishurdi | 142 | 03:00 | 132 | 12:00 | Shahmirpur | 135 | 18:00 | 129 | 11:00
| Jaldhaka | 132 | 03:00 | 117 | 09:00 | Shariatpur | 136 | 03:00 | 128 | 13:00
| Jamalpur | 130 | 17:00 | 120 | 12:00 | Sherpur | 130 | 17:00 | 117 | 08:00
| Jashore | 138 | 04:00 | 126 | 12:00 | Shikalbaha | 124 | 17:00 | 118 | 12:00
| Jhenaidah | 138 | 01:00 | 129 | 12:00 | Shikalbaha-230 | 136 | 04:00 | 130 | 12:00
| Jhenaidah-230 | 141 | 03:00 | 129 | 12:00 | Shitalakhya | 134 | 03:00 | 126 | 12:00
| Joydebpur | 138 | 07:00 | 131 | 12:00 | Sholosohor | 134 | 04:00 | 129 | 12:00
| Joypurhat | 137 | 03:00 | 125 | 12:00 | Shyampur | 131 | 00:00 | 125 | 12:00
| Juldah | 136 | 18:30 | 129 | 12:00 | Shyampur-230 | 134 | 03:00 | 126 | 12:00
| Kabirpur | 131 | 23:00 | 124 | 12:00 | Siddhirganj | 132 | 00:00 | 127 | 12:00
| Kachua | 134 | 18:00 | 124 | 13:00 | Sirajganj | 140 | 06:00 | 130 | 11:00
| Kaliakoir | 139 | 05:00 | 125 | 12:00 | Sonargaon | 133 | 05:00 | 125 | 12:00
| Kallyanpur | 134 | 01:00 | 126 | 12:00 | Sreemongol | 137 | 02:00 | 132 | 12:00
| Kalurghat | 135 | 04:00 | 129 | 12:00 | Sreepur | 132 | 04:00 | 124 | 12:00
| Kamrangirchar | 134 | 01:00 | 126 | 11:00 | Srinagar | 135 | 06:00 | 126 | 12:00
| Kaptai | 141 | 1:00 | 127 | 12:00 | SSM | 139 | 01:00 | 134 | 14:00
| Kazla | 134 | 03:00 | 124 | 12:00 | Sunamganj | 134 | 00:00 | 131 | 12:00
| Keranigonj | 135 | 03:00 | 127 | 12:00 | Sylhet | 137 | 03:00 | 133 | 12:00
| Khagrachori | 134 | 02:00 | 128 | 12:00 | Sylhet-132 | 136 | 00:00 | 133 | 12:00
| Khulna | 138 | 04:00 | 128 | 12:00 | Tangail | 129 | 04:00 | 120 | 12:00
| Khulna(S) | 140 | 03:00 | 130 | 12:00 | Thakurgaon | 133 | 04:00 | 114 | 09:00
| Khulshi | 134 | 18:00 | 128 | 12:00 | TK | 135 | 18:00 | 130 | 12:00
| Kishoreganj | 134 | 17:00 | 128 | 12:00 | Tongi | 134 | 02:00 | 128 | 12:00
| Kodda | 135 | 17:00 | 122 | 10:00 | Ullahpara | 140 | 05:00 | 131 | 12:00
| KSRM | 136 | 18:00 | 129 | 12:00 | Ullon | 134 | 01:00 | 126 | 12:00
| Kulaura | 138 | 00:00 | 135 | 12:00 | Uttara | 135 | 04:00 | 126 | 12:00
| Kurigram | 131 | 02:00 | 120 | 07:00 | UttaraNew | 135 | 03:00 | 127 | 12:00

## L-Curve
Date | 2024-12-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 932 | 4958 | 3432 | 8390 |  |  |  | QF-LDC-11
0:30 | 941 | 4888.5 | 3260.5 | 8149 | Date: | 2024-12-25
1:00 | 950 | 4819 | 3089 | 7908
1:30 | 900 | 4713 | 2985.5 | 7698.5
2:00 | 850 | 4607 | 2882 | 7489
2:30 | 797 | 4560.5 | 2799.5 | 7360 | [5 empty] | Gen. at Eve. Peak | 10341 | 10341 MW (18:00 )
3:00 | 744 | 4514 | 2717 | 7231 | [6 empty] | 18:00
3:30 | 676 | 4443.5 | 2691.5 | 7135 | [5 empty] | Gen. at Day Peak | 9712 | 9712 MW (12:00 )
4:00 | 608 | 4373 | 2666 | 7039 | [6 empty] | 12:00
4:30 | 604 | 4350 | 2624.5 | 6974.5 | [5 empty] | Highest Generation | 10341
5:00 | 600 | 4327 | 2583 | 6910 | [6 empty] | 18:00
5:30 | 610 | 4420 | 2610 | 7030
6:00 | 620 | 4513 | 2637 | 7150
6:30 | 637 | 4719.5 | 2700 | 7419.5
7:00 | 654 | 4926 | 2763 | 7689
7:30 | 662 | 5116.5 | 3002 | 8118.5
8:00 | 670 | 5307 | 3241 | 8548
8:30 | 755 | 5270.5 | 3483 | 8753.5
9:00 | 840 | 5234 | 3725 | 8959
9:30 | 1022 | 5165 | 3746 | 8911
10:00 | 1204 | 5096 | 3767 | 8863
10:30 | 1287 | 5165.5 | 3841.5 | 9007
11:00 | 1370 | 5235 | 3916 | 9151
11:30 | 1317 | 5329.5 | 4102 | 9431.5
12:00 | 1264 | 5424 | 4288 | 9712
12:30 | 1208 | 5526 | 4343.5 | 9869.5
13:00 | 1152 | 5628 | 4399 | 10027
13:30 | 1170 | 5528.5 | 4213 | 9741.5
14:00 | 1188 | 5429 | 4027 | 9456
14:30 | 1233 | 5345.5 | 3964 | 9309.5
15:00 | 1278 | 5262 | 3901 | 9163
15:30 | 1239 | 5285.5 | 3735.5 | 9021
16:00 | 1200 | 5309 | 3570 | 8879
16:30 | 1188 | 5425.5 | 3558.5 | 8984
17:00 | 1176 | 5542 | 3547 | 9089
17:30 | 981 | 5919 | 3796 | 9715
18:00 | 786 | 6296 | 4045 | 10341
18:30 | 715 | 6190.5 | 4082.5 | 10273
19:00 | 644 | 6085 | 4120 | 10205
19:30 | 664 | 5990 | 4074 | 10064
20:00 | 682 | 5963 | 4070 | 10033 |  |  |  | Executive Engineer
20:30 | 680 | 5847.5 | 4049 | 9896.5 |  |  |  | Network Operation Division
21:00 | 678 | 5732 | 4028 | 9760
21:30 | 754 | 5552.5 | 3969 | 9521.5
22:00 | 830 | 5373 | 3910 | 9283 |  |  |  |  | Page 6 of 7
22:30 | 827 | 5335 | 3779 | 9114
23:00 | 824 | 5297 | 3648 | 8945
23:30 | 878 | 5127.5 | 3540 | 8667.5
24:00 | 932 | 4958 | 3432 | 8390
10341 MW (18:00 )
9712 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-12-25 |  |  | Energy |  | 214044176
[17 empty] | 2024-12-25 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | Nepal | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 2932 | 920 | 0 | 1632 | 0 | 17 | 2082 | 40 | 0 | 163 | 46 | 526 | 0 | 32 | 0
0:30 | 2936.5 | 921.5 | 0 | 1592 | 0 | 17 | 1909 | 40 | 0 | 163 | 46 | 502.5 | 0 | 21.5 | 0 |  |  | Date: | 44189
1:00 | 2941 | 923 | 0 | 1552 | 0 | 17 | 1736 | 40 | 0 | 163 | 46 | 479 | 0 | 11 | 0
1:30 | 2923 | 828.5 | 0 | 1468.5 | 0 | 8.5 | 1738 | 40 | 0 | 163 | 45 | 469 | 0 | 15 | 0 | [8 empty] | Total Energy | 214.0442 | 214.0442 | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr | Total Energy Gen 214.044 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 214.044 MKWHr
2:00 | 2905 | 734 | 0 | 1385 | 0 | 0 | 1740 | 40 | 0 | 163 | 44 | 459 | 0 | 19 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2868 | 688 | 0 | 1378 | 0 | 0 | 1717.5 | 40 | 0 | 163 | 42 | 443 | 0 | 20.5 | 0 | [8 empty] | Energy Requirement | 214.0442 | 214.0442
3:00 | 2831 | 642 | 0 | 1371 | 0 | 0 | 1695 | 40 | 0 | 163 | 40 | 427 | 0 | 22 | 0
3:30 | 2773 | 641 | 0 | 1347.5 | 0 | 0 | 1692.5 | 40 | 0 | 163 | 41 | 421.5 | 0 | 15.5 | 0 | [7 empty] | Shortage
4:00 | 2715 | 640 | 0 | 1324 | 0 | 0 | 1690 | 40 | 0 | 163 | 42 | 416 | 0 | 9 | 0
4:30 | 2686.5 | 640 | 0 | 1326 | 0 | 0 | 1656 | 40 | 0 | 163 | 42 | 416.5 | 0 | 4.5 | 0
5:00 | 2658 | 640 | 0 | 1328 | 0 | 0 | 1622 | 40 | 0 | 163 | 42 | 417 | 0 | 0 | 0
5:30 | 2712 | 640 | 0 | 1387 | 0 | 0 | 1628 | 40 | 0 | 163 | 42 | 418 | 0 | 0 | 0
6:00 | 2766 | 640 | 0 | 1446 | 0 | 0 | 1634 | 40 | 0 | 163 | 42 | 419 | 0 | 0 | 0
6:30 | 2925.5 | 687 | 0 | 1485 | 0 | 9.5 | 1633.5 | 40 | 0 | 171 | 41 | 420 | 5.5 | 1.5 | 0 | [6 empty] | Coal
7:00 | 3085 | 734 | 0 | 1524 | 0 | 19 | 1633 | 40 | 0 | 179 | 40 | 421 | 11 | 3 | 0
7:30 | 3156 | 828.5 | 0 | 1576.5 | 0 | 39 | 1775 | 40 | 0 | 179 | 42 | 418 | 59 | 5.5 | 0 | [5 empty] | Oil
8:00 | 3227 | 923 | 0 | 1629 | 0 | 59 | 1917 | 40 | 0 | 179 | 44 | 415 | 107 | 8 | 0
8:30 | 3181 | 923 | 0 | 1640 | 0 | 62 | 2036 | 40 | 0 | 179 | 43 | 467.5 | 172.5 | 9.5 | 0
9:00 | 3135 | 923 | 0 | 1651 | 0 | 65 | 2155 | 40 | 0 | 179 | 42 | 520 | 238 | 11 | 0
9:30 | 3107.5 | 923 | 0 | 1533.5 | 0 | 81 | 2164.5 | 40 | 0 | 179 | 43 | 516.5 | 316.5 | 6.5 | 0
10:00 | 3080 | 923 | 0 | 1416 | 0 | 97 | 2174 | 40 | 0 | 179 | 44 | 513 | 395 | 2 | 0
10:30 | 3051 | 920 | 0 | 1417.5 | 0 | 100.5 | 2238 | 40 | 0 | 179 | 46 | 564 | 449.5 | 1.5 | 0
11:00 | 3022 | 917 | 0 | 1419 | 0 | 104 | 2302 | 40 | 0 | 179 | 48 | 615 | 504 | 1 | 0
11:30 | 3073.5 | 917 | 0 | 1434.5 | 0 | 112 | 2438.5 | 40 | 0 | 179 | 51 | 692 | 492.5 | 1.5 | 0
12:00 | 3125 | 917 | 0 | 1450 | 0 | 120 | 2575 | 40 | 0 | 179 | 54 | 769 | 481 | 2 | 0
12:30 | 3122.5 | 917 | 0 | 1551.5 | 0 | 155.5 | 2584 | 40 | 0 | 187 | 59 | 764.5 | 487 | 1.5 | 0
13:00 | 3120 | 917 | 0 | 1653 | 0 | 191 | 2593 | 40 | 0 | 195 | 64 | 760 | 493 | 1 | 0
13:30 | 3120 | 917 | 0 | 1653 | 0 | 191 | 2593 | 40 | 0 | 195 | 64 | 760 | 493 | 1 | 0
14:00 | 3120 | 917 | 0 | 1653 | 0 | 191 | 2593 | 40 | 0 | 195 | 64 | 760 | 493 | 1 | 0
14:30 | 3030.5 | 917.5 | 0 | 1644 | 0 | 125 | 2434.5 | 40 | 0 | 187 | 56 | 754.5 | 403.5 | 2.5 | 0
15:00 | 2941 | 918 | 0 | 1635 | 0 | 59 | 2276 | 40 | 0 | 179 | 48 | 749 | 314 | 4 | 0
15:30 | 3006 | 917.5 | 0 | 1684 | 0 | 67.5 | 2179 | 40 | 0 | 187 | 49 | 676.5 | 210 | 4.5 | 0
16:00 | 3071 | 917 | 0 | 1733 | 0 | 76 | 2082 | 40 | 0 | 195 | 50 | 604 | 106 | 5 | 0
16:30 | 3012.5 | 917 | 0 | 1651.5 | 0 | 314 | 2130.5 | 40 | 0 | 212 | 53 | 591.5 | 58.5 | 3.5 | 0
17:00 | 2954 | 917 | 0 | 1570 | 0 | 552 | 2179 | 40 | 0 | 229 | 56 | 579 | 11 | 2 | 0
17:30 | 2996.5 | 917.5 | 0 | 1654.5 | 0 | 782.5 | 2341 | 40 | 0 | 282 | 58 | 633.5 | 5.5 | 4 | 0
18:00 | 3039 | 918 | 0 | 1739 | 0 | 1013 | 2503 | 40 | 0 | 335 | 60 | 688 | 0 | 6 | 0
18:30 | 3159 | 919 | 0 | 1767.5 | 0 | 740 | 2544.5 | 40 | 0 | 314.5 | 60 | 717.5 | 0 | 11 | 0
19:00 | 3279 | 920 | 0 | 1796 | 0 | 467 | 2586 | 40 | 0 | 294 | 60 | 747 | 0 | 16 | 0
19:30 | 3233 | 921 | 0 | 1857 | 0 | 364 | 2582 | 40 | 0 | 238 | 52 | 759 | 0 | 18 | 0
20:00 | 3210 | 920 | 0 | 1831 | 0 | 364 | 2584 | 40 | 0 | 238 | 54 | 759 | 0 | 33 | 0
20:30 | 3176.5 | 920.5 | 0 | 1832.5 | 0 | 292.5 | 2585 | 40 | 0 | 208.5 | 53 | 758.5 | 0 | 29.5 | 0
21:00 | 3143 | 921 | 0 | 1834 | 0 | 221 | 2586 | 40 | 0 | 179 | 52 | 758 | 0 | 26 | 0
21:30 | 3124 | 921 | 0 | 1798 | 0 | 148 | 2486 | 40 | 0 | 179 | 54 | 744.5 | 0 | 27 | 0
22:00 | 3105 | 921 | 0 | 1762 | 0 | 75 | 2386 | 40 | 0 | 179 | 56 | 731 | 0 | 28 | 0
22:30 | 3079.5 | 921 | 0 | 1778 | 0 | 63 | 2319 | 40 | 0 | 179 | 53 | 647.5 | 0 | 34 | 0
23:00 | 3054 | 921 | 0 | 1794 | 0 | 51 | 2252 | 40 | 0 | 179 | 50 | 564 | 0 | 40 | 0
23:30 | 2993 | 920.5 | 0 | 1713 | 0 | 34 | 2167 | 40 | 0 | 171 | 48 | 545 | 0 | 36 | 0 |  |  | Max Temp. in Dhaka |  | 26.7°C
24:00 | 2932 | 920 | 0 | 1632 | 0 | 17 | 2082 | 40 | 0 | 163 | 46 | 526 | 0 | 32 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 214.044 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 214.044 MKWHr
Note on Y13: Author:

## Generation
2024-12-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 968220
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 2 | 6 | 9 | 10 | 7 | 6 | 7 | 5 | 1 | 0 | [9 empty] | 57645
6 | Sikalbaha 225MW CCPP (Gas) | 198 | 187 | 186 | 186 | 186 | 186 | 225 | 227 | 228 | 227 | 228 | 226 | 226 | 224 | 225 | 226 | 226 | 226 |  | 225 | 226 | 229 | 232 | 231 | 230 | 230 | 5144901
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 49429
12 | Hathazari 100 MW peaking PP | [16 empty] | 17 | 24 | [8 empty] | 32046
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [16 empty] | 9 | 17 | [7 empty] | 0 | 41818
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 270 | 263 | 262 | 262 | 259 | 259 | 262 | 245 | 245 | 251 | 260 | 260 | 260 | 260 | 257 | 260 | 255 | 252 |  | 250 | 245 | 245 | 240 | 228 | 228 | 225 | 6134730
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 168 | 78 | 78 | 78 | 78 | 78 | 125 | 190 | 197 | 108 | 108 | 145 | 194 | 195 | 195 | 197 | 199 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 130 | 3830545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 400 | 402 | 402 | 402 | 373 | 373 | 375 | 464 | 500 | 502 | 555 | 612 | 612 | 558 | 500 | 450 | 452 | 530 |  | 609 | 609 | 610 | 610 | 559 | 450 | 412 | 11809089
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 40 | 40 | 40 | 10 | 10 | 20 | 37 | 37 | 37 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 878328
33 | Ashuganj 225 MW CCPP | 182 | 181 | 181 | 182 | 181 | 205 | 222 | 208 | 186 | 193 | 181 | 200 | 183 | 198 | 181 | 203 | 182 | 182 |  | 229 | 204 | 181 | 182 | 180 | 188 | 182 | 4623000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 310 | 295 | 295 | 295 | 295 | 335 | 365 | 360 | 320 | 330 | 310 | 340 | 310 | 315 | 285 | 325 | 280 | 295 |  | 335 | 315 | 315 | 310 | 280 | 300 | 300 | 7796600
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 23 | 23 | 23 | 23 | 24 | 22 | 20 | 20 | 20 | 22 | 24 | 24 | 21 | 24 | 25 | 24 | 27 | 28 |  | 28 | 28 | 29 | 28 | 29 | 29 | 28 | 588960
36 | Chandpur 150 MW CCPP | 45 | 45 | 45 | 45 | 45 | 45 | 50 | 50 | 50 | 45 | 45 | 40 | 42 | 40 | 40 | 40 | 40 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 988180
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 351 | 351 | 347 | 305 | 302 | 315 | 351 | 349 | 343 | 336 | 337 | 338 | 340 | 306 | 325 | 341 | 341 | 336 |  | 336 | 335 | 335 | 331 | 327 | 317 | 317 | 8067600
| Meghnaghat Unique power | 300 | 300 | 290 | 290 | 290 | 330 | 330 | 330 | 330 | 280 | 280 | 280 | 330 | 400 | 400 | 400 | 320 | 400 |  | 400 | 400 | 400 | 400 | 350 | 350 | 350 | 8214545
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 350 | 350 | 300 | 300 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 350 |  | 400 | 420 | 400 | 400 | 400 | 400 | 400 | 8278000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | [5 empty] | 11 | 11 | 9 | 5 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 |  | 4 | 6 | 6 | 8 | 9 | 9 | 8 | 97920
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 7 | 25 | 35 | 41 | 42 | 37 | 31 | 20 | 9 | 0 | [9 empty] | 254340
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 33 | 33 | 20 | 20 | 20 | 20 | 32 | 32 | 20 | 20 | 20 | 30 | 30 | 31 | 31 | 33 | 32 |  | 33 | 32 | 32 | 33 | 33 | 32 | 33 | 692928
48 | Shahjibazar 86 MW PP (Shahjibazar) | 42 | 5 | 5 | 5 | 5 | 5 | 5 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 5 | 769920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 138 | 138 | 139 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 |  | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 3319660
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 58032
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 356784
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 275 | 285 | 285 | 305 | 305 | 300 | 305 | 290 | 310 | 295 | 300 | 290 | 290 | 300 | 290 | 265 |  | 280 | 315 | 305 | 300 | 260 | 290 | 280 | 7089500
| Bibiyana South 400 MW | 346 | 346 | 316 | 316 | 316 | 316 | 400 | 390 | 340 | 340 | 316 | 340 | 340 | 340 | 320 | 350 | 320 | 346 |  | 400 | 400 | 400 | 346 | 346 | 346 | 346 | 8239300
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 17 | [7 empty] | 0 | 45660
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 5 | 24 |  | 24 | 23 | 23 | 23 |  |  | 0 | 111120
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 46 | 44 | 40 | 42 | 42 | 42 | 40 | 44 | 42 | 44 | 48 | 54 | 64 | 60 | 48 | 50 | 56 | 60 |  | 60 | 52 | 54 | 52 | 56 | 50 | 46 | 1201920
64 | Malancha, Ctg. EPZ (United) | 26 | 28 | 29 | 22 | 25 | 25 | 15 | 2 | 2 | 2 | 2 | 11 | 11 | 4 | 4 | 8 | 11 | 10 |  | 2 | 7 | 10 | 19 | 36 | 38 | 39 | 346560
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 11 | 11 | 11 | 11 | 16 | 16 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 382940
69 | Summit Ashulia | 19 | 15 | 15 | 15 | 15 | 15 | 20 | 22 | 21 | 21 | 20 | 20 | 21 | 21 | 20 | 20 | 19 | 19 |  | 19 | 19 | 20 | 19 | 20 | 20 | 19 | 462000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 520200
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 520920
72 | Rupganj 33 MW PP(Summit) | 24 | 24 | 24 | 26 | 26 | 26 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 |  | 22 | 22 | 22 | 22 | 24 | 24 | 24 | 584000
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0
| Chowmuhani 113 MW | [12 empty] | 4 |  |  |  | 4 | 42 |  | 9 | 9 | 9 |  |  |  | 0 | 130200
| Manikgonj 162MW PP(MPGL) | [12 empty] | 10 |  |  |  | 54 | 72 |  | 17 | [5 empty] | 0 | 182880
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 8 | 25 | 25 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 16 | 8 |  | 515040
79 | Kodda 150 MW PP | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 16 | 16 | 32 | 32 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 331200
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 8 | 8 | [8 empty] | 18072
| Gazipur 100 MW PP | 17 | [5 empty] | 11 | 34 | 40 | 52 | 52 | 52 | 52 | 17 | 17 | 34 | 52 | 70 |  | 52 | 52 | 52 | 35 | 35 | 35 | 17 | 779520
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 1 | 0 | [10 empty] | 12602
| Jodiac Power | [12 empty] | 17 |  |  |  | 54 | 54 |  | 54 | 54 | 54 | 54 |  |  | 0 | 292070
| Karnaphuli Power Ltd. | [16 empty] | 5 | 17 | [7 empty] | 0 | 35127
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [16 empty] | 4 | 16 | [7 empty] | 0 | 22080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 201168
93 | Ashuganj 51 MW PP (Midland) | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 32 | 43 | 43 | 25 | 25 | 43 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 5 | 972712
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 8 | 8 | 8 | 8 |  |  | 0 | 22608
95 | Patenga 50MW PP (Baraka) | [12 empty] | 1 |  |  |  | 4 | 25 |  | 26 | 26 | 26 | 26 |  |  | 0 | 132000
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 26 | [7 empty] | 0 | 47040
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 3 | 17 | [7 empty] | 0 | 28889
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 120 | 120 | 120 | 163 | 120 | 120 | 163 | 120 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3607445
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [10 empty] | 11100
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 35 | [7 empty] | 0 | 68400
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 8 | 8 |  | 8 | [5 empty] | 0 | 24000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [10 empty] | 1 | 17 | 17 |  |  |  | 9 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 113904
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 24 | 36 | [7 empty] | 0 | 59520
116 | Chandpur 200 MW (Desh energy) | [16 empty] | 6 | 17 | [7 empty] | 0 | 32640
117 | Ashuganj 150 MW PP (Midland) | [16 empty] | 10 | 80 |  | 45 | 10 | 10 |  |  |  | 0 | 197381
118 | Bibiyana-III 400 MW CCPP | 347 | 347 | 303 | 303 | 300 | 310 | 366 | 385 | 342 | 342 | 335 | 371 | 358 | 340 | 340 | 341 | 381 | 381 |  | 381 | 383 | 383 | 380 | 381 | 382 | 381 | 8865000
| Jamalpur 115 MW PP (United) | [12 empty] | 8 | 8 | 8 | 8 | 19 | 45 |  | 45 | 45 | 45 | 24 | 24 | 8 | 0 | 259200
| Anwara 300 MW PP (United) | [12 empty] | 15 |  |  |  | 49 | 45 |  | 45 | 15 | 15 |  |  |  | 0 | 173127
| Juldah unit-2 (Acorn) | [16 empty] | 36 | 50 |  | 12 | [5 empty] | 0 | 92160
| Anlima Energy Ltd. | [12 empty] | 5 |  |  |  | 18 | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 154309
| Bhairob 54.5 MW | [16 empty] | 10 | 35 | [7 empty] | 0 | 61920
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 10 | 9 | 9 | 28 | 29 | 28 | 15 | 16 | 4 | 1 | [9 empty] | 145426
| Chandpur 115(Doreen) | [16 empty] | 4 | 46 | [7 empty] | 0 | 82560
| Kanchan Purbachal Power Generation Ltd. | [9 empty] | 11 | 17 | 17 | 28 | 30 |  |  | 25 | 36 |  | 36 | 36 | 36 | 17 |  |  | 0 | 289080
| Mirsharai 150 MW (Oil) | [16 empty] | 17 | 17 | [7 empty] | 0 | 31782
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 11 | 19 | 22 | 9 | 0 | 0 | 3 | 8 | 11 | 2 | 1 | 2 | 1 | 1 | 4 | 5 | 2 | 6 |  | 16 | 18 | 33 | 26 | 28 | 40 | 32 | 252960
| Sonagazi 75 MW Solar Plant | [6 empty] | 2 | 12 | 17 | 24 | 54 | 32 | 30 | 39 | 43 | 17 | 1 | [8 empty] | 0 | 249445
| Matarbari 2*600 MW (CPGCL) | 373 | 374 | 375 | 375 | 374 | 374 | 374 | 500 | 500 | 504 | 577 | 575 | 575 | 575 | 560 | 505 | 502 | 575 |  | 575 | 575 | 575 | 575 | 523 | 525 | 454 | 11818181
JERA Meghnaghat Power Limited
| Sreepur 150 MW | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3926400
120
121 | Eastern Zone Total | 4819 | 4607 | 4514 | 4373 | 4327 | 4513 | 4926 | 5307 | 5234 | 5096 | 5235 | 5424 | 5628 | 5429 | 5262 | 5309 | 5542 | 6296 |  | 6085 | 5990 | 5963 | 5732 | 5373 | 5297 | 4958 | 127511488
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 11 | 12 | 48 | 49 | 26 | 59 | 35 | 52 | 9 | 1 | [9 empty] | 277920
132 | Rampal 1320 MW (BIFPCL) | 805 | 808 | 760 | 755 | 718 | 730 | 724 | 802 | 1002 | 1010 | 1010 | 1228 | 1246 | 1060 | 1056 | 968 | 1063 | 1236 |  | 1240 | 1238 | 1240 | 1228 | 1094 | 1012 | 912 | 24007280
133 | United Payra Power Ltd. | [16 empty] | 30 | 54 | [7 empty] | 0 | 152400
| Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 180 | 180 | 220 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5166760
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | [22 empty] | 13 | 55 | 105 | 150 | 196000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2019
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 40 | 40 | 50 | 50 | 50 | 50 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1438000
141 | Bhola 33 MW PP (Venture) | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 4 | 4 | 3 | 3 | 4 | 4 | 3 | 3 | 5 | 6 |  | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 133180
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
| Bheramara HVDC | 923 | 734 | 642 | 640 | 640 | 640 | 734 | 923 | 923 | 923 | 917 | 917 | 917 | 917 | 918 | 917 | 917 | 918 |  | 920 | 921 | 920 | 921 | 921 | 921 | 920 | 20843636
147 | Nepal
148 | Bheramara 410 MW CCPP
149 | Payra 1320 MW
150
151 | Barapukuria TPP Unit-1
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 158 | 156 | 158 | 158 | 157 | 157 | 160 | 151 | 153 | 158 | 160 | 160 | 160 | 160 | 160 | 159 | 162 | 162 |  | 162 | 160 | 159 | 160 | 155 | 160 | 154 | 3875000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 3 | 4 | 4 | 4 | 3 | 2 | 0 | [10 empty] | 27180
157 | Sirajganj 68 MW Solar Park | [6 empty] | 0 | 7 | 9 | 43 | 50 | 52 | 50 | 40 | 24 | 9 | 1 | [9 empty] | 306752
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 144 | 214 | 214 | 214 | 214 | 214 | 214 | 180 | 185 | 214 | 170 | 180 |  | 214 | 214 | 214 | 214 | 214 | 194 | 170 | 4531000
Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 177 | 179 | 184 | 186 | 140 | 140 | 145 | 195 | 220 | 160 | 160 | 160 | 200 | 218 | 190 | 171 | 164 | 188 |  | 220 | 220 | 216 | 214 | 220 | 194 | 153 | 4701964
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
| Sirajgonj 225MW CCPP Unit-3 (Gas) | 175 | 175 | 165 | 130 | 130 | 130 | 133 | 172 | 220 | 220 | 220 | 220 | 220 | 180 | 162 | 169 | 164 | 187 |  | 220 | 220 | 220 | 220 | 220 | 198 | 150 | 4738445
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 146448
166 | Amnura 50 MW PP(Sinha)
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP
169 | Santahar 50 MW Peaking PP | [26 empty] | 0
170 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
171 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 98 |  | 98 | 42 | 42 |  |  |  | 0 | 223728
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
173 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [25 empty] | 0 | 0
178 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 3 | 4 | 4 | 5 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 29751
| Energypac Power Venture Thakurgaon Ltd. | [16 empty] | 34 | 35 | [7 empty] | 0 | 73564
| Intraco Solar 30 MW | [6 empty] | 0 | 5 | 14 | 21 | 26 | 28 | 26 | 21 | 15 | 6 | 1 | [9 empty] | 164309
178 | Adani Power Jharkhanda Ltd | 479 | 459 | 427 | 416 | 417 | 419 | 421 | 415 | 520 | 513 | 615 | 769 | 760 | 756 | 749 | 604 | 579 | 688 |  | 747 | 759 | 759 | 758 | 731 | 564 | 526 | 13990182
| Teesta Solar Limited | [6 empty] | 4 | 37 | 91 | 128 | 152 | 165 | 158 | 131 | 89 | 36 | 4 | [9 empty] | 990000
179 | Pabna Solar 100 MW | [6 empty] | 1 | 14 | 49 | 68 | 82 | 87 | 87 | 69 | 44 | 14 | 2 | [9 empty] | 517170
| Western Zone Total | 3089 | 2882 | 2717 | 2666 | 2583 | 2637 | 2763 | 3241 | 3725 | 3767 | 3916 | 4288 | 4399 | 4027 | 3901 | 3570 | 3547 | 4045 |  | 4120 | 4074 | 4070 | 4028 | 3910 | 3648 | 3432 | 86532688
[27 empty] | Total | 214044176