## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: October 2024
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2024-10-01 |  | 2024-09-01 |  | 2023-10-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 14677 | 2024-10-01 | 15717 | 2024-09-19 | 14356 | 2023-10-11 | 16477 | 2024-04-30
|  |  | 20:00 |  | 21:00 |  | 20:00 |  | 21:00
2 | Minimum Generation (MW) | 8574 | 2024-10-25 | 7847 | 2024-09-14 | 8008 | 2023-10-06 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 15717 | 2024-09-19 | 15717 | 2024-09-19 | 14356 | 2023-10-11 | 16477 | 2024-04-30
|  |  | 21:00 |  | 21:00 |  | 20:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 12738 | 2024-10-01 | 13785 | 2024-09-19 | 12530 | 2023-10-01 | 14488 | 2024-05-16
|  |  | 11:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 15200 | 2024-10-01 | 16300 | 2024-09-30 | 14470 | 2023-10-30 | 17200 | 2024-04-29
|  |  | 20:00 |  | 20:00 |  | 18:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 13360.3226 |  | 14156.9333 |  | 12963.6129 |  | - | -
7 | Average Generation (MW) at Day Peak | 11846.0323 |  | 12483.1 |  | 11283.7097 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 931 | 2024-10-30 | 910 | 2024-09-27 | 920 | 2023-10-11 | 970 | 2024-07-06
|  |  | 0:30 |  | 15:30 |  | 4:30 |  | 14:30
9 | Maximum Power Import from Tripura, India (MW) | 92 | 2024-10-19 | 104 | 2024-09-18 | 160 | 2023-10-01 | 194 | 12/06/19
|  |  | 13:00 |  | 14:30 |  | 15:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1301 | 2024-10-31 | 1973 | 2024-09-09 | 244 | 2023-10-12 | 4395 | 04/10/2022
|  |  | 21:00 |  | 21:00 |  | 19:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 12638 | 2024-10-31 | 14034 | 2024-09-09 | 13944 | 45211 | 14965 | 2024-05-16
|  |  | 21:00 |  | 21:00 | - | 0.8125 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2024-10-04 | 0 | 2024-09-14 | 0 | 45212 | - | -
|  |  | 21:00 |  | 20:00 |  | 20:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12218 | 2024-10-04 | 11456 | 2024-09-14 | 12852 | 2023-10-13 | - | -
|  |  | 21:00 |  | 20:00 |  | 20:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 760 | 2024-10-02 | 1749 | 2024-09-10 | 469 | 45222 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 12704 | 2024-10-02 | 12869 | 2024-09-10 | 11359 | 45222 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2024-10-04 | 0 | 2024-09-14 | 0 | 45212 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 10526 | 2024-10-04 | 10079 | 2024-09-14 | 10593 | 45212 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 23 |  | 26 |  | 17 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 22 |  | 26 |  | 8 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1472.1777 |  | 1362.8967 |  | 2096.5113 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 58.8403 |  | 56.005 |  | 34.051 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1413.3374 |  | 1306.8916 |  | 2062.4603 |  | - | -
23 | Net Generation of IPP (MKWH) | 2911.4144 |  | 3540.7158 |  | 2908.74 |  | - | -
23b | Net Generation by Generation Companies | 2897.3002 |  | 2703.457 |  | 2356.1995
24 | Net Generation of REB (MKWH) | 93.2436 |  | 80.3803 |  | 117.5706 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 131.2355 |  | 140.2199 |  | 198.4182 |  | - | -
25 | Total Net Generation (MKHWh) (Excluding Import) | 7446.531 |  | 7771.6647 |  | 7643.39 |  | - | -
26 | Energy Generation by Gas (MKWH) | 3827.7099 |  | 3600.4368 |  | 4134.9757 |  | - | -
27 | Energy Generation by Diesel (MKWH) | 21.0254 |  | 21.8892 |  | 47.9579 |  | - | -
28 | Energy Generation by Furnace Oil (MKWH) | 1145.4273 |  | 1317.2118 |  | 909.08 |  | - | -
29 | Energy Generation by Hydro (MKWH) | 143.6604 |  | 154.5809 |  | 134.4035 |  | - | -
30 | Energy Generation by Solar (MKWH) | 94.1464 |  | 92.3345 |  | 70.3503 |  | - | -
30b | Energy Generation by Wind (MKWH) | 4.2288 |  | 8.4058 |  | 2.0664 |  | - | -
31 | Energy Generation by Coal (MKWH) | 2269.173 |  | 2632.8107 |  | 2377.7026 |  | - | -
32 | Enegry Import from India (MKWH) | 1444.8078 |  | 1398.3326 |  | 723.4527 |  | - | -
33 | Monthly Load Factor (%) | 81.9637 |  | 81.5289 |  | 78.905 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: October 2024
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 14677 | 2024-10-01 | 20:00
Generation Period
| Dhaka | MW | 5247.96
| Chattogram | MW | 1330
| Cumilla | MW | 1309
| Mymensingh | MW | 1067
| Sylhet | MW | 570
a) | Total supply in East zone | MW | 9523.96
| Khulna | MW | 1726
| Barisal | MW | 497
| Rajshahi | MW | 1406.8
| Rangpur | MW | 943
b) | Total supply in West zone | MW | 4572.8
c) | Total supply in both zone ( a+b) | MW | 14096.76
Ref: | 27.21.0000.603.16.087.20.877 | Date: 19/11/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:October 2024
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 716 | 2024-10-15 | 6:00
| b) Ishurdi end | MW | 438 | 2024-10-20 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1142 | 2024-10-20 | 10:00
| b) Ishurdi end | MW | 74 | 2024-10-15 | 5:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0
| b) Ishurdi end | MKWH | 213.9351
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 207.5171
| b) Ishurdi end | MKWH | 0
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 300 | 2024-10-05 | 11:00
| b)Serajganj end | MW | 780 | 2024-10-27 | 9:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 410 | 2024-10-25 | 15:00
| b)Sirajganj end | MW | -270 | 2024-10-11 | 19:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0
| b)Sirajganj end | MKWH | 423.186
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 408.4052
| b)Sirajganj end | MKWH | 0
30 | Transmission loss of EWI /NO-2 | % | 3.493'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2760 | 2024-10-01 | 12:00
|  | MW | 1708
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2680 | 2024-10-01 | 12:00
|  | MW | 1690
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 34722 | 2024-10-01 | 12:00
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 34655 | 2024-10-01
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MKWH | 940.831
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MKWH | 937.907
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.311
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: October 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirzapur 132/33kV Grid Sub-Station | Transformer-01(E05) LT | 2024-10-04 03:57 | 2024-10-04 11:44 | 7:47 | E/O | Due to emergency maint.work at 33 kV feeder | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Tr-02 HT | 2024-10-04 13:13 | 2024-10-05 14:23 | 25:10 | T | Tripped showing . General trip . Diff Trip ( R & Y ph) relay | 0 | 0 | No interruption
Kamrangirchar 132/33kV Grid Sub-Station | GT-1 HT | 2024-10-06 05:05 | 2024-10-06 07:50 | 2:45 | T | Tripped showing PRD relays Due to PRD trip | 0 | 0 | No interruption
Kamrangirchar 132/33kV Grid Sub-Station | GT-1 HT | 2024-10-06 10:45 | 2024-10-06 11:45 | 1:00 | T | Tripped showing PRD relays Due to PRD trip | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 33 kV BUS | 2024-10-06 18:56 | 2024-10-06 19:47 | 0:51 | E/O | Due to emergency maint.work at 33 kV feeder | 70 | 59.5 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2024-10-07 09:54 | 2024-10-07 12:58 | 3:04 | E/O | Due to 33kv bus PT change by BPDB | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-10-07 12:40 | 2024-10-07 14:38 | 1:58 | E/O | Due to emergency maint.work by PBS | 25 | 49.1667 | Power interruption
Sreepur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-10-08 11:38 | 2024-10-08 13:36 | 1:58 | E/O | Due to Red hot remove | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 LT | 2024-10-10 09:57 | 2024-10-10 10:22 | 0:25 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2024-10-17 11:40 | 2024-10-17 12:14 | 0:34 | T | Due to 33kv Bhuapur (PDB) feeder. | 40 | 22.6667 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 LT | 2024-10-17 11:40 | 2024-10-17 12:14 | 0:34 | T | Due to 33kv Bhuapur (PDB) feeder. | 40 | 22.6667 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-10-19 18:12 | 2024-10-19 18:46 | 0:34 | E/O | Due to emergency maint.work at 33 kV feeder | 25 | 14.1667 | Power interruption
Mirzapur 132/33kV Grid Sub-Station | Transformer-01(E05) LT | 2024-10-20 13:31 | 2024-10-20 15:17 | 1:46 | E/O | Due to emergency maint.work at PBS | 20 | 35.3333 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2024-10-20 13:43 | 2024-10-20 14:43 | 1:00 | E/O | Due to emergency maint.work at 33 kV feeder | 48 | 48 | Power interruption
Sreepur 230/132kV Grid Sub-Station | T-1 HT | 2024-10-22 12:54 | 2024-10-22 22:19 | 9:25 | E/O | Due to emergency maint.work at 33 kV feeder | 52 | 489.6667 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) LT & 2 | 2024-10-23 14:59 | 2024-10-23 15:10 | 0:11 | T | Due to 33 kV feeder fault | 67 | 12.2833 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2024-10-24 09:20 | 2024-10-24 10:18 | 0:58 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Joydebpur132/33kV Grid Sub-Station | GT-4 HT | 2024-10-24 11:31 | 2024-10-24 11:42 | 0:11 | T | Tripped showing lockout relay | 30 | 5.5 | Power interruption
Joydebpur132/33kV Grid Sub-Station | GT-3 HT | 2024-10-24 15:07 | 2024-10-24 17:07 | 2:00 | T | Tripped showing AUX TRANS. PRESS. RELIEF TRIP Back up Protection trip relays. | 29 | 58 | Power interruption
|  |  | Total : | 62:11 |  | Unserved Energy: |  | 816.95
Dhaka (South) Grid Circle :
Srinagar 132/33kV Grid Sub-Station | Tr-01 HT | 2024-10-01 01:25 | 2024-10-01 01:25 | 0:00 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2024-10-01 19:52 | 2024-10-01 21:42 | 1:50 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2024-10-02 16:39 | 2024-10-02 20:08 | 3:29 | E/O | Due to red hot working in 132KV mi Cement DS | 0 | 0 | No interruption
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2024-10-03 10:28 | 2024-10-03 10:40 | 0:12 | T | Due to Over current | 80 | 16 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 | 2024-10-03 12:30 | 2024-10-03 12:39 | 0:09 | T | Tripped showing Overcurrent relay | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-3 (50/75 MVA) LT | 2024-10-04 20:12 | 2024-10-04 21:24 | 1:12 | E/O | Due to emergency maint.work | 60 | 72 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-10-06 05:04 | 2024-10-06 05:24 | 0:20 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | GT-2 LT | 2024-10-06 16:52 | 2024-10-06 19:13 | 2:21 | T | Due to 33 kV feeder fault | 5 | 11.75 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | GT-2 | 2024-10-09 11:21 | 2024-10-09 16:36 | 5:15 | E/O | Due to Oil Leakage Chaek | 0 | 0 | No interruption
Rampura 230/132/33kV Grid Sub-Station | Trafo HT | 2024-10-11 18:34 | 2024-10-11 18:42 | 0:08 | E/O | Due to Tap change | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-3 (50/75 MVA) HT | 2024-10-12 07:20 | 2024-10-12 08:41 | 1:21 | E/O | Due to emergency maint.work | 40 | 54 | Power interruption
Keraniganj 230/132kV Grid Sub-Station | TR-1 LT | 2024-10-13 10:20 | 2024-10-13 13:53 | 3:33 | E/O | Due to High temperature maintenance at various joint. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Main Bus Sec-2 | 2024-10-14 13:50 | 2024-10-14 19:45 | 5:55 | E/O | Due to Breaker problem. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | EGCB GT2 | 2024-10-14 07:10 | 2024-10-14 14:07 | 6:57 | E/O | Due to Oil leakage maintenance work. | 0 | 0 | No interruption
Keraniganj 230/132kV Grid Sub-Station | TR-1 LT | 2024-10-16 12:26 | 2024-10-16 12:26 | 0:00 | T | Tripped showing Over current relay at 33 kV | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-10-16 15:20 | 2024-10-16 15:51 | 0:31 | E/O | Oil leakage maintenance work. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-10-17 00:52 | 2024-10-17 01:10 | 0:18 | T | Tripped showing Trip relay MVAJ relays Due to PBS feeder | 33 | 9.9 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-10-20 03:10 | 2024-10-20 09:26 | 6:16 | T | Tripped showing LBB initiation, Diff. prot. optd. relays. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-10-20 03:10 | 2024-10-20 04:10 | 1:00 | T | Tripped showing LBB initiation relays Due to General trip | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-10-21 07:07 | 2024-10-21 07:23 | 0:16 | T | Due to 33 kV feeder fault | 37 | 9.8667 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-10-21 07:07 | 2024-10-21 07:24 | 0:17 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-10-23 12:16 | 2024-10-23 12:29 | 0:13 | T | Due to 33 kV feeder fault | 28 | 6.0667 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-10-23 12:16 | 2024-10-23 12:28 | 0:12 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-10-23 12:31 | 2024-10-23 13:05 | 0:34 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-10-23 12:31 | 2024-10-23 13:01 | 0:30 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Rampura 230/132/33kV Grid Sub-Station | Trafo HT | 2024-10-24 15:03 | 2024-10-24 15:16 | 0:13 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Rampura 230/132/33kV Grid Sub-Station | Trafo HT | 2024-10-24 16:58 | 2024-10-24 16:58 | 0:00 | T | Tripped showing E/F relay at 33 kV | 0 | 0 | No interruption
Rampura 230/132/33kV Grid Sub-Station | Trafo HT | 2024-10-24 17:20 | 2024-10-24 17:20 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bhulta132/33kV Grid Sub-Station | GT2 HT | 2024-10-25 07:07 | 2024-10-25 08:00 | 0:53 | E/O | Due to CT nut red hot | 20 | 17.6667 | Power interruption
Rampura 230/132kV Grid Sub-Station | Auto TR-1 LT | 2024-10-26 11:10 | 2024-10-26 12:12 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | TR-2 LT | 2024-10-26 17:45 | 2024-10-26 18:06 | 0:21 | T | Tripped showing Overcurrent protection relay | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-10-27 08:59 | 2024-10-27 12:20 | 3:21 | T | Tripped showing 1. 86 2. LBB initiation in RED670 relay | 0 | 0 | No interruption
|  |  | Total : | 48:39 |  | Unserved Energy: |  | 197.25
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | TR-2, 416T LT | 2024-10-01 01:19 | 2024-10-01 01:21 | 0:02 | E/O | Due to emergency maint.work | 24 | 0.8 | Power interruption
TK chemical 132/33kV Grid Sub-Station | 50/75 MVA T-1(405T) HT | 2024-10-02 10:45 | 2024-10-02 13:40 | 2:55 | E/O | Due to emergency maint.work | 1 | 2.9167 | Power interruption
Sikalbaha 230/132kV Grid Sub-Station | ATR 02 LT | 2024-10-04 09:18 | 2024-10-04 10:06 | 0:48 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
BSRM 230/132/33kV Grid Sub-Station | Transformer-2 (125/140 MVA) HT | 2024-10-05 09:07 | 2024-10-05 14:46 | 5:39 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Hathazari 230/132kV Grid Sub-Station | MT-03 LT | 2024-10-06 15:48 | 2024-10-06 17:46 | 1:58 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 405T (T1) LT | 2024-10-09 14:29 | 2024-10-09 14:38 | 0:09 | T | Due to 33 kV feeder fault | 54 | 8.1 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | 415T-T2 HT | 2024-10-11 10:33 | 2024-10-11 12:19 | 1:46 | T | Tripped showing Siemens relay | 50 | 88.3333 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | 415T-T2 HT | 2024-10-11 06:00 | 2024-10-11 07:06 | 1:06 | E/O | Due to 33 KV PDB Chakaria post insulator damaged. | 50 | 55 | Power interruption
Bakulia 132/33kV Grid Sub-Station | T-2 (412T) LT | 2024-10-13 06:08 | 2024-10-13 10:08 | 4:00 | T | Tripped showing no operatrd relay | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) LT | 2024-10-16 07:02 | 2024-10-16 07:02 | 0:00 | E/O | Due to Red Hot maintenance | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) LT | 2024-10-24 17:46 | 2024-10-24 18:53 | 1:07 | E/O | Due to emergency maint.by PDB | 30 | 33.5 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) HT | 2024-10-27 12:47 | 2024-10-27 14:00 | 1:13 | E/O | Due to Red Hot maintenance at 33 kV | 0 | 0 | No interruption
|  |  | Total : | 20:43 |  | Unserved Energy: |  | 188.65
Cumilla Grid Circle :
Sreemongol 132/33kV Grid Sub-Station | T-3 HT | 2024-10-01 13:18 | 2024-10-01 13:21 | 0:03 | T | Tripped showing Neutral Earth Fault relay | 20 | 1 | Power interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2024-10-01 20:36 | 2024-10-01 22:34 | 1:58 | E/O | Due to Red Hot maint.work | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | T-2 HT | 2024-10-02 17:17 | 2024-10-02 19:35 | 2:18 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | T-2 LT | 2024-10-03 11:36 | 2024-10-03 11:58 | 0:22 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2024-10-06 15:25 | 2024-10-06 22:26 | 7:01 | T | Tripped showing O/C relays Due to Fault of 33 KV feeder fault | 27 | 189.45 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2024-10-06 15:25 | 2024-10-06 16:01 | 0:36 | T | Tripped showing O/C relays Due to Fault of 33 KV feeder fault | 18 | 10.8 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2024-10-11 16:33 | 2024-10-11 16:40 | 0:07 | E/O | Due to emergency maint.work | 16 | 1.8667 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2-425T LT | 2024-10-20 08:32 | 2024-10-20 10:30 | 1:58 | E/O | Due to emergency maint.work at 33 kV | 25 | 49.1667 | Power interruption
Cumilla(S)132/33kV Grid Sub-Station | TR-1 LT | 2024-10-22 16:40 | 2024-10-22 18:06 | 1:26 | T | Due to 33 kV feeder fault | 42 | 60.2 | Power interruption
Cumilla(S)132/33kV Grid Sub-Station | TR-2 LT | 2024-10-22 16:40 | 2024-10-22 17:15 | 0:35 | T | Due to 33 kV feeder fault | 42 | 24.5 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2024-10-22 19:22 | 2024-10-22 19:36 | 0:14 | T | Tripped showing O/C, E/F relays | 80 | 18.6667 | Power interruption
Sylhet(S) 132/33kV Grid Sub-Station | Trafo-1 LT | 2024-10-24 17:40 | 2024-10-24 17:51 | 0:11 | E/O | Due to A monkey removed work from 33 kv bus side. | 18 | 3.3 | Power interruption
Sylhet(S) 132/33kV Grid Sub-Station | Trafo-2 LT | 2024-10-24 17:41 | 2024-10-24 17:51 | 0:10 | E/O | Due to A monkey removed work from 33 kv bus side. | 18 | 3 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-10-31 22:59 | 2024-10-31 23:07 | 0:08 | T | Tripped showing O/C, E/F relays | 30 | 4 | Power interruption
|  |  | Total : | 17:07 |  | Unserved Energy: |  | 365.95
Khulna Grid Circle :
Faridpur 230/132kV Grid Sub-Station | Transformer 02 | 2024-10-02 11:17 | 2024-10-02 11:17 | 0:00 | E/O | Due to DFDR & Commissioning work. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2024-10-02 11:33 | 2024-10-02 13:34 | 2:01 | E/O | Due to PBS 33 KV REDHOT FIXATION | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-10-02 22:28 | 2024-10-02 22:28 | 0:00 | T | Tripped showing Micom relays Due to Underground cable blast | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-10-04 17:14 | 2024-10-04 17:36 | 0:22 | T | Due to 33 kV feeder fault | 32 | 11.7333 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-10-04 17:14 | 2024-10-04 17:36 | 0:22 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-10-06 07:28 | 2024-10-06 09:09 | 1:41 | T | Due to High temperature | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2024-10-06 21:15 | 2024-10-06 22:03 | 0:48 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | (T-1) HT | 2024-10-06 13:15 | 2024-10-06 13:28 | 0:13 | E/O | Due to emergency maint.work | 9 | 1.95 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) | 2024-10-09 08:44 | 2024-10-09 10:05 | 1:21 | E/O | Due to emergency maint.work | 40 | 54 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2024-10-09 17:44 | 2024-10-09 17:53 | 0:09 | T | Tripped showing REF630 relays | 15 | 2.25 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2024-10-09 18:56 | 2024-10-09 19:01 | 0:05 | T | Due to 33 kV feeder fault | 11.5 | 0.95833 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-1 LT | 2024-10-09 18:56 | 2024-10-09 19:01 | 0:05 | T | Due to 33 kV feeder fault | 11.5 | 0.95833 | Power interruption
Barguna 132/33kV Grid Sub-Station | Tr-2(413T) HT | 2024-10-19 00:15 | 2024-10-19 01:10 | 0:55 | E/O | Due to emergency maint.work | 12 | 11 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-10-19 04:06 | 2024-10-19 04:11 | 0:05 | T | Due to 33 kV feeder fault | 28 | 2.3333 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-10-19 15:24 | 2024-10-19 15:47 | 0:23 | T | Due to 33 kV feeder fault | 15 | 5.75 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2024-10-19 15:24 | 2024-10-19 15:47 | 0:23 | T | Due to 33 kV feeder fault | 15 | 5.75 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2024-10-22 20:26 | 2024-10-22 21:43 | 1:17 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-10-23 13:10 | 2024-10-23 14:22 | 1:12 | T | Due to 33 kV feeder fault | 6 | 7.2 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2024-10-28 07:03 | 2024-10-28 08:30 | 1:27 | E/O | Due to emergency maint.work | 35 | 50.75 | Power interruption
Gallamari 132/33kV Grid Sub-Station | Tr-2 LT | 2024-10-30 15:20 | 2024-10-30 16:12 | 0:52 | E/O | Due to emergency maint.work at 33 kV | 1.5 | 1.3 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-10-31 00:12 | 2024-10-31 17:45 | 17:33 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
|  |  | Total : | 31:14 |  | Unserved Energy: |  | 155.9333
HVDC Grid Circle :
Ishurdi 132/33kV Grid Sub-Station | T-2 LT | 2024-10-01 12:15 | 2024-10-01 12:15 | 0:00 | T | Due to oil centrifugal work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | T-3 HT | 2024-10-01 13:21 | 2024-10-01 13:30 | 0:09 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-10-01 18:43 | 2024-10-01 19:40 | 0:57 | E/O | Due to Bushing red hot Maintenance 33kv site | 0 | 0 | No interruption
Baghabari 230/132 Grid Sub-Station | T-1 HT | 2024-10-04 20:18 | 2024-10-05 09:07 | 12:49 | T | Tripped showing ALSTOM,P 643 relays Due to Rain. | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-10-05 07:11 | 2024-10-05 08:48 | 1:37 | E/O | Due to Red hot maintenance at 33 kV | 8 | 12.9333 | Power interruption
Ishurdi 230/132kV Grid Sub-Station | T-01 HT | 2024-10-06 13:46 | 2024-10-06 17:44 | 3:58 | T | Due to Oil Temperature | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | T-2 LT | 2024-10-08 12:05 | 2024-10-08 13:02 | 0:57 | E/O | Due to Maligasa 33 kv Redhot | 20 | 19 | Power interruption
Jashore 132/33kV Grid Sub-Station | JH-2(L1) | 2024-10-09 19:15 | 2024-10-09 19:32 | 0:17 | T | Tripped showing Trip ABC , Phase -C ,Zone-1, D-6.7Km relays Due to Thandaring | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-2 LT | 2024-10-09 06:17 | 2024-10-09 07:27 | 1:10 | E/O | Due to emergency maint.work | 20 | 23.3333 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-10-10 10:11 | 2024-10-10 12:07 | 1:56 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-03 LT | 2024-10-13 19:36 | 2024-10-14 12:54 | 17:18 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2024-10-16 13:24 | 2024-10-16 13:54 | 0:30 | T | Due to PBS feeder fault | 37 | 18.5 | Power interruption
Jashore 132/33kV Grid Sub-Station | JH-1(L2) | 2024-10-16 16:35 | 2024-10-16 16:35 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2024-10-16 17:36 | 2024-10-16 17:56 | 0:20 | T | Due to PBS feeder fault | 38 | 12.6667 | Power interruption
BIPTC | 10CF15 | 2024-10-20 11:42 | 2024-10-20 12:56 | 1:14 | T | Tripped showing 87.1 relays Due to C1 unbalance 60/61 instant L2 trip | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-10-24 10:04 | 2024-10-24 11:15 | 1:11 | E/O | Due to Red hot maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | T-1 LT | 2024-10-27 11:13 | 2024-10-27 14:04 | 2:51 | E/O | Due to 33 kv CT oil leakage maintenance | 0 | 0 | No interruption
|  |  | Total : | 47:14 |  | Unserved Energy: |  | 86.4333
Bogura Grid Circle:
Saidpur 132/33kV Grid Sub-Station | TR-5 (434T) LT | 2024-10-04 06:30 | 2024-10-04 08:29 | 1:59 | E/O | Due to High temperature at 33kv VCB Y-phase | 25 | 49.5833 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-10-04 07:13 | 2024-10-04 13:11 | 5:58 | E/O | Due to Red-Hot Maintenance Work | 15 | 89.5 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) LT | 2024-10-05 19:16 | 2024-10-05 19:33 | 0:17 | T | Due to 33kv feeder fault | 15 | 4.25 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) LT | 2024-10-06 18:28 | 2024-10-06 18:32 | 0:04 | T | Due to 33kv feeder fault | 15 | 1 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-5 (434T) LT | 2024-10-07 20:13 | 2024-10-07 21:49 | 1:36 | E/O | Due to emergency maint.work at 33 kV | 25 | 40 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2024-10-08 08:40 | 2024-10-08 09:23 | 0:43 | E/O | Due to Red hot maintenance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) LT | 2024-10-09 06:43 | 2024-10-09 06:43 | 0:00 | E/O | Due to emergency maint.work at 33 kV | 25 | 0 | Power interruption
Bogura -Sherpur132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2024-10-12 06:50 | 2024-10-12 09:49 | 2:59 | E/O | Due to Red hot maintenance | 28 | 83.5333 | Power interruption
Bogura -Sherpur132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2024-10-12 11:17 | 2024-10-12 14:11 | 2:54 | E/O | Due to Red hot maintenance | 6 | 17.4 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2024-10-12 11:22 | 2024-10-12 11:42 | 0:20 | T | Tripped showing E/F Instt relays Due to 33kv NPBS Feeder LA B-ph baust. | 16 | 5.3333 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2024-10-13 17:03 | 2024-10-13 17:17 | 0:14 | T | Tripped showing Instt.E/E relay at 33 kV | 23 | 5.3667 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2024-10-13 17:03 | 2024-10-13 17:15 | 0:12 | T | Tripped showing Instt.E/E relay at 33 kV | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2024-10-14 12:06 | 2024-10-14 13:19 | 1:13 | T | Due to 33kv feeder fault | 15 | 18.25 | Power interruption
Sirajganj132/33kV Grid Sub-Station | T4-(445) HT | 2024-10-18 09:18 | 2024-10-18 11:17 | 1:59 | E/O | Due to emergency maint.work of PBS | 0 | 0 | No interruption
Sirajganj132/33kV Grid Sub-Station | T3-(435) HT | 2024-10-18 16:25 | 2024-10-18 16:58 | 0:33 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Sirajganj132/33kV Grid Sub-Station | T4-(445) LT | 2024-10-18 16:25 | 2024-10-18 16:59 | 0:34 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Sirajganj132/33kV Grid Sub-Station | T4-(445) LT | 2024-10-19 11:16 | 2024-10-19 18:08 | 6:52 | E/O | Due to Tarash 33 kv Feeder damage CT (Y Phase) Replacement | 0 | 0 | No interruption
Mithapukur132/33kV Grid Sub-Station | TR-2 (414T) HT | 2024-10-22 17:56 | 2024-10-23 13:39 | 19:43 | T | Tripped showing 86A Relay & 86B Relay Operated. | 0 | 0 | No interruption
Mithapukur132/33kV Grid Sub-Station | TR-1(404T) LT | 2024-10-22 17:56 | 2024-10-22 18:23 | 0:27 | T | Tripped showing 86A Relay & 86B Relay Operated. | 48 | 21.6 | Power interruption
Mithapukur132/33kV Grid Sub-Station | TR-1(404T) LT | 2024-10-24 10:59 | 2024-10-24 13:26 | 2:27 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 51:04 |  | Unserved Energy: |  | 335.8167
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 278:12 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: October 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV Grid Sub-Station | BR Powergen Ckt- 01 | 2024-10-02 03:13 | 2024-10-02 04:03 | 0:50 | T | Tripped showing Distance (RY)-Phase, zone-1 relays. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | BR Powergen Ckt- 01 | 2024-10-02 03:13 | 2024-10-02 04:18 | 1:05 | T | Tripped showing Distance (RY)-Phase, zone-1 relays. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2024-10-04 02:58 | 2024-10-04 02:58 | 0:00 | T | Tripped showing REL 670 REF 615 relays Due to bad weather | 0 | 0 | No interruption
Mirzapur 132/33kV Grid Sub-Station | Tangail-ckt-2A(E04 | 2024-10-04 02:59 | 2024-10-04 03:13 | 0:14 | T | Tripped showing TRIP RELAY OPTD ( 86.1/86.2/96) relay | 0 | 0 | No interruption
Mirzapur 132/33kV Grid Sub-Station | Tangail-ckt-2B(E03) | 2024-10-04 02:59 | 2024-10-04 03:13 | 0:14 | T | Tripped showing TRIP RELAY OPTD ( 86.1/86.2/96) relay | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur Ckt- 02 | 2024-10-04 07:39 | 2024-10-04 07:56 | 0:17 | T | Due to Over current | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi -132kV Ckt-2 | 2024-10-04 10:24 | 2024-10-04 11:34 | 1:10 | T | Tripped showing Distance relay. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj-1 | 2024-10-08 08:25 | 2024-10-08 08:45 | 0:20 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj-2 | 2024-10-08 08:45 | 2024-10-08 09:17 | 0:32 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-1 | 2024-10-09 07:57 | 2024-10-09 15:48 | 7:51 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ghatail 132/33kV Grid Sub-Station | GH- RPCL both Ckt | 2024-10-09 15:43 | 2024-10-09 15:53 | 0:10 | T | Tripped showing Distance relay. | 228 | 38 | Power interruption
Mymensingh RPCL | Tangail 132kV Ckt-1 | 2024-10-09 15:41 | 2024-10-09 15:53 | 0:12 | T | Tripped showing REL 650, REL 670 relays. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur Ckt- 02 & 1 | 2024-10-18 18:41 | 2024-10-18 19:13 | 0:32 | T | Tripped showing Over current relay | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi 132kV Ckt-1 | 2024-10-23 13:59 | 2024-10-23 14:26 | 0:27 | E/O | Tripped showing Distance relay. | 0 | 0 | No interruption
|  |  | Total : | 13:54 |  | Unserved Energy: |  | 38
Dhaka (South) Grid Circle :
Gulsan 132/33kV Grid Sub-Station | Rampura 132kV Ckt-2 | 2024-10-02 06:42 | 2024-10-02 07:34 | 0:52 | T | Tripped showing Dic O/C relay | 0 | 0 | No interruption
Rampura 230/132/33kV Grid Sub-Station | Gulshan 132 kV line-2 | 2024-10-02 06:50 | 2024-10-02 07:35 | 0:45 | T | Tripped showing Dic O/C relay | 40 | 30 | Power interruption
Rampura 230/132/33kV Grid Sub-Station | Bashundhara ckt-2 | 2024-10-02 09:14 | 2024-10-02 09:22 | 0:08 | T | Tripped showing distance (zone-1, B phase) relay. | 0 | 0 | No interruption
Haripur 230/132/33kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-10-02 19:51 | 2024-10-02 20:40 | 0:49 | T | Tripped showing Distance Z-1, R Phase. relay | 0 | 0 | No interruption
Sitalakhya 132/33kV Grid Sub-Station | Hasnabad-1 | 2024-10-04 10:07 | 2024-10-04 15:41 | 5:34 | T | Tripped showing gen. trip,Zone-1,R-phase relay | 118 | 656.8667 | Power interruption
Hasnabad 132/33kV Grid Sub-Station | Sitalakhya 132kV Ckt-1 | 2024-10-04 13:34 | 2024-10-04 15:36 | 2:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Shitalakhya 132 kv Ckt | 2024-10-04 23:33 | 2024-10-04 23:33 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Haripur 230/132/33kV Grid Sub-Station | Madanganj-1 | 2024-10-15 22:10 | 2024-10-16 08:36 | 10:26 | T | Tripped Main protection trip relay | 27 | 281.7 | Power interruption
Meghnaghat 230/132kV Grid Sub-Station | Shyampur 230kV Ckt-2 | 2024-10-16 07:34 | 2024-10-16 11:53 | 4:19 | E/O | Due to emergency maint.work | 120 | 518 | Power interruption
Madanganj 132/33kV Grid Sub-Station | Shitalakhya 132 kv Ckt | 2024-10-17 13:40 | 2024-10-17 13:40 | 0:00 | E/O | Due to Shitalakhya-Hasnabad ckt overload | 0 | 0 | No interruption
Haripur 230/132/33kV Grid Sub-Station | Siddirganj 132kV Ckt-1 | 2024-10-20 03:10 | 2024-10-20 03:33 | 0:23 | T | Tripped showing OC/EF, CN. Relays | 0 | 0 | No interruption
Haripur 230/132/33kV Grid Sub-Station | Siddirganj 132kV Ckt-2 | 2024-10-20 03:12 | 2024-10-20 03:33 | 0:21 | T | Tripped showing OC/EF. CN relays | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bashundhara-1 | 2024-10-22 13:04 | 2024-10-22 13:17 | 0:13 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | Shyampur(New) 132 kV Ckt-1 | 2024-10-23 12:54 | 2024-10-23 14:36 | 1:42 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Haripur 230/132/33kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-10-24 14:30 | 2024-10-24 16:18 | 1:48 | T | Tripped showing Distance relay. | 20 | 36 | Power interruption
Ghorashal 230/132/33kV Grid Sub-Station | Ishwardi 230 kV Ckt-1 | 2024-10-27 08:42 | 2024-10-27 11:10 | 2:28 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Haripur 230/132/33kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-10-27 08:59 | 2024-10-27 14:41 | 5:42 | T | Tripped showing MiCOM P441: PH Y, Z 2. relays. | 15 | 85.5 | Power interruption
|  |  | Total : | 37:32 |  | Unserved Energy: |  | 1608.0667
Chattogram Grid Circle :
BSRM 230/33kV Grid Sub-Station | 230 kV GPH-2 | 2024-10-01 10:20 | 2024-10-01 10:59 | 0:39 | E/O | Tripped showing 21.1 Relay OPTD OPTD 86.1 Trip relay | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | 230 kV GPH-1 | 2024-10-01 10:21 | 2024-10-01 11:00 | 0:39 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Shikalbaha 230/33kV Grid Sub-Station | Intermediate-2 | 2024-10-04 11:29 | 2024-10-04 14:46 | 3:17 | T | Tripped showing FN-1 and FN-2 relays. | 0 | 0 | No interruption
Shikalbaha 230/33kV Grid Sub-Station | Intermediate-2 | 2024-10-06 23:28 | 2024-10-06 23:43 | 0:15 | T | Tripped showing FN-1 & FN-2 relays. | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-2 | 2024-10-07 11:19 | 2024-10-07 11:56 | 0:37 | T | Tripped showing REL-670 relay | 0 | 0 | No interruption
Cox'sbazar 132/33kV Grid Sub-Station | Dohazari 132 kV Ckt-2 | 2024-10-23 18:39 | 2024-10-23 18:57 | 0:18 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hathazari 132 kV Ckt-1 | 2024-10-26 07:06 | 2024-10-26 09:03 | 1:57 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Cox'sbazar 132/33kV Grid Sub-Station | Dohazari 132 kV Ckt-1 | 2024-10-28 10:48 | 2024-10-28 10:57 | 0:09 | T | Tripped showing Distance relay | 30 | 4.5 | Power interruption
|  |  | Total : | 7:51 |  | Unserved Energy: |  | 4.5
Cumilla Grid Circle :
Cumilla(N) 230/132kV Grid Sub-Station | Daudkandi 132 kV Ckt-2 | 2024-10-02 05:52 | 2024-10-02 07:59 | 2:07 | T | Due to Red hot remove maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Daudkandi 132 kV Ckt-1 | 2024-10-02 08:30 | 2024-10-02 10:24 | 1:54 | E/O | Due to Red hot remove maintenance work. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni 132 kV Ckt-2 | 2024-10-05 11:34 | 2024-10-05 11:43 | 0:09 | T | Tripped showing Distance relay | 22 | 3.3 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon 132 kV Ckt-2 | 2024-10-06 12:07 | 2024-10-06 17:40 | 5:33 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Kachua 132 kV Ckt-1 | 2024-10-06 10:27 | 2024-10-06 12:00 | 1:33 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Shahjibazar 132 kV Ckt-2 | 2024-10-06 23:01 | 2024-10-07 19:44 | 20:43 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Brahmanbaria-2 | 2024-10-10 06:15 | 2024-10-10 06:15 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj 132 kV Ckt-1 & 2 | 2024-10-11 09:07 | 2024-10-11 11:03 | 1:56 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Shahjibazar 230 kV Ckt-1 | 2024-10-12 06:53 | 2024-10-12 21:37 | 14:44 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Feni 132 kV Ckt-2 | 2024-10-13 12:29 | 2024-10-13 12:29 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Kachua 132 kV Ckt-1 | 2024-10-18 15:17 | 2024-10-18 15:42 | 0:25 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Fenchuganj 132/33kV Grid Sub-Station | Sreemangal 132kV Ckt-2 | 2024-10-18 07:51 | 2024-10-18 08:03 | 0:12 | T | Tripped showing Distance relay | 40 | 8 | Power interruption
Chnadpur 132/33kV Grid Sub-Station | 115MW CPGL Power Plant Incomer (L5) | 2024-10-30 08:36 | 2024-10-30 09:20 | 0:44 | T | Tripped showing Line protection relay | 0 | 0 | No interruption
|  |  | Total : | 50:00 |  | Unserved Energy: |  | 11.3
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Bhandaria-1 | 2024-10-01 14:01 | 2024-10-01 14:36 | 0:35 | T | Tripeed showing S E relays Due o Unknown. Stormy weather exists. | 0 | 0 | No interruption
Gopalganj 400/230/132 kV Grid Sub-Station | 230kV Faridpur CKT-02 | 2024-10-02 11:34 | 2024-10-02 23:00 | 11:26 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Bhandaria-1 | 2024-10-02 16:24 | 2024-10-02 16:51 | 0:27 | T | Tripped showing Over current relay | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | Bhandaria 132 kV Ckt-1 | 2024-10-03 02:58 | 2024-10-03 03:12 | 0:14 | T | Tripped showing E/F relay | 40 | 9.3333 | Power interruption
Barishal 230/132kV Grid Sub-Station | Bhola 230 kV Ckt-2 | 2024-10-06 13:13 | 2024-10-06 13:13 | 0:00 | T | Tripped showing Distance Relay | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Bhola 230 kV Ckt-1 | 2024-10-06 13:13 | 2024-10-06 13:41 | 0:28 | T | Tripped showing Distance relay | 140 | 65.3333 | Power interruption
Barishal 230/132kV Grid Sub-Station | Bhola 230 KV ckt-1 | 2024-10-06 13:13 | 2024-10-06 13:35 | 0:22 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Bhola 230 KV ckt-2 | 2024-10-06 13:13 | 2024-10-06 13:40 | 0:27 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Bhandaria-1 | 2024-10-09 13:48 | 2024-10-09 14:08 | 0:20 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Goalpara 132 kV Ckt-1 | 2024-10-09 15:53 | 2024-10-09 16:05 | 0:12 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | Barishal(N) 132 kV Ckt-1 | 2024-10-17 17:04 | 2024-10-17 17:57 | 0:53 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Gopalganj(N) 132 kV Ckt-2 | 2024-10-20 12:45 | 2024-10-20 13:50 | 1:05 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 kV Rajbari ckt-2 | 2024-10-20 12:45 | 2024-10-20 17:25 | 4:40 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 kV Rajbari ckt-2 | 2024-10-20 13:05 | 2024-10-20 17:25 | 4:20 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | Bhandaria 132 kV Ckt-1 | 2024-10-27 10:33 | 2024-10-27 10:38 | 0:05 | T | Tripped showing Distance relay | 29 | 2.4167 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Bhandaria 132 kV Ckt-1 | 2024-10-27 11:49 | 2024-10-27 12:10 | 0:21 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bhandaria 132 kV Ckt-1 | 2024-10-27 12:19 | 2024-10-27 14:14 | 1:55 | T | Tripped showing Distance relay | 0 | 0 | No interruption
|  |  | Total : | 27:50 |  | Unserved Energy: |  | 77.0833
HVDC Grid Circle :
Jhenaidah 132/33kV Grid Sub-Station | Magura 132 kV Ckt-2 | 2024-10-01 14:08 | 2024-10-01 14:27 | 0:19 | E/O | Tripped showing Distance relay. | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | Baghabari-1 | 2024-10-03 03:06 | 2024-10-03 03:52 | 0:46 | T | Tripped showing distance protection relay, earth fault O/C relay | 0 | 0 | No interruption
HVDC Bheramera | Jhenaidah 230kV Ckt-2 | 2024-10-03 06:26 | 2024-10-03 07:03 | 0:37 | T | Tripped showing Distance Zone-1 relay | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jashore Ckt-2 | 2024-10-17 08:33 | 2024-10-17 14:56 | 6:23 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
BIPTC | Baharampur-2 | 2024-10-29 20:20 | 2024-10-29 23:54 | 3:34 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
|  |  | Total : | 11:39 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura(new) 132/33kV Grid Sub-Station | Bogura(Sherpur) 132 kV Ckt-2 | 2024-10-01 07:37 | 2024-10-01 08:57 | 1:20 | E/O | Due to red hot maintenance work | 0 | 0 | No interruption
Bogura(new) 132/33kV Grid Sub-Station | Bogura(Sherpur) 132 kV Ckt-2 | 2024-10-01 15:12 | 2024-10-01 18:11 | 2:59 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 2024-10-02 09:40 | 2024-10-02 09:40 | 0:00 | T | Tripped showing 67 67N 50 50N relays Due to Fault | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullahpara 132KV Ckt-1 | 2024-10-03 03:44 | 2024-10-03 04:30 | 0:46 | T | showing Distance Relay (21): Quadramho SHPM-101 relays. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullahpara 132KV Ckt-2 | 2024-10-03 03:44 | 2024-10-03 04:30 | 0:46 | T | showing Distance Relay (21): Quadramho SHPM-101 relays. | 0 | 0 | No interruption
Bogura(New)-132/33kV Grid Sub-Station | Bogura(Sherpur) 132 kV Ckt-2 | 2024-10-09 07:35 | 2024-10-09 16:18 | 8:43 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Sherpur(Bogura) 132/33kV Grid Sub-Station | 132 kV Sirajganj -1 | 2024-10-09 13:30 | 2024-10-10 17:36 | 28:06 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Sherpur(Bogura) 132/33kV Grid Sub-Station | 132 kV Sirajganj -2 | 2024-10-14 14:30 | 2024-10-14 17:53 | 3:23 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Sherpur(Bogura) 132/33kV Grid Sub-Station | 132 kV Sirajganj -1 | 2024-10-14 14:30 | 2024-10-14 15:35 | 1:05 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Bogura 230/132/kV Grid Sub-Station | Bogura (W) CKT-2 | 2024-10-21 18:43 | 2024-10-22 16:08 | 21:25 | E/O | Due to CVT Secondery Voltage Problem. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi 132kV Ckt-2 | 2024-10-22 14:39 | 2024-10-22 16:21 | 1:42 | E/O | Due to CB Test | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | Bogura 230 kV Ckt-2 & 1 | 2024-10-29 07:11 | 2024-10-29 07:11 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
|  |  | Total : | 70:15 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 219:01 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: October 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydebpur 230/132kV Grid Sub-Station | GT-4 LT | 2024-10-02 14:57 | 2024-10-02 16:11 | 1:14 | S/O | Due to replacement work | 25 | 30.8333 | Power interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-10-03 09:39 | 2024-10-03 09:39 | 0:00 | S/O | Due to For DPBS-3 maintenance work. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2024-10-04 08:16 | 2024-10-04 10:39 | 2:23 | S/O | Due to Fixing Breather Problem. | 0 | 0 | No interruption
Zigatola 132/33kV Grid Sub-Station | GT-2 HT | 2024-10-04 08:34 | 2024-10-04 14:18 | 5:44 | S/O | Due to Yearly Maintenance. | 0 | 0 | No interruption
Mirzapur 132/33kV Grid Sub-Station | Transformer-01(E05) LT | 2024-10-05 09:16 | 2024-10-05 15:56 | 6:40 | S/O | Project Work at 33 kV side | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-1 HT | 2024-10-06 07:59 | 2024-10-06 09:13 | 1:14 | S/O | Due to Transformer Oil filing | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2024-10-07 11:38 | 2024-10-07 17:58 | 6:20 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2024-10-08 11:10 | 2024-10-08 11:38 | 0:28 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-10-09 06:16 | 2024-10-09 07:23 | 1:07 | S/O | Due to 33kv Incoming DS temperature high | 30 | 33.5 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-10-09 07:25 | 2024-10-09 08:40 | 1:15 | S/O | Due to 33kv Incoming DS temperature high | 30 | 37.5 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2024-10-09 09:48 | 2024-10-09 12:56 | 3:08 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2024-10-14 20:22 | 2024-10-14 20:22 | 0:00 | S/O | Due to Red-hot Maintenance of 33kV Bypass feeder | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-4 (50/75 MVA) LT | 2024-10-15 09:51 | 2024-10-15 12:58 | 3:07 | S/O | Maintenance work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-3 (50/75 MVA) LT | 2024-10-15 13:03 | 2024-10-15 13:20 | 0:17 | S/O | Maintenance work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-2(35/50 MVA) HT | 2024-10-15 13:32 | 2024-10-15 14:56 | 1:24 | S/O | Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Tr-03 LT | 2024-10-16 07:39 | 2024-10-16 09:00 | 1:21 | S/O | Due to Red hot maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 LT | 2024-10-19 06:35 | 2024-10-19 08:05 | 1:30 | S/O | Maintenance work | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2024-10-20 22:18 | 2024-10-20 23:04 | 0:46 | S/O | Maintenance work | 35 | 26.8333 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2024-10-21 07:13 | 2024-10-21 17:06 | 9:53 | S/O | Project Work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-10-21 07:30 | 2024-10-21 17:08 | 9:38 | S/O | Project Work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2024-10-21 07:50 | 2024-10-21 09:15 | 1:25 | S/O | Maintenance work | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-3 HT | 2024-10-21 11:34 | 2024-10-21 14:06 | 2:32 | S/O | Due to Relay Testing by SPMD-2 | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | STR-2 LT | 2024-10-21 14:14 | 2024-10-21 15:02 | 0:48 | S/O | Due to Relay Testing by SPMD-2 | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-2 HT | 2024-10-21 14:25 | 2024-10-21 15:01 | 0:36 | S/O | Due to Relay Testing by SPMD-2 | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-1 HT | 2024-10-21 15:04 | 2024-10-21 15:51 | 0:47 | S/O | Due to Relay Testing by SPMD-2 | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2024-10-22 08:20 | 2024-10-22 15:34 | 7:14 | S/O | Due to Development work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-10-22 08:38 | 2024-10-22 15:39 | 7:01 | S/O | Due to Development work | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 LT | 2024-10-22 10:48 | 2024-10-22 11:13 | 0:25 | S/O | Due to Y-Phase cable maintenance | 30 | 12.5 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2024-10-24 06:47 | 2024-10-24 07:31 | 0:44 | S/O | Maintenance work | 28 | 20.5333 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 LT | 2024-10-24 08:28 | 2024-10-24 16:16 | 7:48 | S/O | Due to Development work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2024-10-24 08:39 | 2024-10-24 16:30 | 7:51 | S/O | Due to Development work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Bus-A | 2024-10-24 08:55 | 2024-10-24 11:48 | 2:53 | S/O | Project Work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | BUS-B | 2024-10-24 12:00 | 2024-10-24 12:59 | 0:59 | S/O | Project Work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2024-10-25 06:35 | 2024-10-25 12:20 | 5:45 | S/O | Project Work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-3 (50/75 MVA) LT | 2024-10-25 07:06 | 2024-10-25 08:27 | 1:21 | S/O | Maintenance work by Pbs | 25 | 33.75 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 LT | 2024-10-25 08:11 | 2024-10-25 17:22 | 9:11 | S/O | Project Work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2024-10-25 08:20 | 2024-10-25 17:26 | 9:06 | S/O | Project Work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | BUS-B | 2024-10-25 10:19 | 2024-10-25 12:09 | 1:50 | S/O | Project Work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 HT | 2024-10-26 08:16 | 2024-10-26 17:13 | 8:57 | S/O | Due to Development work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 LT | 2024-10-26 08:16 | 2024-10-26 17:10 | 8:54 | S/O | Project Work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-10-26 08:20 | 2024-10-26 08:20 | 0:00 | S/O | Due to Development work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-10-26 08:20 | 2024-10-27 16:28 | 32:08 | S/O | Due to Development work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-10-26 08:44 | 2024-10-26 12:59 | 4:15 | S/O | Maintenance work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2024-10-27 08:20 | 2024-10-27 16:25 | 8:05 | S/O | Project Work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-10-27 08:27 | 2024-10-27 16:27 | 8:00 | S/O | Project Work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-10-27 09:31 | 2024-10-27 17:27 | 7:56 | S/O | Maintenance work | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2024-10-27 15:21 | 2024-10-27 16:47 | 1:26 | S/O | Maintenance work | 12 | 17.2 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-10-28 07:13 | 2024-10-28 07:55 | 0:42 | S/O | Due to Relay Test Works. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 HT | 2024-10-28 07:18 | 2024-10-28 09:01 | 1:43 | S/O | Due to Relay Test Works. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-10-28 08:08 | 2024-10-28 14:39 | 6:31 | S/O | Due to Development work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 HT | 2024-10-28 08:29 | 2024-10-28 16:53 | 8:24 | S/O | Due to Development work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2024-10-28 08:34 | 2024-10-28 15:51 | 7:17 | S/O | Due to New T2 Loop connection (33kv Side) | 10 | 72.8333 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2024-10-28 12:57 | 2024-10-28 16:35 | 3:38 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2024-10-28 15:43 | 2024-10-28 16:21 | 0:38 | S/O | Due to Relay tested by SPMD. | 25 | 15.8333 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2024-10-28 16:37 | 2024-10-28 17:40 | 1:03 | S/O | Due to Relay tested by SPMD. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) LT | 2024-10-29 09:20 | 2024-10-29 16:12 | 6:52 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-10-30 07:50 | 2024-10-30 10:49 | 2:59 | S/O | Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-10-30 10:12 | 2024-10-30 17:20 | 7:08 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-10-30 08:50 | 2024-10-30 16:46 | 7:56 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
|  |  | Total : | 260:17 |  | Unserved Energy: |  | 301.3167
Dhaka (South) Grid Circle :
Rampura 230/132kV Grid Sub-Station | Busbar-1 | 2024-10-05 08:42 | 2024-10-05 15:29 | 6:47 | S/O | Due to Project work. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-10-06 08:47 | 2024-10-06 10:03 | 1:16 | S/O | Maintenance work at 33 kV | 40 | 50.6667 | Power interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 2024-10-13 07:20 | 2024-10-13 09:20 | 2:00 | S/O | Due to Relay testing (G2G project work) | 0 | 0 | No interruption
Keraniganj 230/132kV Grid Sub-Station | TR-1 | 2024-10-14 11:29 | 2024-10-14 11:36 | 0:07 | S/O | Maintenance work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bus Coupler | 2024-10-14 16:38 | 2024-10-14 19:45 | 3:07 | S/O | Maintenance work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-1 | 2024-10-16 11:55 | 2024-10-16 17:05 | 5:10 | S/O | Project Work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-2 | 2024-10-17 12:27 | 2024-10-17 20:07 | 7:40 | S/O | Project Work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2024-10-18 04:23 | 2024-10-18 10:37 | 6:14 | S/O | Project Work | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-10-22 09:05 | 2024-10-22 21:56 | 12:51 | S/O | Due to Protection relay change. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 2024-10-25 03:21 | 2024-10-25 12:37 | 9:16 | S/O | Project Work | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 2024-10-25 09:05 | 2024-10-25 10:50 | 1:45 | S/O | Maintenance work at 33 kV | 24 | 42 | Power interruption
Rampura 230/132kV Grid Sub-Station | Transformer - 04 LT | 2024-10-26 03:06 | 2024-10-26 06:45 | 3:39 | S/O | Project Work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | ATR-01 (706T) HT | 2024-10-27 06:55 | 2024-10-27 06:55 | 0:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | ATR-02 (716T) HT | 2024-10-28 07:06 | 2024-10-28 07:06 | 0:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 HT | 2024-10-29 08:23 | 2024-10-29 14:40 | 6:17 | S/O | Maintenance work | 45 | 282.75 | Power interruption
Narsingdi 132/33kV Grid Sub-Station | 132 kV Main Bus-2 | 2024-10-29 16:06 | 2024-10-29 18:16 | 2:10 | S/O | Project Work | 0 | 0 | No interruption
Narsingdi 132/33kV Grid Sub-Station | Main Bus-1 | 2024-10-30 06:28 | 2024-10-30 16:20 | 9:52 | S/O | Project Work | 0 | 0 | No interruption
|  |  | Total : | 78:11 |  | Unserved Energy: |  | 375.4167
Chattogram Grid Circle :
Chandraghona 132/33kV Grid Sub-Station | TR-02(416T) LT | 2024-10-03 07:50 | 2024-10-03 11:57 | 4:07 | S/O | Due to Red hot maintenance | 0 | 0 | No interruption
KSRM 230/132/33kV Grid Sub-Station | Transformer-01 HT | 2024-10-07 10:23 | 2024-10-07 12:54 | 2:31 | S/O | Due to loop change secondary | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 LT | 2024-10-08 06:11 | 2024-10-08 10:22 | 4:11 | S/O | Due to Red hot maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-02 LT | 2024-10-09 06:18 | 2024-10-09 06:18 | 0:00 | S/O | Due to 33kv bus maintenance by PDB | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 LT | 2024-10-09 06:18 | 2024-10-09 06:18 | 0:00 | S/O | Due to 33kv bus maintenance by PDB | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | 415T-T2 HT | 2024-10-13 06:27 | 2024-10-13 08:14 | 1:47 | S/O | Due to PDB Chakaria 33 kV breaker maintenance | 45 | 80.25 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | MAIN BUS-01 | 2024-10-14 06:04 | 2024-10-14 06:04 | 0:00 | S/O | Due to Red hot maintenance. | 0 | 0 | No interruption
GPS 230/132/33kV Grid Sub-Station | Transformer-01(D05) HT | 2024-10-14 07:04 | 2024-10-14 10:07 | 3:03 | S/O | Maintenance work | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-02 HT | 2024-10-17 22:30 | 2024-10-20 16:32 | 66:02 | S/O | Due to MT -02 oil centrifuging | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 230 KV Bus-1 | 2024-10-23 09:04 | 2024-10-23 09:04 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-02 LT | 2024-10-24 07:21 | 2024-10-24 08:25 | 1:04 | S/O | Maintenance work | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2024-10-24 08:50 | 2024-10-24 09:44 | 0:54 | S/O | Due to Red hot maintenance. | 42 | 37.8 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 132 kV Single Bus | 2024-10-24 06:21 | 2024-10-24 06:21 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Rampur 230/132/33kV Grid Sub-Station | TR-1 LT | 2024-10-26 06:52 | 2024-10-26 14:18 | 7:26 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-01 LT | 2024-10-29 07:30 | 2024-10-29 14:52 | 7:22 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-02 LT | 2024-10-30 08:06 | 2024-10-30 13:59 | 5:53 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
|  |  | Total : | 104:20 |  |  |  | 118.05
Cumilla Grid Circle :
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2024-10-01 06:10 | 2024-10-01 08:12 | 2:02 | S/O | Maintenance work | 5 | 10.1667 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2024-10-01 07:09 | 2024-10-01 09:17 | 2:08 | S/O | Due to Red hot maintenance.at 33 kV feeder | 30 | 64 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2024-10-01 17:11 | 2024-10-01 17:30 | 0:19 | S/O | Maintenance work | 30 | 9.5 | Power interruption
Beanibazar 132/33kV Grid Sub-Station | Transformer TR-02 LT | 2024-10-02 09:04 | 2024-10-02 13:38 | 4:34 | S/O | Maintenance work | 0 | 0 | No interruption
Sylhe(S) 132/33kV Grid Sub-Station | Trafo-1 HT | 2024-10-02 14:27 | 2024-10-02 15:36 | 1:09 | S/O | Due to For OLTC Oil Collection Work | 0 | 0 | No interruption
Sylhe(S) 132/33kV Grid Sub-Station | Trafo-2 HT | 2024-10-02 15:39 | 2024-10-02 16:25 | 0:46 | S/O | Due to OLTC oil sample collection | 0 | 0 | No interruption
Ashuganj 230/132/33kV Grid Sub-Station | 230 kv bus - 2 | 2024-10-04 07:42 | 2024-10-04 07:42 | 0:00 | S/O | Due to insulator replacement. | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-1 HT | 2024-10-07 10:32 | 2024-10-07 13:16 | 2:44 | S/O | Due to Relay test | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-2 HT | 2024-10-07 13:32 | 2024-10-07 15:17 | 1:45 | S/O | Due to Relay test by SPMD. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2024-10-07 18:31 | 2024-10-07 19:32 | 1:01 | S/O | Due to Maintenance work.by PBS | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2024-10-08 07:18 | 2024-10-08 09:20 | 2:02 | S/O | Maintenance work | 0 | 0 | No interruption
Sreemongal 132/33kV Grid Sub-Station | T-3 LT | 2024-10-08 10:23 | 2024-10-08 10:56 | 0:33 | S/O | Due to For 33 kV GCB Gas refilling work. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2024-10-09 07:05 | 2024-10-09 09:32 | 2:27 | S/O | Due to Red hot maintenance. | 30 | 73.5 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 LT | 2024-10-09 10:41 | 2024-10-09 12:07 | 1:26 | S/O | Due to Red hot maintenance. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 LT | 2024-10-14 08:20 | 2024-10-14 09:51 | 1:31 | S/O | Red hot maintenance by PDB. | 30 | 45.5 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2024-10-14 08:21 | 2024-10-14 09:51 | 1:30 | S/O | Maintenance work | 30 | 45 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 HT | 2024-10-14 16:26 | 2024-10-14 17:15 | 0:49 | S/O | Maintenance work at 33 kV feeder | 12 | 9.8 | Power interruption
Beanibazar 132/33kV Grid Sub-Station | Transformer TR-01 LT | 2024-10-16 09:20 | 2024-10-16 13:49 | 4:29 | S/O | Due to Red hot condition . | 0 | 0 | No interruption
Chandpur132/33kV Grid Sub-Station | 50MW(ST) Power Plant(T3) | 2024-10-16 17:22 | 2024-10-20 14:07 | 92:45 | S/O | Maintenance work | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Transformer -02 LT | 2024-10-17 07:27 | 2024-10-17 07:27 | 0:00 | S/O | Due to Red hot maintenance | 10 | 0 | Power interruption
Ramganj 132/33kV Grid Sub-Station | Transformer-01 LT | 2024-10-18 07:40 | 2024-10-18 10:34 | 2:54 | S/O | Due to Red hot maintenances | 10 | 29 | Power interruption
Sylhet 132/33kV Grid Sub-Station | Trafo-2 LT | 2024-10-19 09:24 | 2024-10-19 10:13 | 0:49 | S/O | Due to 33 KV Bus -02 PBS work | 20 | 16.3333 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-10-20 06:36 | 2024-10-20 09:20 | 2:44 | S/O | Due to TR-02 33 KV Side C.T Hotspot Maintenece Work | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2024-10-23 07:07 | 2024-10-23 08:43 | 1:36 | S/O | Due to B Phase Bushing Maintenece Work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 HT | 2024-10-23 14:30 | 2024-10-23 17:42 | 3:12 | S/O | Due to Loop Maintenance by PDB. | 20 | 64 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-10-24 08:14 | 2024-10-24 10:09 | 1:55 | S/O | Maintenance work By PBS | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | 230 KV Bus-2 | 2024-10-24 09:05 | 2024-10-24 09:05 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Sylhet(S) 132/33kV Grid Sub-Station | Trafo-2 LT | 2024-10-26 08:32 | 2024-10-26 10:59 | 2:27 | S/O | Due to PDB work | 22 | 53.9 | Power interruption
Chandpur 132/33kV Grid Sub-Station | Power Plant Incomer(T3) | 2024-10-28 09:55 | 2024-10-28 09:55 | 0:00 | S/O | Maintenance work By P/S | 0 | 0 | No interruption
|  |  | Total : | 139:37 |  | Unserved Energy: |  | 420.7
Khulna Grid Circle :
Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 2024-10-01 08:07 | 2024-10-01 18:09 | 10:02 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 230kV Bus-1 | 2024-10-01 13:27 | 2024-10-01 13:27 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T1-406T LT | 2024-10-02 08:11 | 2024-10-02 17:29 | 9:18 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) HT | 2024-10-03 06:23 | 2024-10-03 08:10 | 1:47 | S/O | Maintenance work | 12 | 21.4 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (403T) HT | 2024-10-03 06:23 | 2024-10-03 08:10 | 1:47 | S/O | Maintenance work | 12 | 21.4 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-6 HT | 2024-10-03 07:54 | 2024-10-03 11:38 | 3:44 | S/O | Maintenance work | 1 | 3.7333 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2024-10-03 07:54 | 2024-10-03 11:37 | 3:43 | S/O | Maintenance work | 1 | 3.7167 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-10-04 08:00 | 2024-10-04 11:43 | 3:43 | S/O | Due to PDB work | 10 | 37.1667 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2024-10-04 08:04 | 2024-10-04 11:38 | 3:34 | S/O | Due to PDB work | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Bus-02 | 2024-10-04 08:48 | 2024-10-04 16:44 | 7:56 | S/O | Project Work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-10-04 09:42 | 2024-10-04 10:46 | 1:04 | S/O | Due to Red hot maintenance of 33kV Fdder | 7 | 7.4667 | Power interruption
Gopalpara 132/33kV Grid Sub-Station | T-5 LT | 2024-10-05 08:00 | 2024-10-05 12:26 | 4:26 | S/O | Due to T3 renovation work by KPS | 10 | 44.3333 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | 400kV Bus-01 | 2024-10-05 10:00 | 2024-10-05 16:41 | 6:41 | S/O | Project Work | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 2024-10-05 10:45 | 2024-10-05 17:10 | 6:25 | S/O | Maintenance work | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 230/132KV ATR-1 | 2024-10-05 11:46 | 2024-10-05 11:46 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 2024-10-06 07:43 | 2024-10-06 21:50 | 14:07 | S/O | Due to Annual Maintenance . | 0 | 0 | No interruption
Borhanuddin 230/33kV Grid Sub-Station | Tr-Load HT | 2024-10-06 13:05 | 2024-10-06 14:40 | 1:35 | S/O | Maintenance work | 55 | 87.0833 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-10-06 18:59 | 2024-10-06 19:50 | 0:51 | S/O | Due to Removal red Hot work. | 20 | 17 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-10-08 06:30 | 2024-10-08 07:38 | 1:08 | S/O | Maintenance work | 15 | 17 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | Main Bus - 1 | 2024-10-08 08:44 | 2024-10-08 20:03 | 11:19 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | Auxiliary-02 (PGCB) LT | 2024-10-09 08:25 | 2024-10-09 15:33 | 7:08 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) HT | 2024-10-09 09:10 | 2024-10-09 09:10 | 0:00 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-10-11 06:05 | 2024-10-11 16:55 | 10:50 | S/O | Project Work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-10-12 06:02 | 2024-10-12 16:56 | 10:54 | S/O | Project Work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-10-14 08:49 | 2024-10-14 15:11 | 6:22 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2024-10-15 07:17 | 2024-10-15 20:41 | 13:24 | S/O | Due to 33 kV loop change | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-10-15 08:07 | 2024-10-15 14:47 | 6:40 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Transformer-03 HT | 2024-10-15 08:11 | 2024-10-15 19:54 | 11:43 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Transformer-03 LT | 2024-10-16 07:58 | 2024-10-16 17:30 | 9:32 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Khulna(C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2024-10-16 08:02 | 2024-10-16 16:43 | 8:41 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-10-16 09:01 | 2024-10-16 14:59 | 5:58 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Bhola 132/33kV Grid Sub-Station | 120/140 MVA power transformer | 2024-10-16 12:44 | 2024-10-16 17:26 | 4:42 | S/O | Maintenance work | 55 | 258.5 | Power interruption
Khulna(C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-10-17 08:00 | 2024-10-17 15:15 | 7:15 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Transformer-03 LT | 2024-10-17 08:56 | 2024-10-17 16:24 | 7:28 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-10-17 09:29 | 2024-10-17 14:16 | 4:47 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2024-10-19 08:11 | 2024-10-19 17:05 | 8:54 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Transformer-04 LT | 2024-10-19 08:15 | 2024-10-19 17:06 | 8:51 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Transformer-04 HT | 2024-10-19 08:18 | 2024-10-19 17:06 | 8:48 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Khulna(C) 132/33kV Grid Sub-Station | Tr-2 415 T LT | 2024-10-19 08:39 | 2024-10-19 12:24 | 3:45 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bus-I | 2024-10-19 11:28 | 2024-10-19 15:27 | 3:59 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2024-10-20 07:55 | 2024-10-20 17:07 | 9:12 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Khulna(C) 132/33kV Grid Sub-Station | Tr-2 415 T LT | 2024-10-20 08:02 | 2024-10-20 15:58 | 7:56 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Transformer-04 LT | 2024-10-20 08:18 | 2024-10-20 17:20 | 9:02 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | 132 kV Bus-I | 2024-10-20 10:24 | 2024-10-20 17:41 | 7:17 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2024-10-21 08:06 | 2024-10-21 17:33 | 9:27 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2024-10-21 08:12 | 2024-10-21 15:50 | 7:38 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-10-21 08:14 | 2024-10-21 16:30 | 8:16 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Transformer-04 LT | 2024-10-21 08:19 | 2024-10-21 17:03 | 8:44 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | Bus B | 2024-10-21 13:45 | 2024-10-21 13:45 | 0:00 | S/O | Due to Completion of Bus Coupler Breaker CT | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2024-10-22 08:05 | 2024-10-22 16:11 | 8:06 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-10-22 08:10 | 2024-10-22 16:58 | 8:48 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2024-10-22 08:12 | 2024-10-22 16:48 | 8:36 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Bus-I ( 132KV Bus) | 2024-10-22 08:50 | 2024-10-22 12:27 | 3:37 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | BUS-2 (230 kV) | 2024-10-22 12:32 | 2024-10-22 13:44 | 1:12 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-10-23 06:07 | 2024-10-23 08:18 | 2:11 | S/O | Due to WZPDCL work | 15 | 32.75 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2024-10-23 06:08 | 2024-10-23 08:18 | 2:10 | S/O | Due to WZPDCL work | 15 | 32.5 | Power interruption
Khulna(C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2024-10-23 08:10 | 2024-10-23 14:34 | 6:24 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2024-10-23 08:26 | 2024-10-23 17:00 | 8:34 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 HT | 2024-10-23 08:26 | 2024-10-23 15:05 | 6:39 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T2 HT | 2024-10-23 08:27 | 2024-10-23 16:59 | 8:32 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2024-10-24 08:25 | 2024-10-24 14:36 | 6:11 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulna(C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2024-10-24 08:27 | 2024-10-24 11:44 | 3:17 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 2024-10-24 12:12 | 2024-10-24 13:54 | 1:42 | S/O | Due to Red Hot Maintenance by PBS | 10 | 17 | Power interruption
Noapara132/33kV Grid Sub-Station | T-1 LT | 2024-10-25 07:22 | 2024-10-25 09:24 | 2:02 | S/O | Due to REB-4 Feeder High Temperature Maintenance. | 12 | 24.4 | Power interruption
Noapara132/33kV Grid Sub-Station | Bus Section-1 | 2024-10-25 07:30 | 2024-10-25 09:15 | 1:45 | S/O | Due to REB-4 Feeder High Temperature Maintenance. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2024-10-26 08:35 | 2024-10-26 13:32 | 4:57 | S/O | Maintenance work | 2 | 9.9 | Power interruption
Barishal 230/132kV Grid Sub-Station | ATR-1 LT | 2024-10-26 08:40 | 2024-10-26 16:58 | 8:18 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-10-26 08:40 | 2024-10-26 13:32 | 4:52 | S/O | Due to 33 kv T-4 Renuvenation work by KPS. | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Auto Transformer-01 LT | 2024-10-26 09:22 | 2024-10-26 18:32 | 9:10 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulna(C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2024-10-27 07:42 | 2024-10-27 13:25 | 5:43 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2024-10-27 08:12 | 2024-10-27 12:30 | 4:18 | S/O | Maintenance work by PDB | 6 | 25.8 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-10-27 08:12 | 2024-10-27 14:10 | 5:58 | S/O | Maintenance work by PDB | 6 | 35.8 | Power interruption
Barishal 230/132kV Grid Sub-Station | ATR-1 LT | 2024-10-27 08:43 | 2024-10-27 16:48 | 8:05 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Payra 400/230/132/33kV Grid Sub-Station | Auto Transformer-01 HT | 2024-10-27 09:05 | 2024-10-27 16:59 | 7:54 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Payra 400/230/132/33kV Grid Sub-Station | Auto Transformer-01 LT | 2024-10-28 07:46 | 2024-10-28 17:23 | 9:37 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-10-28 08:24 | 2024-10-28 15:22 | 6:58 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | ATR-2 LT | 2024-10-28 08:42 | 2024-10-28 17:04 | 8:22 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (403T) LT | 2024-10-29 06:45 | 2024-10-29 08:20 | 1:35 | S/O | Due to Red hot maintenance work at 33 kV | 35 | 55.4167 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-10-29 06:45 | 2024-10-29 08:19 | 1:34 | S/O | Due to Red hot maintenance work at 33 kV | 35 | 54.8333 | Power interruption
Payra 400/230/132/33kV Grid Sub-Station | Auto Transformer-02 LT | 2024-10-29 07:45 | 2024-10-29 17:12 | 9:27 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-10-29 08:25 | 2024-10-29 15:22 | 6:57 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | ATR-2 LT | 2024-10-29 08:37 | 2024-10-29 16:26 | 7:49 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Payra 400/230/132/33kV Grid Sub-Station | Transformer-02 HT | 2024-10-30 08:02 | 2024-10-30 16:36 | 8:34 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Noapara132/33kV Grid Sub-Station | T-1 LT | 2024-10-30 08:04 | 2024-10-30 12:10 | 4:06 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | 230kV BUS | 2024-10-30 08:50 | 2024-10-30 17:07 | 8:17 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | ATR-01 LT | 2024-10-30 15:43 | 2024-10-30 19:49 | 4:06 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Madaripur132/33kV Grid Sub-Station | T1-405T LT | 2024-10-31 07:42 | 2024-10-31 16:41 | 8:59 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2024-10-31 08:40 | 2024-10-31 13:57 | 5:17 | S/O | Project Work | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | 230kV BUS | 2024-10-31 08:50 | 2024-10-31 16:45 | 7:55 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | 132 kV Bus-I | 2024-10-31 09:38 | 2024-10-31 11:30 | 1:52 | S/O | Project Work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2024-10-31 14:10 | 2024-10-31 17:10 | 3:00 | S/O | Project Work | 0 | 0 | No interruption
|  |  | Total : | 553:49 |  | Unserved Energy : |  | 807.2
HVDC Grid Circle
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-10-15 07:04 | 2024-10-15 09:10 | 2:06 | S/O | Due to Red hot maintenance work | 0 | 0 | No interruption
BIPTC | 20DF12 | 2024-10-16 11:16 | 2024-10-16 15:38 | 4:22 | S/O | Due to For DC rectification . | 0 | 0 | No interruption
BIPTC | 20DF11 | 2024-10-16 11:16 | 2024-10-16 15:38 | 4:22 | S/O | Due to For DC rectification . | 0 | 0 | No interruption
BIPTC | 20DF13 | 2024-10-16 11:16 | 2024-10-16 15:38 | 4:22 | S/O | Due to For DC rectification . | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-10-18 07:32 | 2024-10-18 08:46 | 1:14 | S/O | Due to WZPDCL work | 10 | 12.3333 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | T-2 HT | 2024-10-19 08:49 | 2024-10-20 13:19 | 28:30 | S/O | Due to For oil centrifuge work. | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | T-03 LT | 2024-10-19 09:43 | 2024-10-19 17:05 | 7:22 | S/O | Maintenance work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Bus 1 | 2024-10-19 09:48 | 2024-10-19 17:01 | 7:13 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 20DF13 | 2024-10-20 10:28 | 2024-10-20 11:44 | 1:16 | S/O | Due to CB general fault | 0 | 0 | No interruption
BIPTC | 10CF15 | 2024-10-20 12:12 | 2024-10-20 12:56 | 0:44 | S/O | Maintenance work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | T-03 LT | 2024-10-23 11:09 | 2024-10-23 15:44 | 4:35 | S/O | Due to oil centrifuse work. | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Bus 2 | 2024-10-26 11:26 | 2024-10-26 12:47 | 1:21 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-1 HT | 2024-10-30 08:22 | 2024-10-30 16:27 | 8:05 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 HT | 2024-10-31 08:06 | 2024-10-31 14:18 | 6:12 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 (425T) LT | 2024-10-31 10:47 | 2024-10-31 12:36 | 1:49 | S/O | Due to SCADA Integration work. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 (425T) HT | 2024-10-31 18:40 | 2024-10-31 20:13 | 1:33 | S/O | Due to SCADA Integration work. | 0 | 0 | No interruption
|  |  | Total : | 85:06 |  | Unserved Energy : |  | 12.3333
Bogura Grid Circle:
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2024-10-01 07:23 | 2024-10-01 07:23 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) HT | 2024-10-01 07:48 | 2024-10-01 11:58 | 4:10 | S/O | Maintenance work | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2024-10-02 07:03 | 2024-10-02 09:01 | 1:58 | S/O | Due to Maintenance Work | 33 | 64.9 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 1 LT | 2024-10-02 07:11 | 2024-10-02 08:55 | 1:44 | S/O | Due to Maintenance Work | 27 | 46.8 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T-1 LT | 2024-10-02 08:11 | 2024-10-02 17:57 | 9:46 | S/O | Due to Maintenance Work | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-4 (414T) LT | 2024-10-02 09:04 | 2024-10-02 09:04 | 0:00 | S/O | Due to Maintenance Work | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T-1 LT | 2024-10-03 08:12 | 2024-10-03 17:59 | 9:47 | S/O | Due to Annual Maintenance of TR-1 | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 HT | 2024-10-03 11:33 | 2024-10-03 14:10 | 2:37 | S/O | Due to relay change | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | T-01 (406T) LT | 2024-10-04 08:08 | 2024-10-04 09:59 | 1:51 | S/O | Due to Nesco work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2024-10-05 07:00 | 2024-10-05 07:00 | 0:00 | S/O | Due to General cleaning. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | T-3 (425T) HT | 2024-10-05 07:01 | 2024-10-05 11:05 | 4:04 | S/O | Due to General cleaning. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T-2 LT | 2024-10-05 08:15 | 2024-10-05 17:55 | 9:40 | S/O | Due to For Annual Maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) LT | 2024-10-05 08:18 | 2024-10-05 15:47 | 7:29 | S/O | Due to For Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) HT | 2024-10-05 11:19 | 2024-10-05 13:17 | 1:58 | S/O | Due to For Annual Maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T-2 LT | 2024-10-06 08:10 | 2024-10-06 16:11 | 8:01 | S/O | Due to For Annual Maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-10-06 08:25 | 2024-10-06 15:28 | 7:03 | S/O | Due to For Annual Maintenance | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Main Bus | 2024-10-06 11:19 | 2024-10-06 11:19 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) HT | 2024-10-07 12:00 | 2024-10-07 16:44 | 4:44 | S/O | Due to For Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2024-10-08 06:52 | 2024-10-08 08:35 | 1:43 | S/O | Due to NESCO will do maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) LT | 2024-10-08 08:17 | 2024-10-08 15:18 | 7:01 | S/O | Maintenance work | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | T-3(432T) LT | 2024-10-09 08:20 | 2024-10-09 15:58 | 7:38 | S/O | Due to Maintenance Work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) HT | 2024-10-09 08:24 | 2024-10-09 15:55 | 7:31 | S/O | Due to Maintenance Work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) LT | 2024-10-09 09:05 | 2024-10-09 17:42 | 8:37 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-10-12 08:19 | 2024-10-12 13:06 | 4:47 | S/O | Due to Maintenance work (33 KV bus) | 12 | 57.4 | Power interruption
Panchugarh 132/33kV Grid Sub-Station | T-1(407T) HT | 2024-10-14 08:15 | 2024-10-14 15:48 | 7:33 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 132KV Main 1 | 2024-10-15 08:25 | 2024-10-15 12:20 | 3:55 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Panchugarh 132/33kV Grid Sub-Station | T-1(407T) LT | 2024-10-15 10:19 | 2024-10-15 15:26 | 5:07 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR1-414T LT | 2024-10-16 08:10 | 2024-10-16 16:30 | 8:20 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Panchugarh 132/33kV Grid Sub-Station | T-2(417T) LT | 2024-10-16 08:28 | 2024-10-16 15:43 | 7:15 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Panchugarh 132/33kV Grid Sub-Station | T-2(417T) LT | 2024-10-17 08:35 | 2024-10-17 08:35 | 0:00 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Bus A | 2024-10-17 08:36 | 2024-10-17 14:55 | 6:19 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR1-414T LT | 2024-10-17 08:48 | 2024-10-17 14:32 | 5:44 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Sherpur(Bogura) 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2024-10-17 10:06 | 2024-10-17 17:07 | 7:01 | S/O | Due to Hot temperature maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) LT | 2024-10-18 06:45 | 2024-10-18 08:21 | 1:36 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR2-404T LT | 2024-10-19 08:25 | 2024-10-19 14:19 | 5:54 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-4 LT | 2024-10-19 08:47 | 2024-10-19 10:17 | 1:30 | S/O | Due to Red hot maintenance | 15 | 22.5 | Power interruption
Panchugarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-10-19 08:55 | 2024-10-19 16:59 | 8:04 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Bus B | 2024-10-19 09:20 | 2024-10-19 12:37 | 3:17 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2024-10-19 09:45 | 2024-10-19 10:55 | 1:10 | S/O | Due to For PBS redhot maintenance. | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR2-404T LT | 2024-10-20 08:24 | 2024-10-20 14:20 | 5:56 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Panchugarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-10-20 09:04 | 2024-10-20 16:16 | 7:12 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR3-424T LT | 2024-10-21 08:27 | 2024-10-21 14:26 | 5:59 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | ATR-01 (704T) LT | 2024-10-21 09:29 | 2024-10-21 09:29 | 0:00 | S/O | Due to Maintenance Work | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR3-424T LT | 2024-10-22 09:10 | 2024-10-22 14:40 | 5:30 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-4 LT | 2024-10-23 07:10 | 2024-10-23 08:51 | 1:41 | S/O | ue to 132KV CT RED HOT | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR4-434T HT | 2024-10-23 08:28 | 2024-10-23 14:52 | 6:24 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2024-10-23 10:13 | 2024-10-23 16:35 | 6:22 | S/O | Due to For PBS redhot maintenance. | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-3 (427 T) LT | 2024-10-23 11:56 | 2024-10-23 12:31 | 0:35 | S/O | Project Work | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) LT | 2024-10-23 12:41 | 2024-10-23 13:27 | 0:46 | S/O | Project Work | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR4-434T LT | 2024-10-24 13:20 | 2024-10-24 14:51 | 1:31 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) LT | 2024-10-26 06:15 | 2024-10-26 08:20 | 2:05 | S/O | Due to Maintenance Work By PBS | 20 | 41.6667 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | Capacitor Bank | 2024-10-27 08:30 | 2024-10-27 15:50 | 7:20 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | BUS-1 (132KV) | 2024-10-27 10:36 | 2024-10-27 13:25 | 2:49 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Lalmonirhat 132/33kV Grid Sub-Station | Transformer T-1 425T LT | 2024-10-28 08:25 | 2024-10-28 15:56 | 7:31 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Lalmonirhat 132/33kV Grid Sub-Station | T-2 415T HT | 2024-10-29 08:20 | 2024-10-29 16:18 | 7:58 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-03 LT | 2024-10-29 08:20 | 2024-10-29 15:07 | 6:47 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-03 LT | 2024-10-30 16:17 | 2024-10-30 16:17 | 0:00 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Lalmonirhat 132/33kV Grid Sub-Station | T-2 415T LT | 2024-10-30 10:45 | 2024-10-30 15:28 | 4:43 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | 132KV Bus B | 2024-10-31 10:20 | 2024-10-31 17:18 | 6:58 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | BUS-B | 2024-10-31 10:44 | 2024-10-31 13:50 | 3:06 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
|  |  | Total : | 276:07 |  | Unserved Energy : |  | 233.2667
Others :
Ashuganj 230/132kV Grid Sub-Station | TR-OAT-12 LT | 2024-10-26 08:30 | 2024-10-26 12:23 | 3:53 | S/O | Project Work | 0 | 0 | No interruption
|  |  | Total : | 3:53 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1501:20 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:October 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-10-01 07:17 | 2024-10-01 07:17 | 0:00 | S/O | Due to Main bus DS maintenance. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | BR Powergen Ckt- 01 | 2024-10-03 14:24 | 2024-10-03 14:45 | 0:21 | S/O | Due to Line parameter measurement | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | BR Powergen Ckt- 02 | 2024-10-03 14:24 | 2024-10-03 14:46 | 0:22 | S/O | Due to Line parameter measurement | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Uttara 3rd Phase Ckt | 2024-10-06 09:50 | 2024-10-06 16:21 | 6:31 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Lalbag 132kV Ckt-2 | 2024-10-06 10:06 | 2024-10-06 17:25 | 7:19 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi 132kV Ckt-2 | 2024-10-07 07:19 | 2024-10-07 09:18 | 1:59 | S/O | Due to B-phase conductor armoring purpose | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-2 | 2024-10-07 08:27 | 2024-10-07 08:27 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | BR Powergen Ckt- 01 | 2024-10-07 08:32 | 2024-10-07 15:09 | 6:37 | S/O | Project Work | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | BR Powergen Ckt- 02 | 2024-10-07 08:32 | 2024-10-07 08:32 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Uttara 3rd Phase Ckt | 2024-10-07 09:22 | 2024-10-07 16:10 | 6:48 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Uttara 3rd Phase Ckt | 2024-10-08 09:23 | 2024-10-08 16:41 | 7:18 | S/O | Due to maintenance work | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Lalbag 132kV Ckt-2 | 2024-10-08 09:43 | 2024-10-08 16:24 | 6:41 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-2 | 2024-10-08 09:51 | 2024-10-08 11:50 | 1:59 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Uttara 3rd Phase Ckt | 2024-10-09 09:20 | 2024-10-09 09:20 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Airport(Old) 230kV Ckt-2 | 2024-10-10 10:18 | 2024-10-10 21:42 | 11:24 | S/O | Due to relay change | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-1 | 2024-10-14 09:49 | 2024-10-14 16:36 | 6:47 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi 132kV Ckt-1 | 2024-10-14 10:29 | 2024-10-14 19:03 | 8:34 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-1 | 2024-10-14 10:38 | 2024-10-14 16:36 | 5:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Sub-Station | Uttara 3PH 132kV Ckt-1 | 2024-10-15 08:27 | 2024-10-15 17:03 | 8:36 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2024-10-15 09:24 | 2024-10-15 17:01 | 7:37 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj 132kV Ckt-1 | 2024-10-15 09:52 | 2024-10-15 12:58 | 3:06 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi 132kV Ckt-2 | 2024-10-15 11:30 | 2024-10-15 15:30 | 4:00 | S/O | Due to relay testing | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj 132kV Ckt-2 | 2024-10-15 13:32 | 2024-10-15 14:54 | 1:22 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Uttara 3rd Phase Ckt | 2024-10-16 08:44 | 2024-10-16 15:47 | 7:03 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Kodda B 132 kV Ckt-1 | 2024-10-16 10:48 | 2024-10-16 11:45 | 0:57 | S/O | Due to relay test | 0 | 0 | No interruption
Kadda 132/33kV Grid Sub-Station | Rajendrapur 132kV Ckt-1 | 2024-10-16 13:33 | 2024-10-16 15:37 | 2:04 | S/O | Due to relay test | 0 | 0 | No interruption
Kadda 132/33kV Grid Sub-Station | Rajendrapur 132kV Ckt-2 | 2024-10-16 15:40 | 2024-10-16 16:01 | 0:21 | S/O | Due to relay test | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2024-10-17 09:15 | 2024-10-17 16:23 | 7:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-1 | 2024-10-17 09:22 | 2024-10-17 11:04 | 1:42 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-2 | 2024-10-17 11:08 | 2024-10-17 11:39 | 0:31 | S/O | Due to relay test | 0 | 0 | No interruption
Mymensingh- 132/33kV Grid Sub-Station | Netrokona 132kV Ckt-1 | 2024-10-19 09:10 | 2024-10-19 09:10 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Bashundhara-1 | 2024-10-19 09:24 | 2024-10-19 15:40 | 6:16 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Netrokona 132kV Ckt-1 | 2024-10-20 09:21 | 2024-10-20 18:09 | 8:48 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Kaliakoir 132 kV Ckt-1 | 2024-10-20 11:11 | 2024-10-20 13:40 | 2:29 | S/O | Due to Relay Test | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Kaliakoir 132 kV Ckt-2 | 2024-10-20 13:42 | 2024-10-20 14:28 | 0:46 | S/O | Due to Relay Test | 0 | 0 | No interruption
Jamalpur United (20MW) | Jamalpur 132kV Ckt-2 | 2024-10-21 09:17 | 2024-10-21 10:22 | 1:05 | S/O | Maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | 132 kV Bashundhara-1 | 2024-10-21 09:29 | 2024-10-21 16:32 | 7:03 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Netrokona 132kV Ckt-1 | 2024-10-21 09:31 | 2024-10-21 09:31 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Kadda 132/33kV Grid Sub-Station | Rajendrapur 132kV Ckt-1 | 2024-10-21 11:53 | 2024-10-21 13:45 | 1:52 | S/O | Due to Relay Testing by SPMD-2 | 0 | 0 | No interruption
Kadda 132/33kV Grid Sub-Station | Rajendrapur 132kV Ckt-2 | 2024-10-21 13:45 | 2024-10-21 15:23 | 1:38 | S/O | Due to Relay Testing by SPMD-2 | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Airport(Old) 230kV Ckt-1 | 2024-10-24 10:05 | 2024-10-24 16:39 | 6:34 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-2 | 2024-10-26 08:49 | 2024-10-26 13:15 | 4:26 | S/O | Project Work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur 132kV Ckt-2 | 2024-10-26 09:11 | 2024-10-26 12:13 | 3:02 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Bhasantek 132kV Ckt-1 | 2024-10-26 09:31 | 2024-10-26 17:06 | 7:35 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Airport(Old) 230kV Ckt-1 | 2024-10-27 09:14 | 2024-10-27 17:14 | 8:00 | S/O | Maintenance work | 0 | 0 | No interruption
Jamalpur United (20MW) | Sherpur 132kV Ckt-1 | 2024-10-28 08:57 | 2024-10-28 09:59 | 1:02 | S/O | Due to Relay Test | 0 | 0 | No interruption
Jamalpur United (20MW) | Sherpur 132kV Ckt-2 | 2024-10-28 10:00 | 2024-10-28 12:45 | 2:45 | S/O | Maintenance work | 0 | 0 | No interruption
Jamalpur United (20MW) | Jamalpur 132kV Ckt-1 | 2024-10-28 12:53 | 2024-10-28 13:44 | 0:51 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur United (20MW) | Jamalpur 132kV Ckt-2 | 2024-10-28 13:45 | 2024-10-28 14:24 | 0:39 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-2 | 2024-10-28 14:28 | 2024-10-28 14:50 | 0:22 | S/O | Maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-1 | 2024-10-28 14:51 | 2024-10-28 15:33 | 0:42 | S/O | Maintenance work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Netrokona 132kV Ckt-2 | 2024-10-29 09:13 | 2024-10-29 17:30 | 8:17 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Airport(Old) 230kV Ckt-2 | 2024-10-29 09:31 | 2024-10-29 13:29 | 3:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Bhasantek 132kV Ckt-1 | 2024-10-30 07:31 | 2024-10-30 18:34 | 11:03 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Lalbag 132kV Ckt-1 | 2024-10-30 08:10 | 2024-10-30 17:46 | 9:36 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Netrokona 132kV Ckt-2 | 2024-10-30 09:47 | 2024-10-30 17:19 | 7:32 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Airport(Old) 230kV Ckt-2 | 2024-10-30 09:59 | 2024-10-30 17:11 | 7:12 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Lalbag 132kV Ckt-1 | 2024-10-31 08:26 | 2024-10-31 16:33 | 8:07 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-1 | 2024-10-31 08:39 | 2024-10-31 16:47 | 8:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 252:53 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Rampura 230/132kV Grid Sub-Station | Bashundhara-2 | 2024-10-05 08:49 | 2024-10-05 17:13 | 8:24 | S/O | Maintenance work | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Rampura 230 kV Ckt-2 | 2024-10-08 07:06 | 2024-10-08 07:06 | 0:00 | S/O | Due to Red Hot problem | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Rampura 230 kV Ckt-2 | 2024-10-08 07:40 | 2024-10-08 07:40 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Sonargaon-1 | 2024-10-09 09:50 | 2024-10-09 16:54 | 7:04 | S/O | Maintenance work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Rampura 132 kV Ckt-2 | 2024-10-15 05:17 | 2024-10-15 07:57 | 2:40 | S/O | Maintenance work | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Shyampur 230kV Ckt-1 | 2024-10-15 07:05 | 2024-10-15 09:09 | 2:04 | S/O | Due to Tower Construction | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Shyampur 230kV Ckt-2 | 2024-10-15 09:17 | 2024-10-15 13:14 | 3:57 | S/O | Project Work | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Shyampur 230kV Ckt-2 | 2024-10-15 13:47 | 2024-10-15 13:47 | 0:00 | S/O | Due to Tower Construction | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Shyampur 230kV Ckt-2 | 2024-10-16 07:28 | 2024-10-16 11:54 | 4:26 | S/O | Due to Red hot maintenance work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddirganj 230kV Ckt-2 | 2024-10-22 08:44 | 2024-10-22 12:03 | 3:19 | S/O | Due to Abnormal temperature in line DS | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddirganj 132kV Ckt-2 | 2024-10-22 08:45 | 2024-10-22 12:04 | 3:19 | S/O | Due to Red Hot Maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2024-10-23 11:35 | 2024-10-23 17:15 | 5:40 | S/O | Due to Corrective maintenance work | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-1 & 2 | 2024-10-27 09:54 | 2024-10-27 09:54 | 0:00 | S/O | Due to According to NLDC instruction. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Shyampur 230kV Ckt-2 | 2024-10-27 10:01 | 2024-10-27 10:01 | 0:00 | S/O | Due to For Tower Construction | 0 | 0 | No interruption
keraniganj 230/132kV Grid Sub-Station | Aggreko-1 | 2024-10-29 10:24 | 2024-10-29 15:19 | 4:55 | S/O | Due to According to NLDC | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Keraniganj-2 (Pre- Aourahati) | 2024-10-29 10:35 | 2024-10-29 15:10 | 4:35 | S/O | Due to Hydraulic oil cable of Circuit | 0 | 0 | No interruption
keraniganj 230/132kV Grid Sub-Station | 132 kV Hasnabad Ckt. 1 | 2024-10-31 12:20 | 2024-10-31 14:15 | 1:55 | S/O | Maintenance work | 0 | 0 | No interruption
keraniganj 230/132kV Grid Sub-Station | Aggreko-1 | 2024-10-31 12:20 | 2024-10-31 14:15 | 1:55 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Keraniganj-1 (Pre- Lalbag) | 2024-10-31 12:31 | 2024-10-31 12:31 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Keraniganj-2 (Pre- Aourahati) | 2024-10-31 12:31 | 2024-10-31 12:31 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 54:13 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Khagrachari 132/33kV Sub-Station | Rangamati 132kV Ckt-1 | 2024-10-05 09:32 | 2024-10-05 16:43 | 7:11 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-1 | 2024-10-06 08:24 | 2024-10-06 16:17 | 7:53 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-1 | 2024-10-06 08:25 | 2024-10-06 16:51 | 8:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-1 | 2024-10-08 08:22 | 2024-10-08 16:45 | 8:23 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-1 | 2024-10-09 08:23 | 2024-10-09 16:11 | 7:48 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-1 | 2024-10-09 08:36 | 2024-10-09 17:07 | 8:31 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Madunaghat132/33kV Grid Sub-Station | TKCL 132kV Ckt-1 | 2024-10-10 06:48 | 2024-10-10 14:44 | 7:56 | S/O | Due to According to NLDC suggestions and directions. | 0 | 0 | No interruption
Hathazari 230/33kV Grid Sub-Station | Madunaghat 132kV Ckt-1 | 2024-10-10 07:06 | 2024-10-10 10:33 | 3:27 | S/O | Maintenance work | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-1 | 2024-10-10 07:50 | 2024-10-10 15:52 | 8:02 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-1 | 2024-10-10 09:47 | 2024-10-10 16:45 | 6:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-2 | 2024-10-10 10:48 | 2024-10-10 13:42 | 2:54 | S/O | Due to NLDC work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-1 | 2024-10-12 08:29 | 2024-10-12 15:05 | 6:36 | S/O | Maintenance work | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-2 | 2024-10-14 08:55 | 2024-10-14 16:08 | 7:13 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-1 | 2024-10-14 09:16 | 2024-10-14 17:18 | 8:02 | S/O | ue to Annual Deadline Checking | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-2 | 2024-10-15 08:19 | 2024-10-15 16:52 | 8:33 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-1 | 2024-10-15 08:36 | 2024-10-15 17:43 | 9:07 | S/O | Due to Annual Deadline Checking | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-2 | 2024-10-16 08:25 | 2024-10-16 16:14 | 7:49 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-2 | 2024-10-16 08:40 | 2024-10-16 17:44 | 9:04 | S/O | Maintenance work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-2 | 2024-10-17 07:39 | 2024-10-17 17:37 | 9:58 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-2 | 2024-10-17 08:28 | 2024-10-17 16:03 | 7:35 | S/O | Maintenance work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-1 | 2024-10-18 07:37 | 2024-10-18 17:18 | 9:41 | S/O | Due to Change Disk of Tower | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-2 | 2024-10-18 07:45 | 2024-10-18 16:33 | 8:48 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-2 | 2024-10-19 08:17 | 2024-10-19 15:36 | 7:19 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-2 | 2024-10-19 08:38 | 2024-10-19 16:02 | 7:24 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-2 | 2024-10-19 08:59 | 2024-10-19 16:03 | 7:04 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-1 | 2024-10-20 08:25 | 2024-10-20 16:10 | 7:45 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-2 | 2024-10-20 08:30 | 2024-10-20 17:37 | 9:07 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-1 | 2024-10-21 08:22 | 2024-10-21 16:31 | 8:09 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Madunaghat 132 kV Ckt-2 | 2024-10-21 08:32 | 2024-10-21 16:52 | 8:20 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-1 | 2024-10-22 08:27 | 2024-10-22 16:32 | 8:05 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Sikalbaha 132kV Ckt-2 | 2024-10-22 08:35 | 2024-10-22 18:30 | 9:55 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-1 | 2024-10-23 08:32 | 2024-10-23 16:27 | 7:55 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Sikalbaha 132kV Ckt-2 | 2024-10-23 08:32 | 2024-10-23 17:04 | 8:32 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-2 | 2024-10-24 08:17 | 2024-10-24 16:21 | 8:04 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Sikalbaha 132kV Ckt-2 | 2024-10-24 08:37 | 2024-10-24 16:57 | 8:20 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Rampur 230/132kV Grid Sub-Station | Halishahar-2 | 2024-10-25 06:26 | 2024-10-25 14:52 | 8:26 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Julda 132kV Ckt-1 | 2024-10-25 06:28 | 2024-10-25 14:53 | 8:25 | S/O | Project Work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-2 | 2024-10-26 08:19 | 2024-10-26 16:27 | 8:08 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Sikalbaha 132kV Ckt-2 | 2024-10-26 08:37 | 2024-10-26 18:39 | 10:02 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-2 | 2024-10-27 08:27 | 2024-10-27 16:17 | 7:50 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TKCL 132kV Ckt-1 | 2024-10-27 08:45 | 2024-10-27 17:16 | 8:31 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-2 | 2024-10-28 08:27 | 2024-10-28 16:32 | 8:05 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TKCL 132kV Ckt-1 | 2024-10-28 08:32 | 2024-10-28 17:17 | 8:45 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-2 | 2024-10-28 08:39 | 2024-10-28 16:34 | 7:55 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TKCL 132kV Ckt-1 | 2024-10-29 08:53 | 2024-10-29 16:16 | 7:23 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sikalbaha 132/33kV Grid Sub-Station | TKCL 132kV Ckt-1 | 2024-10-30 08:52 | 2024-10-30 17:48 | 8:56 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Feni 132 kV Ckt-2 | 2024-10-30 10:15 | 2024-10-30 11:24 | 1:09 | S/O | Due to SF6 gas refilling. | 0 | 0 | No interruption
|  |  | Total : | 369:29 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Cumilla(N) 230/33kV Grid Sub-Station | BSRM-230 kV Ckt-1 | 2024-10-06 10:37 | 2024-10-06 16:04 | 5:27 | S/O | Due to relay test | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon 132 kV Ckt-2 | 2024-10-06 11:53 | 2024-10-06 17:35 | 5:42 | S/O | Maintenance work | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon 132 kV Ckt-2 | 2024-10-07 10:45 | 2024-10-07 14:37 | 3:52 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sylhet 132 kV Ckt-2 | 2024-10-10 06:43 | 2024-10-10 07:35 | 0:52 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Desh Energy Ckt-02 | 2024-10-11 09:09 | 2024-10-11 11:02 | 1:53 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Bibiana 400/230kV Grid Sub-Station | Bibiyana-South (Back feed) | 2024-10-17 12:11 | 2024-10-17 12:11 | 0:00 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Kishoreganj 132kV Ckt-1 & 2 | 2024-10-18 07:05 | 2024-10-18 12:10 | 5:05 | S/O | Project Work | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Ghorasal 132kV Ckt-1 | 2024-10-18 07:45 | 2024-10-18 12:22 | 4:37 | S/O | Due to 132KV high voltage test | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Brahmanbaria 132kV Ckt-1 | 2024-10-18 08:00 | 2024-10-18 12:08 | 4:08 | S/O | Due to 132KV high voltage test | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Brahmanbaria 132kV Ckt-2 | 2024-10-19 06:33 | 2024-10-19 11:16 | 4:43 | S/O | Project Work | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Ghorasal 132kV Ckt-2 | 2024-10-19 06:34 | 2024-10-19 12:17 | 5:43 | S/O | Project Work | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Kishoreganj 132kV Ckt-2 | 2024-10-19 07:09 | 2024-10-19 11:42 | 4:33 | S/O | Due to 132kv GIS work | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Desh Energy Ckt-01 | 2024-10-19 07:35 | 2024-10-19 11:05 | 3:30 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Fenchuganj 230/33kV Grid Sub-Station | Kulaura 132 kV Ckt-2 | 2024-10-19 12:46 | 2024-10-19 17:15 | 4:29 | S/O | Due to For LA Base maintenance. | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Feni 132 kV Ckt-1 | 2024-10-20 08:26 | 2024-10-20 17:58 | 9:32 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Feni 132 kV Ckt-1 | 2024-10-21 08:20 | 2024-10-21 08:20 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon 132 kV Ckt-1 | 2024-10-21 09:54 | 2024-10-21 18:02 | 8:08 | S/O | Due to relay change | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Cumilla(S) 132 kV Ckt-1 | 2024-10-23 08:27 | 2024-10-23 16:38 | 8:11 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Cumilla(S) 132 kV Ckt-1 | 2024-10-23 08:45 | 2024-10-23 16:40 | 7:55 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Cumilla(S) 132 kV Ckt-1 | 2024-10-24 08:28 | 2024-10-24 16:28 | 8:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Cumilla(S) 132 kV Ckt-2 | 2024-10-26 09:25 | 2024-10-26 09:25 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Cumilla(S) 132 kV Ckt-2 | 2024-10-27 08:22 | 2024-10-27 16:25 | 8:03 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sylhet 132 kV Ckt-1 | 2024-10-29 08:17 | 2024-10-29 17:40 | 9:23 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Shahjibazar 132kV Ckt-1 | 2024-10-29 08:35 | 2024-10-29 16:52 | 8:17 | S/O | Maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Fenchuganj 132 kV Ckt-1 | 2024-10-29 09:08 | 2024-10-29 15:42 | 6:34 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Shahjibazar 132kV Ckt-1 | 2024-10-30 08:47 | 2024-10-30 08:47 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sylhet 132 kV Ckt-1 | 2024-10-30 09:03 | 2024-10-30 17:49 | 8:46 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Fenchuganj 132 kV Ckt-1 | 2024-10-30 09:10 | 2024-10-30 15:25 | 6:15 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132kV Grid Sub-Station | Ashuganj(S) 230kV Ckt-1 | 2024-10-30 09:50 | 2024-10-30 16:16 | 6:26 | S/O | Maintenance work | 0 | 0 | No interruption
Sylhet(S)132/33kV Grid Sub-Station | Fenchugonj 132KV Ckt-1 & 2 | 2024-10-31 07:04 | 2024-10-31 10:03 | 2:59 | S/O | Maintenance work | 40 | 119.3333 | Power interruption
Fenchuganj 132/33kV Grid Sub-Station | Sylhe 132kV Ckt-1 | 2024-10-31 07:05 | 2024-10-31 10:06 | 3:01 | S/O | Maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sylhet (T at Bianibazar) 132kV Ckt-2 | 2024-10-31 07:07 | 2024-10-31 10:03 | 2:56 | S/O | Maintenance work | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sylhet 132 kV Ckt-1 | 2024-10-31 08:20 | 2024-10-31 08:20 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Ashuganj 230/132kV Grid Sub-Station | Shahjibazar 132kV Ckt-1 | 2024-10-31 08:51 | 2024-10-31 18:35 | 9:44 | S/O | project work | 0 | 0 | No interruption
Ashuganj 230/132kV Grid Sub-Station | Ashuganj( S) 230 kV Ckt-2 | 2024-10-31 09:05 | 2024-10-31 16:36 | 7:31 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 176:15 |  | Unserved Energy: |  | 119.3333
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Labanchura 132 kV Ckt-2 | 2024-10-01 09:30 | 2024-10-01 13:09 | 3:39 | S/O | Due to Red hot maintenance work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | Bhandaria 132 kV Ckt-1 | 2024-10-03 09:26 | 2024-10-03 14:17 | 4:51 | S/O | Due to To remove fault | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Bhola 230 kV Ckt-1 | 2024-10-17 10:05 | 2024-10-17 18:26 | 8:21 | S/O | Due to ALDC work | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Bhola 230 kV Ckt-2 | 2024-10-18 10:25 | 2024-10-18 13:00 | 2:35 | S/O | Due to Power plant taken shutdown | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | Bhandaria 132 kV Ckt-1 | 2024-10-27 10:40 | 2024-10-27 12:36 | 1:56 | S/O | Due to Checking the line. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bhandaria 132 kV Ckt-1 | 2024-10-29 09:24 | 2024-10-29 15:00 | 5:36 | S/O | Due to Conductor armaring | 0 | 0 | No interruption
Gopalganj 400/230/132/33kV Grid Sub-Station | Madaripur 132kV Ckt-1 | 2024-10-29 09:26 | 2024-10-29 12:58 | 3:32 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj 400/230/132/33kV Grid Sub-Station | Madaripur 132kV Ckt-2 | 2024-10-29 13:00 | 2024-10-29 13:40 | 0:40 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj 400/230/132/33kV Grid Sub-Station | Faridpur-1 | 2024-10-29 14:08 | 2024-10-29 15:31 | 1:23 | S/O | Due to Instruction by ALDC for SCADA work. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Gopalganj(N) 132 kV Ckt-2 | 2024-10-29 15:46 | 2024-10-29 17:11 | 1:25 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj 400/230/132/33kV Grid Sub-Station | 230kV Faridpur CKT-02 | 2024-10-29 15:47 | 2024-10-29 17:10 | 1:23 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj 400/230/132/33kV Grid Sub-Station | 132kV Madaripur Ckt-4 | 2024-10-30 08:47 | 2024-10-30 19:17 | 10:30 | S/O | Maintenance work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-04 | 2024-10-30 08:48 | 2024-10-30 19:16 | 10:28 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj(O) 132/33kV Grid Sub-Station | Gopalgan (N) Ckt-1 | 2024-10-30 10:01 | 2024-10-30 11:36 | 1:35 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj(O) 132/33kV Grid Sub-Station | Gopalganj(N) 132kV Ckt-2 | 2024-10-30 11:42 | 2024-10-30 15:26 | 3:44 | S/O | project work | 0 | 0 | No interruption
Gopalganj 400/230/132/33kV Grid Sub-Station | Madaripur 132kV Ckt-3 | 2024-10-30 13:48 | 2024-10-30 16:19 | 2:31 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 64:09 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
BIPTC | Baharampur-3 | 2024-10-03 11:10 | 2024-10-03 12:05 | 0:55 | S/O | Due to upgradation work | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-2(L1) | 2024-10-17 08:24 | 2024-10-17 14:56 | 6:32 | S/O | Maintenance work | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Shahjadpur 132kV Ckt-1 | 2024-10-23 09:03 | 2024-10-23 13:31 | 4:28 | S/O | Due to BKR Gas Leakage Maintenance work. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Ishurdi 230 kV Ckt-1 | 2024-10-26 11:12 | 2024-10-26 12:54 | 1:42 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 13:37 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 2024-10-03 10:50 | 2024-10-03 14:44 | 3:54 | S/O | Due to GTPS Was tripping condition. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sirajganj 230 kV Ckt-1 | 2024-10-05 08:19 | 2024-10-05 09:49 | 1:30 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Rajshahi 132kV Ckt-2 | 2024-10-19 08:40 | 2024-10-19 20:52 | 12:12 | S/O | Due to CB problem | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | Bogura 230 kV Ckt-1 | 2024-10-19 10:24 | 2024-10-20 15:30 | 29:06 | S/O | Project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sirajganj 230 kV Ckt-2 | 2024-10-20 08:11 | 2024-10-20 16:26 | 8:15 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura 230 kV Ckt-2 | 2024-10-21 06:38 | 2024-10-21 06:38 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sirajganj 230 kV Ckt-2 | 2024-10-21 08:16 | 2024-10-21 16:23 | 8:07 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sirajganj 230 kV Ckt-2 | 2024-10-22 08:15 | 2024-10-22 17:31 | 9:16 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-1 | 2024-10-24 09:03 | 2024-10-24 17:34 | 8:31 | S/O | Project work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | RPC | 2024-10-24 09:30 | 2024-10-24 15:30 | 6:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-2 | 2024-10-25 08:56 | 2024-10-25 17:08 | 8:12 | S/O | Project work | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | Bogura 230 kV Ckt-1 | 2024-10-26 06:57 | 2024-10-26 06:57 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Chowdala 132 KV Line Ckt-02 | 2024-10-30 08:44 | 2024-10-30 08:44 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Chowdala 132 KV Line Ckt-02 | 2024-10-30 08:45 | 2024-10-30 08:45 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Rahanpur Ckt-1 | 2024-10-30 09:09 | 2024-10-30 17:16 | 8:07 | S/O | Project work | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Niamatpur 132 KV Line Ckt-01 | 2024-10-30 09:13 | 2024-10-30 17:16 | 8:03 | S/O | Maintenance work | 0 | 0 | No interruption
Mithapukur132/33kV Grid Sub-Station | Palashbari 132kV Ckt-1 | 2024-10-31 10:09 | 2024-10-31 13:50 | 3:41 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 114:54 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0:00 |  |  |  | 0:00
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1045:30 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:October 2024
| Area | Previous Month (September' 2024) |  |  |  | Current Month (October '2024)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 30 | 20 | 55 | 105 | 19 | 14 | 118 | 151
2 | Dhaka (South) Grid Circle. | 19 | 9 | 24 | 52 | 19 | 18 | 35 | 72
3 | Chattogram Grid Circle. | 20 | 13 | 24 | 57 |  | 9 | 65 | 74
4 | Cumilla Grid Circle. | 25 | 13 | 49 | 87 | 7 | 6 | 64 | 77
5 | Khulna Grid Circle. | 30 | 39 | 65 | 134 | 13 | 2 | 107 | 122
6 | HVDC Grid Circle | 7 | 23 | 28 | 58 | 7 | 3 | 20 | 30
7 | Bogura Grid Circle. | 34 | 25 | 35 | 94 | 10 | 6 | 77 | 93
8 | Others | Total number of T: 3; Total number of Total: 3; Total number of S/O: 1; Total number of Total: 1
9 | Total | 168 | 142 | 280 | 590 | 75 | 58 | 487 | 620
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:October 2024
| Area | Previous Month (September' 2024) |  |  |  | Current Month (October '2024)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 428.47 | 927 | 1494.6 | 2850.07 | 157.12 | 733.83 | 301.32 | 1192.27
2 | Dhaka (South) Grid Circle. | 35.02 | 630.42 | 820 | 1485.44 | 1107.65 | 661.67 | 375.4 | 2144.72
3 | Chattogram Grid Circle. | 231.26 | 602.63 | 179.77 | 1013.66 | 100.93 | 92.22 | 118.05 | 311.2
4 | Cumilla Grid Circle. | 135.45 | 185 | 764.49 | 1084.94 | 319.92 | 57.33 | 540.03 | 917.28
5 | Khulna Grid Circle. | 286.28 | 1074.47 | 838.42 | 2199.17 | 114.01 | 119 | 807.2 | 1040.21
6 | HVDC Grid Circle | 13.33 | 178.53 | 856.03 | 1047.89 | 31.17 | 55.27 | 12.33 | 98.77
7 | Bogura Grid Circle. | 1515.15 | 447.22 | 2047.45 | 4009.82 | 55.8 | 280.01 | 233.27 | 569.08
8 | Others | 21.25 | - | - | 21.25 |  | - | - | 0
9 | Total | 2666.21 | 4045.27 | 7000.76 | 13712.24 | 1886.6 | 1999.33 | 2387.6 | 6273.53
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:October 2024
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 10 | 9 | 19 | 1 | 8 | 10 | 1118.27
2 | Dhaka (South) | 5031.6 | 8 | 3 | 11 | 4 | 1 | 6 | 572.67
3 | Chattogram | 2042 | 6 | 2 | 8 | 2 |  | 6 | 306.7
4 | Khulna | 2434 | 14 | 20 | 34 | 8 | 3 | 23 | 963.13
5 | HVDC | 5954.3 | 5 | 1 | 6 | 2 | 1 | 3 | 98.76
6 | Bogura | 3145.6 | 11 | 5 | 16 | 5 |  | 11 | 569.09
7 | Cumilla | 2981 | 11 | 11 | 22 | 7 | 4 | 11 | 786.65
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 4415.27
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 96.55%
2 | Dhaka (South) | 99.96%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | HVDC | 99.98%
6 | Bogura | 99.98%
7 | Cumilla | 99.97%
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:October 2024
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 |  | 2 | 1 | - | 1 | 74
2 | Dhaka (South) | 990.29 | - | 5 | - | 5 | - | 1 | 4 | 1572.07
3 | Chattogram | 917 | - | 1 | - | 1 | 1 | - | - | 4.5
4 | Khulna | 1238.4 | - | 3 |  | 3 | 3 | - |  | 77.08
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | - | - | - | - | - | - | -
7 | Cumilla | 1648.16 | - | 2 | 1 | 3 | 2 | - | 1 | 130.63
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 1858.28
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 97.76%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 100%
7 | Cumilla | 99.99%
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:October 2024
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2024-10-01 | 9 | - | 14 | 23hr27 min | 1 | 4hr19 min | - | - |  |  | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:October 2024
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Sreepur 230/132/33kV Grid Sub-Station | 1 | 0:51 | 59.5
Bhaluka 132/33kV Grid Sub-Station | 1 | 1:58 | 49.1667
Tangail 132/33kV Grid Sub-Station | 2 | 1:08 | 45.33
Sherpur 132/33kV Grid Sub-Station | 1 | 0:34 | 14.1667
Mirzapur 132/33kV Grid Sub-Station | 1 | 1:46 | 35.3333
Kishoreganj 132/33kV Grid Sub-Station | 1 | 1:00 | 48
Sreepur 230/132kV Grid Sub-Station | 1 | 9:25 | 489.6667
Mymensingh 132/33kV Grid Sub-Station | 1 | 0:11 | 12.2833
Joydebpur132/33kV Grid Sub-Station | 2 | 4:00 | 63.5
Ghatail 132/33kV Grid Sub-Station | 1 | 0:10 | 38
Haripur 230/132/33kV Grid Sub-Station | 1 | 1:48 | 36
Joydebpur 230/132kV Grid Sub-Station | 1 | 1:14 | 30.8333
Bhaluka 132/33kV Grid Sub-Station | 2 | 2:22 | 71
Joydebpur 132/33kV Grid Sub-Station | 3 | 1:55 | 59.87
Manikganj 132/33kV Grid Sub-Station | 1 | 1:21 | 33.75
Joydebpur 132/33kV Grid Sub-Station | 1 | 1:26 | 17.2
Kishoreganj 132/33kV Grid Sub-Station | 1 | 7:17 | 72.8333
Jamalpur 132/33kV Grid Sub-Station | 1 | 0:38 | 15.8333
Bhulta 132/33kV Grid Sub-Station | 1 | 0:12 | 16
Manikganj 132/33kV Grid Sub-Station | 1 | 1:12 | 72
Madanganj 132/33kV Grid Sub-Station | 1 | 2:21 | 11.75
Manikganj 132/33kV Grid Sub-Station | 1 | 1:21 | 54
Sonargaon 132/33kV Grid Sub-Station | 1 | 0:18 | 9.9
Munshiganj 132/33kV Grid Sub-Station | 1 | 0:29 | 15.93
Bhulta132/33kV Grid Sub-Station | 1 | 0:53 | 17.6667
Rampura 230/132/33kV Grid Sub-Station | 2 | 0:45 | 30
Sitalakhya 132/33kV Grid Sub-Station | 1 | 5:34 | 656.8667
Haripur 230/132/33kV Grid Sub-Station | 1 | 10:26 | 281.7
Meghnaghat 230/132kV Grid Sub-Station | 1 | 4:19 | 518
Haripur 230/132/33kV Grid Sub-Station | 1 | 5:42 | 85.5
Sonargaon 132/33kV Grid Sub-Station | 3 | 9:18 | 375.42
Baroirhat 132/33kV Grid Sub-Station | 1 | 0:02 | 0.8
TK chemical 132/33kV Grid Sub-Station | 1 | 2:55 | 2.9167
Khulshi 132/33kV Grid Sub-Station | 1 | 0:09 | 8.1
Coxsbazar 132/33kV Grid Sub-Station | 2 | 2:52 | 143.33
Halishahar 132/33kV Grid Sub-Station | 1 | 1:07 | 33.5
Cox'sbazar 132/33kV Grid Sub-Station | 1 | 0:09 | 4.5
Coxsbazar 132/33kV Grid Sub-Station | 1 | 1:47 | 80.25
Dohazari 132/33kV Grid Sub-Station | 1 | 0:54 | 37.8
Sreemongol 132/33kV Grid Sub-Station | 1 | 0:03 | 1
Sylhet 132/33kV Grid Sub-Station | 2 | 7:37 | 200.25
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 0:07 | 1.8667
Chowmuhani 132/33kV Grid Sub-Station | 1 | 1:58 | 49.1667
Cumilla(S)132/33kV Grid Sub-Station | 2 | 2:01 | 84.7
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 0:14 | 18.6667
Sylhet(S) 132/33kV Grid Sub-Station | 2 | 0:21 | 6.3
Shahjibazar 132/33kV Grid Sub-Station | 1 | 0:08 | 4
Chowmuhani 132/33kV Grid Sub-Station | 1 | 0:09 | 3.3
Fenchuganj 132/33kV Grid Sub-Station | 1 | 0:12 | 8
Shahjibazar 132/33kV Grid Sub-Station | 1 | 2:02 | 10.1667
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 2:08 | 64
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 0:19 | 9.5
Cumilla(S) 132/33kV Grid Sub-Station | 3 | 5:28 | 164
Sylhet 132/33kV Grid Sub-Station | 1 | 0:49 | 9.8
Ramganj 132/33kV Grid Sub-Station | 1 | 2:54 | 29
Sylhet 132/33kV Grid Sub-Station | 1 | 0:49 | 16.3333
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 3:12 | 64
Sylhet(S) 132/33kV Grid Sub-Station | 2 | 5:26 | 173.23
Faridpur 132/33kV Grid Sub-Station | 2 | 0:22 | 11.7333
Patuakhali 132/33kV Grid Sub-Station | 1 | 0:13 | 1.95
Satkhira 132/33kV Grid Sub-Station | 1 | 1:21 | 54
Benapole 132/33kV Grid Sub-Station | 1 | 0:09 | 2.25
Noapara 132/33kV Grid Sub-Station | 2 | 0:10 | 1.92
Barguna 132/33kV Grid Sub-Station | 1 | 0:55 | 11
Barishal 132/33kV Grid Sub-Station | 1 | 0:05 | 2.33
Bagerhat 132/33kV Grid Sub-Station | 2 | 0:46 | 5.75
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:23 | 5.75
Satkhira 132/33kV Grid Sub-Station | 1 | 1:17 | 0
Faridpur 132/33kV Grid Sub-Station | 1 | 1:12 | 7.2
Satkhira 132/33kV Grid Sub-Station | 1 | 1:27 | 50.75
Gallamari 132/33kV Grid Sub-Station | 1 | 0:52 | 1.3
Barishal 132/33kV Grid Sub-Station | 3 | 0:47 | 77.08
Bagerhat 132/33kV Grid Sub-Station | 2 | 3:34 | 42.8
Goalpara 132/33kV Grid Sub-Station | 3 | 11:10 | 44.62
Barishal 132/33kV Grid Sub-Station | 1 | 1:04 | 7.4667
Gopalpara 132/33kV Grid Sub-Station | 1 | 4:26 | 44.3333
Borhanuddin 230/33kV Grid Sub-Station | 1 | 1:35 | 87.0833
Barishal 132/33kV Grid Sub-Station | 1 | 0:51 | 17
Bagerhat 132/33kV Grid Sub-Station | 1 | 1:08 | 17
Bhola 132/33kV Grid Sub-Station | 1 | 4:42 | 258.5
Bagerhat 132/33kV Grid Sub-Station | 2 | 4:21 | 65.25
Shariatpur 132/33kV Grid Sub-Station | 1 | 1:42 | 17
Noapara132/33kV Grid Sub-Station | 2 | 2:02 | 24.4
Goalpara 132/33kV Grid Sub-Station | 3 | 15:13 | 71.5
Bagerhat 132/33kV Grid Sub-Station | 2 | 3:09 | 110.25
Kushtia 132/33kV Grid Sub-Station | 1 | 1:37 | 12.9333
Ishurdi 230/132kV Grid Sub-Station | 1 | 3:58 | 0
Pabna 132/33kV Grid Sub-Station | 1 | 0:57 | 19
Jashore 132/33kV Grid Sub-Station | 1 | 1:10 | 23.3333
Shahjadpur 132/33kV Grid Sub-Station | 1 | 1:56 | 0
Ishurdi 230/132 Grid Sub-Station | 1 | 17:18 | 0
Jhenaidah 132/33kV Grid Sub-Station | 1 | 0:30 | 18.5
Jashore 132/33kV Grid Sub-Station | 1 | 0:00 | 0
Jhenaidah 132/33kV Grid Sub-Station | 1 | 0:20 | 12.6667
Kushtia 132/33kV Grid Sub-Station | 1 | 1:14 | 12.3333
Saidpur 132/33kV Grid Sub-Station | 1 | 1:59 | 49.5833
Bogura 132/33kV Grid Sub-Station | 1 | 5:58 | 89.5
Saidpur 132/33kV Grid Sub-Station | 3 | 1:57 | 45.25
Bogura -Sherpur132/33kV Grid Sub-Station | 2 | 5:53 | 100.93
Naogaon 132/33kV Grid Sub-Station | 3 | 1:47 | 28.95
Mithapukur132/33kV Grid Sub-Station | 1 | 0:27 | 21.6
Mahasthangarh 132/33kV Grid Sub-Station | 2 | 3:42 | 111.7
Bogura 132/33kV Grid Sub-Station | 1 | 4:47 | 57.4
Purbasadipur 132/33kV Grid Sub-Station | 1 | 1:30 | 22.5
Rangpur 132/33kV Grid Sub-Station | 1 | 2:05 | 41.6667
Total Unserved energy : | 139 | 251:47 | 6273.54
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: October 2024
Sl. No | Sub-station | Load (MW) | Time
1 | AKS | 11 | 2024-10-13 20:00
2 | AKSML | 129 | 2024-10-29 08:00
3 | Aftabnagar | 62 | 2024-10-01 13:00
4 | Agargaon | 129 | 2024-10-01 13:00
5 | Agrabad | 144 | 2024-10-12 12:00
6 | Amnura | 62 | 2024-10-02 20:00
7 | Ashuganj | 92 | 2024-10-28 23:00
8 | BSRM | 148 | 2024-10-09 19:30
9 | Bagerhat | 95 | 2024-10-17 20:00
10 | Bakulia | 111 | 2024-10-27 16:00
11 | Banani | 77.8 | 2024-10-01 13:00
12 | Bangabhaban | 24 | 2024-10-01 11:00
13 | Barapukuria | 62 | 2024-10-02 20:00
14 | Barguna | 24 | 2024-10-02 22:00
15 | Barishal | 120 | 2024-10-08 12:00
16 | Barishal-230 | 132 | 2024-10-13 07:00
17 | Baroaulia | 81 | 2024-10-22 12:00
18 | Baroirhat | 79 | 2024-10-17 19:30
19 | Bashundhara | 198 | 2024-10-01 13:00
20 | BashundharaCement | 13 | 2024-10-22 11:00
21 | Beanibazar | 80 | 2024-10-02 22:00
22 | Benapole | 67 | 2024-10-01 22:00
23 | Bhaluka | 174 | 2024-10-02 19:30
24 | Bhandaria | 63 | 2024-10-08 21:00
25 | Bhangura | 39 | 2024-10-02 19:30
26 | Bheramara(GK) | 65 | 2024-10-07 20:00
27 | Bhulta | 305 | 2024-10-01 06:00
28 | Bog-Sherpur | 64 | 2024-10-16 19:00
29 | Bogura | 170 | 2024-10-02 19:00
30 | Borhanuddin | 92 | 2024-10-10 21:00
31 | Brahmanbaria | 192 | 2024-10-27 19:30
32 | Cantonment | 130 | 2024-10-17 13:00
33 | Chandpur | 71 | 2024-10-28 19:30
34 | Chandraghona | 37 | 2024-10-17 19:30
35 | Chapai | 65 | 2024-10-02 21:00
36 | Charsaidpur | 45 | 2024-10-22 03:00
37 | Chauddagram | 80 | 2024-10-22 19:30
38 | Chhatak | 40 | 2024-10-02 22:00
39 | Chowmuhani | 232 | 2024-10-09 19:30
40 | Chuadanga | 116 | 2024-10-17 18:30
41 | Coxsbazar | 121 | 2024-10-14 13:00
42 | Cumilla(N) | 173 | 2024-10-01 20:00
43 | Cumilla(S) | 184 | 2024-10-21 18:00
44 | Daudkandi | 167 | 2024-10-22 19:30
45 | Dhaka | 44 | 2024-10-28 12:00
46 | Dhamrai | 136 | 2024-10-17 13:00
47 | Dhanmondi | 150 | 2024-10-02 12:00
48 | Dohazari | 109 | 2024-10-20 18:00
49 | Faridpur | 173 | 2024-10-01 21:00
50 | Fatullah | 108 | 2024-10-02 15:00
51 | Fenchuganj | 48 | 2024-10-17 19:00
52 | Feni | 120 | 2024-10-01 19:30
53 | GPH | 103 | 2024-10-17 18:00
54 | Ghatail | 68 | 2024-10-10 18:30
55 | Ghorashal | 65 | 2024-10-01 19:30
56 | Goalpara | 38 | 2024-10-13 00:00
57 | Gollamari | 86 | 2024-10-17 13:00
58 | Gopalganj | 115.6 | 2024-10-02 20:00
59 | Gulshan | 90 | 2024-10-01 13:00
60 | Halishahar | 80 | 2024-10-26 16:00
61 | HaripurSBU | 198 | 2024-10-02 13:00
62 | Hasnabad | 109 | 2024-10-02 19:30
63 | Hathazari | 89 | 2024-10-17 20:00
64 | Ishurdi | 81 | 2024-10-02 19:00
65 | Jaldhaka | 84 | 2024-10-07 18:30
66 | Jamalpur | 122 | 2024-10-03 18:30
67 | Jashore | 143 | 2024-10-01 20:00
68 | Jhenaidah | 130 | 2024-10-01 20:00
69 | Joydebpur | 222 | 2024-10-02 18:30
70 | Joypurhat | 62 | 2024-10-02 20:00
71 | Juldah | 21 | 2024-10-07 00:00
72 | KSRM | 48 | 2024-10-23 09:00
73 | Kabirpur | 307 | 2024-10-06 19:00
74 | Kachua | 94 | 2024-10-16 22:00
75 | Kallyanpur | 120 | 2024-10-16 18:00
76 | Kalurghat | 40 | 2024-10-07 12:00
77 | Kamrangirchar | 67 | 2024-10-31 13:00
78 | Kaptai | N/A | N/A
79 | Kazla | 121 | 2024-10-09 13:00
80 | Keranigonj | 90 | 2024-10-17 16:00
81 | Khagrachori | 34 | 2024-10-13 18:00
82 | Khulna | 98 | 2024-10-02 13:00
83 | Khulshi | 190 | 2024-10-21 18:30
84 | Kishoreganj | 162 | 2024-10-07 18:00
85 | Kodda | 316 | 2024-10-22 18:00
86 | Kulaura | 54 | 2024-10-17 19:00
87 | Kurigram | 68 | 2024-10-02 19:30
88 | Kushtia | 152 | 2024-10-07 19:00
89 | Lalbag | 96 | 2024-10-15 13:00
90 | Lalmonirhat | 62 | 2024-10-01 00:00
91 | MI_Cement | 17.7 | 2024-10-31 00:00
92 | Madanganj | 44 | 2024-10-01 18:00
93 | Madaripur | 109 | 2024-10-02 19:00
94 | Madartek | 89.72 | 2024-10-31 18:00
95 | Madunaghat | 60 | 2024-10-29 18:30
96 | Magura | 66 | 2024-10-02 21:00
97 | Mahasthangarh | 82 | 2024-10-12 00:00
98 | Manikganj | 131 | 2024-10-02 20:00
99 | Maniknagar | 78 | 2024-10-08 13:00
100 | Matarbari | 50 | 2024-10-01 19:00
101 | Matuail | 70 | 2024-10-29 16:00
102 | Millgate | 133 | 2024-10-01 15:00
103 | Mirpur | 149 | 2024-10-01 15:00
104 | Mirsorai | 7 | 2024-10-01 17:00
105 | Mirzapur | 58 | 2024-10-23 18:00
106 | Mithapukur | 80 | 2024-10-22 23:00
107 | Modern | 0 | 2024-10-01 00:00
108 | Mogbazar | 131.7 | 2024-10-31 15:00
109 | Mongla | 46 | 2024-10-16 12:00
110 | Motijheel | 56 | 2024-10-01 13:00
111 | Munshiganj | 111 | 2024-10-01 22:00
112 | Mymensingh | 240 | 2024-10-02 21:00
113 | Naogaon | 131 | 2024-10-01 20:00
114 | Narail | 60 | 2024-10-01 07:00
115 | Narinda | 80 | 2024-10-01 13:00
116 | Narshingdi | 175 | 2024-10-04 20:00
117 | Natore | 145 | 2024-10-19 18:30
118 | Nawabganj | 70.6 | 2024-10-21 14:00
119 | Netrakona | 129 | 2024-10-10 18:30
120 | New | 58 | 2024-10-08 12:00
121 | Niamatpur | 71 | 2024-10-17 19:00
122 | Noapara | 45 | 2024-10-02 19:30
123 | PHP | 10 | 2024-10-01 04:00
124 | Pabna | 124 | 2024-10-07 18:30
125 | Palashbari | 133 | 2024-10-01 19:00
126 | Panchagarh | 62 | 2024-10-08 18:30
127 | Patuakhali | 84.5 | 2024-10-01 21:00
128 | Payra | 48 | 2024-10-02 18:30
129 | Postogola | 56 | 2024-10-01 00:00
130 | Purbachal | 12 | 2024-10-01 00:00
131 | Purbasadipur | 123 | 2024-10-01 21:00
132 | Rahim | 56 | 2024-10-08 12:00
133 | Rajbari | 84 | 2024-10-02 21:00
134 | Rajendrapur | 124 | 2024-10-02 12:00
135 | Rajshahi | 149 | 2024-10-01 21:00
136 | Rajshahi-230 | 74 | 2024-10-29 13:00
137 | Ramganj | 124 | 2024-10-22 22:00
138 | Rampur | 45 | 2024-10-24 18:00
139 | Rangamati | 18 | 2024-10-01 19:00
140 | Rangpur | 151 | 2024-10-07 18:30
141 | Ruppur | 7.4 | 2024-10-02 10:00
142 | SSM | 19 | 2024-10-03 03:00
143 | Saidpur | 116 | 2024-10-08 18:30
144 | Satkhira | 136 | 2024-10-01 22:00
145 | Satmasjid | 119 | 2024-10-02 13:00
146 | Savar | 225 | 2024-10-23 18:00
147 | SevenRings | 17.94 | 2024-10-10 17:00
148 | ShahCement | 32 | 2024-10-11 19:00
149 | Shahjadpur | 94 | 2024-10-02 19:00
150 | Shahjibazar | 140 | 2024-10-09 18:30
151 | Shahmirpur | 59 | 2024-10-21 02:00
152 | Shariatpur | 90 | 2024-10-01 07:00
153 | Sherpur | 144 | 2024-10-11 18:30
154 | Shikalbaha | 80 | 2024-10-03 01:00
155 | Shitalakhya | 90.8 | 2024-10-16 13:00
156 | Sholosohor | 49 | 2024-10-14 18:00
157 | Shyampur | 178 | 2024-10-27 11:00
158 | Siddhirganj | 126 | 2024-10-01 11:00
159 | Sirajganj | 124 | 2024-10-02 19:30
160 | Sonargaon | 101 | 2024-10-06 14:00
161 | Sreemongol | 82 | 2024-10-06 18:30
162 | Sreepur | 83 | 2024-10-03 03:00
163 | Srinagar | 50 | 2024-10-01 21:00
164 | Sunamganj | 60 | 2024-10-02 19:00
165 | Sylhet | 80 | 2024-10-27 13:00
166 | Sylhet-132 | 131 | 2024-10-02 16:00
167 | TK | 35.4 | 2024-10-01 00:00
168 | Tangail | 192 | 2024-10-02 23:00
169 | Thakurgaon | 106 | 2024-10-01 20:00
170 | Tongi | 142 | 2024-10-29 10:00
171 | Ullahpara | 43 | 2024-10-28 18:30
172 | Ullon | 61 | 2024-10-02 18:00
173 | Uttara | 95 | 2024-10-07 12:00
174 | UttaraNew | 57 | 2024-10-01 15:00
175 | Zigatola | 108 | 2024-10-01 14:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: October 2024
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5400.07 | 2024-10-01 | 14:00
Chattogram | 1479 | 2024-10-09 | 19:00
Cumilla | 1404 | 2024-10-22 | 20:00
Mymensingh | 1160 | 2024-10-02 | 19:30
Sylhet | 632 | 2024-10-02 | 22:00
Khulna | 1753.6 | 2024-10-02 | 20:00
Barishal | 497 | 2024-10-01 | 20:00
Rajshahi | 1478.6 | 2024-10-02 | 20:00
Rangpur | 986 | 2024-10-02 | 20:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: October 2024
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 392 | 2024-10-05 06:00 | 358 | 2024-10-15 19:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 405 | 2024-10-11 17:00 | 221 | 2024-10-28 15:00
4 | Bibiana | 400 | 401 | 2024-10-11 17:00 | 379 | 2024-10-16 11:00
5 | BIPTC | 400 | 409 | 2024-10-10 02:00 | 295 | 2024-10-06 19:30
6 | Bogura | 400 | 391 | 2024-10-02 02:00 | 368 | 2024-10-11 20:00
7 | Gopalganj | 400 | 402 | 2024-10-05 06:00 | 360 | 2024-10-20 17:00
8 | Kaliakoir | 400 | 396 | 2024-10-31 18:00 | 330 | 2024-10-06 17:00
9 | Madunaghat | 400 | 401 | 2024-10-03 08:00 | 309 | 2024-10-25 18:00
| Meghnaghat | 400 | 385 | 2024-10-19 04:00 | 219 | 2024-10-09 01:00
11 | Payra | 400 | 414 | 2024-10-05 06:00 | 400 | 2024-10-30 12:00
12 | Rahanpur | 400 | 406 | 2024-10-05 08:00 | 381 | 2024-10-11 20:00
13 | Rampal | 400 | 407 | 2024-10-11 17:00 | 381 | 2024-10-22 23:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 236 | 2024-10-11 17:00 | 214 | 2024-10-16 11:00
2 | AKSML | 230 | 242 | 2024-10-02 19:00 | 223 | 2024-10-20 08:00
3 | Aminbazar | 230 | 249 | 2024-10-02 13:00 | 210 | 2024-10-16 14:00
4 | Ashuganj | 230 | 236 | 2024-10-11 18:30 | 232 | 2024-10-05 20:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 235 | 2024-10-05 05:00 | 221 | 2024-10-06 12:00
7 | Barapukuria | 230 | 227 | 2024-10-25 06:00 | 222 | 2024-10-11 01:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 239 | 2024-10-05 06:00 | 230 | 2024-10-16 02:00
10 | Bheramara | 230 | 236 | 2024-10-01 20:00 | 222 | 2024-10-05 23:00
11 | Bhulta | 230 | 238 | 2024-10-11 17:00 | 216 | 2024-10-02 13:00
12 | Bibiana | 230 | 229 | 2024-10-11 17:00 | 217 | 2024-10-30 11:00
13 | BIPTC | 230 | 239 | 2024-10-27 07:00 | 221 | 2024-10-05 23:00
14 | Bogura | 230 | 235 | 2024-10-25 05:00 | 222 | 2024-10-01 00:00
15 | Bogura-400 | 230 | 254 | 2024-10-10 03:00 | 226 | 2024-10-10 03:00
16 | Borhanuddin | 230 | 242 | 2024-10-17 17:00 | 225 | 2024-10-06 16:00
17 | BSRM | 230 | 241 | 2024-10-02 20:00 | 222 | 2024-10-17 10:00
18 | Cumilla(N) | 230 | 234 | 2024-10-11 17:00 | 226 | 2024-10-16 05:00
19 | Faridpur | 230 | 237 | 2024-10-05 05:00 | 219 | 2024-10-24 03:00
20 | Fenchuganj | 230 | 232 | 2024-10-11 17:00 | 229 | 2024-10-11 18:00
22 | Ghorashal | 230 | 238 | 2024-10-05 01:00 | 222 | 2024-10-16 13:00
23 | Ghorashal-230 | 230 | 236 | 2024-10-11 17:00 | 215 | 2024-10-02 13:00
24 | Gopalganj | 230 | 260 | 2024-10-01 16:00 | 224 | 2024-10-22 23:00
25 | GPH | 230 | 242 | 2024-10-02 22:00 | 225 | 2024-10-17 10:00
26 | Haripur | 230 | 234 | 2024-10-11 17:00 | 216 | 2024-10-21 11:00
27 | Hasnabad | 230 | 255 | 2024-10-15 20:00 | 228 | 2024-10-04 00:00
28 | Hathazari | 230 | 244 | 2024-10-19 19:30 | 235 | 2024-10-12 13:00
29 | Ishurdi | 230 | 238 | 2024-10-19 03:00 | 224 | 2024-10-05 23:00
30 | Jhenaidah | 230 | 232 | 2024-10-24 04:00 | 214 | 2024-10-17 19:30
31 | Kaliakoir | 230 | 238 | 2024-10-11 17:00 | 216 | 2024-10-16 11:00
32 | Keranigonj | 230 | 235 | 2024-10-11 17:00 | 211 | 2024-10-16 11:00
33 | Khulna(S) | 230 | 233 | 2024-10-04 08:00 | 217 | 2024-10-06 19:00
34 | Madunaghat | 230 | N/A | N/A | N/A | N/A
35 | Madunaghat-400 | 230 | 243 | 2024-10-03 20:00 | 229 | 2024-10-16 12:00
37 | Maniknagar | 230 | 234 | 2024-10-11 17:00 | 215 | 2024-10-02 13:00
38 | Meghnaghat | 230 | 241 | 2024-10-12 03:00 | 224 | 2024-10-09 10:00
39 | Meghnaghat-400 | 230 | 389 | 2024-10-11 17:00 | 220 | 2024-10-30 12:00
40 | Mirsorai | 230 | 242 | 2024-10-19 19:00 | 225 | 2024-10-09 11:00
41 | Rajshahi | 230 | 237 | 2024-10-23 06:00 | 222 | 2024-10-04 23:00
42 | Rampal | 230 | 233 | 2024-10-04 08:00 | 217 | 2024-10-07 22:00
43 | Rampur | 230 | N/A | N/A | N/A | N/A
44 | Rampura | 230 | 236 | 2024-10-11 17:00 | 214 | 2024-10-02 13:00
45 | Shikalbaha | 230 | 242 | 2024-10-02 18:30 | 226 | 2024-10-17 09:00
46 | Shyampur | 230 | 236 | 2024-10-11 17:00 | 233 | 2024-10-10 21:00
47 | Siddhirganj | 230 | 237 | 2024-10-11 17:00 | 217 | 2024-10-02 14:00
48 | Sirajgonj | 230 | 241 | 2024-10-31 06:00 | 231 | 2024-10-06 12:00
49 | Sreepur | 230 | 233 | 2024-10-04 07:00 | 226 | 2024-10-07 01:00
50 | Tongi | 230 | 237 | 2024-10-11 17:00 | 212 | 2024-10-09 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 164 | 2024-10-11 06:00 | 130 | 2024-10-30 10:00
2 | Agargaon | 132 | 139 | 2024-10-05 06:00 | 35 | 2024-10-03 02:00
3 | Agrabad | 132 | 138 | 2024-10-02 18:30 | 112 | 2024-10-12 14:00
4 | AKS | 132 | 137 | 2024-10-02 19:00 | 126 | 2024-10-09 11:00
5 | Aminbazar | 132 | 142 | 2024-10-11 17:00 | 122 | 2024-10-16 15:00
6 | Amnura | 132 | 145 | 2024-10-29 07:00 | 121 | 2024-10-11 22:00
7 | Ashuganj | 132 | 140 | 2024-10-04 21:00 | 133 | 2024-10-21 11:00
8 | Bagerhat | 132 | 138 | 2024-10-01 17:00 | 119 | 2024-10-07 23:00
9 | Bakulia | 132 | 167 | 2024-10-09 22:00 | 128 | 2024-10-09 11:00
10 | Banani | 132 | 139 | 2024-10-25 09:00 | 119 | 2024-10-02 13:00
11 | Bangabhaban | 132 | 133 | 2024-10-12 07:00 | 118 | 2024-10-02 13:00
12 | Barapukuria | 132 | 142 | 2024-10-25 06:00 | 129 | 2024-10-03 00:00
13 | Barguna | 132 | 141 | 2024-10-01 17:00 | 131 | 2024-10-05 19:30
14 | Barishal | 132 | 135 | 2024-10-03 06:00 | 122 | 2024-10-22 23:00
15 | Barishal-230 | 132 | 138 | 2024-10-24 11:00 | 124 | 2024-10-06 14:00
16 | Baroaulia | 132 | 139 | 2024-10-01 18:30 | 128 | 2024-10-09 12:00
17 | Baroirhat | 132 | 135 | 2024-10-17 17:00 | 112 | 2024-10-02 08:00
18 | Bashundhara | 132 | 138 | 2024-10-11 17:00 | 120 | 2024-10-09 09:00
19 | BashundharaCement | 132 | 137 | 2024-10-14 18:30 | 119 | 2024-10-02 13:00
20 | Beanibazar | 132 | 132 | 2024-10-01 05:00 | 123 | 2024-10-04 04:00
21 | Benapole | 132 | 138 | 2024-10-09 19:00 | 120 | 2024-10-17 19:30
22 | Bhaluka | 132 | 132 | 2024-10-18 07:00 | 117 | 2024-10-18 19:00
23 | Bhandaria | 132 | 136 | 2024-10-05 06:00 | 115 | 2024-10-07 22:00
24 | Bhangura | 132 | 141 | 2024-10-17 17:00 | 132 | 2024-10-02 19:30
25 | Bheramara | 132 | 138 | 2024-10-17 17:00 | 135 | 2024-10-28 09:00
26 | Bheramara(GK) | 132 | 138 | 2024-10-23 05:00 | 128 | 2024-10-14 11:00
27 | Bhulta | 132 | 127 | 2024-10-11 21:00 | 110 | 2024-10-23 10:00
28 | Bog-Sherpur | 132 | 141 | 2024-10-25 06:00 | 129 | 2024-10-09 11:00
29 | Bogura | 132 | 142 | 2024-10-17 17:00 | 129 | 2024-10-09 18:00
30 | Bogura-230 | 132 | 142 | 2024-10-17 17:00 | 132 | 2024-10-05 01:00
31 | Brahmanbaria | 132 | 136 | 2024-10-11 17:00 | 120 | 2024-10-06 12:00
32 | Cantonment | 132 | 139 | 2024-10-11 17:00 | 124 | 2024-10-16 11:00
33 | Chandpur | 132 | 138 | 2024-10-17 15:00 | 116 | 2024-10-16 15:00
34 | Chandraghona | 132 | 140 | 2024-10-02 19:00 | 131 | 2024-10-09 11:00
35 | Chapai | 132 | 134 | 2024-10-04 08:00 | 123 | 2024-10-10 22:00
36 | Charsaidpur | 132 | 132 | 2024-10-04 18:00 | 120 | 2024-10-02 13:00
37 | Chauddagram | 132 | 135 | 2024-10-17 17:00 | 115 | 2024-10-16 15:00
38 | Chhatak | 132 | 132 | 2024-10-17 17:00 | 116 | 2024-10-07 18:00
39 | Chowmuhani | 132 | 135 | 2024-10-17 15:00 | 130 | 2024-10-08 03:00
40 | Chuadanga | 132 | 136 | 2024-10-09 17:00 | 114 | 2024-10-07 22:00
41 | Coxsbazar | 132 | 131 | 2024-10-01 16:00 | 116 | 2024-10-09 11:00
42 | Cumilla(N) | 132 | 143 | 2024-10-27 18:30 | 122 | 2024-10-16 15:00
43 | Cumilla(S) | 132 | 139 | 2024-10-05 18:30 | 116 | 2024-10-11 10:00
44 | Daudkandi | 132 | 132 | 2024-10-24 15:00 | 116 | 2024-10-22 11:00
45 | Dhaka | 132 | 139 | 2024-10-25 09:00 | 122 | 2024-10-02 13:00
46 | Dhamrai | 132 | 135 | 2024-10-08 18:30 | 127 | 2024-10-12 22:00
47 | Dhanmondi | 132 | 139 | 2024-10-31 06:00 | 112 | 2024-10-18 01:00
48 | Dohazari | 132 | 139 | 2024-10-02 19:00 | 113 | 2024-10-08 15:00
49 | Faridpur | 132 | 133 | 2024-10-05 06:00 | 112 | 2024-10-28 19:00
50 | Fatullah | 132 | 138 | 2024-10-11 17:00 | 123 | 2024-10-16 10:00
51 | Fenchuganj | 132 | 140 | 2024-10-11 17:00 | 127 | 2024-10-08 01:00
52 | Feni | 132 | 133 | 2024-10-17 17:00 | 115 | 2024-10-16 15:00
53 | Ghatail | 132 | 132 | 2024-10-17 16:00 | 115 | 2024-10-13 19:30
54 | Ghorashal | 132 | 139 | 2024-10-09 20:00 | 128 | 2024-10-22 15:00
55 | Goalpara | 132 | 140 | 2024-10-18 15:00 | 126 | 2024-10-06 19:30
56 | Gollamari | 132 | 139 | 2024-10-04 08:00 | 127 | 2024-10-07 22:00
57 | Gopalganj | 132 | 137 | 2024-10-01 17:00 | 125 | 2024-10-07 22:00
58 | Gopalganj-400 | 132 | 134 | 2024-10-03 06:00 | 126 | 2024-10-06 14:00
59 | Gulshan | 132 | 138 | 2024-10-25 06:00 | 121 | 2024-10-02 13:00
60 | Halishahar | 132 | 139 | 2024-10-02 18:30 | 127 | 2024-10-17 10:00
61 | Haripur | 132 | 132 | 2024-10-11 17:00 | 111 | 2024-10-12 08:00
62 | HaripurSBU | 132 | 126 | 2024-10-26 18:30 | 121 | 2024-10-21 11:00
63 | Hasnabad | 132 | 140 | 2024-10-11 17:00 | 124 | 2024-10-16 11:00
64 | Hathazari | 132 | 142 | 2024-10-02 19:00 | 131 | 2024-10-24 12:00
65 | Ishurdi | 132 | 139 | 2024-10-09 16:00 | 131 | 2024-10-04 23:00
66 | Jaldhaka | 132 | 136 | 2024-10-25 05:00 | 116 | 2024-10-03 01:00
67 | Jamalpur | 132 | 141 | 2024-10-05 19:00 | 119 | 2024-10-04 04:00
68 | Jashore | 132 | 138 | 2024-10-09 19:00 | 120 | 2024-10-17 19:30
69 | Jhenaidah | 132 | 138 | 2024-10-03 09:00 | 125 | 2024-10-07 22:00
70 | Jhenaidah-230 | 132 | 139 | 2024-10-24 04:00 | 112 | 2024-10-28 13:00
71 | Joydebpur | 132 | 140 | 2024-10-11 17:00 | 115 | 2024-10-15 16:00
72 | Joypurhat | 132 | 132 | 2024-10-04 10:00 | 116 | 2024-10-17 19:00
73 | Juldah | 132 | 140 | 2024-10-02 20:00 | 135 | 2024-10-27 02:00
74 | Kabirpur | 132 | 136 | 2024-10-11 17:00 | 117 | 2024-10-16 14:00
75 | Kachua | 132 | 137 | 2024-10-22 18:00 | 118 | 2024-10-16 11:00
76 | Kaliakoir | 132 | 136 | 2024-10-08 18:30 | 120 | 2024-10-16 12:00
77 | Kallyanpur | 132 | 158 | 2024-10-23 08:00 | 121 | 2024-10-02 13:00
78 | Kalurghat | 132 | 140 | 2024-10-03 19:00 | 115 | 2024-10-22 21:00
79 | Kamrangirchar | 132 | 138 | 2024-10-12 06:00 | 120 | 2024-10-02 13:00
80 | Kaptai | 132 | N/A | N/A | N/A | N/A
81 | Kazla | 132 | 133 | 2024-10-12 07:00 | 117 | 2024-10-02 13:00
82 | Keranigonj | 132 | 138 | 2024-10-11 17:00 | 123 | 2024-10-16 11:00
83 | Khagrachori | 132 | 138 | 2024-10-02 19:00 | 127 | 2024-10-16 12:00
84 | Khulna | 132 | 139 | 2024-10-04 09:00 | 113 | 2024-10-06 03:00
85 | Khulna(S) | 132 | 140 | 2024-10-04 08:00 | 127 | 2024-10-07 22:00
86 | Khulshi | 132 | 138 | 2024-10-02 18:30 | 126 | 2024-10-09 12:00
87 | Kishoreganj | 132 | 133 | 2024-10-11 19:00 | 122 | 2024-10-19 11:00
88 | Kodda | 132 | 139 | 2024-10-11 17:00 | 113 | 2024-10-16 14:00
89 | KSRM | 132 | 140 | 2024-10-02 18:30 | 115 | 2024-10-27 19:30
90 | Kulaura | 132 | 138 | 2024-10-11 17:00 | 126 | 2024-10-07 19:30
91 | Kurigram | 132 | 137 | 2024-10-25 06:00 | 112 | 2024-10-03 05:00
92 | Kushtia | 132 | 138 | 2024-10-08 02:00 | 127 | 2024-10-05 23:00
93 | Lalbag | 132 | 138 | 2024-10-12 07:00 | 122 | 2024-10-16 11:00
94 | Lalmonirhat | 132 | 136 | 2024-10-25 06:00 | 113 | 2024-10-16 06:00
95 | Madanganj | 132 | 131 | 2024-10-04 17:00 | 115 | 2024-10-17 08:00
96 | Madaripur | 132 | 134 | 2024-10-11 17:00 | 124 | 2024-10-30 16:00
97 | Madartek | 132 | 138 | 2024-10-25 06:00 | 120 | 2024-10-02 13:00
98 | Madunaghat | 132 | 140 | 2024-10-02 19:30 | 130 | 2024-10-09 11:00
99 | Magura | 132 | 138 | 2024-10-03 09:00 | 122 | 2024-10-07 22:00
100 | Mahasthangarh | 132 | 140 | 2024-10-17 17:00 | 129 | 2024-10-02 19:30
101 | Manikganj | 132 | 130 | 2024-10-08 18:00 | 113 | 2024-10-15 14:00
102 | Maniknagar | 132 | 133 | 2024-10-11 17:00 | 119 | 2024-10-24 20:00
103 | Matarbari | 132 | 135 | 2024-10-02 18:30 | 115 | 2024-10-17 19:00
104 | Matuail | 132 | 133 | 2024-10-11 17:00 | 108.6 | 2024-10-04 12:00
105 | Millgate | 132 | 158 | 2024-10-14 18:30 | 120 | 2024-10-16 14:00
106 | Mirpur | 132 | 141 | 2024-10-11 17:00 | 132 | 2024-10-26 17:00
107 | Mirzapur | 132 | 131 | 2024-10-11 17:00 | 117 | 2024-10-12 12:00
108 | Mithapukur | 132 | 138 | 2024-10-03 03:00 | 116 | 2024-10-28 03:00
109 | MI_Cement | 132 | 140 | 2024-10-12 07:00 | 121.4 | 2024-10-16 15:00
110 | Modern | 132 | 139 | 2024-10-02 18:30 | 127 | 2024-10-17 10:00
111 | Mogbazar | 132 | 142 | 2024-10-25 08:00 | 110 | 2024-10-29 14:00
112 | Mongla | 132 | 138 | 2024-10-18 15:00 | 110 | 2024-10-07 23:00
113 | Motijheel | 132 | 133 | 2024-10-12 07:00 | 118 | 2024-10-02 13:00
114 | Munshiganj | 132 | 131 | 2024-10-04 17:00 | 120 | 2024-10-02 13:00
115 | Mymensingh | 132 | 137 | 2024-10-01 00:00 | 114 | 2024-10-19 08:00
116 | Naogaon | 132 | 139 | 2024-10-17 17:00 | 118 | 2024-10-17 19:00
117 | Narail | 132 | 139 | 2024-10-03 09:00 | 112 | 2024-10-21 12:00
118 | Narinda | 132 | 8 | 2024-10-02 07:00 | 8 | 2024-10-02 07:00
119 | Narshingdi | 132 | 131 | 2024-10-24 15:00 | 110 | 2024-10-02 13:00
120 | Natore | 132 | 138 | 2024-10-17 17:00 | 108 | 2024-10-03 12:00
121 | Nawabganj | 132 | 138 | 2024-10-25 08:00 | 123 | 2024-10-16 11:00
122 | Netrakona | 132 | 136 | 2024-10-01 13:00 | 114 | 2024-10-09 18:30
123 | New | 132 | 138 | 2024-10-12 08:00 | 121 | 2024-10-21 11:00
124 | Niamatpur | 132 | 135 | 2024-10-04 08:00 | 125 | 2024-10-11 19:30
125 | Noapara | 132 | 139 | 2024-10-18 15:00 | 124 | 2024-10-07 19:30
126 | Pabna | 132 | 140 | 2024-10-09 16:00 | 129 | 2024-10-05 23:00
127 | Palashbari | 132 | 138 | 2024-10-25 06:00 | 122 | 2024-10-02 20:00
128 | Panchagarh | 132 | 140 | 2024-10-05 21:00 | 110 | 2024-10-03 01:00
129 | Patuakhali | 132 | 169 | 2024-10-22 00:00 | 122 | 2024-10-20 23:00
130 | Payra | 132 | 139 | 2024-10-02 14:00 | 133 | 2024-10-09 12:00
131 | PHP | 132 | 135 | 2024-10-17 17:00 | 113 | 2024-10-16 15:00
132 | Postogola | 132 | 140 | 2024-10-11 17:00 | 113 | 2024-10-27 05:00
133 | Purbachal | 132 | 139 | 2024-10-25 02:00 | 120 | 2024-10-02 13:00
134 | Purbasadipur | 132 | 138 | 2024-10-26 20:00 | 115 | 2024-10-03 02:00
135 | Rahanpur | 132 | 136 | 2024-10-01 17:00 | 128 | 2024-10-11 20:00
136 | Rahim | 132 | 138 | 2024-10-07 18:30 | 121 | 2024-10-21 11:00
137 | Rajbari | 132 | 133 | 2024-10-07 18:00 | 122 | 2024-10-22 23:00
138 | Rajendrapur | 132 | 134 | 2024-10-06 17:00 | 112 | 2024-10-16 15:00
139 | Rajshahi | 132 | 138 | 2024-10-31 18:00 | 116 | 2024-10-22 06:00
140 | Rajshahi-230 | 132 | 138 | 2024-10-23 19:00 | 118 | 2024-10-11 20:00
141 | Ramganj | 132 | 135 | 2024-10-22 18:00 | 112 | 2024-10-29 01:00
142 | Rampur | 132 | 139 | 2024-10-02 19:30 | 128 | 2024-10-09 11:00
143 | Rampura | 132 | 139 | 2024-10-25 07:00 | 121 | 2024-10-02 13:00
144 | Rangamati | 132 | 138 | 2024-10-01 18:30 | 130 | 2024-10-09 10:00
145 | Rangpur | 132 | 138 | 2024-10-29 06:00 | 113 | 2024-10-12 23:00
146 | Ruppur | 132 | 140 | 2024-10-23 06:00 | 130 | 2024-10-10 20:00
147 | Saidpur | 132 | 139 | 2024-10-26 20:00 | 113 | 2024-10-06 23:00
148 | Satkhira | 132 | 138 | 2024-10-24 06:00 | 120 | 2024-10-07 22:00
149 | Satmasjid | 132 | 139 | 2024-10-05 16:00 | 124 | 2024-10-02 13:00
150 | Savar | 132 | 141 | 2024-10-11 17:00 | 108 | 2024-10-21 02:00
151 | SevenRings | 132 | 141 | 2024-10-11 17:00 | 128 | 2024-10-22 16:00
152 | ShahCement | 132 | 132 | 2024-10-04 18:00 | 120 | 2024-10-02 13:00
153 | Shahjadpur | 132 | 143 | 2024-10-20 04:00 | 130 | 2024-10-21 19:00
154 | Shahjibazar | 132 | 137 | 2024-10-11 17:00 | 120 | 2024-10-07 22:00
155 | Shahmirpur | 132 | 139 | 2024-10-02 18:00 | 128 | 2024-10-09 11:00
156 | Shariatpur | 132 | 135 | 2024-10-04 16:00 | 122 | 2024-10-22 23:00
157 | Sherpur | 132 | 140 | 2024-10-17 15:00 | 115 | 2024-10-10 18:00
158 | Shikalbaha | 132 | 129 | 2024-10-02 18:30 | 117 | 2024-10-09 11:00
159 | Shikalbaha-230 | 132 | 141 | 2024-10-02 19:00 | 111 | 2024-10-29 20:00
160 | Shitalakhya | 132 | 140 | 2024-10-12 07:00 | 121 | 2024-10-16 15:00
161 | Sholosohor | 132 | 139 | 2024-10-02 18:30 | 128 | 2024-10-09 10:00
162 | Shyampur | 132 | 137 | 2024-10-29 07:00 | 120 | 2024-10-22 16:00
163 | Shyampur-230 | 132 | 138 | 2024-10-11 17:00 | 137 | 2024-10-10 21:00
164 | Siddhirganj | 132 | 133 | 2024-10-11 17:00 | 121 | 2024-10-02 13:00
165 | Sirajganj | 132 | 139 | 2024-10-17 17:00 | 127 | 2024-10-02 21:00
166 | Sonargaon | 132 | 132 | 2024-10-11 17:00 | 117 | 2024-10-09 11:00
167 | Sreemongol | 132 | 136 | 2024-10-11 17:00 | 122 | 2024-10-07 21:00
168 | Sreepur | 132 | 133 | 2024-10-19 04:00 | 123 | 2024-10-02 14:00
169 | Srinagar | 132 | 138 | 2024-10-12 06:00 | 122 | 2024-10-16 10:00
170 | SSM | 132 | 141 | 2024-10-27 18:00 | 129 | 2024-10-09 12:00
171 | Sunamganj | 132 | 130 | 2024-10-01 04:00 | 116 | 2024-10-07 18:00
172 | Sylhet | 132 | 133 | 2024-10-01 05:00 | 120 | 2024-10-07 18:30
173 | Sylhet-132 | 132 | 133 | 2024-10-11 17:00 | 120 | 2024-10-07 18:00
174 | Tangail | 132 | 132 | 2024-10-01 00:00 | 115 | 2024-10-13 19:30
175 | Thakurgaon | 132 | 141 | 2024-10-26 20:00 | 109 | 2024-10-03 01:00
176 | TK | 132 | 140 | 2024-10-02 20:00 | 128 | 2024-10-17 10:00
177 | Tongi | 132 | 140 | 2024-10-11 17:00 | 124 | 2024-10-07 12:00
178 | Ullahpara | 132 | 140 | 2024-10-17 16:00 | 124 | 2024-10-08 08:00
179 | Ullon | 132 | 138 | 2024-10-11 17:00 | 121 | 2024-10-02 13:00
180 | Uttara | 132 | 140 | 2024-10-11 17:00 | 124 | 2024-10-22 12:00
181 | UttaraNew | 132 | 141 | 2024-10-11 18:30 | 123 | 2024-10-15 11:00
182 | Zigatola | 132 | 137 | 2024-10-12 07:00 | 132 | 2024-10-30 03:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: October 2024
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 16-10-2024 | 10:00 | 400 | 150 | 82.1539
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 01-10-2024 | 12:00 | 401 | 92 | 79.1189
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 01-10-2024 | 12:00 | 401 | 92 | 79.1189
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 10-10-2024 | 18:30 | 256 | 70 | 81.6609
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 28-10-2024 | 10:00 | -284 | -122 | 59.4414
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 28-10-2024 | 10:00 | -284 | -122 | 59.4414
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 09-10-2024 | 19:30 | -195 | 0 | 37.5
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 09-10-2024 | 19:30 | -184 | 7 | 35.4102
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 01-10-2024 | 00:00 | 377 | 8 | 50.278
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 01-10-2024 | 00:00 | 377 | 8 | 50.278
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 01-10-2024 | 00:00 | 377 | 8 | 50.278
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 06-10-2024 | 19:30 | -141 | -2 | 18.8019
Gopalganj 400/230kV Grid Sub-Station | ATR-05 | 400/230 | 750 | 06-10-2024 | 19:30 | -141 | -2 | 18.8019
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 02-10-2024 | 22:00 | -135 | -25 | 42.2447
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 02-10-2024 | 22:00 | -135 | -25 | 42.2447
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 02-10-2024 | 22:00 | -135 | -25 | 42.2447
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 18-10-2024 | 10:00 | 249 | 63 | 49.3935
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 22-10-2024 | 00:00 | 287 | 68 | 56.7203
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 12-10-2024 | 18:00 | 304 | 33 | 94.088
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 12-10-2024 | 18:00 | 304 | 33 | 94.088
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 01-10-2024 | 14:00 | -448 | -263 | 69.2657
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 01-10-2024 | 14:00 | -448 | -263 | 69.2657
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 02-10-2024 | 20:00 | -277 | -64 | 54.6726
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 02-10-2024 | 20:00 | -273 | -64 | 53.9234
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 30-10-2024 | 14:00 | -69 | -17 | 21.8656
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 26-10-2024 | 13:00 | -81 | -28 | 26.3701
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 11-10-2024 | 04:00 | 504 | 182 | 103.0489
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 11-10-2024 | 04:00 | 504 | 182 | 103.0489
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 01-10-2024 | 13:00 | 180 | 66 | 63.9062
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 01-10-2024 | 13:00 | 180 | 66 | 63.9062
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 30-10-2024 | 11:00 | 223 | 45 | 101.1089
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 16-10-2024 | 08:00 | 187 | 47 | 85.696
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 05-10-2024 | 09:00 | 193 | 56 | 89.3156
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 26-10-2024 | 20:00 | 230 | 104 | 84.1401
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 18-10-2024 | 19:00 | 156 | 30 | 52.9528
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 11-10-2024 | 19:30 | 121 | 56 | 44.4435
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 04-10-2024 | 22:00 | 125 | 58 | 61.2447
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 01-10-2024 | 18:00 | 198 | 30 | 89.0044
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 01-10-2024 | 18:00 | 170 | 57 | 79.6895
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 01-10-2024 | 18:30 | 19 | 5 | 6.549
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 29-10-2024 | 12:00 | 164 | 28 | 55.4577
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 21-10-2024 | 21:00 | 183 | 18 | 61.2944
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 14-10-2024 | 09:00 | -74 | 38 | 36.9718
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 14-10-2024 | 09:00 | -74 | 38 | 36.9718
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 29-10-2024 | 14:00 | 175 | 56 | 81.663
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 03-10-2024 | 17:00 | 140 | 35 | 64.1372
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 04-10-2024 | 21:00 | 188 | 49 | 64.7602
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 04-10-2024 | 21:00 | 188 | 49 | 64.7602
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 13-10-2024 | 04:00 | 172 | 70 | 82.5327
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 13-10-2024 | 04:00 | 170 | 68 | 81.3758
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 13-10-2024 | 04:00 | 184 | 73 | 87.9787
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 07-10-2024 | 19:00 | 162 | 67 | 58.4361
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 07-10-2024 | 19:00 | 198 | 88 | 72.225
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 10-10-2024 | 18:00 | 99 | 0 | 79.2
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 10-10-2024 | 18:00 | 99 | 0 | 79.2
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 12-10-2024 | 08:00 | 131 | 54 | 62.9748
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 23-10-2024 | 10:00 | 127 | 18 | 57.0086
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 23-10-2024 | 10:00 | 115 | 13 | 51.4366
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 30-10-2024 | 12:00 | 78 | 52 | 41.6641
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 30-10-2024 | 12:00 | 78 | 52 | 41.6641
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 30-10-2024 | 12:00 | 78 | 52 | 41.6641
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 18-10-2024 | 06:00 | 126 | 49 | 90.1283
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 09-10-2024 | 11:00 | 120 | 47 | 85.9173
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 18-10-2024 | 06:00 | 126 | 49 | 90.1283
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 18-10-2024 | 06:00 | 126 | 49 | 90.1283
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 13-10-2024 | 20:00 | 79 | 52 | 42.0347
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 13-10-2024 | 20:00 | 79 | 52 | 42.0347
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 02-10-2024 | 21:00 | 73 | 40 | 36.9958
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 02-10-2024 | 22:00 | -191 | -70 | 67.8077
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 02-10-2024 | 22:00 | -191 | -70 | 67.8077
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 17-10-2024 | 14:00 | 136 | 64 | 50.1021
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 27-10-2024 | 18:30 | 113 | 37 | 39.6344
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 27-10-2024 | 18:30 | 113 | 37 | 39.6344
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 27-10-2024 | 18:30 | 113 | 37 | 39.6344
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 02-10-2024 | 20:00 | -146 | -48 | 68.3058
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 02-10-2024 | 20:00 | -146 | -48 | 68.3058
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 02-10-2024 | 20:00 | -189 | -56 | 65.7073
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 02-10-2024 | 12:00 | 172 | 66 | 61.4094
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 02-10-2024 | 12:00 | 172 | 66 | 61.4094
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 31-10-2024 | 07:00 | -46 | 0 | 15.3333
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 31-10-2024 | 07:00 | -46 | 0 | 15.3333
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-10-2024 | 00:00 | 0 | 0 | 0
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-10-2024 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 01-10-2024 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 25-10-2024 | 12:00 | 427 | 35 | 95.2071
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 18-10-2024 | 10:00 | 376 | -19 | 83.6622
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 09-10-2024 | 12:00 | 253 | 107 | 91.5654
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 09-10-2024 | 12:00 | 253 | 107 | 91.5654
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 09-10-2024 | 03:00 | 127 | 87 | 51.3138
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 09-10-2024 | 03:00 | 127 | 87 | 51.3138
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 30-10-2024 | 19:30 | 226 | 116 | 84.6772
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 01-10-2024 | 09:00 | 165 | 136 | 71.2749
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 03-10-2024 | 03:00 | 179 | 54 | 62.3226
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 03-10-2024 | 03:00 | 179 | 54 | 62.3226
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 01-10-2024 | 18:30 | 210 | 37 | 94.7709
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 01-10-2024 | 18:30 | 190 | 48 | 87.0975
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 01-10-2024 | 18:30 | 190 | 48 | 87.0975
Executive Engineer
Information Management Division
[5 empty] | LDC, Power Grid, Dhaka. |  |  |  | 270

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: October 2024 | [6 empty] | (For Evening Peak) | [7 empty] | Month: October 2024 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2024-10-01 | 14677 | 15200 | 499 | 20:00 | 60 | 0 | 80 | 70 | 60 | 130 | 34 | 0 | 65 | - | 2024-10-01 | 12738 | 13030 | 584 | 11:00 | 280 | 0 | 115 | 0 | 60 | 129 | 0 | 0 | 0 | -
2024-10-02 | 14082 | 14344 | 250 | 19:00 | 50 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | - | 2024-10-02 | 12704 | 13500 | 760 | 12:00 | 187 | 74 | 106 | 0 | 154 | 167 | 51 | 21 | 0 | -
2024-10-03 | 13390 | 13390 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-10-03 | 12037 | 12100 | 60 | 12:00 | 45 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | -
2024-10-04 | 12218 | 11528 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-10-04 | 10526 | 10526 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-05 | 13204 | 13204 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-10-05 | 10767 | 10767 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-06 | 13928 | 14030 | 97 | 20:00 | 45 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | - | 2024-10-06 | 12188 | 12280 | 88 | 12:00 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-07 | 14347 | 14520 | 165 | 19:00 | 75 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | - | 2024-10-07 | 12514 | 12600 | 82 | 12:00 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-08 | 13705 | 13750 | 43 | 21:00 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-10-08 | 12552 | 12670 | 113 | 12:00 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-09 | 13510 | 13510 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-10-09 | 12644 | 12680 | 34 | 12:00 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-10 | 13804 | 13900 | 92 | 19:00 | 20 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | - | 2024-10-10 | 11785 | 11785 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-11 | 12798 | 12635 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-10-11 | 11253 | 11253 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-12 | 13950 | 14010 | 57 | 19:00 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | - | 2024-10-12 | 12025 | 12025 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-13 | 13719 | 13790 | 68 | 19:00 | 0 | 0 | 0 | 0 | 28 | 40 | 0 | 0 | 0 | - | 2024-10-13 | 11998 | 11998 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-14 | 14122 | 14220 | 94 | 20:00 | 20 | 0 | 0 | 0 | 15 | 59 | 0 | 0 | 0 | - | 2024-10-14 | 12573 | 12620 | 45 | 12:00 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-15 | 14092 | 14270 | 170 | 20:00 | 67 | 0 | 0 | 0 | 42 | 61 | 0 | 0 | 0 | - | 2024-10-15 | 12276 | 12550 | 262 | 12:00 | 129 | 0 | 71 | 0 | 62 | 0 | 0 | 0 | 0 | -
2024-10-16 | 13863 | 14320 | 436 | 19:30 | 147 | 0 | 6 | 0 | 126 | 157 | 0 | 0 | 0 | - | 2024-10-16 | 11984 | 12500 | 493 | 12:00 | 347 | 0 | 0 | 0 | 88 | 58 | 0 | 0 | 0 | -
2024-10-17 | 13818 | 13900 | 78 | 19:30 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-10-17 | 11757 | 11860 | 98 | 12:00 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-18 | 12197 | 11814 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-10-18 | 10995 | 10995 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-19 | 13501 | 13545 | 42 | 19:00 | 27 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | - | 2024-10-19 | 11819 | 11850 | 30 | 12:00 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-20 | 13654 | 13730 | 73 | 19:00 | 35 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | - | 2024-10-20 | 12174 | 12270 | 92 | 12:00 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-21 | 13785 | 13900 | 110 | 19:00 | 32 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | - | 2024-10-21 | 12143 | 12200 | 54 | 12:00 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-22 | 13994 | 14150 | 149 | 20:00 | 34 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | - | 2024-10-22 | 12254 | 12620 | 350 | 12:00 | 231 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | -
2024-10-23 | 13391 | 13125 | 37 | 18:00 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | - | 2024-10-23 | 12328 | 12550 | 212 | 12:00 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-24 | 11358 | 11243 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-10-24 | 10943 | 10943 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-25 | 11329 | 11329 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-10-25 | 9989 | 9989 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-26 | 13296 | 13480 | 176 | 19:30 | 39 | 0 | 0 | 0 | 15 | 122 | 0 | 0 | 0 | - | 2024-10-26 | 11199 | 11199 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-10-27 | 13638 | 13820 | 174 | 19:30 | 124 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | - | 2024-10-27 | 11771 | 12250 | 457 | 12:00 | 227 | 106 | 0 | 0 | 82 | 42 | 0 | 0 | 0 | -
2024-10-28 | 13404 | 14000 | 569 | 19:30 | 30 | 0 | 124 | 65 | 65 | 165 | 45 | 15 | 60 | - | 2024-10-28 | 11920 | 12300 | 363 | 12:00 | 273 | 10 | 0 | 0 | 70 | 10 | 0 | 0 | 0 | -
2024-10-29 | 13176 | 14000 | 787 | 19:30 | 170 | 30 | 120 | 50 | 125 | 130 | 60 | 42 | 60 |  | 2024-10-29 | 11859 | 12400 | 517 | 12:00 | 268 | 78 | 0 | 0 | 110 | 61 | 0 | 0 | 0
2024-10-30 | 12933 | 13900 | 923 | 20:00 | 85 | 95 | 150 | 140 | 160 | 110 | 73 | 30 | 80 |  | 2024-10-30 | 11700 | 12400 | 669 | 12:00 | 250 | 100 | 95 | 0 | 120 | 84 | 20 | 0 | 0
2024-10-31 | 12638 | 14000 | 1301 | 21:00 | 158 | 224 | 237 | 164 | 154 | 136 | 78 | 69 | 81 |  | 2024-10-31 | 11812 | 12500 | 657 | 12:00 | 231 | 52 | 100 | 56 | 117 | 55 | 12 | 8 | 26
|  | - | - | - | [11 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: October 2024
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 14677 | 2024-10-01 | 20:00
2 | Maximum Day Peak Genaration | MW | 12738 | 2024-10-01 | 11:00
3 | Maximum Evening Peak Demand | MW | 15200 | 2024-10-01 | 20:00
4 | Minimum Generation | MW | 8574 | 2024-10-25 | 6:00
5 | Average of the daily evening peak Genaration | MW | 13360.3226 | - | -
6 | Average of the daily day peak Genaration | MW | 11846.0323 | - | -
7 | Maximum load shed (Evening Peak) | MW | 1301 | 2024-10-31 | 21:00
8 | Minimum load shed | MW | 0 | 2024-10-04 | 21:00
9 | Total nos. of load shed days | Day | 23 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 206.129 | - | -
11 | Total Generation | MkWh | 8950.179 | - | -
12 | Total Generation by BPDB | MkWh | 1472.1777 | % of total Gen. | 16.45%
13 | Total Generation by IPP | MkWh | 2911.4144 | '' | 32.53%
14 | A) Total Generation by Generation Companies | MkWh | 2897.3002 | '' | 32.37%
| B) Total Generation by REB | MkWh | 93.2436 | " | 1.042%
| C) Total Generation by RENTAL | MkWh | 131.2355 | " | 1.466%
| D) Total Imported from India (BIPTC) | MkWh | 639.8034 | " | 7.148%
| E) Total Imported from Tripura, India (A.C) | MkWh | 48.6125 | " | 0.5431%
| F) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 756.3919 |  | 8.451%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3827.7099 | % of total Gen. | 42.77%
| B) Oil | MkWh | 1166.4527 | '' | 13.03%
| C) Hydro | MkWh | 143.6604 | '' | 1.605%
| D) Solar | MkWh | 94.1464 | '' | 1.052%
| E) Coal | MkWh | 2269.173 | '' | 25.35%
| F) BIPTC (Import from India) | MkWh | 639.8034 | '' | 7.148%
| G) A.C (Import from Tripura, India) | MkWh | 48.6125 | '' | 0.5431%
| H) Adani (Import from India) | MkWh | 756.3919 | '' | 8.451%
| I) Wind | MkWh | 4.2288 | '' | 0.04725%
16 | Maximun of the daily total Generation . | MkWh | 315.828 | 2024-10-01
17 | Monthly Load factor | % | 81.9637 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 56774.4904 | - | -
| A) Gas | M.Taka | 11363.6145 | - | -
| B) Liquid fuel | M.Taka | 21358.7401 | - | -
| C) Coal | M.Taka | 15772.7975 | - | -
| D) BIPTC (Import from India) | M.Taka | 2811.936 | - | -
| E) Tripura(Import from India) | M.Taka | 467.6521 | - | -
| F) Adani (Import from India) | M.Taka | 4999.7502 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2335.323 | 2024-10-01
| A) Gas | M.Taka | 382.0432 | 2024-10-28
| B) Liquid fuel | M.Taka | 1108.7993 | 2024-10-01
| C) Coal | M.Taka | 600.3115 | 2024-10-01
| D) BIPTC (Import from India) | M.Taka | 173.7829 | 2024-10-11
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.3434
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.4469
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 108.9 | 31/10/2024 | 06:00
b) | Actual | FT (MSL) | 101.84 | 31/10/2024 | 06:00
22 | Peak Genaration of October 2023 | MW | 14356 | 2023-10-11 | 20:00
23 | Peak Demand of October 2023 | MW | 14470 | 2023-10-30 | 18:00
24 | Maximum peak Generation recorded upto 31/10/2024 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 31/10/2024 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/10/2024 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: October 2024
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ |  | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400 |  |  |  |  | √
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
9 | Meghnaghat CCPP(Summit) | IPP | 335
10 | Ashuganj 225 MW CCPP | APSCL | 221 |  |  |  |  | √ | [11 empty] | √ | √ | √ | √ | √
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361 |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable | [14 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable | [14 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | [5 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | [9 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable | [12 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | [9 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable | [12 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | [9 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant