## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-12-27 | Friday
|  | Date (day): | 2024-12-27 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13790.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14419 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-12-26 | 2024-12-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 308 | 311 | 350 | 350 |  | 50 | Machine problem
| Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450 | 0
| Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
| Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Engine problem
11 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | under maint
13 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 236 | 254 | 0 | 300
15 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 94 |  | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
17 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 34 | 54
18 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 48 | 149 | 149
19 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 55 | 55
20 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
21 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 42 | 40 | 42 |  | 38 | Engine problem
23 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 22 | 25 | 25 |  | 8 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 22 | 33 | 33
25 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 34 | 34 | 34 | 34 | 18 |  | Fuel shoratage
26 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 34 | 149 | 149
29 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 8 | 7 | 17 | 87 |  | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 162 | 162
32 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 35 | 0
33 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 36 | 28 | 36 | 38 | 17 |  | Fuel shortage
34 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 355 | 420 | 589 | 400
35 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| JERA Meghnaghat Power Limited |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Dhaka area Total |  |  |  |  | 6268 | 5915 | 1607 | 1798 | 2608 | 2781 | 1927 | 931
36 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
37 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25
38 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
39 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 24 | 33 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 0 | 40 | 40 | 40 | 190 |  | Low water level
41 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 226 | 225 | 225
42 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 12 | 85 | 105
44 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 17 | 57 | 75 |  | 23 | Engine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 50 | 50 |  | 52 | Engine problem
| Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 40 | 100 | 100
| Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 8 | 20 | 20
47 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 6 | 20 | 50 | 58 |  | Fuel shortage
48 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
49 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 49 | 50 | 100 | 200 |  | Fuel shortage
50 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 54 | 54
51 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 12 | 110 | 110
52 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 50 | 100 | 100
53 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 30 | 50 | 108
54 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 17 | 17 | 160
55 | SS Power I |  | Coal | IPP | 2*612 | 1224 | 1224 | 580 | 590 | 612 | 612 | 612 |  | Unit-2 under maint
56 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 5 | 40 | 15 | 38 |  |  | On test.
57 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 2*575 | 1150 | 1150 | 576 | 575 | 575 | 575 |  | 575 | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4917 | 4857 | 1447 | 1799 | 2263 | 2597 | 1060 | 1160
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 187 | 209 | 215 | 215 |  |  | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 345 | 350 | 350 |  |  | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
62 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 42 | 43 | 43
63 | Ashuganj 55 MW PP (Precision) |  | Gas | NENP | 0 | 55 | 55 | 28 | 28 | 25 | 25 | 30 |  | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 190 | 185 | 185 | 195
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 38 | 140 | 150
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 30 | 40 |  | 12 | Engine problem
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 35 | 35 | 50 | 50 | 113 |  | Gas shortage
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 12 | 200 | 200
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 54 | 60 | 66 | 70
| Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 18 | 16 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
73 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
74 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 30 | 95 | 100 |  | 13 | Engine problem
75 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 4 | 50 | 92 | 23 |  | Fuel shortage
76 | Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 65 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2925 | 2917 | 978 | 1065 | 1752 | 1764 | 166 | 793
77 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 4 | 4 | 10 | 10 | 192 |  | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
80 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 66 | 100 | 200
81 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 65 | 55 | 115
82 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 43 | 0 | 50 | 0
83 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 9 | 22 | 22
84 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 52
| Sreepur 150 MW |  | HFO | BPDB-RPCL | 150 | 0 | 0 | 163 | 163 | 163 | 0
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 228 | 324 | 418.6 | 399 | 192 | 0
85 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
88 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
| Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
89 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
90 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 0 | 32 | 32 | 34 |  | Gas shortage
92 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 42 | 42 | 62 | 62 | 24 |  | Gas shortage
93 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
94 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 138 | 138 | 138 | 138 |  | 93 | ST Under maint.
95 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 13 | 13 | 13 |  | 12 | Engine problem
97 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 310 | 315 |  |  | FGMO
98 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 342 | 335 | 380 | 380
| Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 340 | 360 | 383 | 383
| Sylhet Area Total |  |  |  |  | 2411 | 2366 | 1405 | 1398 | 1518 | 1523 | 103 | 574
100 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 922 | 921 | 730 | 920
| Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 35 |  | 19 | Engine problem
102 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
103 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 34 | 60 |  | 49 | Engine problem
104 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 7 | 180 | 180 |  | 230 | ST Under maint.
| Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
106 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 72 | 0 | 100 | 0
108 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
109 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 1015 | 1135 | 1234 | 1234
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
** | Nepal |  | 0 | Imported power | 40 | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 2009 | 2063 | 2298 | 2429 | 456 | 298
110 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 | 110 |  | Fuel shortage
111 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 2 | 7 | 5 | 6 |  | 4 | Engine problem
112 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 68 | 68 |  | 126 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
113 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 0 | 0 | 0 | 0 |  |  | Gopalganj(N)-Payara 400 kV ckt-1 & 2 S/D
114 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 54 | 150
116 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 180 | 150 | 170 |  |  | Gopalganj(N)-Payara 400 kV ckt-1 & 2 S/D
117 | Barisal 1 MW Solar Plant |  | Solar | PDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 437 | 472 | 497 | 614 | 110 | 130
118 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 40 |  | 12 | Engine problem
120 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
121 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
| Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 26 | 32 |  | 18 | Engine problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 214 | 168 | 200 | 200 | 10
124 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 201 | 175 | 200 | 200 | 20
125 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 202 | 178 | 200 | 200 | 20
126 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | IPP, SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint |  | 2025-01-31
127 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 24 | 24 |  | 26 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
128 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
129 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 45 | 52
130 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 69 | 53 | 100
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 95 | 113
132 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
133 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 618 | 684 | 750 | 750
134 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 53 | 0 | 29 | 0
| Pabna Solar 100 MW |  | Solar | IPP | 100 | 0 | 0 | 87 | 0 | 47 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1384 | 1279 | 1793 | 1854 | 221 | 522
135 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 70 | 70 |  | 15 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
136 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 158 | 156 | 160 | 160 |  | 114 | Machine problem
137 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
138 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
139 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 90 | 113
140 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
141 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 70 | 115 | 115
142 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0
143 | Teesta Solar Limited |  | Solar | IPP | 16*12.5 | 200 | 200 | 169 | 0 | 170 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 361 | 226 | 643 | 458 | 40 | 214 | .
| Total |  |  |  |  | 27740 | 27035 | 9856 | 10424 | 13790.6 | 14419 | 4275 | 4622
A. |  | 2024-12-26 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 10424 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 6950 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10424 | MW
3 | Day peak Generation : |  |  | 9856 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10270.74 | MW
4 | Evening peak Generation : |  |  | 10424 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 216.9987 | MKWHr | By Solar | 3.5371 | MKWHr
| By Gas : | 111.923 | MKWHr |  | By Oil: | 9.4657 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 54.5931 | MKWHr |  | By Hydro: | 0.9591 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Adani: | 13.988 | MKWHr |  | By Wind: | 0.5784 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4275 | MW | Dhaka | 3957.74 | 3957.74 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4622 | MW | Chittagong | 1068 | 1068 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 8897 | MW | Khulna | 1173 | 1173 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  | 833.72 | MMCFD | **Import Adani: | Taka | 92460508.14 | Rajshahi | 963.8 | 963.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : |  | 311771160.5 | ii) Oil : | Taka | 104946166.6 | Comilla | 889 | 889 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 384141793.01 | Total | Taka | 893319628.25 | Mymensingh | 863 | 863 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7128 | MKWHr. | Sylhet | 352 | 352 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 648 | MW (W to E) at | 18:00 | hrs | Barisal | 297.2 | 297.2 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 350 | MW at | 7:00 | hrs | Rangpur | 707 | 707 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.5°C |  |  | Total | 10270.74 | 10270.74 |  | 0
B. |  | 2024-12-27 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 28.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14419 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8700 | MW
4 | Reserve(Generation end) |  |  |  | 3819 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 220.6625 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6981 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector(India) : |  |  |  |  | i) Energy | 20.784 | MKWHr. | ii) HVDC Flow at Peak Time |  | 921 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.1702 | MKWHr. | iii) Maximum HVDC Flow : |  | 922 | MW at | 12:00 | hrs.
* Import Through HVDC C/B Interconnector(Nepal) : |  |  |  |  | i) Energy | 0 | MKWHr.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.3 |  | (b) Today: | 94.24 |  | (c) Rule Curve: |  | 103.5
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-12-26 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | JERA Meghnaghat Power Limited | Sreepur 150 MW | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | Pabna Solar 100 MW | Nepal | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Nepal | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Adani | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 17 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 300 | 0 | 182 | 130 | 31 | 40 | 28 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 42 | 8 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 33 | 5 | 0 | 138 | 0 | 0 | 0 | 270 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 24 | 371 | 310 | 0 | 0 | 0 | 163 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 167 | 0 | 150 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 828 | 0 | 150 | 414 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4706 | 3232 | 7938 | 2860 | 920 | 0 | 1584 | 0 | 0 | 1891 | 40 | 0 | 163 | 42 | 414 | 0 | 24 | 0 | 94.31
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 305 | 0 | 182 | 78 | 30 | 36 | 29 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 40 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 33 | 5 | 0 | 138 | 0 | 0 | 0 | 265 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 31 | 373 | 300 | 0 | 0 | 0 | 163 |  | 732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 144 | 0 | 149 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 150 | 415 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4633 | 2921 | 7554 | 2821 | 732 | 0 | 1477 | 0 | 0 | 1835 | 40 | 0 | 163 | 40 | 415 | 0 | 31 | 0 | 94.31
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 300 | 0 | 182 | 8 | 40 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 38 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 120 | 0 | 20 | 5 | 0 | 138 | 0 | 0 | 0 | 270 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 33 | 371 | 300 | 0 | 0 | 0 | 163 |  | 731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 142 | 0 | 149 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 150 | 409 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4360 | 2912 | 7272 | 2794 | 731 | 0 | 1280 | 0 | 0 | 1784 | 40 | 0 | 163 | 38 | 409 | 0 | 33 | 0 | 94.31
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 300 | 0 | 181 | 8 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 38 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 120 | 0 | 20 | 5 | 0 | 138 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 36 | 372 | 300 | 0 | 0 | 0 | 163 |  | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 144 | 0 | 150 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767 | 0 | 150 | 414 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4271 | 2799 | 7070 | 2710 | 637 | 0 | 1250 | 0 | 0 | 1782 | 40 | 0 | 163 | 38 | 414 | 0 | 36 | 0 | 94.3
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 300 | 0 | 153 | 8 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 38 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 120 | 0 | 20 | 5 | 0 | 138 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 25 | 372 | 300 | 0 | 0 | 0 | 163 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 144 | 0 | 150 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 766 | 0 | 150 | 414 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4151 | 2799 | 6950 | 2647 | 636 | 0 | 1244 | 0 | 0 | 1743 | 40 | 0 | 163 | 38 | 414 | 0 | 25 | 0 | 94.3
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 17 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 310 | 0 | 199 | 8 | 40 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 40 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 163 | 0 | 20 | 5 | 0 | 138 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 32 | 374 | 350 | 0 | 0 | 0 | 163 |  | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 155 | 0 | 162 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 150 | 415 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4523 | 2881 | 7404 | 2853 | 637 | 0 | 1443 | 0 | 0 | 1781 | 40 | 0 | 163 | 40 | 415 | 0 | 32 | 0 | 94.3
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 17 | 26 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 300 | 0 | 186 | 184 | 40 | 37 | 8 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 33 | 42 | 0 | 138 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 365 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 364 | 35 | 455 | 273 | 0 | 2 | 0 | 163 |  | 733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 164 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 854 | 0 | 150 | 417 | 4 | 0 | 0 | 0 | 1 | 0 |  | 4915 | 3099 | 8014 | 2904 | 733 | 0 | 1658 | 0 | 15 | 1983 | 40 | 0 | 179 | 38 | 417 | 12 | 35 | 0 | 94.29
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 17 | 26 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 370 | 0 | 217 | 185 | 40 | 36 | 26 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 8 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 42 | 0 | 138 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 380 | 0 | 22 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 9 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 460 | 15 | 529 | 276 | 0 | 20 | 0 | 163 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 157 | 0 | 0 | 176 | 0 | 170 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 220 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 962 | 6 | 150 | 415 | 37 | 0 | 0 | 10 | 18 | 0 |  | 5312 | 3492 | 8804 | 3097 | 921 | 0 | 1679 | 0 | 30 | 2258 | 40 | 0 | 179 | 38 | 415 | 132 | 15 | 0 | 94.29
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 21 | 22 | 17 | 24 | 13 | 0 | 40 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 300 | 0 | 182 | 110 | 40 | 36 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 42 | 5 | 0 | 0 | 1 | 30 | 0 | 0 | 5 | 163 | 0 | 31 | 42 | 0 | 138 | 0 | 0 | 0 | 300 | 0 | 2 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 6 | 0 | 0 | 0 | 358 | 16 | 37 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 23 | 0 | 0 | 0 | 0 | 16 | 0 | 7 | 0 | 0 | 0 | 550 | 17 | 575 | 276 | 0 | 40 | 0 | 163 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 128 | 0 | 0 | 192 | 0 | 193 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 180 | 0 | 0 | 2 | 39 | 0 | 0 | 0 | 1104 | 15 | 150 | 517 | 91 | 0 | 0 | 28 | 44 | 0 |  | 5299 | 3854 | 9153 | 2950 | 921 | 0 | 1584 | 0 | 88 | 2507 | 40 | 0 | 179 | 42 | 517 | 308 | 17 | 0 | 94.29
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 25 | 20 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 5 | 0 | 0 | 0 | 280 | 0 | 182 | 110 | 40 | 40 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 4 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 20 | 11 | 0 | 138 | 0 | 0 | 0 | 280 | 8 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 13 | 0 | 0 | 0 | 323 | 8 | 52 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 34 | 0 | 0 | 0 | 0 | 23 | 0 | 36 | 0 | 0 | 0 | 550 | 5 | 575 | 320 | 0 | 55 | 0 | 163 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 144 | 0 | 0 | 156 | 0 | 157 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 180 | 0 | 0 | 3 | 45 | 0 | 0 | 0 | 1110 | 21 | 150 | 511 | 133 | 0 | 0 | 42 | 65 | 0 |  | 5239 | 3862 | 9101 | 2781 | 921 | 0 | 1463 | 0 | 181 | 2529 | 40 | 0 | 179 | 48 | 511 | 443 | 5 | 0 | 94.29
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 25 | 20 | 34 | 0 | 76 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3 | 0 | 0 | 0 | 310 | 0 | 195 | 66 | 40 | 39 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 52 | 4 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 20 | 11 | 0 | 138 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 15 | 0 | 0 | 0 | 309 | 8 | 52 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 41 | 0 | 0 | 0 | 0 | 27 | 0 | 36 | 0 | 0 | 0 | 550 | 5 | 576 | 320 | 0 | 63 | 0 | 163 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 152 | 0 | 157 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 180 | 0 | 0 | 4 | 67 | 0 | 0 | 0 | 1005 | 26 | 150 | 511 | 162 | 0 | 0 | 51 | 82 | 0 |  | 5302 | 3853 | 9155 | 2848 | 921 | 0 | 1391 | 0 | 184 | 2441 | 76 | 0 | 179 | 52 | 511 | 547 | 5 | 0 | 94.29
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 25 | 20 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3 | 0 | 0 | 0 | 315 | 0 | 187 | 190 | 35 | 39 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 54 | 4 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 163 | 0 | 30 | 42 | 0 | 138 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 18 | 0 | 0 | 0 | 342 | 8 | 52 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 12 | 340 | 0 | 43 | 0 | 0 | 0 | 0 | 29 | 0 | 36 | 0 | 0 | 0 | 580 | 5 | 576 | 355 | 0 | 65 | 0 | 163 |  | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 214 | 0 | 201 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 220 | 0 | 0 | 4 | 72 | 0 | 0 | 0 | 1015 | 29 | 150 | 618 | 169 | 0 | 0 | 53 | 87 | 0 |  | 5665 | 4191 | 9856 | 3032 | 922 | 0 | 1779 | 0 | 208 | 2479 | 0 | 0 | 179 | 54 | 618 | 580 | 5 | 0 | 94.29
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 22 | 25 | 20 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 5 | 0 | 0 | 0 | 305 | 0 | 182 | 182 | 35 | 40 | 28 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 56 | 3 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 163 | 0 | 30 | 42 | 0 | 138 | 0 | 0 | 0 | 285 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 17 | 0 | 0 | 0 | 335 | 8 | 62 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 12 | 346 | 0 | 39 | 0 | 0 | 0 | 0 | 26 | 0 | 36 | 0 | 0 | 0 | 612 | 1 | 501 | 355 | 0 | 61 | 0 | 163 |  | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 162 | 0 | 0 | 214 | 0 | 218 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 220 | 0 | 0 | 4 | 69 | 0 | 0 | 0 | 1128 | 26 | 150 | 760 | 158 | 0 | 0 | 51 | 84 | 0 |  | 5633 | 4463 | 10096 | 3049 | 922 | 0 | 1751 | 0 | 225 | 2553 | 40 | 0 | 195 | 56 | 760 | 544 | 1 | 0 | 94.28
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 22 | 25 | 20 | 25 | 0 | 40 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 5 | 0 | 0 | 0 | 300 | 0 | 193 | 135 | 35 | 40 | 28 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 60 | 4 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 120 | 0 | 31 | 42 | 0 | 138 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 14 | 0 | 0 | 0 | 335 | 8 | 52 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 12 | 355 | 0 | 34 | 0 | 0 | 0 | 0 | 22 | 0 | 36 | 0 | 0 | 0 | 501 | 3 | 502 | 350 | 0 | 51 | 0 | 163 |  | 921 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 162 | 0 | 0 | 164 | 0 | 170 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 180 | 0 | 0 | 3 | 57 | 0 | 0 | 0 | 1018 | 22 | 150 | 756 | 139 | 0 | 0 | 40 | 74 | 0 |  | 5325 | 4145 | 9470 | 2955 | 921 | 0 | 1550 | 0 | 208 | 2333 | 40 | 0 | 179 | 60 | 756 | 465 | 3 | 0 | 94.29
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 25 | 22 | 25 | 0 | 40 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 4 | 0 | 0 | 0 | 290 | 0 | 182 | 137 | 35 | 37 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 56 | 4 | 0 | 0 | 1 | 30 | 0 | 0 | 5 | 120 | 0 | 30 | 42 | 0 | 138 | 0 | 0 | 0 | 270 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 0 | 0 | 335 | 8 | 52 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 12 | 316 | 0 | 23 | 0 | 0 | 0 | 0 | 15 | 0 | 17 | 0 | 0 | 0 | 476 | 8 | 463 | 350 | 0 | 36 | 0 | 163 |  | 922 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 163 | 0 | 0 | 155 | 0 | 159 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 180 | 0 | 0 | 2 | 39 | 0 | 0 | 0 | 982 | 15 | 150 | 755 | 97 | 0 | 0 | 28 | 51 | 0 |  | 5144 | 3968 | 9112 | 2877 | 922 | 0 | 1539 | 0 | 181 | 2234 | 40 | 0 | 179 | 56 | 755 | 321 | 8 | 0 | 94.28
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 0 | 22 | 25 | 0 | 40 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 5 | 0 | 0 | 0 | 310 | 0 | 195 | 137 | 35 | 41 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 48 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 30 | 42 | 0 | 138 | 0 | 0 | 0 | 305 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 0 | 0 | 0 | 335 | 8 | 52 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 12 | 346 | 0 | 9 | 0 | 0 | 0 | 0 | 7 | 0 | 17 | 0 | 0 | 0 | 445 | 13 | 454 | 350 | 0 | 17 | 0 | 163 |  | 921 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 161 | 0 | 168 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 180 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 968 | 7 | 150 | 676 | 42 | 0 | 0 | 11 | 23 | 0 |  | 5136 | 3764 | 8900 | 2954 | 921 | 0 | 1575 | 0 | 181 | 2172 | 40 | 0 | 179 | 48 | 676 | 141 | 13 | 0 | 94.28
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 22 | 22 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 17 | 0 | 0 | 0 | 33 | 0 | 8 | 0 | 0 | 0 | 325 | 0 | 192 | 167 | 35 | 41 | 28 | 0 | 51 | 0 | 0 | 1 | 0 | 0 | 0 | 16 | 50 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 31 | 42 | 0 | 138 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 5 | 0 | 17 | 0 | 12 | 0 | 3 | 335 | 18 | 55 | 0 | 0 | 15 | 7 | 0 | 0 | 1 | 12 | 316 | 0 | 1 | 17 | 7 | 0 | 0 | 1 | 0 | 17 | 0 | 0 | 0 | 501 | 24 | 454 | 350 | 0 | 2 | 0 | 163 |  | 921 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 172 | 0 | 178 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 1009 | 1 | 150 | 659 | 4 | 0 | 0 | 1 | 3 | 0 |  | 5393 | 3799 | 9192 | 2996 | 921 | 0 | 1666 | 0 | 271 | 2272 | 40 | 0 | 277 | 50 | 659 | 16 | 24 | 0 | 94.27
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 20 | 22 | 22 | 22 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 9 | 17 | 0 | 0 | 6 | 33 | 0 | 8 | 0 | 0 | 0 | 345 | 0 | 209 | 185 | 35 | 42 | 28 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 60 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 0 | 42 | 0 | 138 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 66 | 0 | 34 | 0 | 40 | 12 | 38 | 335 | 65 | 70 | 12 | 0 | 49 | 54 | 12 | 0 | 30 | 50 | 360 | 8 | 0 | 54 | 30 | 0 | 17 | 0 | 4 | 28 | 0 | 17 | 0 | 590 | 40 | 575 | 420 | 0 | 0 | 0 | 163 |  | 921 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 156 | 0 | 0 | 168 | 0 | 175 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 1135 | 0 | 180 | 684 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6384 | 4040 | 10424 | 3006 | 921 | 0 | 1839 | 0 | 884 | 2636 | 40 | 0 | 314 | 60 | 684 | 0 | 40 | 0 | 94.27
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 246 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 20 | 22 | 22 | 22 | 25 | 0 | 40 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 15 | 0 | 0 | 0 | 295 | 0 | 191 | 187 | 35 | 42 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 5 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 0 | 72 | 0 | 138 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 23 | 0 | 24 | 0 | 65 | 346 | 75 | 70 | 30 | 0 | 15 | 17 | 28 | 0 | 9 | 24 | 346 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 32 | 17 | 0 | 0 | 0 | 605 | 38 | 575 | 420 | 0 | 0 | 0 | 163 |  | 921 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 156 | 0 | 0 | 214 | 0 | 213 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 1035 | 0 | 170 | 752 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6124 | 4130 | 10254 | 3063 | 921 | 0 | 1843 | 0 | 719 | 2603 | 40 | 0 | 221 | 54 | 752 | 0 | 38 | 0 | 94.26
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 20 | 22 | 22 | 22 | 25 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 15 | 0 | 0 | 0 | 285 | 0 | 181 | 187 | 35 | 42 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | 6 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 0 | 86 | 0 | 138 | 0 | 0 | 0 | 265 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 0 | 24 | 0 | 65 | 380 | 75 | 70 | 34 | 0 | 15 | 17 | 28 | 0 | 9 | 24 | 346 | 0 | 0 | 90 | 17 | 0 | 0 | 0 | 34 | 17 | 0 | 0 | 0 | 602 | 34 | 575 | 420 | 0 | 0 | 0 | 163 |  | 921 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 160 | 0 | 0 | 214 | 0 | 209 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 1026 | 0 | 170 | 751 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6134 | 4121 | 10255 | 3076 | 921 | 0 | 1846 | 0 | 719 | 2595 | 40 | 0 | 221 | 52 | 751 | 0 | 34 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 22 | 22 | 25 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 18 | 0 | 0 | 0 | 345 | 0 | 203 | 189 | 35 | 42 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 60 | 8 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 120 | 0 | 20 | 86 | 0 | 138 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 0 | 0 | 0 | 65 | 380 | 75 | 70 | 0 | 0 | 15 | 17 | 0 | 0 | 9 | 0 | 400 | 0 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 603 | 31 | 575 | 420 | 0 | 0 | 0 | 163 |  | 921 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 0 | 161 | 0 | 0 | 214 | 0 | 195 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 170 | 752 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6015 | 4056 | 10071 | 3177 | 921 | 0 | 1839 | 0 | 451 | 2579 | 40 | 0 | 221 | 60 | 752 | 0 | 31 | 0 | 94.27
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 |  | 0 | 390 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 20 | 22 | 25 | 0 | 40 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 18 | 0 | 0 | 0 | 310 | 0 | 182 | 189 | 35 | 43 | 29 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 9 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 20 | 61 | 0 | 138 | 0 | 0 | 0 | 295 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 0 | 0 | 0 | 65 | 381 | 75 | 70 | 0 | 0 | 15 | 17 | 0 | 0 | 9 | 0 | 346 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 603 | 35 | 575 | 500 | 0 | 0 | 0 | 163 |  | 921 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 164 | 0 | 0 | 214 | 0 | 173 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 170 | 757 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5783 | 4096 | 9879 | 2916 | 921 | 0 | 1928 | 0 | 425 | 2582 | 40 | 0 | 221 | 54 | 757 | 0 | 35 | 0 | 94.26
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 17 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 23 | 0 | 0 | 0 | 310 | 0 | 182 | 189 | 30 | 43 | 29 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 20 | 163 | 0 | 25 | 86 | 0 | 20 | 0 | 0 | 0 | 275 | 13 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 16 | 0 | 0 | 0 | 40 | 381 | 45 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 39 | 575 | 584 | 0 | 0 | 0 | 54 |  | 921 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 160 | 0 | 0 | 214 | 0 | 155 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 0 | 170 | 754 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5529 | 3999 | 9528 | 2732 | 921 | 0 | 2098 | 0 | 252 | 2568 | 40 | 0 | 70 | 54 | 754 | 0 | 39 | 0 | 94.26
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 17 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 290 | 0 | 189 | 189 | 30 | 43 | 29 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 54 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 35 | 163 | 0 | 25 | 86 | 0 | 20 | 0 | 0 | 0 | 280 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 54 | 575 | 592 | 0 | 0 | 0 | 35 |  | 922 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 160 | 0 | 0 | 173 | 0 | 158 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814 | 0 | 150 | 659 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5255 | 3756 | 9011 | 2732 | 922 | 0 | 2137 | 0 | 43 | 2319 | 40 | 0 | 51 | 54 | 659 | 0 | 54 | 0 | 94.26
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 16 | 24 | 8 | 0 | 35 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 295 | 0 | 182 | 189 | 35 | 43 | 29 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 8 | 0 | 0 | 0 | 30 | 0 | 0 | 36 | 120 | 0 | 25 | 84 | 0 | 20 | 0 | 0 | 0 | 290 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 60 | 575 | 588 | 0 | 0 | 0 | 35 |  | 921 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71 | 0 | 160 | 0 | 0 | 150 | 0 | 157 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 150 | 510 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5068 | 3474 | 8542 | 2684 | 921 | 0 | 1966 | 0 | 25 | 2234 | 35 | 0 | 51 | 56 | 510 | 0 | 60 | 0 | 94.26
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7520400 | 0 |  | 0 | 9152500 | 0 | 0 | 0 | 0 | 4780866 | 0 | 0 | 0 | 18144 | 356160 | 0 | 0 | 0 | 0 | 78120 | 227568 | 35593 | 0 | 456000 | 529200 | 472680 | 571000 | 421920 | 0 | 959100 | 0 | 0 | 0 | 0 | 5237403 | 0 | 0 | 0 |  | 23040 | 27504 | 0 | 0 | 12480 | 329760 | 0 | 501120 | 0 | 0 | 0 | 7759000 | 0 | 4574000 | 3111273 | 860180 | 868680 | 547200 | 0 | 873196 | 0 | 0 | 11496 | 0 | 0 | 0 | 364000 | 1170240 | 153600 | 0 | 0 | 11950 | 716000 | 0 | 0 | 222336 | 3752345 | 0 | 1257216 | 871680 | 0 | 3052230 | 0 | 0 | 0 | 7080500 | 338160 | 58224 | 0 | 0 | 0 | 0 | 338400 | 0 | 253584 | 106245 | 83520 | 22080 | 287709 | 8751000 | 450000 | 936960 | 68581 | 20641 | 125455 | 144067 | 72763 | 0 | 114240 | 152640 | 8197000 | 10560 | 261380 | 240480 | 124200 | 0 | 25920 | 168664 | 66240 | 363600 | 0 | 20073 | 0 | 11639999 | 578400 | 11978181 | 8905909 | 0 | 409609 | 0 | 3619200 |  | 20784000 | 0 | 642240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1478000 | 125445 | 0 | 0 | 0 | 0 | 0 | 0 | 251936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149850 | 341236 | 0 | 3848000 | 0 | 0 | 4217364 | 0 | 4272736 | 0 | 0 | 0 | 4286445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30854 | 0 | 0 | 5216040 | 0 | 0 | 27780 | 434880 | 151728 | 0 | 0 | 23032730 | 170328 | 3753000 | 13987974 | 1030320 | 0 | 3001 | 318000 | 543440 | 0 |  | 127901364 | 89097327 | 216998691 | 71563474 | 20784000 | 0 | 40359544 | 0 | 5190848 | 54593146 | 959100 | 0 | 4274873 | 1170240 | 13987974 | 3537092 | 578400 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21658752 | 0 |  | 0 | 29104950 | 0 | 0 | 0 | 0 | 14581641.3 | 0 | 0 | 0 | 325684.8 | 6916627.2 | 0 | 0 | 0 | 0 | 1426471.2 | 3586471.68 | 650995.97 | 0 | 342000 | 0 | 0 | 0 | 7556587.2 | 0 | 0 | 0 | 0 | 0 | 0 | 16707315.57 | 0 | 0 | 0 |  | 405273.6 | 484345.44 | 0 | 0 | 244233.6 | 5427849.6 | 0 | 0 | 0 | 0 | 0 | 21647610 | 0 | 15185680 | 10422764.55 | 2778381.4 | 2927451.6 | 2396736 | 0 | 3501515.96 | 0 | 0 | 207617.76 | 0 | 0 | 0 | 273000 | 7676774.4 | 477696 | 0 | 0 | 0 | 2792400 | 0 | 0 | 1011628.8 | 12833019.9 | 0 | 6977548.8 | 4550169.6 | 0 | 8515721.7 | 0 | 0 | 0 | 21878745 | 253620 | 44250.24 | 0 | 0 | 0 | 0 | 6500664 | 0 | 4465614.24 | 0 | 1487491.2 | 383088 | 4770215.22 | 23190150 | 8577000 | 17577369.6 | 1230343.14 | 0 | 2051189.25 | 2800662.48 | 1305368.22 | 0 | 2217398.4 | 2718518.4 | 21804020 | 180259.2 | 0 | 4398379.2 | 2084076 | 0 | 463190.4 | 0 | 1193644.8 | 6159384 | 0 | 282627.84 | 0 | 81130793.03 | 0 | 70671267.9 | 0 | 0 | 0 | 0 | 0 |  | 58403040 | 0 | 1894608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4670480 | 594609.3 | 0 | 0 | 0 | 0 | 0 | 0 | 4235044.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113436.45 | 3763833.08 | 0 | 32477120 | 0 | 0 | 13917301.2 | 0 | 14228210.88 | 0 | 0 | 0 | 14273861.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16221884.4 | 0 | 0 | 0 | 0 | 2632480.8 | 0 | 0 | 168138929 | 0 | 27959850 | 92460508.14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 503414245.39 | 455985197.26 | 959399442.65 | 209255136.99 | 58403040 | 0 | 102516023.51 | 0 | 93027521.96 | 384141793.01 | 0 | 0 | 11918644.64 | 7676774.4 | 92460508.14 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 22 | 25 | 20 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 3 | 0 | 0 | 0 | 315 | 0 | 187 | 190 | 35 | 39 | 28 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 54 | 4 | 0 | 0 | 2 | 30 | 0 | 0 | 5 | 163 | 0 | 30 | 42 | 0 | 138 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 18 | 0 | 0 | 0 | 342 | 8 | 52 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 12 | 340 | 0 | 43 | 0 | 0 | 0 | 0 | 29 | 0 | 36 | 0 | 0 | 0 | 580 | 5 | 576 | 355 | 0 | 65 | 0 | 163 |  | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 158 | 0 | 0 | 214 | 0 | 201 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 220 | 0 | 0 | 4 | 72 | 0 | 0 | 0 | 1015 | 29 | 150 | 618 | 169 | 0 | 0 | 53 | 87 | 0 |  | 9856 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 20 | 22 | 22 | 22 | 34 | 0 | 40 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 9 | 17 | 0 | 0 | 6 | 33 | 0 | 8 | 0 | 0 | 0 | 345 | 0 | 209 | 185 | 35 | 42 | 28 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 60 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 0 | 42 | 0 | 138 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 0 | 0 | 0 | 66 | 0 | 34 | 0 | 40 | 12 | 38 | 335 | 65 | 70 | 12 | 0 | 49 | 54 | 12 | 0 | 30 | 50 | 360 | 8 | 0 | 54 | 30 | 0 | 17 | 0 | 4 | 28 | 0 | 17 | 0 | 590 | 40 | 575 | 420 | 0 | 0 | 0 | 163 |  | 921 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 156 | 0 | 0 | 168 | 0 | 175 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 1135 | 0 | 180 | 684 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10424 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 22 | 25 | 33 | 34 | 0 | 40 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 |  | 22 | 75 | 50 | 0 | 50 | 50 | 0 | 20 | 0 | 0 |  | 350 | 0 | 215 | 195 | 50 | 43 | 25 | 0 | 51 | 0 | 40 | 52 | 0 | 0 |  | 17 | 70 | 10 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 62 | 0 | 138 | 0 | 0 | 0 | 315 | 13 | 2 | 0 | 300 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 150 | 380 | 115 | 105 | 105 | 0 | 100 | 54 | 110 | 114 | 100 | 100 | 383 | 17 | 0 | 162 | 108 | 0 | 52 | 0 | 92 | 38 | 0 | 160 | 0 | 612 | 38 | 575 | 400 | 0 |  | 0 |  |  | 920 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 35 | 60 | 0 | 68 | 6 | 0 | 0 | 0 | 0 | 40 | 25 | 100 | 0 | 0 | 32 | 52 | 24 | 0 | 0 | 5 | 70 | 0 | 160 | 0 | 0 | 200 | 0 | 200 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 0 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 1234 | 0 | 170 | 750 | 0 | 0 |  |  |  | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 |  | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 |  | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 34 | 55 | 55 | 0 | 18 | 22 | 25 | 33 | 34 | 0 | 40 | 0 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 22 | 57 | 50 | 0 | 20 | 50 | 0 | 20 | 0 | 0 | 0 | 350 | 0 | 215 | 185 | 50 | 43 | 25 | 0 | 51 | 0 | 30 | 52 | 0 | 0 |  | 16 | 66 | 10 | 0 | 0 | 1.6 | 30 | 0 | 0 | 5 | 163 | 0 | 32 | 62 | 0 | 138 | 0 | 0 | 0 | 310 | 13 | 2 | 0 | 300 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 200 | 140 | 380 | 55 | 50 | 85 | 5 | 50 | 54 | 110 | 114 | 95 | 100 | 383 | 7 | 50 | 162 | 50 | 0 | 17 | 35 | 50 | 36 | 0 | 17 | 0 | 612 | 15 | 575 | 589 | 0 | 70 | 0 | 163 |  | 730 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 68 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 26 | 45 | 24 | 0 | 0 | 5 | 70 | 0 | 160 | 0 | 0 | 200 | 0 | 200 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 95 | 0 | 90 | 0 | 8 | 113 | 0 | 220 |  | 54 | 6 | 100 | 115 | 0 | 0 | 1234 | 30 | 150 | 750 | 170 | 0 |  | 29 | 47 | 0 |  |  |  |  | gas | hvdc |  | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 30 | 8 | 0 | 35 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 365 | 0 | 182 | 187 | 50 | 43 | 15 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 11 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 163 | 0 | 25 | 62 | 0 | 95 | 0 | 0 | 0 | 300 | 13 | 2 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 365 | 24 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 11 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 0 | 0 | 350 | 50 | 450 | 589 | 0 | 24 | 0 | 35 | 0 | 730 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72 | 0 | 120 | 0 | 0 | 171 | 0 | 177 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 220 | 0 | 0 | 1 | 18 | 0 | 0 | 0 | 863 | 6 | 150 | 416 | 40 | 0 | 0 | 0 | 19 | 0 | 0 |  |  |  | 111923018 | 20784000 |  | 0 | 54593146 | 9465721 | 1170240 | 3537092 | 578400 | 959100 |  |  |  | 203010717
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [14 empty] | 399527 | 399528 | [9 empty] | 399427 | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 |  | 299798 | [7 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [7 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [14 empty] | 499227 |  | 499229 |  |  | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [11 empty] | 111.923 | 20.784 |  | 0 | 54.5931 | 9.4657 | 1.1702 | 3.5371 | 0.5784 | 0.9591
| Minimum Generation |  | 6950 | 5:00
| Highest Generation |  | 10424 | 18:00 | [129 empty] | 0 | [77 empty] | 203.0107
| Day Peak Generation |  | 9856 | 12:00
| Evening Peak Generation |  | 10424 | 18:00 | [207 empty] | 202699852
| HVDC Max Flow |  | 922 | 12:00 | [207 empty] | 202.6999
| HVDC EvPeak Flow |  | 921 | 18:00
| Load factor L.F |  | 86.74% | [169 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-12-27
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-12-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9856 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6981
Evening Peak Generation : |  |  | 10424 | MW Hour : | 18:00 | Available Max Generation : |  | 14419
E.P. Demand (at gen end) : |  |  | 10424 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 10600
Maximum Generation : |  |  | 10424 | MW Hour : | 18:00 | Reserve(Generation end) |  | 3819
Total Gen. (MKWH) : |  |  | 216.9987 | System Load Factor : | 86.74% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 350 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-12-27
Actual : |  | 94.24 | Ft.(MSL) , | Rule curve : | 103.5 | Ft.( MSL )
Gas Consumed : |  | Total = | 833.72 | MMCFD. | Oil Consumed (PDB) :
HSD:
FO:
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 311771160.5 | Adani : | 92460508.14
|  |  | Coal : | 384141793.01 | Oil: | 104946166.6 | Total: | 893319628.25
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3596.4247 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 982.3952 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1374.3707 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1192.9441 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 982.4152 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 729.8039 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 410.003 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 340.8433 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 666.6492 |  |  | 0 | 0%
Total |  | 0 |  | 10275.8492 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:11 | 09:29 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Scheduled S/D Due to PBS Badgram Feeder red hot Maintenance. | [5 empty] | 12 MW load interrup.
08:11 | 09:28 | Mirzapur 132/33kV S/S Transformer-02(E07) HT Scheduled S/D Due to PBS Badgram Feeder red hot Maintenance.
08:14 | 20:42 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to annual maintenance and DS replacement work.
08:14 | 20:42 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to annual maintenance and DS replacement work.
08:16 | 15:32 | Goalpara 132/33kV S/S Goalpara-NWPGCL Scheduled S/D Due to annual maintenance.
08:18 | 09:34 | Bashundhara-Rampura 132 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end.
08:20 | 16:33 | Amnura-Chapainawabganj-132kV Ckt-1 Scheduled S/D from Chapai 132/33kV end Due to Annual Maintenance
and from Amnura 132/33kV end Due to Annual maintenance.
08:25 | 16:57 | Daudkandi-Sonargaon 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to Annual Maintenance Sonargaon
SS End. and from Sonargaon 132/33kV end Due to Deadline chaking work. Shutdown taken by Siddhirganj 132KV grid SS.
08:33 | 15:59 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end. and from Shahjibazar 132/33kV
end Due to Annual Maintenance. Load flow by B-Baria circuit-02.
08:34 | 15:11 | Bakulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Khulshi 132/33kV end Due to Annual Maintenance(Dead line) checking work.
08:38 | 18:44 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) LT Scheduled S/D Due to Annual maintenance.
08:39 | 18:42 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT Scheduled S/D Due to Annual maintenance.
08:43 | 17:23 | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to Maintenance work and
from Bogura 400/230kV end Due to annual maintenance.
08:43 | 17:23 | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to Maintenance work and
from Bogura 400/230kV end Due to annual maintenance.
08:52 | 14:54 | Cumilla(N) 230/132/33kV S/S 132KV T-05 LT Scheduled S/D.
08:52 | 14:54 | Cumilla(N) 230/132/33kV S/S 132KV T-05 HT Scheduled S/D.
08:57 | 15:09 | Bakulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Bakulia 132/33kV end.
09:12 | 17:12 | Sirajgonj 230 S/S Bus-2 Scheduled S/D Due to SNWPCL Unit-4 Bay 3 Bus DS Maintenance.
09:14 | 12:27 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-1 Scheduled S/D from Jamalpur 132/33kV end Due to Annual maintenance work.
09:22 | 13:08 | Savar 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance work.
09:31 | Bheramara 230/132kV S/S GTG (NW) is restored.
10:10 | 17:07 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to annual maintenance.
10:18 | 16:22 | Shikalbaha 230/132kV S/S Hathazari - 01 Scheduled S/D
10:23 | 11:59 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT Scheduled S/D Due to 132kV B-Bus DS Annual maintenance of TR-3.
10:23 | 11:58 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D Due to 132kV B-Bus DS Annual maintenance of TR-3.
10:36 | 18:16 | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to Dead line cheek.
10:37 | 18:14 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-2 Scheduled S/D
10:42 | 16:41 | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-1 Scheduled S/D Due to Annual Maintenance taken by Shikalbaha end.
10:54 | 16:41 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Scheduled S/D Due to Annual maintenance work. | [5 empty] | 10 MW load interrup.
10:55 | 16:33 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT Scheduled S/D Due to Annual maintenance work.
11:24 | 14:34 | BIPTC S/S 10CF14 Forced S/D Due to Shutdown is taken for emergency maintenance work.
11:26 | 13:03 | Sherpur 132/33kV S/S Transformer- 04 LT Forced S/D Due to spbs 33kv bus work.
11:26 | 13:03 | Sherpur 132/33kV S/S Transformer- 04 HT Forced S/D Due to spbs 33kV bus work.
12:30 | 16:12 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due to Annual maintenance work.
| 13:28 | Bheramara 410MW GT was sync.
13:36 | 14:20 | Savar 132/33kV S/S Bus-A Scheduled S/D Due to Annual maintenance work.
| 14:45 | Ramganj 132/33kV S/S 132 Kv Bus- A is restored.
15:01 | 17:30 | Ramganj 132/33kV S/S 132 Kv Bus-B Scheduled S/D Due to Annual Maintenance.
| 17:28 | Ramganj 132/33kV S/S Ramgonj- Desh Energy Ckt-01 is restored.
| 17:36 | Baroaulia-Hathazari 132 kV Ckt-2 is restored.
17:43 |  | Shahjibazar GT-9 tripped due to loss of fame.
| 18:07 | From NLDC: Barapukuria-1 was sync. at 18:07 hrs.
| 19:09 | Hasnabad 230/132kV S/S AUTO TR-3 LT is restored.
| 19:09 | Hasnabad 230/132kV S/S AUTO TR-3 HT is restored.
| 19:44 | Shajibajar GT8 was sync.
20:02 |  | Siddhirganj CCPP 335 MW 335 MW ST was forced shutdown due to the malfunction of SP drum LCV.
21:04 |  | Siddhirganj CCPP 335 MW 335 MW GT was shutdown.
06:16 |  | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 Scheduled S/D Due to Annual Maintenance.
06:20 |  | Rampur 230/132/33 S/S Halishahar-2 Scheduled S/D
06:33 | 06:49 | Tangail 132/33kV S/S Kaliakair-2 Tripped showing REL316*4 relays. | [5 empty] | 50 MW load interrup.
06:38 |  | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to Halishahar Grid S/S Main Bus annual maintenance work.
07:01 |  | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-2 Project Work S/D from Mithapukur 132/33kV end.
07:01 |  | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 Project Work S/D from Mithapukur 132/33kV end.
07:17 |  | Mahasthangar-Palashbari 132kV Ckt-2 Project Work S/D from Palashbari 132/33kV end Due to Project Work.
07:32 |  | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to Annual maintenance.
07:32 |  | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to Annual maintenance.
07:40 |  | Sirajganj 132/33kV S/S Solar Park 1 Project Work S/D Due to Bogura Kaliyakor 400KV Project Work(Cable Guard Installation work).
07:47 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Naogaon 132/33kV end Due to OPGW maintenance and from Bogura
230/132kV end.
07:54 |  | Sirajganj 132/33kV S/S Solar Park 2 Project Work S/D Due to Bogura Kaliyakor 400KV Project Work(Cable Guard Installation work).
|  | Sub-Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
|  | Network Operation Division |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-12-26
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 311 | 7520400 | DP High
| Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9152500 | Frequency control
| Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
| Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
10 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | NENP
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 254 | 4780866 | DP High
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 18144 | Fuel shortage
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 78120 | Low demand
18 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 356160 | Low demand
19 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 227568 | Low demand
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 35593 | Low demand
21 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
22 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 985200 | Engine problem
23 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 472680 | Engine problem
24 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 571000 | Engine problem
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 34 | 421920 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 34 | 253584 | Low demand
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 936960 | Low demand
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 8 | 10560 | Fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 240480 | Low demand
32 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 168664
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 28 | 363600 | Low demand
34 | Meghnaghat Unique power |  | IPP | 586 | 584 | 420 | 8905909 | Gas shortage
35 | Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 718 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5915 | 1798 | 35499908
36 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
37 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
38 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 106245
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 329760 | Low demand
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 959100 | Low water level
41 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 226 | 5237403
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 12 | 68581 | Low demand
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 17 | 27504 | Low demand
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
| Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 0 | 0 | 0 | Contract Expired
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 40 | 83520 | Low demand
| Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 8 | 501120
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 6 | 12480 | Low demand
48 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20641
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 49 | 125455 | Low demand
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 144067
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 12 | 72763 | Low demand
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 152640 | Fuel shortage
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 30 | 124200 | Low demand
54 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 20073 | Low demand
55 | SS Power I |  | IPP | 2*612 | 1224 | 590 | 11639999 | Unit-2 Under maint
56 | Cox's Bazar Wind |  | IPP | 66 | 60 | 40 | 578400
57 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 2*575 | 1150 | 575 | 11978181 | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4857 | 1799 | 32182132
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0
58 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 209 | 4574000
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7759000 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 42 | 868680
63 | Ashuganj 55 MW PP (Precision) |  | NENP | 0 | 55 | 28 | 547200 | Gas shortage
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 185 | 3111273
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 873196
66 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 38 | 287709 | Low demand
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 860180 | Machine problem.
69 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 12 | 22080 | Low demand
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 60 | 1170240
| Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 11496 | Low demand
72 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 364000 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 30 | 114240 | Low demand
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 4 | 66240 | Low demand
76 | Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 409609
| Cumilla Area Total |  |  |  | 2917 | 1065 | 21039143
77 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 4 | 153600 | Gas shortage
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
79 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11950
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 66 | 338400 | Low demand
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 65 | 450000 | Low demand
82 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 261380
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 9 | 23040
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 25920 | Low demand
| Sreepur 150 MW |  | BPDB-RPCL | 150 | 0 | 163 | 3619200
| Mymensingh Area Total |  |  |  | 646 | 324 | 4883490
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 716000 | Machine problem.
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3752345
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
89 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 0 | 0 | 0 | Contact expired
90 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 222336 | Gas shortage
91 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 58224 | Engine problem
92 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 1257216 | Gas shortage
93 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 42 | 871680 | Gas shortage
94 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 138 | 3052230 | ST under maint
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
97 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 13 | 338160 | Engine problem
98 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7080500 | FGMO
99 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 335 | 8751000
| Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
100 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 360 | 8197000 | FGMO
| Sylhet Area Total |  |  |  | 2366 | 1398 | 34296691
101 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 921 | 20784000
| Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
102 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
103 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
104 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
105 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 7 | 642240 | under maint
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Fuel shortage
107 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
108 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 434880
109 | Khulna 330 MW CCPP (OIL) |  | PDB | 1*220+1*110 | 336 | 0 | 0 | On test.
110 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 1135 | 23032730
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Nepal |  | Imported power | 40 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 2063 | 44893850
111 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Fuel shortage
112 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 7 | 125445 | Engine problem
113 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1478000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
114 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 0 | 0 | Development work.
115 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5216040
116 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
117 | Barisal 307 MW |  | IPP | 307*1 | 307 | 180 | 3753000
118 | Barisal 1 MW Solar Plant |  | PDB | 1 | 1 | 0 | 3001
| Barisal Area Total |  |  |  | 2236 | 472 | 10575486
119 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
120 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
121 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
122 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | NENP
| Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
123 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
124 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 168 | 4217364 | Gas shortage
125 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 175 | 4272736
126 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 178 | 4286445 | Gas shortage
127 | Sirajgonj 400 MW CCPP Unit-4 |  | IPP, SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
128 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
129 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 149850 | Engine problem
130 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
131 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 69 | 251936 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
132 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
133 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
134 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 27780
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 684 | 13987974
135 | Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 318000
| Pabna Solar 100 MW |  | IPP | 100 | 0 | 0 | 543440
| Rajshahi Area Total |  |  |  | 3449 | 1279 | 28055525
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 341236 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 156 | 3848000 | Machine problem.
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | Reserve
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30854
142 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 70 | 151728 | Low demand
143 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 170328
144 | Teesta Solar Limited |  | IPP | 16*12.5 | 200 | 0 | 1030320
| Rangpur Area Total |  |  |  | 950 | 226 | 5572466
| Total |  |  |  | 27035 | 10424 | 216998691
| Eastern Grid Total |  |  |  | 16701 | 6384 | 127901364
| Western Grid Total |  |  |  | 10334 | 4040 | 89097327
| National Grid Total |  |  |  | 27035 | 10424 | 216998691
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-12-2024
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7129.74 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3141 | MW
i) Dhaka area |  |  | 3957.74 |  | MW | i) Khulna area |  |  |  | 1173 | MW
ii) Chattogram area |  |  | 1068 |  | MW | ii) Barishal area |  |  |  | 297.2 | MW
iii) Cumilla area |  |  | 889 |  | MW | iii) Rajshahi area |  |  |  | 963.8 | MW
iv) Mymensingh area |  |  | 863 |  | MW | iv) Rangpur area |  |  |  | 707 | MW
v) Sylhet area |  |  | 352 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10270.74 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 80 | 18:00 | 133 | Rahim | 53 | 09:00
2 | AKSML | 108 | 16:00 | 68 | Jashore | 94 | 13:00 | 134 | Rajbari | 54 | 18:00
3 | Aftabnagar | 24 | 13:00 | 69 | Jhenaidah | 91 | 18:00 | 135 | Rajendrapur | 92 | 18:30
4 | Agargaon | 71 | 13:00 | 70 | Joydebpur | 132 | 12:00 | 136 | Rajshahi | 90 | 13:00
5 | Agrabad | 66 | 18:00 | 71 | Joypurhat | 40 | 13:00 | 137 | Rajshahi-230 | 40 | 13:00
6 | Amnura | 45 | 08:00 | 72 | Juldah | 8 | 23:00 | 138 | Ramganj | 70 | 19:30
7 | Ashuganj | 61 | 13:00 | 73 | KSRM | 32 | 11:00 | 139 | Rampur | 26 | 18:00
8 | BSRM | 147 | 18:30 | 74 | Kabirpur | 194 | 18:00 | 140 | Rangamati | 12 | 18:00
9 | Bagerhat | 65 | 18:00 | 75 | Kachua | 47 | 19:00 | 141 | Rangpur | 105 | 18:00
10 | Bakulia | 68 | 13:00 | 76 | Kallyanpur | 75 | 11:00 | 142 | Ruppur | 4.6 | 11:00
11 | Banani | 39.2 | 13:00 | 77 | Kalurghat | 22 | 09:00 | 143 | SSM | 15 | 03:00
12 | Bangabhaban | 8 | 11:00 | 78 | Kamrangirchar | 52.55 | 18:30 | 144 | Saidpur | 88 | 18:00
13 | Barapukuria | 42 | 18:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 83 | 18:30
14 | Barguna | 14 | 18:00 | 80 | Kazla | 83 | 12:00 | 146 | Satmasjid | 72 | 13:00
15 | Barishal | 78 | 12:00 | 81 | Keranigonj | 54 | 12:00 | 147 | Savar | 158 | 12:00
16 | Barishal-230 | 64 | 18:00 | 82 | Khagrachori | 22 | 18:00 | 148 | SevenRings | 12.17 | 05:00
17 | Baroaulia | 59 | 11:00 | 83 | Khulna | 74 | 13:00 | 149 | ShahCement | 23 | 09:00
18 | Baroirhat | 43 | 18:30 | 84 | Khulshi | 150 | 12:00 | 150 | Shahjadpur | 50 | 10:00
19 | Bashundhara | 128 | 13:00 | 85 | Kishoreganj | 106 | 19:30 | 151 | Shahjibazar | 78 | 18:30
20 | BashundharaCement | 11 | 09:00 | 86 | Kodda | 266 | 18:30 | 152 | Shahmirpur | 32 | 17:00
21 | Beanibazar | 42 | 18:30 | 87 | Kulaura | 28 | 18:00 | 153 | Shariatpur | 51 | 21:00
22 | Benapole | 40 | 08:00 | 88 | Kurigram | 46 | 18:00 | 154 | Sherpur | 114 | 18:30
23 | Bhaluka | 116 | 18:30 | 89 | Kushtia | 102 | 18:00 | 155 | Shikalbaha | 20 | 12:00
24 | Bhandaria | 33.5 | 20:00 | 90 | Lalbag | 63 | 13:00 | 156 | Shitalakhya | 63 | 12:00
25 | Bhangura | 22 | 18:30 | 91 | Lalmonirhat | 42 | 18:30 | 157 | Sholosohor | 22 | 09:00
26 | Bheramara(GK) | 41 | 18:00 | 92 | MI_Cement | 18.8 | 14:00 | 158 | Shyampur | 166 | 11:00
27 | Bhulta | 244 | 12:00 | 93 | Madanganj | 30 | 18:30 | 159 | Siddhirganj | 86 | 09:00
28 | Bog-Sherpur | 56 | 18:00 | 94 | Madaripur | 65 | 13:00 | 160 | Sirajganj | 64 | 18:30
29 | Bogura | 109 | 18:30 | 95 | Madartek | 57.52 | 13:00 | 161 | Sonargaon | 81 | 10:00
30 | Borhanuddin | 53 | 21:00 | 96 | Madunaghat | 34 | 17:00 | 162 | Sreemongol | 44 | 18:00
31 | Brahmanbaria | 105 | 19:00 | 97 | Magura | 46 | 18:00 | 163 | Sreepur | 62 | 16:00
32 | Cantonment | 78 | 13:00 | 98 | Mahasthangarh | 50 | 18:00 | 164 | Srinagar | 28.6 | 13:00
33 | Chandpur | 42 | 18:30 | 99 | Manikganj | 96 | 18:30 | 165 | Sunamganj | 34 | 17:00
34 | Chandraghona | 25 | 18:00 | 100 | Maniknagar | 44 | 13:00 | 166 | Sylhet | 34 | 12:00
35 | Chapai | 50 | 12:00 | 101 | Matarbari | 33 | 18:00 | 167 | Sylhet-132 | 73 | 16:00
36 | Charsaidpur | 44 | 23:00 | 102 | Matuail | 46 | 15:00 | 168 | TK | 17.5 | 00:00
37 | Chauddagram | 42 | 13:00 | 103 | Millgate | 76 | 10:00 | 169 | Tangail | 132 | 18:30
38 | Chhatak | 21 | 19:00 | 104 | Mirpur | 85 | 13:00 | 170 | Thakurgaon | 74 | 18:00
39 | Chowmuhani | 145 | 18:00 | 105 | Mirsorai | 7 | 18:00 | 171 | Tongi | 87 | 11:00
40 | Chuadanga | 70 | 18:00 | 106 | Mirzapur | 30 | 18:00 | 172 | Ullahpara | 21 | 18:30
41 | Coxsbazar | 98 | 18:00 | 107 | Mithapukur | 38 | 08:00 | 173 | Ullon | 37 | 13:00
42 | Cumilla(N) | 102 | 18:30 | 108 | Modern | 0 | 00:00 | 174 | Uttara | 52 | 13:00
43 | Cumilla(S) | 122 | 18:00 | 109 | Mogbazar | 78.9 | 14:00 | 175 | UttaraNew | 38 | 08:00
44 | Daudkandi | 110 | 19:30 | 110 | Mongla | 28 | 12:00 | 176 | Zigatola | 67 | 13:00
45 | Dhaka | 32 | 13:00 | 111 | Motijheel | 25 | 13:00
46 | Dhamrai | 104 | 12:00 | 112 | Munshiganj | 72 | 13:00
47 | Dhanmondi | 95.6 | 13:00 | 113 | Mymensingh | 167 | 18:00
48 | Dohazari | 67 | 18:30 | 114 | Naogaon | 83 | 08:00
49 | Faridpur | 107 | 18:00 | 115 | Narail | 39 | 18:30
50 | Fatullah | 80 | 15:00 | 116 | Narinda | 51.5 | 13:00
51 | Fenchuganj | 24 | 18:30 | 117 | Narshingdi | 146 | 19:00
52 | Feni | 70 | 18:00 | 118 | Natore | 96 | 18:30
53 | GPH | 28 | 19:30 | 119 | Nawabganj | 29 | 13:00
54 | Ghatail | 46 | 18:00 | 120 | Netrakona | 101 | 18:30
55 | Ghorashal | 7 | 18:30 | 121 | New | 73 | 12:00
56 | Ghorashal-230 | 57 | 18:30 | 122 | Niamatpur | 52 | 08:00
57 | Goalpara | 18 | 13:00 | 123 | Noapara | 33 | 18:30

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-12-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 406 | 03:00 | 366 | 22:00 | Kaliakoir | 381 | 04:00 | 363 | 12:00
| Ashuganj | 406 | 4:23 | 383 | 12:30 | Madunaghat | 407 | 04:00 | 394 | 13:00
| Bhulta | 403 | 04:00 | 384 | 12:00 | Meghnaghat | 399 | 03:00 | 380 | 12:00
| Bibiana | 396 | 03:00 | 387 | 10:00 | Payra | 423 | 05:00 | 414 | 13:00
| BIPTC | 407 | 02:00 | 390 | 10:00 | Rahanpur | 415 | 03:00 | 400 | 08:00
| Bogura | 411 | 03:00 | 393 | 08:00 | Rampal | 410 | 05:00 | 396 | 18:00
| Gopalganj | 409 | 03:00 | 394 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 235 | 03:00 | 221 | 12:00 | Haripur | 235 | 00:00 | 224 | 12:00
| AKSML | 234 | 02:00 | 224 | 11:00 | Hasnabad | 236 | 05:00 | 220 | 13:00
| Aminbazar | 233 | 01:00 | 220 | 12:00 | Hathazari | 233 | 03:00 | 224 | 12:00
| Ashuganj | 239 | 02:00 | 229 | 11:00 | Ishurdi | 243 | 04:00 | 226 | 12:00
| Ashuganj-400 | 239 | 02:00 | 229 | 11:00 | Jhenaidah | 241 | 05:00 | 219 | 02:00
| Baghabari | 241 | 05:00 | 229 | 12:00 | Kaliakoir | 237 | 04:00 | 224 | 12:00
| Barapukuria | 227 | 02:00 | 215 | 09:00 | Keranigonj | 235 | 03:00 | 221 | 12:00
| Barapukuria-230 | 227 | 02:00 | 215 | 09:00 | Khulna(S) | 240 | 03:00 | 226 | 13:00
| Barishal | 245 | 04:00 | 237 | 12:00 | Madunaghat | 232 | 01:00 | 225 | 11:00
| Bheramara | 241 | 04:00 | 223 | 12:00 | Madunaghat-400 | 234 | 03:00 | 226 | 12:00
| Bhulta | 238 | 02:00 | 224 | 12:00 | Maniknagar | 238 | 04:00 | 224 | 12:00
| Bibiana | 229 | 06:00 | 223 | 11:00 | Meghnaghat | 245 | 05:00 | 231 | 12:00
| BIPTC | 243 | 04:00 | 224 | 12:00 | Meghnaghat-400 | 239 | 02:00 | 227 | 12:00
| Bogura | 238 | 02:00 | 228 | 18:00 | Mirsorai | 235 | 03:00 | 223 | 12:00
| Bogura-400 | 239 | 03:00 | 228 | 08:00 | Rajshahi | 242 | 05:00 | 223 | 12:00
| Borhanuddin | 247 | 04:00 | 241 | 13:00 | Rampal | 238 | 05:00 | 225 | 12:00
| BSRM | 234 | 03:00 | 224 | 11:00 | Rampur | N/A | N/A | N/A | N/A
| Cumilla(N) | 234 | 06:00 | 223 | 12:00 | Rampura | 238 | 03:00 | 224 | 12:00
| Faridpur | 242 | 00:00 | 234 | 12:00 | Shikalbaha | 232 | 03:00 | 221 | 12:00
| Fenchuganj | 233 | 00:00 | 228 | 11:00 | Shyampur | 237 | 05:00 | 223 | 12:00
| Ghorashal | 235 | 00:00 | 235 | 00:00 | Siddhirganj | 238 | 01:00 | 226 | 12:00
| Ghorashal-230 | 237 | 02:00 | 223 | 12:00 | Sirajgonj | 248 | 04:00 | 239 | 12:00
| Gopalganj | 242 | 02:00 | 233 | 13:00 | Sreepur | 239 | 02:00 | 229 | 11:00
| GPH | 234 | 03:00 | 223 | 12:00 | Tongi | 237 | 04:00 | 222 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 135 | 01:00 | 125 | 12:00 | Kushtia | 138 | 03:00 | 130 | 12:00
| Agargaon | 137 | 02:00 | 126 | 12:00 | Lalbag | 135 | 03:00 | 126 | 12:00
| Agrabad | 134 | 01:00 | 126 | 12:00 | Lalmonirhat | 133 | 04:00 | 124 | 10:00
| AKS | 132 | 03:00 | 125 | 12:00 | Madanganj | 132 | 01:00 | 124 | 12:00
| Aminbazar | 135 | 00:00 | 125 | 12:00 | Madaripur | 135 | 02:00 | 130 | 11:00
| Amnura | 140 | 04:00 | 125 | 12:00 | Madartek | 135 | 02:00 | 126 | 12:00
| Ashuganj | 140 | 00:00 | 136 | 11:00 | Madunaghat | 135 | 18:30 | 128 | 12:00
| Bagerhat | 138 | 05:00 | 128 | 18:00 | Magura | 140 | 04:00 | 128 | 12:00
| Bakulia | 134 | 01:00 | 127 | 12:00 | Mahasthangarh | 137 | 05:00 | 128 | 08:00
| Banani | 136 | 03:00 | 125 | 12:00 | Manikganj | 132 | 04:00 | 124 | 11:00
| Bangabhaban | 136 | 02:00 | 127 | 12:00 | Maniknagar | 136 | 02:00 | 127 | 12:00
| Barapukuria | 136 | 02:00 | 126 | 09:00 | Matarbari | 129 | 03:00 | 120 | 12:00
| Barguna | 136 | 04:00 | 131 | 12:00 | Matuail | 134 | 05:00 | 126 | 13:00
| Barishal | 135 | 05:00 | 130 | 12:00 | Millgate | 135 | 04:00 | 125 | 12:00
| Barishal-230 | 136 | 02:00 | 131 | 11:00 | Mirpur | 135 | 02:00 | 125 | 12:00
| Baroaulia | 134 | 00:00 | 128 | 14:00 | Mirzapur | 130 | 03:00 | 123 | 23:00
| Baroirhat | 131 | 04:00 | 124 | 12:00 | Mithapukur | 135 | 02:00 | 124 | 09:00
| Bashundhara | 135 | 01:00 | 125 | 12:00 | MI_Cement | 134 | 02:00 | 125 | 12:00
| BashundharaCement | 132 | 01:00 | 124 | 12:00 | Modern | 134 | 02:00 | 127 | 11:00
| Beanibazar | 136 | 02:00 | 131 | 12:00 | Mogbazar | 135 | 00:00 | 126 | 12:00
| Benapole | 138 | 02:00 | 127 | 12:00 | Mongla | 136 | 04:00 | 127 | 12:00
| Bhaluka | 133 | 05:00 | 127 | 11:00 | Motijheel | 136 | 02:00 | 127 | 12:00
| Bhandaria | 132 | 06:00 | 127 | 13:00 | Munshiganj | 132 | 02:00 | 125 | 12:00
| Bhangura | 140 | 01:00 | 131 | 12:00 | Mymensingh | 129 | 05:00 | 117 | 23:00
| Bheramara | 139 | 04:00 | 129 | 12:00 | Naogaon | 137 | 02:00 | 127 | 08:00
| Bheramara(GK) | 138 | 05:00 | 129 | 12:00 | Narail | 140 | 04:00 | 128 | 12:00
| Bhulta | 125 | 05:00 | 118 | 12:00 | Narinda | 136 | 02:00 | 127 | 12:00
| Bog-Sherpur | 137 | 02:00 | 129 | 08:00 | Narshingdi | 125 | 01:00 | 118 | 12:00
| Bogura | 138 | 03:00 | 134 | 16:00 | Natore | 136 | 02:00 | 129 | 12:00
| Bogura-230 | 138 | 02:00 | 130 | 09:00 | Nawabganj | 135 | 04:00 | 127 | 11:00
| Brahmanbaria | 136 | 01:00 | 131 | 11:00 | Netrakona | 131 | 04:00 | 123 | 11:00
| Cantonment | 137 | 02:00 | 126 | 12:00 | New | 135 | 02:00 | 126 | 11:00
| Chandpur | 130 | 01:00 | 120 | 13:00 | Niamatpur | 140 | 06:00 | 135 | 08:00
| Chandraghona | 135 | 02:00 | 129 | 12:00 | Noapara | 139 | 02:00 | 129 | 12:00
| Chapai | 138 | 05:00 | 132 | 08:00 | Pabna | 140 | 02:00 | 131 | 12:00
| Charsaidpur | 134 | 02:00 | 124 | 12:00 | Palashbari | 134 | 02:00 | 124 | 13:00
| Chauddagram | 133 | 01:00 | 123 | 13:00 | Panchagarh | 137 | 03:00 | 122 | 08:00
| Chhatak | 136 | 04:00 | 131 | 14:00 | Patuakhali | 136 | 02:00 | 132 | 11:00
| Chowmuhani | 127 | 05:00 | 116 | 13:00 | Payra | 139 | 04:00 | 135 | 12:00
| Chuadanga | 140 | 03:00 | 125 | 12:00 | PHP | 132 | 02:00 | 121 | 13:00
| Coxsbazar | 128 | 04:00 | 120 | 12:00 | Postogola | 138 | 03:00 | 126 | 12:00
| Cumilla(N) | 136 | 01:00 | 128 | 12:00 | Purbachal | 135 | 04:00 | 125 | 12:00
| Cumilla(S) | 134 | 05:00 | 126 | 12:00 | Purbasadipur | 131 | 03:00 | 120 | 08:00
| Daudkandi | 132 | 00:00 | 124 | 12:00 | Rahanpur | N/A | N/A | N/A | N/A
| Dhaka | 135 | 02:00 | 126 | 12:00 | Rahanpur-400 | 141 | 02:00 | 136 | 01:00
| Dhamrai | 137 | 02:00 | 127 | 12:00 | Rahim | 132 | 02:00 | 125 | 12:00
| Dhanmondi | 135 | 02:00 | 126 | 12:00 | Rajbari | 135 | 03:00 | 129 | 12:00
| Dohazari | 132 | 02:00 | 125 | 13:00 | Rajendrapur | 136 | 20:00 | 128 | 12:00
| Faridpur | 135 | 05:00 | 130 | 12:00 | Rajshahi | 140 | 04:00 | 129 | 12:00
| Fatullah | 135 | 04:00 | 125 | 12:00 | Rajshahi-230 | 139 | 02:00 | 130 | 08:00
| Fenchuganj | 139 | 00:00 | 136 | 11:00 | Ramganj | 128 | 01:00 | 118 | 13:00
| Feni | 130 | 04:00 | 123 | 13:00 | Rampur | 135 | 02:00 | 127 | 13:00
| Ghatail | 132 | 02:00 | 119 | 23:00 | Rampura | 135 | 03:00 | 126 | 12:00
| Ghorashal | 141 | 07:00 | 135 | 12:00 | Rangamati | 134 | 01:00 | 129 | 12:00
| Goalpara | 140 | 01:00 | 129 | 12:00 | Rangpur | 133 | 05:00 | 121 | 09:00
| Gollamari | 138 | 03:00 | 131 | 11:00 | Ruppur | 139 | 00:00 | 132 | 12:00
| Gopalganj | 137 | 03:00 | 130 | 12:00 | Saidpur | 134 | 05:00 | 119 | 09:00
| Gopalganj-400 | 136 | 02:00 | 130 | 12:00 | Satkhira | 138 | 04:00 | 128 | 12:00
| Gulshan | 133 | 02:00 | 124 | 12:00 | Satmasjid | 137 | 03:00 | 125 | 12:00
| Halishahar | 135 | 01:00 | 126 | 12:00 | Savar | 133 | 00:00 | 124 | 12:00
| Haripur | 133 | 02:00 | 126 | 12:00 | SevenRings | 141 | 02:00 | 139 | 19:00
| HaripurSBU | 133 | 02:00 | 126 | 12:00 | ShahCement | 134 | 02:00 | 124 | 12:00
| Hasnabad | 133 | 00:00 | 126 | 12:00 | Shahjadpur | 145 | 03:00 | 135 | 10:00
| Hathazari | 135 | 06:00 | 130 | 12:00 | Shahjibazar | 136 | 01:00 | 132 | 12:00
| Ishurdi | 141 | 03:00 | 132 | 12:00 | Shahmirpur | 133 | 03:00 | 127 | 11:00
| Jaldhaka | 132 | 04:00 | 118 | 09:00 | Shariatpur | 135 | 03:00 | 129 | 12:00
| Jamalpur | 134 | 18:30 | 115 | 23:00 | Sherpur | 132 | 18:30 | 113 | 23:00
| Jashore | 138 | 03:00 | 127 | 12:00 | Shikalbaha | 123 | 00:00 | 117 | 12:00
| Jhenaidah | 140 | 05:00 | 129 | 12:00 | Shikalbaha-230 | 135 | 02:00 | 128 | 12:00
| Jhenaidah-230 | 141 | 03:00 | 130 | 12:00 | Shitalakhya | 134 | 02:00 | 125 | 12:00
| Joydebpur | 140 | 19:30 | 130 | 12:00 | Sholosohor | 135 | 03:00 | 127 | 12:00
| Joypurhat | 136 | 02:00 | 127 | 08:00 | Shyampur | 132 | 04:00 | 125 | 12:00
| Juldah | 133 | 00:00 | 128 | 10:00 | Shyampur-230 | 135 | 05:00 | 125 | 12:00
| Kabirpur | 134 | 03:00 | 125 | 11:00 | Siddhirganj | 134 | 02:00 | 126 | 12:00
| Kachua | 133 | 01:00 | 124 | 12:00 | Sirajganj | 140 | 03:00 | 130 | 12:00
| Kaliakoir | 139 | 04:00 | 126 | 12:00 | Sonargaon | 132 | 01:00 | 124 | 12:00
| Kallyanpur | 134 | 04:00 | 126 | 11:00 | Sreemongol | 137 | 02:00 | 132 | 11:00
| Kalurghat | 134 | 03:00 | 128 | 12:00 | Sreepur | 132 | 02:00 | 125 | 11:00
| Kamrangirchar | 134 | 05:00 | 124 | 12:00 | Srinagar | 135 | 02:00 | 127 | 12:00
| Kaptai | 136 | 7:00 | 132 | 12:00 | SSM | 138 | 00:00 | 136 | 09:00
| Kazla | 136 | 05:00 | 126 | 13:00 | Sunamganj | 134 | 00:00 | 131 | 14:00
| Keranigonj | 135 | 02:00 | 126 | 12:00 | Sylhet | 137 | 02:00 | 133 | 11:00
| Khagrachori | 134 | 02:00 | 127 | 13:00 | Sylhet-132 | 136 | 01:00 | 133 | 13:00
| Khulna | 137 | 02:00 | 129 | 12:00 | Tangail | 128 | 03:00 | 120 | 23:00
| Khulna(S) | 139 | 02:00 | 131 | 12:00 | Thakurgaon | 134 | 03:00 | 118 | 09:00
| Khulshi | 133 | 04:00 | 126 | 12:00 | TK | 134 | 03:00 | 128 | 11:00
| Kishoreganj | 134 | 18:30 | 127 | 11:00 | Tongi | 137 | 04:00 | 128 | 11:00
| Kodda | 136 | 19:30 | 122 | 12:00 | Ullahpara | 140 | 04:00 | 132 | 12:00
| KSRM | 135 | 05:00 | 128 | 11:00 | Ullon | 134 | 03:00 | 125 | 12:00
| Kulaura | 137 | 00:00 | 134 | 16:00 | Uttara | 136 | 05:00 | 127 | 11:00
| Kurigram | 132 | 05:00 | 118 | 18:00 | UttaraNew | 135 | 01:00 | 125 | 12:00
| Zigatola | 135 | 04:00 | 126 | 12:00

## L-Curve
Date | 2024-12-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 828 | 5068 | 3474 | 8542 |  |  |  | QF-LDC-11
0:30 | 715 | 4887 | 3353 | 8240 | Date: | 2024-12-26
1:00 | 602 | 4706 | 3232 | 7938
1:30 | 530 | 4669.5 | 3076.5 | 7746
2:00 | 458 | 4633 | 2921 | 7554
2:30 | 502 | 4496.5 | 2916.5 | 7413 | [5 empty] | Gen. at Eve. Peak | 10424 | 10424 MW (18:00 )
3:00 | 546 | 4360 | 2912 | 7272 | [6 empty] | 18:00
3:30 | 527 | 4315.5 | 2855.5 | 7171 | [5 empty] | Gen. at Day Peak | 9856 | 9856 MW (12:00 )
4:00 | 508 | 4271 | 2799 | 7070 | [6 empty] | 12:00
4:30 | 524 | 4211 | 2799 | 7010 | [5 empty] | Highest Generation | 10424
5:00 | 540 | 4151 | 2799 | 6950 | [6 empty] | 18:00
5:30 | 517 | 4337 | 2840 | 7177
6:00 | 494 | 4523 | 2881 | 7404
6:30 | 422 | 4719 | 2990 | 7709
7:00 | 350 | 4915 | 3099 | 8014
7:30 | 372 | 5113.5 | 3295.5 | 8409
8:00 | 394 | 5312 | 3492 | 8804
8:30 | 459 | 5305.5 | 3673 | 8978.5
9:00 | 524 | 5299 | 3854 | 9153
9:30 | 662 | 5269 | 3858 | 9127
10:00 | 800 | 5239 | 3862 | 9101
10:30 | 912 | 5270.5 | 3857.5 | 9128
11:00 | 1024 | 5302 | 3853 | 9155
11:30 | 1100 | 5483.5 | 4022 | 9505.5
12:00 | 1176 | 5665 | 4191 | 9856
12:30 | 1190 | 5649 | 4327 | 9976
13:00 | 1204 | 5633 | 4463 | 10096
13:30 | 1183 | 5479 | 4304 | 9783
14:00 | 1162 | 5325 | 4145 | 9470
14:30 | 1215 | 5234.5 | 4056.5 | 9291
15:00 | 1268 | 5144 | 3968 | 9112
15:30 | 1211 | 5140 | 3866 | 9006
16:00 | 1154 | 5136 | 3764 | 8900
16:30 | 1060 | 5264.5 | 3781.5 | 9046
17:00 | 966 | 5393 | 3799 | 9192
17:30 | 807 | 5888.5 | 3919.5 | 9808
18:00 | 648 | 6384 | 4040 | 10424
18:30 | 689 | 6254 | 4085 | 10339
19:00 | 730 | 6124 | 4130 | 10254
19:30 | 692 | 6134 | 4121 | 10255
20:00 | 706 | 6015 | 4056 | 10071 |  |  |  | Executive Engineer
20:30 | 758 | 5899 | 4076 | 9975 |  |  |  | Network Operation Division
21:00 | 810 | 5783 | 4096 | 9879
21:30 | 852 | 5656 | 4047.5 | 9703.5
22:00 | 894 | 5529 | 3999 | 9528 |  |  |  |  | Page 6 of 7
22:30 | 904 | 5392 | 3877.5 | 9269.5
23:00 | 914 | 5255 | 3756 | 9011
23:30 | 871 | 5161.5 | 3615 | 8776.5
24:00 | 828 | 5068 | 3474 | 8542
10424 MW (18:00 )
9856 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-12-26 |  |  | Energy |  | 216998691
[17 empty] | 2024-12-26 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | Nepal | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | ADANI | SOLAR | WIND | SHORTAGE
0:00 | 2684 | 921 | 0 | 1966 | 0 | 25 | 2234 | 35 | 0 | 51 | 56 | 510 | 0 | 60 | 0
0:30 | 2772 | 920.5 | 0 | 1775 | 0 | 12.5 | 2062.5 | 37.5 | 0 | 107 | 49 | 462 | 0 | 42 | 0 |  |  | Date: | 44190
1:00 | 2860 | 920 | 0 | 1584 | 0 | 0 | 1891 | 40 | 0 | 163 | 42 | 414 | 0 | 24 | 0
1:30 | 2840.5 | 826 | 0 | 1530.5 | 0 | 0 | 1863 | 40 | 0 | 163 | 41 | 414.5 | 0 | 27.5 | 0 | [8 empty] | Total Energy | 216.9987 | 216.9987 | Total Energy Gen Total Energy MKWHr Energy Not Served Energy not Served MKWHr Energy Requirement Energy Requirement MKWHr | Total Energy Gen 216.999 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 216.999 MKWHr
2:00 | 2821 | 732 | 0 | 1477 | 0 | 0 | 1835 | 40 | 0 | 163 | 40 | 415 | 0 | 31 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 2807.5 | 731.5 | 0 | 1378.5 | 0 | 0 | 1809.5 | 40 | 0 | 163 | 39 | 412 | 0 | 32 | 0 | [8 empty] | Energy Requirement | 216.9987 | 216.9987
3:00 | 2794 | 731 | 0 | 1280 | 0 | 0 | 1784 | 40 | 0 | 163 | 38 | 409 | 0 | 33 | 0
3:30 | 2752 | 684 | 0 | 1265 | 0 | 0 | 1783 | 40 | 0 | 163 | 38 | 411.5 | 0 | 34.5 | 0 | [7 empty] | Shortage
4:00 | 2710 | 637 | 0 | 1250 | 0 | 0 | 1782 | 40 | 0 | 163 | 38 | 414 | 0 | 36 | 0
4:30 | 2678.5 | 636.5 | 0 | 1247 | 0 | 0 | 1762.5 | 40 | 0 | 163 | 38 | 414 | 0 | 30.5 | 0
5:00 | 2647 | 636 | 0 | 1244 | 0 | 0 | 1743 | 40 | 0 | 163 | 38 | 414 | 0 | 25 | 0
5:30 | 2750 | 636.5 | 0 | 1343.5 | 0 | 0 | 1762 | 40 | 0 | 163 | 39 | 414.5 | 0 | 28.5 | 0
6:00 | 2853 | 637 | 0 | 1443 | 0 | 0 | 1781 | 40 | 0 | 163 | 40 | 415 | 0 | 32 | 0
6:30 | 2878.5 | 685 | 0 | 1550.5 | 0 | 7.5 | 1882 | 40 | 0 | 171 | 39 | 416 | 6 | 33.5 | 0 | [6 empty] | Coal
7:00 | 2904 | 733 | 0 | 1658 | 0 | 15 | 1983 | 40 | 0 | 179 | 38 | 417 | 12 | 35 | 0
7:30 | 3000.5 | 827 | 0 | 1668.5 | 0 | 22.5 | 2120.5 | 40 | 0 | 179 | 38 | 416 | 72 | 25 | 0 | [5 empty] | Oil
8:00 | 3097 | 921 | 0 | 1679 | 0 | 30 | 2258 | 40 | 0 | 179 | 38 | 415 | 132 | 15 | 0
8:30 | 3023.5 | 921 | 0 | 1631.5 | 0 | 59 | 2382.5 | 40 | 0 | 179 | 40 | 466 | 220 | 16 | 0
9:00 | 2950 | 921 | 0 | 1584 | 0 | 88 | 2507 | 40 | 0 | 179 | 42 | 517 | 308 | 17 | 0
9:30 | 2865.5 | 921 | 0 | 1523.5 | 0 | 134.5 | 2518 | 40 | 0 | 179 | 45 | 514 | 375.5 | 11 | 0
10:00 | 2781 | 921 | 0 | 1463 | 0 | 181 | 2529 | 40 | 0 | 179 | 48 | 511 | 443 | 5 | 0
10:30 | 2814.5 | 921 | 0 | 1427 | 0 | 182.5 | 2485 | 58 | 0 | 179 | 50 | 511 | 495 | 5 | 0
11:00 | 2848 | 921 | 0 | 1391 | 0 | 184 | 2441 | 76 | 0 | 179 | 52 | 511 | 547 | 5 | 0
11:30 | 2940 | 921.5 | 0 | 1585 | 0 | 196 | 2460 | 38 | 0 | 179 | 53 | 564.5 | 563.5 | 5 | 0
12:00 | 3032 | 922 | 0 | 1779 | 0 | 208 | 2479 | 0 | 0 | 179 | 54 | 618 | 580 | 5 | 0
12:30 | 3040.5 | 922 | 0 | 1765 | 0 | 216.5 | 2516 | 20 | 0 | 187 | 55 | 689 | 562 | 3 | 0
13:00 | 3049 | 922 | 0 | 1751 | 0 | 225 | 2553 | 40 | 0 | 195 | 56 | 760 | 544 | 1 | 0
13:30 | 3049 | 922 | 0 | 1751 | 0 | 225 | 2553 | 40 | 0 | 195 | 56 | 760 | 544 | 1 | 0
14:00 | 3049 | 922 | 0 | 1751 | 0 | 225 | 2553 | 40 | 0 | 195 | 56 | 760 | 544 | 1 | 0
14:30 | 2963 | 922 | 0 | 1645 | 0 | 203 | 2393.5 | 40 | 0 | 187 | 56 | 757.5 | 432.5 | 4.5 | 0
15:00 | 2877 | 922 | 0 | 1539 | 0 | 181 | 2234 | 40 | 0 | 179 | 56 | 755 | 321 | 8 | 0
15:30 | 2915.5 | 921.5 | 0 | 1557 | 0 | 181 | 2203 | 40 | 0 | 179 | 52 | 715.5 | 231 | 10.5 | 0
16:00 | 2954 | 921 | 0 | 1575 | 0 | 181 | 2172 | 40 | 0 | 179 | 48 | 676 | 141 | 13 | 0
16:30 | 2975 | 921 | 0 | 1620.5 | 0 | 226 | 2222 | 40 | 0 | 228 | 49 | 667.5 | 78.5 | 18.5 | 0
17:00 | 2996 | 921 | 0 | 1666 | 0 | 271 | 2272 | 40 | 0 | 277 | 50 | 659 | 16 | 24 | 0
17:30 | 3001 | 921 | 0 | 1752.5 | 0 | 577.5 | 2454 | 40 | 0 | 295.5 | 55 | 671.5 | 8 | 32 | 0
18:00 | 3006 | 921 | 0 | 1839 | 0 | 884 | 2636 | 40 | 0 | 314 | 60 | 684 | 0 | 40 | 0
18:30 | 3034.5 | 921 | 0 | 1841 | 0 | 801.5 | 2619.5 | 40 | 0 | 267.5 | 57 | 718 | 0 | 39 | 0
19:00 | 3063 | 921 | 0 | 1843 | 0 | 719 | 2603 | 40 | 0 | 221 | 54 | 752 | 0 | 38 | 0
19:30 | 3076 | 921 | 0 | 1846 | 0 | 719 | 2595 | 40 | 0 | 221 | 52 | 751 | 0 | 34 | 0
20:00 | 3177 | 921 | 0 | 1839 | 0 | 451 | 2579 | 40 | 0 | 221 | 60 | 752 | 0 | 31 | 0
20:30 | 3046.5 | 921 | 0 | 1883.5 | 0 | 438 | 2580.5 | 40 | 0 | 221 | 57 | 754.5 | 0 | 33 | 0
21:00 | 2916 | 921 | 0 | 1928 | 0 | 425 | 2582 | 40 | 0 | 221 | 54 | 757 | 0 | 35 | 0
21:30 | 2824 | 921 | 0 | 2013 | 0 | 338.5 | 2575 | 40 | 0 | 145.5 | 54 | 755.5 | 0 | 37 | 0
22:00 | 2732 | 921 | 0 | 2098 | 0 | 252 | 2568 | 40 | 0 | 70 | 54 | 754 | 0 | 39 | 0
22:30 | 2732 | 921.5 | 0 | 2117.5 | 0 | 147.5 | 2443.5 | 40 | 0 | 60.5 | 54 | 706.5 | 0 | 46.5 | 0
23:00 | 2732 | 922 | 0 | 2137 | 0 | 43 | 2319 | 40 | 0 | 51 | 54 | 659 | 0 | 54 | 0
23:30 | 2708 | 921.5 | 0 | 2051.5 | 0 | 34 | 2276.5 | 37.5 | 0 | 51 | 55 | 584.5 | 0 | 57 | 0 |  |  | Max Temp. in Dhaka |  | 28.5°C
24:00 | 2684 | 921 | 0 | 1966 | 0 | 25 | 2234 | 35 | 0 | 51 | 56 | 510 | 0 | 60 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 216.999 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 216.999 MKWHr
Note on Y13: Author:

## Generation
2024-12-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 76 | 0 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 959100
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 8 | 6 | 13 | 15 | 18 | 17 | 14 | 10 | 5 | 0 | [9 empty] | 106245
6 | Sikalbaha 225MW CCPP (Gas) | 230 | 230 | 212 | 187 | 187 | 230 | 230 | 230 | 230 | 231 | 227 | 225 | 227 | 224 | 224 | 224 | 226 | 226 |  | 227 | 228 | 228 | 229 | 232 | 228 | 227 | 5237403
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [25 empty] | 0
12 | Hathazari 100 MW peaking PP | [16 empty] | 17 | 17 | [8 empty] | 27504
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 12 |  | 30 | 34 |  |  |  |  | 0 | 68581
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [26 empty] | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 229 | 223 | 223 | 220 | 220 | 220 | 220 | 220 | 220 | 225 | 236 | 236 | 236 | 235 | 248 | 248 | 253 | 254 |  | 246 | 245 | 205 | 20 |  |  | 0 | 4780866
18 | Kodda 300 MW PP Unit-2 (Summit) | [26 empty] | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 130 | 78 | 8 | 8 | 8 | 8 | 184 | 185 | 110 | 110 | 66 | 190 | 182 | 135 | 137 | 137 | 167 | 185 |  | 187 | 187 | 189 | 189 | 189 | 189 | 189 | 3111273
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 384 | 384 | 335 | 335 | 295 | 325 | 364 | 460 | 550 | 550 | 550 | 580 | 612 | 501 | 476 | 445 | 501 | 590 |  | 605 | 602 | 603 | 603 | 602 | 550 | 510 | 11639999
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 40 | 36 | 37 | 5 | 5 | 28 | 37 | 36 | 36 | 40 | 39 | 39 | 40 | 40 | 37 | 41 | 41 | 42 |  | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 868680
33 | Ashuganj 225 MW CCPP | 182 | 182 | 182 | 181 | 153 | 199 | 186 | 217 | 182 | 182 | 195 | 187 | 182 | 193 | 182 | 195 | 192 | 209 |  | 191 | 181 | 203 | 182 | 182 | 189 | 182 | 4574000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 300 | 305 | 300 | 300 | 300 | 310 | 300 | 370 | 300 | 280 | 310 | 315 | 305 | 300 | 290 | 310 | 325 | 345 |  | 295 | 285 | 345 | 310 | 310 | 290 | 295 | 7759000
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 28 | 29 |  |  |  |  | 8 | 26 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 547200
36 | Chandpur 150 MW CCPP | 31 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 30 | 30 | 35 | 860180
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 317 | 317 | 317 | 317 | 317 | 312 | 305 | 302 | 308 | 305 | 302 | 308 | 307 | 307 | 308 | 313 | 313 | 311 |  | 312 | 312 | 311 | 311 | 302 | 302 | 302 | 7520400
| Meghnaghat Unique power | 310 | 300 | 300 | 300 | 300 | 350 | 273 | 276 | 276 | 320 | 320 | 355 | 355 | 350 | 350 | 350 | 350 | 420 |  | 420 | 420 | 420 | 500 | 584 | 592 | 588 | 8905909
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 350 | 300 | 300 | 350 | 400 | 400 | 420 | 350 | 320 | 420 | 420 | 350 | 350 | 350 | 400 | 400 |  | 400 | 400 | 400 | 390 | 450 | 450 | 360 | 9152500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 8 | 10 | 10 | 10 | 11 | 11 | 11 | 8 | 5 | 4 | 4 | 4 | 3 | 4 | 4 | 4 | 4 | 4 |  | 5 | 6 | 8 | 9 | 10 | 10 | 8 | 153600
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 9 | 23 | 34 | 41 | 43 | 39 | 34 | 23 | 9 | 1 | [9 empty] | 261380
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 33 | 20 | 20 | 20 | 20 | 33 | 32 | 31 | 20 | 20 | 30 | 30 | 31 | 30 | 30 | 31 |  |  |  |  | 20 | 20 | 25 | 25 | 25 | 1257216
48 | Shahjibazar 86 MW PP (Shahjibazar) | 5 | 5 | 5 | 5 | 5 | 5 | 42 | 42 | 42 | 11 | 11 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 72 | 86 | 86 | 61 | 86 | 86 | 84 | 871680
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 |  | 138 | 138 | 138 | 138 | 20 | 20 | 20 | 3052230
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 58224
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 8 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 338160
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 265 | 270 | 290 | 285 | 300 | 300 | 305 | 300 | 280 | 285 | 300 | 285 | 290 | 270 | 305 | 310 | 310 |  | 275 | 265 | 295 | 295 | 275 | 280 | 290 | 7080500
| Bibiyana South 400 MW | 316 | 316 | 316 | 316 | 316 | 340 | 340 | 400 | 340 | 320 | 352 | 340 | 346 | 355 | 316 | 346 | 316 | 360 |  | 346 | 346 | 400 | 346 | 346 | 316 | 316 | 8197000
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 | [7 empty] | 0 | 35593
59 | Tangail Palli Power Gen 22 MW | [17 empty] | 9 | [7 empty] | 0 | 23040
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 42 | 40 | 38 | 38 | 38 | 40 | 38 | 38 | 42 | 48 | 52 | 54 | 56 | 60 | 56 | 48 | 50 | 60 |  | 54 | 52 | 60 | 54 | 54 | 54 | 56 | 1170240
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 41 | 41 | 41 | 37 | 2 | 6 | 5 | 3 | 3 | 5 | 5 | 4 | 5 | 8 | 8 |  | 15 | 15 | 18 | 18 | 23 | 34 | 32 | 501120
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 17 | 15 | 15 | 11 | 15 | 11 | 16 | 16 | 16 | 16 | 16 | 14 | 16 | 11 | 16 | 16 | 16 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 364000
69 | Summit Ashulia | 20 | 15 | 15 | 15 | 15 | 15 | 21 | 21 | 21 | 20 | 20 | 20 | 15 | 18 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 19 | 18 | 456000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 529200
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 22 | 22 |  | 22 | 22 | 22 | 20 | 17 | 17 | 16 | 472680
72 | Rupganj 33 MW PP(Summit) | 24 | 24 | 24 | 26 | 26 | 26 | 26 | 26 | 24 | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 24 | 24 | 24 | 571000
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0
| Chowmuhani 113 MW | [16 empty] | 1 | 30 |  | 9 | 9 | 9 | 9 | 9 |  | 0 | 114240
| Manikgonj 162MW PP(MPGL) | [16 empty] | 17 | 54 |  | 90 | 90 | 35 | 17 |  |  | 0 | 240480
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 13 | 34 | 34 | 34 | 34 | 25 | 25 | 25 | 34 | 34 |  | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 421920
79 | Kodda 150 MW PP | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 16 | 16 | 16 | 32 | 48 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 356160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 8 | [8 empty] | 11496
| Gazipur 100 MW PP | [6 empty] | 7 | 22 | 37 | 52 | 52 | 52 | 62 | 52 | 52 | 52 | 55 | 70 |  | 70 | 70 | 70 | 70 | 70 | 35 | 17 | 936960
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 3 | 3 | 4 | 3 | 3 | 2 | 1 | [10 empty] | 20641
| Jodiac Power | [16 empty] | 7 | 54 |  | 17 | 17 | 17 | 17 |  |  | 0 | 144067
| Karnaphuli Power Ltd. | [17 empty] | 12 |  | 28 | 28 | [5 empty] | 72763
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [17 empty] | 8 | [7 empty] | 0 | 10560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 |  |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 20 | 35 | 36 | 222336
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 |  |  |  |  | 20 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 873196
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 8 | 8 | 8 |  |  |  | 0 | 18144
95 | Patenga 50MW PP (Baraka) | [9 empty] | 9 | 12 | 24 | 31 | 33 | 33 | 33 | 33 | 33 |  | 19 | 19 | 19 | 19 | 19 |  | 0 | 329760
96 | Chattogram 108 MW PP (ECPV) | [17 empty] | 6 | [7 empty] | 0 | 12480
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 227568
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 120 | 120 | 163 | 163 | 120 | 120 | 120 | 120 | 163 |  | 163 | 163 | 120 | 163 | 163 | 163 | 120 | 3752345
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 11950
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 17 |  | 35 | 35 |  |  |  |  | 0 | 78120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [8 empty] | 10 | 8 | 8 | 8 | 8 | 8 |  |  | 5 | 66 |  | 45 | 45 | 45 | 45 | 45 |  | 0 | 338400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 23 | 17 | 17 | 17 | 16 |  |  | 253584
115 | Juldah 100 MW PP Unit-3 (Acorn) | [16 empty] | 12 | 40 |  | 24 | 24 |  |  |  |  | 0 | 83520
116 | Chandpur 200 MW (Desh energy) | [17 empty] | 12 | [7 empty] | 0 | 22080
117 | Ashuganj 150 MW PP (Midland) | [16 empty] | 3 | 38 |  | 65 | 65 | 65 | 65 | 40 |  |  | 287709
118 | Bibiyana-III 400 MW CCPP | 356 | 353 | 353 | 353 | 312 | 348 | 365 | 380 | 358 | 323 | 309 | 342 | 335 | 335 | 335 | 335 | 335 | 335 |  | 346 | 380 | 380 | 381 | 381 | 381 | 381 | 8751000
| Jamalpur 115 MW PP (United) | [8 empty] | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 18 | 65 |  | 75 | 75 | 75 | 75 | 45 |  | 0 | 450000
| Anwara 300 MW PP (United) | [16 empty] | 15 | 49 |  | 15 | 15 | 15 | 15 |  |  | 0 | 125455
| Juldah unit-2 (Acorn) | [11 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 50 |  | 24 | 24 |  |  |  |  | 0 | 152640
| Anlima Energy Ltd. | [16 empty] | 7 | 30 |  | 17 | 17 | 17 | 17 |  |  | 0 | 124200
| Bhairob 54.5 MW | [16 empty] | 0 | 17 | [7 empty] | 0 | 25920
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 8 | 16 | 23 | 27 | 29 | 26 | 22 | 15 | 7 | 1 | [9 empty] | 168664
| Chandpur 115(Doreen) | [17 empty] | 4 |  | 32 | 34 |  |  |  |  | 0 | 66240
| Kanchan Purbachal Power Generation Ltd. | [8 empty] | 7 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 28 |  | 17 | 17 | 17 | 17 |  |  | 0 | 363600
| Mirsharai 150 MW (Oil) | [17 empty] | 17 | [7 empty] | 0 | 20073
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 24 | 31 | 33 | 36 | 25 | 32 | 35 | 15 | 17 | 5 | 5 | 5 | 1 | 3 | 8 | 13 | 24 | 40 |  | 38 | 34 | 31 | 35 | 39 | 54 | 60 | 578400
| Sonagazi 75 MW Solar Plant | [6 empty] | 2 | 20 | 40 | 55 | 63 | 65 | 61 | 51 | 36 | 17 | 2 | [9 empty] | 409609
| Matarbari 2*600 MW (CPGCL) | 371 | 373 | 371 | 372 | 372 | 374 | 455 | 529 | 575 | 575 | 576 | 576 | 501 | 502 | 463 | 454 | 454 | 575 |  | 575 | 575 | 575 | 575 | 575 | 575 | 575 | 11978181
| JERA Meghnaghat Power Limited | [25 empty] | 0 | 0
| Sreepur 150 MW | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 54 | 35 | 35 | 3619200
120
121 | Eastern Zone Total | 4706 | 4633 | 4360 | 4271 | 4151 | 4523 | 4915 | 5312 | 5299 | 5239 | 5302 | 5665 | 5633 | 5325 | 5144 | 5136 | 5393 | 6384 |  | 6124 | 6134 | 6015 | 5783 | 5529 | 5255 | 5068 | 127901364
122
123
124 | Khulna 60MW
manik
125 | Khulna 115 PP MW (KPCL-2)
126 | Khulna 330 MW CCPP (GAS)
127 | Khulna 330 MW CCPP (OIL)
128 | Khulna (Aggreeco) 55MW
Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Kulna 225 MW CCPP (GAS)
130 | Rupsha 105 MW PP (Orion rupsha)
131 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 14 | 39 | 45 | 67 | 72 | 69 | 57 | 39 | 18 | 3 | [9 empty] | 434880
132 | Rampal 1320 MW (BIFPCL) | 828 | 770 | 770 | 767 | 766 | 772 | 854 | 962 | 1104 | 1110 | 1005 | 1015 | 1128 | 1018 | 982 | 968 | 1009 | 1135 |  | 1035 | 1026 | 1005 | 1000 | 990 | 814 | 768 | 23032730
133 | United Payra Power Ltd. | [25 empty] | 0 | 0
| Bhola Nutan Biddut BD LTD (GAS) | 220 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 180 | 180 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 5216040
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 180 |  | 170 | 170 | 170 | 170 | 170 | 150 | 150 | 3753000
137 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 3001
Bhola 95 MW PP (Aggreko)
140 | Bhola 225 MW CCPP | 65 | 65 | 65 | 40 | 40 | 40 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1478000
141 | Bhola 33 MW PP (Venture) | 7 | 6 | 6 | 6 | 5 | 6 | 6 | 4 | 3 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 5 | 7 |  | 7 | 6 | 7 | 7 | 8 | 8 | 7 | 125445
142 | Noapara 100 MW PP (Bangla Trac)
143 | Noapara 40 MW PP (Khanjahan Ali)
144 | Gopalganj 100 MW Peaking PP
145 | Bheramara GTPP Unit-3
146 | Madhumati 100 MW PP
| Bheramara HVDC | 920 | 732 | 731 | 637 | 636 | 637 | 733 | 921 | 921 | 921 | 921 | 922 | 922 | 921 | 922 | 921 | 921 | 921 |  | 921 | 921 | 921 | 921 | 921 | 922 | 921 | 20784000
147 | Nepal
148 | Bheramara 410 MW CCPP | [13 empty] | 31 | 37 | 39 | 38 | 7 |  | 23 | 29 | 33 | 112 | 105 | 198 | 185 | 642240
149 | Payra 1320 MW
150
151 | Barapukuria TPP Unit-1 | [19 empty] | 62 | 62 | 65 | 70 | 71 | 70 | 71 | 341236
152 | Barapukuria TPP Unit-2
153 | Barapukuria 275 MW TPP Unit-3 | 158 | 158 | 158 | 158 | 160 | 160 | 160 | 157 | 128 | 144 | 160 | 158 | 162 | 162 | 163 | 155 | 158 | 156 |  | 156 | 160 | 161 | 164 | 160 | 160 | 160 | 3848000
156 | Baghabari 71 MW GTPP
Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
| Sirajgonj 6.55 MW Solar | [7 empty] | 0 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [9 empty] | 27780
157 | Sirajganj 68 MW Solar Park | [6 empty] | 0 | 10 | 28 | 42 | 51 | 53 | 51 | 40 | 28 | 11 | 1 | [9 empty] | 318000
158 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 167 | 144 | 142 | 144 | 144 | 155 | 157 | 176 | 192 | 156 | 152 | 214 | 214 | 164 | 155 | 161 | 172 | 168 |  | 214 | 214 | 214 | 214 | 214 | 173 | 150 | 4217364
Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 150 | 149 | 149 | 150 | 150 | 162 | 164 | 170 | 193 | 157 | 157 | 201 | 218 | 170 | 159 | 168 | 178 | 175 |  | 213 | 209 | 195 | 173 | 155 | 158 | 157 | 4272736
159 | Sirajgonj 225 MW CCPP Unit-2 (Oil)
| Sirajgonj 225MW CCPP Unit-3 (Gas) | 148 | 147 | 147 | 148 | 149 | 159 | 161 | 161 | 175 | 147 | 149 | 202 | 220 | 182 | 159 | 172 | 182 | 178 |  | 208 | 204 | 198 | 173 | 158 | 151 | 145 | 4286445
Sirajgonj 225MW CCPP Unit-3 (Oil)
160 | Sirajgonj 400 MW CCPP Unit-4
161 | Sirajgonj 400MW CCPP Unit-4 (Oil)
162 | Bera 70 MW Peaking PP
163 | Bogra 22 MW PP (GBB)
164 | Bogura 20 MW PP (Energyprima)
165 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 149850
166 | Amnura 50 MW PP(Sinha)
167 | Katakhali 50 MW PP (Northern)
168 | Katakhali 50 MW Peaking PP
169 | Santahar 50 MW Peaking PP
170 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
171 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 65 | 69 |  | 42 | 42 | 42 | 42 |  |  | 0 | 251936
Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
173 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
175 | Rangpur 20 MW GTPP
176 | Saidpur 20 MW GTPP
177 | Rangpur 113 MW PP (Confidence) | [25 empty] | 0 | 0
178 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 4 | 4 | 2 | 1 | 0 | [9 empty] | 30854
| Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 70 |  | 34 | 34 |  |  |  |  | 0 | 151728
| Intraco Solar 30 MW | [6 empty] | 0 | 6 | 15 | 21 | 26 | 29 | 26 | 22 | 15 | 7 | 1 | [9 empty] | 170328
178 | Adani Power Jharkhanda Ltd | 414 | 415 | 409 | 414 | 414 | 415 | 417 | 415 | 517 | 511 | 511 | 618 | 760 | 756 | 755 | 676 | 659 | 684 |  | 752 | 751 | 752 | 757 | 754 | 659 | 510 | 13987974
| Teesta Solar Limited | [6 empty] | 4 | 37 | 91 | 133 | 162 | 169 | 158 | 139 | 97 | 42 | 4 | [9 empty] | 1030320
179 | Pabna Solar 100 MW | [6 empty] | 1 | 18 | 44 | 65 | 82 | 87 | 84 | 74 | 51 | 23 | 3 | [9 empty] | 543440
| Western Zone Total | 3232 | 2921 | 2912 | 2799 | 2799 | 2881 | 3099 | 3492 | 3854 | 3862 | 3853 | 4191 | 4463 | 4145 | 3968 | 3764 | 3799 | 4040 |  | 4130 | 4121 | 4056 | 4096 | 3999 | 3756 | 3474 | 89097327
[27 empty] | Total | 216998691