## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-12-2024 | during | 01-01-2025 | during | 01-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 101.2 | 0 | 0 | 0 | 0 | 1 | 1 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 234.58 | 174.8 | 0 | 0 | 0 | 0 | 1 | 1
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 1 | 1 | Default availability set by nldc
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 1 | 1
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 1 | 1 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 40 | 40 | 1 | 1 | Default availability set by nldc
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 317 | 294 | 400.37 | 400.37 | 250 | 250
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 330 | 450 | 450 | 450 | 450
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 1 | 1
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 25.21 | 0 | 0 | 25.21 | 25.21 | 0 | 0 | Default availability set by nldc
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 1 | 1 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 265 | 230 | 335 | 335 | 160 | 160
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 14 | 53.97 | 53.97 | 34 | 54
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 4 | 32 | 149.36 | 149.36 | 149 | 149
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | Default availability set by nldc
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 19 | 19 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 23 | 22 | 23 | 23 | 23 | 23
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 22 | 33 | 33 | 33 | 33
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 20 | 33 | 33 | 33 | 33
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 16 | 17 | 51.4 | 51.4 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 105 | 105 | 1 | 1 | Default availability set by nldc
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 0 | 0 | 149 | 149 | 149 | 149
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 50 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 7 | 17 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 162 | 162 | 162 | 162
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 16 | 0 | 25 | 0 | 25 | 0
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 17 | 17 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 300 | 584 | 584 | 200 | 200
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 1 | 1 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 718 | 718 | 0 | 0 | 718 | 718 | 1 | 1 | Default availability set by nldc
Dhaka Area Total |  |  |  |  | 7178.63 | 6689.44 | 1475 | 1421 | 5477.41 | 5452.41 | 2292 | 2352
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 360 | 360 | 1 | 1 | Default availability set by nldc
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25 | 25 | 8 | 25
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 18 | 50 | 50 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 26 | 26 | 230 | 230 | 230 | 230 | Default availability set by nldc
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 232 | 227 | 225 | 225 | 225 | 225 | Default availability set by nldc
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 85 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 64 | 56 | 74 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 98 | 98 | 50 | 50 | Default availability set by nldc
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 33 | 33 | 3 | 14 | 33 | 33 | 2 | 8 | Default availability set by nldc
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 20 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4 | 0 | 4 | 0
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 50 | 100
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 50 | 108 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 17 | 150
55 | SS Power | Coal | IPP | 2*660 | 1320 | 1224 | 457 | 606 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 66 | 66 | 18 | 22 | 66 | 66 | 66 | 66 | Default availability set by nldc
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1200 | 1200 | 503 | 575 | 575 | 575 | 575 | 575 | U1 S/D 09/Oct/24 (Maintenance Work)
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 60 | 0 | 60 | 0
Chattogram Area Total |  |  |  |  | 5177.36 | 4987.22 | 1328 | 1505 | 3574.22 | 3491.22 | 2544.36 | 2793.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 182 | 182 | 221 | 221 | 205 | 205
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 356.15 | 300 | 300 | 356.15 | 356.15 | 320 | 320
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 1 | 1
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 1 | 1
62 | Ashuganj 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 30 | 46.94 | 46.94 | 40 | 40 | Default availability set by nldc
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 28 | 29 | 30 | 30 | 20 | 20
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 189 | 195 | 195 | 195 | 195
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 25 | 150 | 150 | 150 | 150
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 30 | 45 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 40 | 163 | 163 | 40 | 40 | Default availability set by nldc
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 12 | 200 | 200 | 200 | 200
| Import (Tripura) | Import | Import |  | 160 | 160 | 50 | 60 | 160 | 160 | 160 | 160 | Default availability set by nldc
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 17 | 7.34 | 20.83 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 113 | 113 | 95 | 100
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 25 | 115 | 115 | 50 | 92
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 53
Cumilla Area Total |  |  |  |  | 2893.7 | 2868.78 | 879 | 996 | 2076.13 | 2089.62 | 1756.2 | 1854.2
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 4 | 210 | 210 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 55 | 200 | 200 | 100 | 200
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 60 | 115 | 115 | 95 | 95
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.47 | 0 | 39.4 | 0 | 39.4 | 0
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | Default availability set by nldc
Mymensingh Area Total |  |  |  |  | 750 | 749.71 | 67.47 | 119 | 738.4 | 697 | 418.4 | 477
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 33 | 29 | 80 | 80 | 30 | 30 | Default availability set by nldc
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 90 | 90 | 1 | 1 | Default availability set by nldc
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 120 | 163 | 163 | 163 | 163
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 330 | 330 | 1 | 1 | Default availability set by nldc
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 40 | 40 | 35 | 35
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 11 | 11 | 2 | 2 | Default availability set by nldc
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 25 | 25 | 66.57 | 66.57 | 25 | 25 | Default availability set by nldc
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 42 | 56 | 86 | 86 | 55 | 55
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 100 | 100 | 1 | 1 | Default availability set by nldc
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 214 | 209 | 225 | 225 | 205 | 205 | Default availability set by nldc
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 1 | 1 | Default availability set by nldc
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 25 | 25 | 13 | 13 | Default availability set by nldc
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 270 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 356 | 358 | 400 | 400 | 380 | 380 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 363 | 340 | 383 | 383 | 220 | 220
Sylhet Area Total |  |  |  |  | 2411 | 2370.57 | 1443 | 1427 | 2360.57 | 2360.57 | 1439 | 1439
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 16 | 16 | 16 | 16 | Default availability set by nldc
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 923 | 923 | 1000 | 1000 | 1000 | 1000 | Default availability set by nldc
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 20 | 35
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 80 | 80 | 34 | 60
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 311 | 250 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71 | 0 | 70 | 0 | 70 | 0
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | Default availability set by nldc
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 949 | 1157 | 1234 | 1234 | 1234 | 1234
** | HVDC(Nepal) | Import | Import | 1*40 | 40 | 40 | 0 | 0 | 40 | 40 | 40 | 40 | Default availability set by nldc
Khulna Area Total |  |  |  |  | 3743 | 3726.2 | 2254 | 2330 | 3668 | 3598 | 3385 | 3356
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 3 | 0 | 10.12 | 10.12 | 10.12 | 10.12
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 130 | 134 | 134 | 134 | 134 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 420 | 400 | 622 | 622 | 622 | 622
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 54 | 150
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 260 | 307 | 307 | 307 | 307 | 307
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 0.29 | 0 | 0.29 | 0
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1033.51 | 1074 | 1553.41 | 1553.12 | 1457.41 | 1553.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 1 | 1 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 1 | 1 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 52 | 52 | Default availability set by nldc
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 66 | 66 | 71 | 71 | Default availability set by nldc
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 35.09 | 35.09 | 35.09 | 35.09 | Default availability set by nldc
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 26 | 32
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 165 | 168 | 214 | 214 | 193 | 193 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 148 | 206 | 220 | 220 | 198 | 198 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 169 | 187 | 220 | 220 | 198 | 198 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 46 | 46 | 24 | 24 | Default availability set by nldc
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 8.5 | 8.25 | 8.25 | 8.5 | 8.5 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 45 | 52
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 33 | 98 | 98 | 53 | 95
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 95 | 113
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 1.31 | 0 | 4.6 | 0 | 4.6 | 0
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 484 | 631 | 1347.54 | 1347.54 | 800 | 800
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 14.89 | 0 | 25 | 0 | 25 | 0
| Pabna Solar 100 MW | Solar | IPP |  | 100 | 100 | 83 | 0 | 75 | 0 | 75 | 0
Rajshahi Area Total |  |  |  |  | 3575.55 | 3393.2 | 1070.7 | 1233.5 | 2800.68 | 2696.08 | 2018.19 | 1986.59
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 76 | 75 | 75 | 75 | 75 | 75
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 176 | 200 | 200 | 200 | 200 | 200
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | Default availability set by nldc
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | Default availability set by nldc
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 90 | 113
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.9 | 0 | 4.6 | 0 | 4.6 | 0
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 28 | 0 | 28 | 0
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 88 | 0 | 115.32 | 0 | 115.32 | 0
Rangpur Area Total |  |  |  |  | 1030 | 950 | 365.9 | 275 | 690.92 | 543 | 667.92 | 543
System Total |  |  |  |  | 29025.24 | 28000.22 | 9916.58 | 10380.5 | 22939.74 | 22481.02 | 15978.48 | 16354.27
Forecast Scenario (01-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8600 |  | 0 |  | 8600
|  |  |  | 1:00 | 8000 |  | 0 |  | 8000
|  |  |  | 2:00 | 7600 |  | 0 |  | 7600
|  |  |  | 3:00 | 7300 |  | 0 |  | 7300
|  |  |  | 4:00 | 7100 |  | 0 |  | 7100
|  |  |  | 5:00 | 7100 |  | 0 |  | 7100
|  |  |  | 6:00 | 7500 |  | 0 |  | 7500
|  |  |  | 7:00 | 8000 |  | 0 |  | 8000
|  |  |  | 8:00 | 8900 |  | 0 |  | 8900
|  |  |  | 9:00 | 9400 |  | 0 |  | 9400
|  |  |  | 10:00 | 9100 |  | 0 |  | 9100
|  |  |  | 11:00 | 9300 |  | 0 |  | 9300
|  |  |  | 12:00 | 9900 |  | 0 |  | 9900
|  |  |  | 13:00 | 10100 |  | 0 |  | 10100
|  |  |  | 14:00 | 9800 |  | 0 |  | 9800
|  |  |  | 15:00 | 9400 |  | 0 |  | 9400
|  |  |  | 16:00 | 9160 |  | 0 |  | 9160
|  |  |  | 17:00 | 9400 |  | 0 |  | 9400
|  |  |  | 18:00 | 10600 |  | 0 |  | 10600
|  |  |  | 18:30 | 10550 |  | 0 |  | 10550
|  |  |  | 19:00 | 10500 |  | 0 |  | 10500
|  |  |  | 19:30 | 10470 |  | 0 |  | 10470
|  |  |  | 20:00 | 10300 |  | 0 |  | 10300
|  |  |  | 21:00 | 10000 |  | 0 |  | 10000
|  |  |  | 22:00 | 9620 |  | 0 |  | 9620
|  |  |  | 23:00 | 8980 |  | 0 |  | 8980
Probable Maximum Temperature: |  |  | 25.60°C
Probable Maximum Demand at Day Peak: |  |  | 9900.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 10600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 215.66 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (31-12-2024) Scenario
Maximum Temperature: |  |  |  |  | 24.60°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 841.32
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 20.8742 | Peak Hour Flow: |  | 923.00 MW at 18:00 hrs.
Energy Flow from West to East |  | 10277981.91 KWhr |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 12.6376 | Peak Hour Flow: |  | 631.00 MW at 18:00 hrs.
Power Flow during Peak Demand |  | 602 MW |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.2221 | Peak Hour Flow: |  | 60.00 MW at 18:00 hrs.
Maximum Power Flow |  | 792 MW |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 34.7338 | Peak Hour Flow: |  | 1614.00 MW at 18:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## Genlog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 31-12-2024 | [28 empty] | Date: | 31-12-2024 | [28 empty] | Date: | 31-12-2024 | [28 empty] | Date: | 31-12-2024 | [28 empty] | Date: | 31-12-2024 | [18 empty] | Date: | 31-12-2024
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | Sonagazi 75 MW (AC) Solar Power Plant | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Bhairob 54.5 MW | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sreepur 150 MW PP | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.00 MW | 105.00 MW | 52.00 MW | 365.00 MW | 260.00 MW | 234.58 MW | 190.00 MW | 108.00 MW | 412.00 MW | 20.00 MW | 718.00 MW | 54.00 MW | 36.09 MW | 20.00 MW | 149.00 MW | 149.00 MW | 300.00 MW | 55.00 MW | 55.00 MW | 162.00 MW | 33.00 MW | 104.00 MW | 450.00 MW | 335.00 MW | 583.00 MW | 583.00 MW | 55.00 MW | 33.00 MW | 335.00 MW | 210.00 MW | 115.00 MW | 35.00 MW | 33.75 MW | 23.00 MW | 105.00 MW | 584.00 MW | 116.00 MW | 300.00 MW | 108.00 MW | 360.00 MW | 66.00 MW | 102.00 MW | 98.00 MW | 54.36 MW | 100.00 MW | 100.00 MW | 7.00 MW | 230.00 MW | 110.00 MW | 33.00 MW | 1150.00 MW | 159.86 MW | 159.86 MW | 50.00 MW | 25.00 MW | 105.00 MW | 225.00 MW | 225.00 MW | 150.00 MW | 150.00 MW | 75.00 MW | 1320.00 MW | 20.00 MW | 51.00 MW | 150.00 MW | 195.00 MW | 400.00 MW | 356.15 MW | 360.00 MW | 45.00 MW | 55.00 MW | 221.00 MW | 54.50 MW | 115.00 MW | 163.00 MW | 200.00 MW | 113.00 MW | 25.00 MW | 114.00 MW | 160.00 MW | 52.20 MW | 52.00 MW | 341.00 MW | 383.00 MW | 400.00 MW | 50.00 MW | 70.00 MW | 90.00 MW | 11.00 MW | 163.00 MW | 25.00 MW | 100.00 MW | 86.00 MW | 66.00 MW | 330.00 MW | 20.00 MW | 231.00 MW | 115.00 MW | 200.00 MW | 210.00 MW | 3.00 MW | 150.00 MW | 50.00 MW | 22.00 MW | - | 1000.00 MW | 410.00 MW | 16.00 MW | 54.00 MW | 109.00 MW | 40.00 MW | 230.00 MW | 230.00 MW | 336.00 MW | 336.00 MW | 105.00 MW | 100.00 MW | 1234.00 MW | 105.00 MW | 1347.54 MW | 35.09 MW | 100.00 MW | 52.00 MW | 71.00 MW | 113.00 MW | 71.00 MW | 104.00 MW | 113.00 MW | 50.00 MW | 52.00 MW | 100.00 MW | 50.00 MW | 68.00 MW | 214.00 MW | 214.00 MW | 220.00 MW | 220.00 MW | 220.00 MW | 220.00 MW | 414.00 MW | 414.00 MW | 6.09 MW | 11.00 MW | 274.00 MW | 170.00 MW | 115.00 MW | 30.00 MW | 113.00 MW | 20.00 MW | 20.00 MW | 8.00 MW | 200.00 MW | 1.00 MW | 110.00 MW | 307.00 MW | 40.00 MW | 194.00 MW | 220.00 MW | 220.00 MW | 1244.00 MW | 150.00 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 24 | 164 | 0 | 0 | 0 | 14 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 36 | 450 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 460 | 0 | 5 | 0 | 16 | 0 | 285 | 0 | 33 | 0 | 180 | 0 | 0 | 45 | 0 | 0 | 18 | 0 | 52 | 0 | 0 | 260 | 346 | 369 | 5 | 30 | 0 | 2 | 163 | 13 | 0 | 11 | 25 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 4403 | 922 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 0 | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 189 | 0 | 175 | 0 | 0 | 0 | 0 | 5.5 | 193 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 130 | 220 | 0 | 400 | 0 | 4149.5 | 8552.5 | 94.07
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 24 | 168 | 0 | 0 | 0 | 16 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 39 | 378 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 350 | 0 | 5 | 0 | 8 | 0 | 290 | 0 | 5 | 0 | 182 | 0 | 0 | 45 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 275 | 300 | 370 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 11 | 25 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4093 | 922 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 191 | 0 | 175 | 0 | 0 | 0 | 0 | 5.5 | 195 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 80 | 180 | 0 | 300 | 0 | 3885.5 | 7978.5 | 94.07
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 24 | 176 | 0 | 0 | 0 | 15 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 39 | 325 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 290 | 0 | 5 | 0 | 8 | 0 | 310 | 0 | 5 | 0 | 193 | 0 | 0 | 45 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 300 | 300 | 370 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 11 | 25 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4023 | 732 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 130 | 0 | 176 | 0 | 0 | 0 | 0 | 5.5 | 195 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 80 | 180 | 0 | 250 | 0 | 3594.5 | 7617.5 | 94.07
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 24 | 181 | 0 | 0 | 0 | 12 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 39 | 277 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 297 | 0 | 5 | 0 | 8 | 0 | 290 | 0 | 5 | 0 | 181 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 290 | 296 | 368 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 11 | 25 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3893 | 733 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 130 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 198 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 250 | 0 | 3471.5 | 7364.5 | 94.07
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 24 | 183 | 0 | 0 | 0 | 12 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 37 | 247 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 8 | 0 | 290 | 0 | 5 | 0 | 182 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 280 | 276 | 313 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 11 | 20 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3786 | 639 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 200 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 250 | 0 | 3366.5 | 7152.5 | 94.06
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 24 | 181 | 0 | 0 | 0 | 12 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 40 | 249 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 8 | 0 | 290 | 0 | 5 | 0 | 181 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 240 | 276 | 311 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 11 | 20 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3728 | 639 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 198 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 250 | 0 | 3373.5 | 7101.5 | 94.06
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 26 | 181 | 0 | 0 | 0 | 12 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 40 | 282 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 55 | 0 | 315 | 0 | 20 | 0 | 182 | 0 | 0 | 50 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 265 | 260 | 365 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 11 | 20 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3968 | 639 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 199 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 130 | 220 | 0 | 250 | 0 | 3517.5 | 7485.5 | 94.06
07:00 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 26 | 181 | 0 | 0 | 1 | 14 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 37 | 330 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 2 | 315 | 1 | 25 | 0 | 158 | 0 | 310 | 0 | 24 | 10 | 183 | 0 | 0 | 50 | 0 | 0 | 15 | 0 | 40 | 0 | 0 | 280 | 250 | 368 | 5 | 30 | 0 | 2 | 163 | 13 | 0 | 42 | 20 | 0 | 0 | 212 | 10 | 0 | 0 | 0 | 0 | 0.83 | 0 | 4243.83 | 733 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.73 | 763 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | 130 | 0 | 130 | 0 | 140 | 0 | 0 | 0 | 0.07 | 5.5 | 211 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.02 | 0 | 150 | 6 | 130 | 220 | 0 | 250 | 0 | 3667.73 | 7911.56 | 94.06
08:00 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 26 | 182 | 0 | 0 | 5 | 17 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 5 | 360 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 13 | 350 | 7 | 51 | 0 | 185 | 0 | 365 | 0 | 32 | 20 | 211 | 0 | 0 | 50 | 0 | 0 | 15 | 0 | 42 | 0 | 0 | 300 | 260 | 368 | 5 | 30 | 0 | 2 | 163 | 13 | 0 | 42 | 25 | 0 | 0 | 212 | 45 | 24 | 8 | 0 | 0 | 8.13 | 0 | 4621.13 | 922 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 843 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 5.49 | 148 | 0 | 130 | 0 | 149 | 0 | 0 | 0 | 0.78 | 5.5 | 210 | 77 | 0 | 2 | 0 | 0 | 0 | 0.6 | 11 | 0.11 | 0 | 200 | 4 | 130 | 220 | 0 | 330 | 0 | 4140.48 | 8761.61 | 94.06
09:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 26 | 195 | 0 | 0 | 15 | 20 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 1 | 26 | 0 | 3 | 423 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 32 | 450 | 12 | 51 | 0 | 185 | 0 | 290 | 0 | 33 | 20 | 237 | 0 | 0 | 50 | 0 | 0 | 15 | 0 | 44 | 0 | 0 | 300 | 250 | 368 | 5 | 30 | 0 | 2 | 163 | 13 | 0 | 42 | 25 | 0 | 0 | 212 | 65 | 24 | 5 | 0 | 0 | 18.39 | 0 | 4816.39 | 923 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 970 | 0 | 477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 6.56 | 155 | 0 | 136 | 0 | 167 | 0 | 0 | 0 | 0.72 | 5.5 | 185 | 76 | 0 | 4 | 0 | 0 | 0 | 1.5 | 23 | 0.22 | 0 | 307 | 3 | 130 | 180 | 0 | 440 | 0 | 4571.5 | 9387.89 | 94.06
10:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 26 | 240 | 0 | 0 | 22 | 20 | 23 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 26 | 0 | 2 | 426 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 50 | 450 | 17 | 51 | 0 | 185 | 0 | 290 | 0 | 33 | 20 | 181 | 0 | 0 | 45 | 0 | 0 | 15 | 0 | 50 | 0 | 0 | 270 | 230 | 353 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 42 | 25 | 0 | 0 | 212 | 45 | 8 | 5 | 0 | 0 | 28.41 | 20 | 4745.41 | 922 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 871 | 0 | 512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 8.52 | 151 | 0 | 136 | 0 | 150 | 0 | 0 | 0 | 1.11 | 5.5 | 175 | 77 | 0 | 6 | 0 | 0 | 0 | 2.5 | 39 | 0.4 | 0 | 307 | 3 | 100 | 180 | 0 | 420 | 0 | 4429.03 | 9174.44 | 94.05
11:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 26 | 253 | 0 | 0 | 27 | 20 | 23 | 0 | 350 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 3 | 26 | 0 | 3 | 425 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 63 | 451 | 19 | 51 | 0 | 175 | 0 | 295 | 0 | 35 | 24 | 182 | 0 | 0 | 45 | 0 | 0 | 11 | 0 | 48 | 0 | 0 | 280 | 300 | 376 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 42 | 25 | 0 | 0 | 214 | 45 | 8 | 5 | 1 | 0 | 36.21 | 12 | 5065.21 | 923 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 859 | 0 | 486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 10.59 | 153 | 0 | 136 | 0 | 150 | 0 | 0 | 0 | 0.95 | 0 | 180 | 77 | 0 | 8 | 0 | 0 | 0 | 4.6 | 52 | 0.5 | 0 | 220 | 3 | 100 | 180 | 0 | 420 | 0 | 4339.64 | 9404.85 | 94.05
12:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 17 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 24 | 265 | 0 | 0 | 16 | 19 | 23 | 0 | 350 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 4 | 26 | 0 | 3 | 503 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 66 | 457 | 19 | 43 | 0 | 185 | 0 | 300 | 0 | 35 | 28 | 182 | 0 | 0 | 45 | 0 | 0 | 11 | 0 | 50 | 0 | 0 | 270 | 363 | 356 | 5 | 33 | 0 | 2 | 120 | 13 | 0 | 42 | 25 | 0 | 0 | 214 | 16 | 8 | 5 | 1 | 0 | 37.47 | 0 | 5192.47 | 923 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 949 | 0 | 484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 14.89 | 165 | 0 | 148 | 0 | 169 | 0 | 0 | 0 | 1.31 | 5.5 | 176 | 76 | 0 | 21 | 0 | 0 | 0 | 4.9 | 88 | 0.51 | 0 | 260 | 3 | 130 | 220 | 0 | 420 | 0 | 4724.11 | 9916.58 | 94.05
13:00 | 0 | 63 | 25 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 24 | 276 | 0 | 0 | 24 | 19 | 23 | 0 | 350 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 3 | 26 | 0 | 11 | 500 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 63 | 463 | 18 | 43 | 0 | 185 | 0 | 300 | 0 | 35 | 29 | 183 | 0 | 0 | 45 | 0 | 0 | 11 | 0 | 62 | 0 | 0 | 285 | 340 | 356 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 42 | 25 | 0 | 0 | 209 | 16 | 8 | 5 | 1 | 0 | 35.9 | 0 | 5294.9 | 921 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 961 | 0 | 512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 19.69 | 167 | 0 | 171 | 0 | 171 | 0 | 0 | 0 | 2.23 | 8.5 | 177 | 76 | 0 | 22 | 0 | 0 | 0 | 4.7 | 107 | 0.5 | 0 | 260 | 3 | 130 | 220 | 0 | 470 | 0 | 4870.62 | 10165.52 | 94.05
14:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 24 | 276 | 0 | 0 | 22 | 19 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 3 | 26 | 0 | 3 | 405 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 53 | 425 | 16 | 43 | 0 | 185 | 0 | 300 | 0 | 36 | 28 | 181 | 0 | 0 | 40 | 0 | 0 | 11 | 0 | 60 | 0 | 0 | 280 | 340 | 357 | 5 | 29 | 0 | 2 | 120 | 13 | 0 | 55 | 25 | 0 | 0 | 210 | 8 | 8 | 5 | 1 | 0 | 29.61 | 0 | 4993.61 | 922 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 962 | 0 | 513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 27.08 | 150 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 2 | 8.5 | 175 | 77 | 0 | 18 | 0 | 0 | 0 | 0 | 91 | 0.41 | 0 | 260 | 3 | 130 | 180 | 0 | 470 | 0 | 4679.99 | 9673.6 | 94.05
15:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 20 | 266 | 0 | 0 | 15 | 19 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 0 | 2 | 406 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 33 | 400 | 11 | 51 | 0 | 108 | 0 | 300 | 0 | 36 | 29 | 182 | 0 | 0 | 40 | 0 | 0 | 16 | 0 | 62 | 0 | 0 | 290 | 340 | 357 | 5 | 29 | 0 | 2 | 120 | 13 | 0 | 56 | 25 | 0 | 0 | 206 | 8 | 8 | 4 | 1 | 0 | 20.58 | 0 | 4836.58 | 923 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 865 | 0 | 514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 22.82 | 150 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 2.06 | 8.5 | 200 | 77 | 0 | 13 | 0 | 0 | 0 | 2.5 | 65 | 0.31 | 0 | 260 | 3 | 130 | 180 | 0 | 400 | 0 | 4457.19 | 9293.77 | 94.05
16:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 20 | 260 | 0 | 0 | 7 | 19.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 1 | 26 | 0 | 7 | 403 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 14 | 400 | 5 | 51 | 0 | 108 | 0 | 345 | 0 | 36 | 27 | 206 | 0 | 0 | 40 | 0 | 0 | 16 | 0 | 52 | 0 | 0 | 295 | 376 | 358 | 5 | 29 | 0 | 2 | 120 | 8 | 0 | 56 | 25 | 0 | 0 | 207 | 8 | 8 | 4 | 0 | 0 | 8.3 | 0 | 4861.8 | 923 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 818 | 0 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8.99 | 150 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0.82 | 8.5 | 200 | 77 | 0 | 6 | 0 | 0 | 0 | 1.2 | 30 | 0.14 | 0 | 170 | 0 | 130 | 220 | 0 | 350 | 0 | 4159.65 | 9021.45 | 94.05
17:00 | 0 | 42 | 17 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 17 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 20 | 244 | 0 | 0 | 1 | 19 | 22 | 0 | 300 | 1 | 5 | 0 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 0 | 26 | 0 | 11 | 503 | 0 | 0 | 1 | 0 | 0 | 227 | 0 | 0 | 0 | 1 | 501 | 1 | 51 | 1 | 108 | 0 | 305 | 0 | 26 | 28 | 182 | 0 | 13 | 40 | 0 | 5 | 16 | 0 | 56 | 5 | 0 | 310 | 340 | 358 | 5 | 29 | 0 | 2 | 120 | 13 | 0 | 56 | 25 | 0 | 0 | 206 | 55 | 22 | 4 | 0 | 0 | 1.02 | 0 | 5057.02 | 923 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 901 | 0 | 509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.19 | 150 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0.13 | 8.5 | 200 | 75 | 0 | 1 | 0 | 0 | 0 | 0 | 4 | 0.02 | 0 | 195 | 0 | 130 | 220 | 0 | 390 | 6 | 4230.84 | 9287.86 | 94.04
18:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 14 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 17 | 22 | 0 | 330 | 0 | 0 | 0 | 17 | 20 | 230 | 0 | 0 | 0 | 19 | 22 | 0 | 300 | 17 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 14 | 575 | 0 | 0 | 18 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 606 | 0 | 51 | 25 | 189 | 0 | 300 | 0 | 30 | 29 | 182 | 0 | 25 | 40 | 12 | 28 | 17 | 0 | 60 | 8 | 0 | 270 | 340 | 358 | 5 | 29 | 0 | 2 | 120 | 13 | 0 | 56 | 25 | 0 | 0 | 209 | 60 | 55 | 4 | 0 | 0 | 0 | 0 | 5468 | 923 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1157 | 0 | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 206 | 0 | 187 | 0 | 0 | 0 | 0 | 8.5 | 200 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 130 | 220 | 0 | 400 | 17 | 4912.5 | 10380.5 | 94.04
19:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 22 | 223 | 0 | 0 | 0 | 19 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 25 | 575 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 540 | 0 | 51 | 0 | 108 | 0 | 320 | 0 | 30 | 29 | 195 | 0 | 47 | 40 | 0 | 0 | 17 | 0 | 64 | 0 | 0 | 290 | 340 | 362 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 56 | 25 | 0 | 0 | 211 | 75 | 75 | 5 | 0 | 0 | 0 | 0 | 5287 | 922 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1001 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 205 | 0 | 188 | 0 | 0 | 0 | 0 | 8.5 | 200 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 5 | 130 | 220 | 0 | 550 | 0 | 4979.5 | 10266.5 | 94.04
19:30 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 22 | 217 | 0 | 0 | 0 | 19.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 20 | 577 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 135 | 0 | 365 | 0 | 30 | 29 | 216 | 0 | 17 | 40 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 310 | 340 | 363 | 5 | 30 | 0 | 2 | 163 | 13 | 0 | 56 | 25 | 0 | 0 | 211 | 75 | 75 | 5 | 0 | 0 | 0 | 0 | 5338.5 | 922 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1013 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 202 | 0 | 195 | 0 | 0 | 0 | 0 | 8.5 | 180 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 130 | 220 | 0 | 550 | 0 | 4978.5 | 10317
20:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 22 | 173 | 0 | 0 | 0 | 19.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 25 | 576 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 189 | 0 | 320 | 0 | 33 | 29 | 189 | 0 | 17 | 40 | 0 | 0 | 17 | 0 | 56 | 0 | 0 | 310 | 330 | 363 | 5 | 30 | 0 | 2 | 163 | 13 | 0 | 56 | 25 | 0 | 0 | 210 | 75 | 55 | 8 | 0 | 0 | 0 | 0 | 5257.5 | 922 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1013 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 201 | 0 | 193 | 0 | 0 | 0 | 0 | 8.5 | 180 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 130 | 220 | 0 | 550 | 0 | 4971.5 | 10229 | 94.04
21:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 22 | 170 | 0 | 0 | 0 | 20 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 29 | 576 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 184 | 0 | 290 | 0 | 33 | 29 | 181 | 0 | 0 | 40 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 290 | 300 | 363 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 56 | 25 | 0 | 0 | 210 | 55 | 24 | 10 | 0 | 0 | 0 | 0 | 5031 | 922 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1009 | 0 | 759.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 201 | 0 | 191 | 0 | 0 | 0 | 0 | 8.5 | 180 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 130 | 220 | 0 | 520 | 0 | 4931.53 | 9962.53 | 94.03
22:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 22 | 170 | 0 | 0 | 0 | 19 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 36 | 576 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 430 | 0 | 51 | 0 | 184 | 0 | 290 | 0 | 33 | 29 | 181 | 0 | 0 | 40 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 275 | 295 | 363 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 56 | 25 | 0 | 0 | 209 | 35 | 16 | 10 | 0 | 0 | 0 | 0 | 4887 | 921 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 908 | 0 | 708.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 201 | 0 | 191 | 0 | 0 | 0 | 0 | 8.5 | 180 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 130 | 220 | 0 | 450 | 0 | 4688.06 | 9575.06 | 94.03
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 22 | 170 | 0 | 0 | 0 | 16 | 22 | 0 | 250 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 578 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 350 | 0 | 51 | 0 | 185 | 0 | 290 | 0 | 33 | 29 | 181 | 0 | 0 | 40 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 265 | 260 | 363 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 56 | 25 | 0 | 0 | 208 | 16 | 0 | 13 | 0 | 0 | 0 | 0 | 4658 | 909 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 806 | 0 | 648.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 188 | 0 | 190 | 0 | 0 | 0 | 0 | 8.5 | 180 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 130 | 220 | 0 | 440 | 0 | 4464.56 | 9122.56 | 94.03
Total KWH | 562 | 755021 | 245280 | 0 | 0 | 0 | 0 | 0 | 6940800 | 0 | 0 | 20520 | 220680 | 0 | 0 | 242400 | 0 | 0 | 0 | 33120 | 522720 | 0 | 7618000 | 0 | 0 | 0 | 46880 | 585500 | 5025711 | 0 | 0 | 158482 | 411600 | 505440 | 0 | 7233636 | 21327 | 15055 | 0 | 0 | 557280 | 4632 | 0 | 22933 | 0 | 0 | 19461 | 762840 | 0 | 509280 | 10436363.6 | 0 | 0 | 20160 | 0 | 0 | 5242709 | 0 | 0 | 0 | 393091 | 9883635 | 125955 | 922400 | 38472 | 2977455 | 0 | 7689700 | 0 | 622440 | 466560 | 4563000 | 0 | 117120 | 1047570 | 17280 | 50400 | 373450 | 0 | 1222080 | 9072 | 0 | 6932000 | 7299300 | 8933000 | 202896 | 710000 | 0 | 55536 | 3439964 | 349344 | 0 | 920640 | 577440 | 0 | 0 | 5307630 | 654000 | 369600 | 81600 | 4500 | 0 | 226560 | 42960 | 114805042.6 | 20874181 | 6608736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 435600 | 21432730 | 0 | 12637579 | 0 | 0 | 0 | 0 | 0 | 0 | 28912 | 0 | 0 | 0 | 47022 | 0 | 126748 | 3920455 | 0 | 4059755 | 0 | 4128555 | 0 | 0 | 0 | 12060 | 153234 | 4616000 | 1766399 | 0 | 100938 | 0 | 0 | 0 | 25047.96 | 509040 | 3140 | 0 | 5237000 | 78375 | 2724000 | 5193330 | 0 | 9786181.82 | 27600 | 104532618.78 | 219337661.38

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 31-12-2024
Power Supply Scenario
Day Peak Generation |  |  | 9916.58 | MW | 12:00 Hr. | Energy Generated |  |  | 219337.6614 |  | MWHr
Day Peak Demand |  |  | 9916.58 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MWHr
Evening Peak Generation |  |  | 10380.5 | MW | 18:00 Hr. | Energy Demand |  |  | 219337.6614 |  | MWHr
Evening Peak Demand |  |  | 10380.5 | MW | 18:00 Hr.
Minimum Generation of the Day |  |  | 7101.5 | MW | 05:00 Hr.
Minimum Demand of the Day |  |  | 7101.5 | MW | 05:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 28843.407 | 0 | 1564.463 | 0 | 0 | 158.482 | 0 | 0 | 30566.352 | Gas | 114933.761 | Gas | 398352684.22
Chattogram Zone |  |  | 5751.989 | 20319.9986 | 84.107 | 0 | 762.84 | 538.507 | 0 | 557.28 | 28014.7216 | Coal | 63158.3094 | Coal | 464806790.9542
Cumilla Zone |  |  | 18662.575 | 0 | 232.344 | 0 | 0 | 0 | 1222.08 | 0 | 20116.999 | HFO | 3003.986 | HFO | 58230792.45
Mymensingh Zone |  |  | 81.6 | 0 | 1066.56 | 0 | 0 | 231.06 | 0 | 0 | 1379.22 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 34727.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34727.75 | Hydro | 762.84 | Hydro | 76284
Khulna Zone |  |  | 6608.736 | 21432.73 | 0 | 0 | 0 | 435.6 | 20874.181 | 0 | 49351.247 | Solar | 2187.645 | Solar | 34344023.646
Barishal Zone |  |  | 7995.705 | 15023.1818 | 27.6 | 0 | 0 | 3.14 | 0 | 0 | 23049.6268 | Import | 34733.84 | Import | 167899949.44
Rajshahi Zone |  |  | 12261.999 | 0 | 28.912 | 0 | 0 | 185.83 | 12637.579 | 0 | 25114.32 | Wind | 557.28 | Wind | 8024832
Rangpur Zone |  |  | 0 | 6382.399 | 0 | 0 | 0 | 635.026 | 0 | 0 | 7017.425
Total |  |  | 114933.761 | 63158.3094 | 3003.986 | 0 | 762.84 | 2187.645 | 34733.84 | 557.28 | 219337.6614
Cost of the consumed fuel (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 398352684.22 |  | Hydro | 76284
|  |  | Coal | 464806790.9542 |  | Solar | 34344023.646
|  |  | HFO | 58230792.45 |  | Import | 167899949.44
|  |  | HSD | 0 |  | Wind | 8024832
|  |  |  | Total: | 1131735356.7102 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Rangpur 20 MW GTPP |  |  | 20 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Baghabari 100 MW GTPP |  |  | 100 | 2 | Ashuganj 55 MW PP (Precision) |  |  | 55
| 3 | Barapukuria TPP Unit-2 |  |  | 85 | 3 | Sirajgonj 225MW CCPP Unit-1 GT |  |  | 150
| 4 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 5 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 619 |  |  |  | Total | 240.09
|  |  | Total Unavailable Capacity |  |  |  | 859.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3985
|  |  | Chattogram |  | 0 |  | 1002
|  |  | Cumilla |  | 0 |  | 869
|  |  | Mymensingh |  | 0 |  | 869
|  |  | Sylhet |  | 0 |  | 360
|  |  | Khulna |  | 0 |  | 1174
|  |  | Barishal |  | 0 |  | 291
|  |  | Rajshahi |  | 0 |  | 941
|  |  | Rangpur |  | 0 |  | 691
|  |  | Total |  | 0 |  | 10182
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:00 | 16:30 | BSRM-Cumilla(N) 230 kV Ckt-2 Scheduled S/D from BSRM 230/33kV end Due to S/D taken by
Feni S/S for maintenance purpose
08:02 | 16:07 | Candpur- Kachua 132kV Ckt-1 Scheduled S/D from Chandpur 132/33kV end Due to Dead line
Check at annual maintenance work. and from Kachua 132/33kV end Due to Annual mainteance
08:11 | 16:13 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Annual
maintenance work. and from Bhandaria 132/33kV end Due to Annual maintenance
08:15 | 16:57 | Faridpur 132/33kV S/S 132 KV Rajbari ckt-1 Scheduled S/D
08:21 | 18:07 | Barishal 230/132kV S/S Gopalgonj CKT-1 Scheduled S/D
08:28 | 16:58 | Rajbari 132/33kV S/S Faridpur -1 Scheduled S/D Due to Annual Maintenance
08:39 | 15:00 | Baroirhat-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to annual
maintenance of barayarhat s/s. and from Baroirhat 132/33kVend.
08:41 | 18:08 | Gopalganj 400/132kV S/S 230kV Barisal CKT-01 Scheduled S/D
08:47 | 16:06 | Bakulia-MSML 132 kV Ckt-2 Scheduled S/D from Bakulia 132/33kV end Due to Annual
Maintenance
08:48 | 16:22 | Sylhet (South) S/S Trafo-2 LT Scheduled S/D Due to Annual Maintenance works
08:49 | 16:21 | Sylhet (South) S/S Trafo-2 HT Scheduled S/D Due to Annual Maitnenance works
08:51 | 16:06 | Kallyanpur 132/33kV S/S GT-1 (132kV) HT Scheduled S/D Due to Annual Maintenance
08:51 | 16:08 | Kallyanpur 132/33kV S/S GT-1 (132kV) LT Scheduled S/D Due to Annual Maintenance
08:52 | 16:38 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end. and
from Shahjibazar 132/33kV end Due to Annual Maintenance
08:53 | 17:38 | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end Due to
Maintenance work and from Bogura 400/230kVend.
08:57 | 16:05 | Rangpur-Saidpur 132kV Ckt-1 Scheduled S/D from Saidpur 132/33kV end Due to For Annual
maintenance and from Rangpur 132/33kV end Due to Annual Maintenance
09:01 | 17:14 | Niamatpur 132/33kV S/S 132 kV Rahanpur Ckt-2 Scheduled S/D Due to Annual maintenance
09:08 | 17:19 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 Forced S/D from Mithapukur 132/33kV
end Due to According to order of ALDC Bogura
09:08 | 17:20 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-2 Forced S/D from Mithapukur 132/33kV
end Due to According to order of ALDC Bogura
09:09 | 17:16 | Mahasthangar-Palashbari 132kV Ckt-2 Project Work S/D from Mahasthangarh 132/33kV end Due
to Palashbari Grid G2G Project Work and from Palashbari 132/33kVend.
09:27 |  | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-2 Scheduled S/D Due to Annual
Maintenance
09:29 | 15:27 | Shikalbaha 230/132kV S/S Hathazari-02 Scheduled S/D
09:32 | 12:07 | Bogura 132/33kV S/S Transformer-4 LT Forced S/D Due to T-4 SPRING CHARGE NOT WORKING
09:32 | 12:07 | Bogura 132/33kV S/S Transformer-4 HT Forced S/D Due to T-4 SPRING CHARGE NOT WORKING
09:35 | 17:25 | Beanibazar 132/33kV S/S 132 KV BUS-1 Scheduled S/D Due to Maintenance work
09:47 |  | Kishoreganj-Mymensingh 132kV Ckt-2 Project Work S/D from Kishoreganj 132/33kV end.
09:50 | 13:12 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Bay
upgrading work
10:12 | 17:56 | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual Maintenance
10:13 | 18:14 | Aminbazar 400/230/132kV S/S 132 kv Bus 01 Scheduled S/D Due to Annual Maintenance
10:43 |  | Khulshi-MSML 132kV Ckt-2 Scheduled S/D from Khulshi 132/33kV end Due to Maintenance work
10:56 | 14:54 | Ishurdi 132/33kV S/S 132 kV Baghabari Line Project Work S/D Due to project work
10:56 | 15:09 | Jamalpur 132/33kV S/S Bus-B Scheduled S/D Due to Bus-cpupler bay(B-bus) annual
maintenance work.
11:08 | 17:28 | Madunaghat-TKCL 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to CT
maintenance at Tk end
12:00 |  | Day peak Generation is 9913 MW
| 12:23 | Sirajganj-Ullahpara 132KV Ckt-2 is restored.
| 12:23 | Sirajganj-Ullahpara 132KV Ckt-1 is restored.
13:13 | 14:02 | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Bay
upgrading work
| 15:52 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT is restored.
| 15:53 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT is restored.
| 16:52 | Magura-Narail 132kV Ckt-1 is restored.
| 17:37 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-2 is restored.
17:39 |  | Amtoli-Gopalganj Ckt-2 is energized for the first time.
18:00 |  | Evening Peak Gen. 10380 MW
05:00 |  | Minimum Generation = 6,952MW
07:36 |  | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to Re-arrangement
of 230kV Haripur-Bhulta Circuit-01
07:37 |  | Bhulta-Haripur 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end Due to
Re-arrangeHaripur-Bhulta Circuit-01.
07:47 |  | Hasnabad 230/132kV S/S Bus-2 Scheduled S/D Due to Annual Maintenance.
07:50 |  | Gopalganj 400/132kV S/S 230kV Barisal CKT-02 Scheduled S/D Due to Annual Maintenance
07:50 |  | Barishal 230/132kV S/S Gopalgonj CKT-2 Scheduled S/D Due to Annual maintenance
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 31-12-2024
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 234.58 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Default availability set by nldc
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | Default availability set by nldc
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 294 | 6940800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 7618000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | Default availability set by nldc
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Default availability set by nldc
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 230 | 5025711 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 562 | Default availability set by nldc
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 14 | 20520 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149 | 32 | 242400 | Default availability set by nldc
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Default availability set by nldc
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 46880 | Default availability set by nldc
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 411600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 505440 | Default availability set by nldc
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 522720 | Default availability set by nldc
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 20 | 585500 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 245280 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Default availability set by nldc
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | Default availability set by nldc
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 0 | Default availability set by nldc
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 755021 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 33120 | Default availability set by nldc
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 158482 | Default availability set by nldc
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 17 | 220680 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 7233636 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Default availability set by nldc
Dhaka Area Total |  |  |  |  | 6940.42 | 1421 | 30566352
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Default availability set by nldc
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125955 | Default availability set by nldc
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 20160 | Default availability set by nldc
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 26 | 762840 | Default availability set by nldc
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 5242709 | Default availability set by nldc
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Default availability set by nldc
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 4632 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Default availability set by nldc
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 33 | 14 | 509280 | Default availability set by nldc
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 19461 | Default availability set by nldc
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 15055 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 22933 | Default availability set by nldc
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Default availability set by nldc
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Default availability set by nldc
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 21327 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1320 | 606 | 9883635 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 66 | 22 | 557280 | Default availability set by nldc
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 575 | 10436363.6 | U1 S/D 09/Oct/24 (Maintenance Work)
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 393091 | Default availability set by nldc
Chattogram Area Total |  |  |  |  | 5064.22 | 1505 | 28014721.6
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 182 | 4563000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 356.15 | 300 | 7689700 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | -
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.96 | 45 | 30 | 622440 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 466560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 189 | 2977455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 922400 | Default availability set by nldc
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 25 | 38472 | Default availability set by nldc
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 1047570 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 12 | 17280 | Default availability set by nldc
| Import (Tripura) |  | Import | 0 | 160 | 60 | 1222080 | Default availability set by nldc
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 9072 | Default availability set by nldc
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 373450 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Default availability set by nldc
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 50400 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 25 | 117120 | -
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Cumilla Area Total |  |  |  |  | 2881.85 | 996 | 20116999
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 4 | 81600 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 3 | 0 | 4500 | Default availability set by nldc
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 55 | 369600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 60 | 654000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 226560 | Default availability set by nldc
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 42960 | Ready to Dispatch as per NLDC Demand.
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 150 | 0 | 0 | Default availability set by nldc
Mymensingh Area Total |  |  |  |  | 750 | 119 | 1379220
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 29 | 710000 | Default availability set by nldc
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Default availability set by nldc
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3439964 | Default availability set by nldc
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Default availability set by nldc
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 202896 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 55536 | Default availability set by nldc
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 577440 | Default availability set by nldc
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 56 | 920640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Default availability set by nldc
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 209 | 5307630 | Default availability set by nldc
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Default availability set by nldc
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 349344 | Default availability set by nldc
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 6932000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 358 | 8933000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 340 | 7299300 | FGMO
Sylhet Area Total |  |  |  |  | 2366 | 1427 | 34727750
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Default availability set by nldc
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 923 | 20874181 | Default availability set by nldc
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | Default availability set by nldc
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Default availability set by nldc
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 6608736 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 435600 | Default availability set by nldc
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | Default availability set by nldc
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234 | 1157 | 21432730 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | Default availability set by nldc
Khulna Area Total |  |  |  |  | 3739 | 2330 | 49351247
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Default availability set by nldc
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 0 | 78375 | Default availability set by nldc
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2724000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 400 | 9786181.82 | -
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5193330 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 27600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5237000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3140 | Default availability set by nldc
Barishal Area Total |  |  |  |  | 2266 | 1074 | 23049626.82
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Default availability set by nldc
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Default availability set by nldc
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Default availability set by nldc
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 168 | 3920455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 206 | 4059755 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 187 | 4128555 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 414 | 0 | 0 | Default availability set by nldc
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Default availability set by nldc
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 8.5 | 153234 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 33 | 28912 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 12060 | Default availability set by nldc
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 631 | 12637579 | Default availability set by nldc
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 126748 | Default availability set by nldc
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 47022 | Default availability set by nldc
Rajshahi Area Total |  |  |  |  | 3411.72 | 1233.5 | 25114320
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 75 | 1766399 | Default availability set by nldc
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4616000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Default availability set by nldc
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Default availability set by nldc
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25047.96 | Default availability set by nldc
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | Default availability set by nldc
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 100938 | Default availability set by nldc
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 509040 | Default availability set by nldc
Rangpur Area Total |  |  |  |  | 950 | 275 | 7017424.96
Eastern Grid Total |  |  |  |  | 18002.49 | 5468 | 114805042.6
Western Grid Total |  |  |  |  | 10366.72 | 4912.5 | 104532618.78
National Grid Total |  |  |  |  | 28369.21 | 10380.5 | 219337661.38
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 31-12-2024
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7084.77 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3097.3 | MW
i) Dhaka area |  |  | 3984.77 |  | MW | i) Khulna area |  |  |  | 1174 | MW
ii) Chattogram area |  |  | 1002 |  | MW | ii) Barishal area |  |  |  | 291.1 | MW
iii) Cumilla area |  |  | 869 |  | MW | iii) Rajshahi area |  |  |  | 941.2 | MW
iv) Mymensingh area |  |  | 869 |  | MW | iv) Rangpur area |  |  |  | 691 | MW
v) Sylhet area |  |  | 360 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10182.07 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 92 | 18:30 | 133 | Rahanpur | 0 | 00:00
2 | AKSML | 145 | 10:00 | 68 | Jashore | 99 | 13:00 | 134 | Rahim | 45 | 14:00
3 | Aftabnagar | 24 | 12:00 | 69 | Jhenaidah | 90 | 18:00 | 135 | Rajbari | 54 | 18:00
4 | Agargaon | 73 | 14:00 | 70 | Joydebpur | 118 | 18:00 | 136 | Rajendrapur | 100 | 18:30
5 | Agrabad | 58 | 12:00 | 71 | Joypurhat | 36 | 13:00 | 137 | Rajshahi | 91 | 13:00
6 | Amnura | 44 | 13:00 | 72 | Juldah | 8 | 00:00 | 138 | Rajshahi-230 | 40 | 13:00
7 | Ashuganj | 62 | 13:00 | 73 | KSRM | 36 | 19:00 | 139 | Ramganj | 76 | 18:00
8 | BSRM | 139 | 02:00 | 74 | Kabirpur | 204 | 18:00 | 140 | Rampur | 24 | 13:00
9 | Bagerhat | 68 | 18:00 | 75 | Kachua | 48 | 19:00 | 141 | Rangamati | 12 | 18:00
10 | Bakulia | 66 | 13:00 | 76 | Kallyanpur | 62 | 12:00 | 142 | Rangpur | 107 | 18:30
11 | Banani | 38 | 13:00 | 77 | Kalurghat | 28 | 11:00 | 143 | Ruppur | 3.4 | 10:00
12 | Bangabhaban | 7 | 11:00 | 78 | Kamrangirchar | 52.1 | 13:00 | 144 | SSM | 3 | 02:00
13 | Barapukuria | 43 | 13:00 | 79 | Kaptai | N/A | N/A | 145 | Saidpur | 87 | 09:00
14 | Barguna | 14 | 20:00 | 80 | Kazla | 83 | 13:00 | 146 | Satkhira | 84 | 08:00
15 | Barishal | 72 | 20:00 | 81 | Keranigonj | 56 | 13:00 | 147 | Satmasjid | 85 | 13:00
16 | Barishal-230 | 66 | 13:00 | 82 | Khagrachori | 24 | 18:00 | 148 | Savar | 180 | 15:00
17 | Baroaulia | 54 | 12:00 | 83 | Khulna | 69 | 13:00 | 149 | SevenRings | 14.98 | 09:00
18 | Baroirhat | 45 | 18:00 | 84 | Khulshi | 148 | 13:00 | 150 | ShahCement | 34 | 17:00
19 | Bashundhara | 126 | 13:00 | 85 | Kishoreganj | 112 | 20:00 | 151 | Shahjadpur | 55 | 19:00
20 | BashundharaCement | 12 | 01:00 | 86 | Kodda | 263 | 18:00 | 152 | Shahjibazar | 72 | 20:00
21 | Beanibazar | 42 | 18:00 | 87 | Kulaura | 28 | 18:00 | 153 | Shahmirpur | 29 | 17:00
22 | Benapole | 42 | 08:00 | 88 | Kurigram | 48 | 18:00 | 154 | Shariatpur | 52 | 20:00
23 | Bhaluka | 114 | 18:00 | 89 | Kushtia | 100 | 18:00 | 155 | Sherpur | 108 | 18:00
24 | Bhandaria | 33.5 | 22:00 | 90 | Lalbag | 63 | 15:00 | 156 | Shikalbaha | 20 | 11:00
25 | Bhangura | 21 | 18:00 | 91 | Lalmonirhat | 43 | 18:00 | 157 | Shitalakhya | 64 | 13:00
26 | Bheramara(GK) | 39 | 18:00 | 92 | MI_Cement | 16.8 | 16:00 | 158 | Sholosohor | 30 | 11:00
27 | Bhulta | 250 | 11:00 | 93 | Madanganj | 29 | 19:00 | 159 | Shyampur | 150 | 13:00
28 | Bog-Sherpur | 102 | 09:00 | 94 | Madaripur | 67 | 20:00 | 160 | Siddhirganj | 101 | 13:00
29 | Bogura | 112 | 18:30 | 95 | Madartek | 58.05 | 13:00 | 161 | Sirajganj | 74 | 19:00
30 | Borhanuddin | 61 | 21:00 | 96 | Madunaghat | 33 | 13:00 | 162 | Sonargaon | 69 | 07:00
31 | Brahmanbaria | 102 | 19:00 | 97 | Magura | 44 | 18:00 | 163 | Sreemongol | 42 | 18:00
32 | Cantonment | 74 | 18:00 | 98 | Mahasthangarh | 48 | 18:00 | 164 | Sreepur | 72 | 18:00
33 | Chandpur | 43 | 18:30 | 99 | Manikganj | 86 | 20:00 | 165 | Srinagar | 30 | 20:00
34 | Chandraghona | 24 | 18:00 | 100 | Maniknagar | 44 | 13:00 | 166 | Sunamganj | 37 | 19:30
35 | Chapai | 49 | 13:00 | 101 | Matarbari | 31 | 19:00 | 167 | Sylhet | 33 | 13:00
36 | Charsaidpur | 42 | 01:00 | 102 | Matuail | 44 | 09:00 | 168 | Sylhet-132 | 71 | 18:00
37 | Chauddagram | 37 | 13:00 | 103 | Millgate | 67 | 12:00 | 169 | TK | 20.5 | 20:00
38 | Chhatak | 19 | 19:00 | 104 | Mirpur | 98 | 15:00 | 170 | Tangail | 142 | 18:00
39 | Chowmuhani | 137 | 18:00 | 105 | Mirsorai | 7 | 12:00 | 171 | Thakurgaon | 73 | 18:30
40 | Chuadanga | 71 | 18:00 | 106 | Mirzapur | 34 | 13:00 | 172 | Tongi | 105 | 11:00
41 | Coxsbazar | 94 | 18:00 | 107 | Mithapukur | 38 | 08:00 | 173 | Ullahpara | 24 | 07:00
42 | Cumilla(N) | 102 | 19:30 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 36 | 13:00
43 | Cumilla(S) | 119 | 19:00 | 109 | Mogbazar | 70.9 | 15:00 | 175 | Uttara | 50 | 13:00
44 | Daudkandi | 108 | 18:30 | 110 | Mongla | 34 | 12:00 | 176 | UttaraNew | 31 | 13:00
45 | Dhaka | 30 | 13:00 | 111 | Motijheel | 26 | 13:00 | 177 | Zigatola | 62 | 18:00
46 | Dhamrai | 118 | 09:00 | 112 | Munshiganj | 70 | 13:00
47 | Dhanmondi | 84 | 13:00 | 113 | Mymensingh | 176 | 18:00
48 | Dohazari | 67 | 12:00 | 114 | Naogaon | 83 | 13:00
49 | Faridpur | 106 | 20:00 | 115 | Narail | 39 | 18:00
50 | Fatullah | 76 | 17:00 | 116 | Narinda | 51 | 13:00
51 | Fenchuganj | 24 | 18:00 | 117 | Narshingdi | 151 | 19:30
52 | Feni | 72 | 18:00 | 118 | Natore | 94 | 18:00
53 | GPH | 26 | 11:00 | 119 | Nawabganj | 28 | 21:00
54 | Ghatail | 0 | 00:00 | 120 | Netrakona | 103 | 18:00
55 | Ghorashal | 7 | 00:00 | 121 | New | 63.5 | 12:00
56 | Ghorashal-230 | 46 | 18:00 | 122 | Niamatpur | 48 | 08:00
57 | Goalpara | 22 | 13:00 | 123 | Noapara | 34 | 18:30
58 | Gollamari | 48 | 13:00 | 124 | PHP | 3 | 17:00
59 | Gopalganj | 73.4 | 18:30 | 125 | Pabna | 77 | 18:00
60 | Gulshan | 64 | 13:00 | 126 | Palashbari | 77 | 18:30
61 | Halishahar | 38 | 10:00 | 127 | Panchagarh | 45 | 18:30
62 | HaripurSBU | 169 | 10:00 | 128 | Patuakhali | 50.1 | 19:00
63 | Hasnabad | 65 | 11:00 | 129 | Payra | 26 | 12:00
64 | Hathazari | 56 | 13:00 | 130 | Postogola | 39 | 13:00
65 | Ishurdi | 54 | 18:30 | 131 | Purbachal | 14 | 13:00
66 | Jaldhaka | 58 | 18:00 | 132 | Purbasadipur | 105 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 31-12-2024
Hour | Generation | Load-Shed |  | Demand
0:00 | 8552.5 | 0 |  | 8552.5
1:00 | 7978.5 | 0 |  | 7978.5
2:00 | 7617.5 | 0 |  | 7617.5
3:00 | 7364.5 | 0 |  | 7364.5
4:00 | 7152.5 | 0 |  | 7152.5
5:00 | 7101.5 | 0 |  | 7101.5
6:00 | 7485.5 | 0 |  | 7485.5
7:00 | 7911.56 | 0 |  | 7911.56
8:00 | 8761.61 | 0 |  | 8761.61
9:00 | 9387.89 | 0 |  | 9387.89
10:00 | 9174.44 | 0 |  | 9174.44
11:00 | 9404.85 | 0 |  | 9404.85
12:00 | 9916.58 | 0 |  | 9916.58
13:00 | 10165.52 | 0 |  | 10165.52
14:00 | 9673.6 | 0 |  | 9673.6
15:00 | 9293.77 | 0 |  | 9293.77
16:00 | 9021.45 | 0 |  | 9021.45
17:00 | 9287.86 | 0 |  | 9287.86
18:00 | 10380.5 | 0 |  | 10380.5
19:00 | 10266.5 | 0 |  | 10266.5
19:30 | 10317 | 0 |  | 10317
20:00 | 10229 | 0 |  | 10229
21:00 | 9962.53 | 0 |  | 9962.53
22:00 | 9575.06 | 0 |  | 9575.06
23:00 | 9122.56 | 0 |  | 9122.56
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2024-12-31 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
Aminbazar | 406 | 05:00 | 387 | 12:00 | Kaliakoir | 378 | 05:00 | 362 | 12:00
Ashuganj | 408 | 5:00 | 395 | 12:00 | Madunaghat | 405 | 03:00 | 394 | 13:00
Bhulta | 399 | 04:00 | 384 | 12:00 | Meghnaghat | 398 | 05:00 | 385 | 12:00
Bibiana | 394 | 04:00 | 386 | 17:00 | Payra | 416 | 05:00 | 409 | 09:00
BIPTC | 409 | 05:00 | 389 | 11:00 | Rahanpur | 416 | 05:00 | 401 | 08:00
Bogura | 410 | 04:00 | 395 | 18:30 | Rampal | 410 | 05:00 | 395 | 13:00
Gopalganj | 411 | 05:00 | 396 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Agargaon | 234 | 04:00 | 223 | 12:00 | Haripur | 237 | 04:00 | 229 | 11:00
AKSML | 233 | 06:00 | 224 | 21:00 | Hasnabad | 235 | 05:00 | 225 | 12:00
Aminbazar | 233 | 01:00 | 223 | 12:00 | Hathazari | 232 | 02:00 | 226 | 13:00
Ashuganj | 237 | 06:00 | 231 | 12:00 | Ishurdi | 244 | 04:00 | 232 | 13:00
Ashuganj-400 | 236 | 23:00 | 226 | 12:00 | Jhenaidah | 241 | 04:00 | 227 | 13:00
Baghabari | 241 | 03:00 | 233 | 12:00 | Kaliakoir | 236 | 05:00 | 223 | 13:00
Barapukuria | 226 | 01:00 | 217 | 09:00 | Keranigonj | 234 | 04:00 | 222 | 13:00
Barapukuria-230 | 228 | 6:00 | 218 | 12:00 | Khulna(S) | 239 | 05:00 | 229 | 13:00
Barishal | 244 | 05:00 | 236 | 12:00 | Madunaghat | 232 | 06:00 | 225 | 17:00
Bheramara | 242 | 04:00 | 229 | 13:00 | Madunaghat-400 | 232 | 04:00 | 225 | 13:00
Bhulta | 237 | 05:00 | 227 | 12:00 | Maniknagar | 235 | 03:00 | 225 | 13:00
Bibiana | 229 | 04:00 | 222 | 12:00 | Meghnaghat | 242 | 00:00 | 233 | 13:00
BIPTC | 244 | 04:00 | 230 | 13:00 | Meghnaghat-400 | 238 | 05:00 | 229 | 12:00
Bogura | 238 | 04:00 | 229 | 09:00 | Mirsorai | 231 | 03:00 | 226 | 13:00
Bogura-400 | 238 | 04:00 | 229 | 08:00 | Rajshahi | 242 | 04:00 | 230 | 13:00
Borhanuddin | 247 | 01:00 | 243 | 12:00 | Rampal | 237 | 03:00 | 226 | 13:00
BSRM | 233 | 04:00 | 226 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Cumilla(N) | 234 | 03:00 | 225 | 12:00 | Rampura | 237 | 05:00 | 226 | 12:00
Faridpur | 244 | 05:00 | 237 | 18:30 | Shikalbaha | 235 | 04:00 | 222 | 13:00
Fenchuganj | 232 | 01:00 | 227 | 13:00 | Shyampur | 235 | 03:00 | 225 | 12:00
Ghorashal | 230 | 00:00 | 230 | 00:00 | Siddhirganj | 237 | 04:00 | 229 | 16:00
Ghorashal-230 | 235 | 04:00 | 224 | 13:00 | Sirajgonj | 247 | 04:00 | 240 | 08:00
Gopalganj | 243 | 05:00 | 234 | 12:00 | Sreepur | 237 | 01:00 | 232 | 12:00
GPH | 232 | 04:00 | 225 | 12:00 | Tongi | 233 | 04:00 | 225 | 11:00
132 KV | KV |  | KV |  | 132 KV | KV |  | KV
Aftabnagar | 134 | 03:00 | 126 | 13:00 | Kushtia | 140 | 05:00 | 134 | 13:00
Agargaon | 136 | 04:00 | 129 | 12:00 | Lalbag | 134 | 03:00 | 127 | 13:00
Agrabad | 134 | 02:00 | 128 | 13:00 | Lalmonirhat | 128 | 21:00 | 121 | 08:00
AKS | 131 | 04:00 | 126 | 12:00 | Madanganj | 132 | 03:00 | 125 | 13:00
Aminbazar | 135 | 23:00 | 127 | 11:00 | Madaripur | 135 | 03:00 | 130 | 13:00
Amnura | 138 | 00:00 | 133 | 13:00 | Madartek | 133 | 03:00 | 126 | 13:00
Ashuganj | 140 | 05:00 | 137 | 13:00 | Madunaghat | 134 | 05:00 | 129 | 13:00
Bagerhat | 137 | 05:00 | 126 | 13:00 | Magura | 141 | 05:00 | 131 | 13:00
Bakulia | 133 | 01:00 | 129 | 11:00 | Mahasthangarh | 137 | 05:00 | 129 | 08:00
Banani | 134 | 04:00 | 126 | 13:00 | Manikganj | 132 | 03:00 | 125 | 12:00
Bangabhaban | 134 | 02:00 | 127 | 13:00 | Maniknagar | 135 | 04:00 | 128 | 12:00
Barapukuria | 137 | 01:00 | 128 | 09:00 | Matarbari | 129 | 05:00 | 120 | 18:30
Barguna | 135 | 05:00 | 131 | 13:00 | Matuail | 133 | 03:00 | 128 | 12:00
Barishal | 135 | 03:00 | 131 | 12:00 | Millgate | 134 | 02:00 | 125 | 12:00
Barishal-230 | 135 | 04:00 | 131 | 12:00 | Mirpur | 134 | 02:00 | 126 | 12:00
Baroaulia | 133 | 02:00 | 128 | 12:00 | Mirzapur | 129 | 03:00 | 122 | 12:00
Baroirhat | 130 | 03:00 | 124 | 14:00 | Mithapukur | 135 | 05:00 | 126 | 18:00
Bashundhara | 135 | 05:00 | 126 | 12:00 | MI_Cement | 133 | 03:00 | 127 | 12:00
BashundharaCement | 132 | 03:00 | 125 | 13:00 | Modern | 134 | 06:00 | 130 | 10:00
Beanibazar | 136 | 06:00 | 131 | 16:00 | Mogbazar | 135 | 04:00 | 126 | 13:00
Benapole | 138 | 03:00 | 127 | 13:00 | Mongla | 135 | 03:00 | 129 | 09:00
Bhaluka | 129 | 03:00 | 121 | 13:00 | Motijheel | 134 | 02:00 | 127 | 13:00
Bhandaria | 134 | 05:00 | 129 | 14:00 | Munshiganj | 132 | 06:00 | 127 | 11:00
Bhangura | 141 | 04:00 | 134 | 18:30 | Mymensingh | 133 | 19:00 | 119 | 23:00
Bheramara | 141 | 05:00 | 135 | 12:00 | Naogaon | 136 | 03:00 | 128 | 08:00
Bheramara(GK) | 140 | 03:00 | 135 | 13:00 | Narail | 140 | 04:00 | 129 | 13:00
Bhulta | 125 | 05:00 | 119 | 12:00 | Narinda | 135 | 4:00 | 128 | 12:00
Bog-Sherpur | 138 | 05:00 | 129 | 09:00 | Narshingdi | 130 | 09:00 | 122 | 12:00
Bogura | 138 | 04:00 | 130 | 08:00 | Natore | 139 | 05:00 | 132 | 13:00
Bogura-230 | 138 | 04:00 | 130 | 09:00 | Nawabganj | 135 | 05:00 | 127 | 13:00
Brahmanbaria | 136 | 05:00 | 127 | 19:00 | Netrakona | 131 | 01:00 | 120 | 12:00
Cantonment | 136 | 04:00 | 129 | 12:00 | New | 134 | 04:00 | 124 | 16:00
Chandpur | 129 | 01:00 | 120 | 12:00 | Niamatpur | 140 | 23:00 | 134 | 12:00
Chandraghona | 134 | 03:00 | 129 | 13:00 | Noapara | 139 | 02:00 | 130 | 13:00
Chapai | 138 | 00:00 | 134 | 08:00 | Pabna | 141 | 04:00 | 135 | 12:00
Charsaidpur | 133 | 06:00 | 126 | 12:00 | Palashbari | 133 | 05:00 | 125 | 08:00
Chauddagram | 133 | 04:00 | 123 | 13:00 | Panchagarh | 136 | 04:00 | 124 | 11:00
Chhatak | 135 | 03:00 | 131 | 11:00 | Patuakhali | 135 | 02:00 | 131 | 14:00
Chowmuhani | 127 | 05:00 | 117 | 13:00 | Payra | 137 | 05:00 | 133 | 13:00
Chuadanga | 140 | 03:00 | 127 | 13:00 | PHP | 131 | 04:00 | 127 | 13:00
Coxsbazar | 128 | 09:00 | 121 | 19:00 | Postogola | 135 | 03:00 | 129 | 12:00
Cumilla(N) | 136 | 03:00 | 129 | 13:00 | Purbachal | 135 | 05:00 | 125 | 12:00
Cumilla(S) | 134 | 05:00 | 127 | 13:00 | Purbasadipur | 132 | 05:00 | 122 | 08:00
Daudkandi | 130 | 00:00 | 124 | 13:00 | Rahanpur | 140 | 00:00 | 136 | 13:00
Dhaka | 134 | 02:00 | 126 | 13:00 | Rahanpur-400 | 140 | 00:00 | 136 | 08:00
Dhamrai | 136 | 04:00 | 126 | 12:00 | Rahim | 132 | 03:00 | 125 | 13:00
Dhanmondi | 134 | 04:00 | 128 | 12:00 | Rajbari | 135 | 04:00 | 130 | 12:00
Dohazari | 132 | 05:00 | 126 | 12:00 | Rajendrapur | 134 | 04:00 | 128 | 15:00
Faridpur | 135 | 03:00 | 130 | 12:00 | Rajshahi | 139 | 03:00 | 133 | 13:00
Fatullah | 134 | 06:00 | 127 | 12:00 | Rajshahi-230 | 140 | 04:00 | 132 | 08:00
Fenchuganj | 139 | 00:00 | 135 | 11:00 | Ramganj | 128 | 03:00 | 119 | 13:00
Feni | 130 | 04:00 | 124 | 13:00 | Rampur | 134 | 03:00 | 128 | 13:00
Ghatail | 131 | 19:00 | 122 | 08:00 | Rampura | 134 | 04:00 | 126 | 13:00
Ghorashal | 139 | 00:00 | 136 | 13:00 | Rangamati | 134 | 04:00 | 129 | 12:00
Goalpara | 141 | 05:00 | 132 | 13:00 | Rangpur | 133 | 06:00 | 123 | 09:00
Gollamari | 138 | 04:00 | 131 | 13:00 | Ruppur | 143 | 05:00 | 136 | 18:30
Gopalganj | 137 | 04:00 | 131 | 12:00 | Saidpur | 135 | 04:00 | 122 | 18:30
Gopalganj-400 | 137 | 05:00 | 131 | 12:00 | Satkhira | 137 | 03:00 | 129 | 13:00
Gulshan | 133 | 01:00 | 126 | 12:00 | Satmasjid | 135 | 01:00 | 128 | 13:00
Halishahar | 133 | 17:00 | 128 | 08:00 | Savar | 133 | 07:00 | 125 | 15:00
Haripur | 133 | 05:00 | 127 | 12:00 | SevenRings | 141 | 04:00 | 136 | 12:00
HaripurSBU | 133 | 05:00 | 127 | 13:00 | ShahCement | 133 | 06:00 | 126 | 12:00
Hasnabad | 134 | 02:00 | 129 | 11:00 | Shahjadpur | 143 | 04:00 | 136 | 13:00
Hathazari | 136 | 02:00 | 130 | 13:00 | Shahjibazar | 135 | 00:00 | 130 | 19:00
Ishurdi | 142 | 04:00 | 136 | 13:00 | Shahmirpur | 134 | 05:00 | 128 | 11:00
Jaldhaka | 132 | 05:00 | 121 | 18:00 | Shariatpur | 136 | 03:00 | 130 | 13:00
Jamalpur | 136 | 19:00 | 119 | 23:00 | Sherpur | 135 | 19:00 | 116 | 23:00
Jashore | 138 | 02:00 | 128 | 13:00 | Shikalbaha | 123 | 03:00 | 117 | 13:00
Jhenaidah | 141 | 05:00 | 132 | 13:00 | Shikalbaha-230 | 135 | 04:00 | 128 | 11:00
Jhenaidah-230 | 141 | 04:00 | 133 | 13:00 | Shitalakhya | 133 | 03:00 | 126.7 | 12:00
Joydebpur | 136 | 03:00 | 130 | 16:00 | Sholosohor | 133 | 01:00 | 129 | 12:00
Joypurhat | 137 | 02:00 | 129 | 08:00 | Shyampur | 132 | 04:00 | 126 | 10:00
Juldah | 134 | 05:00 | 129 | 18:00 | Shyampur-230 | 133 | 02:00 | 124 | 12:00
Kabirpur | 132 | 03:00 | 122 | 12:00 | Siddhirganj | 133 | 04:00 | 128 | 12:00
Kachua | 131 | 03:00 | 123 | 13:00 | Sirajganj | 140 | 03:00 | 127 | 08:00
Kaliakoir | 137 | 03:00 | 125 | 16:00 | Sonargaon | 131 | 04:00 | 124 | 11:00
Kallyanpur | 133 | 01:00 | 127 | 12:00 | Sreemongol | 136 | 02:00 | 132 | 12:00
Kalurghat | 133 | 05:00 | 129 | 12:00 | Sreepur | 130 | 00:00 | 126 | 12:00
Kamrangirchar | 134 | 04:00 | 126 | 12:00 | Srinagar | 134 | 05:00 | 128 | 12:00
Kaptai | N/A | N/A | N/A | N/A | SSM | 143 | 12:00 | 134 | 02:00
Kazla | 135 | 04:00 | 127 | 13:00 | Sunamganj | 134 | 04:00 | 130 | 18:00
Keranigonj | 134 | 03:00 | 127 | 13:00 | Sylhet | 136 | 04:00 | 132 | 13:00
Khagrachori | 133 | 03:00 | 128 | 18:00 | Sylhet-132 | 135 | 04:00 | 132 | 13:00
Khulna | 138 | 06:00 | 130 | 13:00 | Tangail | 128 | 03:00 | 122 | 08:00
Khulna(S) | 139 | 04:00 | 132 | 13:00 | Thakurgaon | 134 | 05:00 | 121 | 18:00
Khulshi | 133 | 04:00 | 127 | 13:00 | TK | 135 | 02:00 | 130 | 12:00
Kishoreganj | 133 | 02:00 | 129 | 13:00 | Tongi | 135 | 04:00 | 130 | 13:00
Kodda | 135 | 17:00 | 120 | 12:00 | Ullahpara | 140 | 03:00 | 134 | 17:00
KSRM | 136 | 07:00 | 128 | 13:00 | Ullon | 134 | 02:00 | 126 | 13:00
Kulaura | 137 | 00:00 | 133 | 13:00 | Uttara | 135 | 03:00 | 126 | 13:00
Kurigram | 133 | 04:00 | 122 | 18:00 | UttaraNew | 135 | 02:00 | 126 | 16:00
Zigatola | 135 | 04:00 | 126 | 12:00
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
QF-LDC-11
Date | 31-12-2024 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4403 | 4149.5 | 8552.5 | DAILY LOAD CURVE
00:30 | 4248 | 4017.5 | 8265.5
01:00 | 4093 | 3885.5 | 7978.5 | 31-12-2024
01:30 | 4058 | 3740 | 7798
02:00 | 4023 | 3594.5 | 7617.5
02:30 | 3958 | 3533 | 7491
03:00 | 3893 | 3471.5 | 7364.5
03:30 | 3839.5 | 3419 | 7258.5
04:00 | 3786 | 3366.5 | 7152.5
04:30 | 3757 | 3370 | 7127
05:00 | 3728 | 3373.5 | 7101.5
05:30 | 3848 | 3445.5 | 7293.5
06:00 | 3968 | 3517.5 | 7485.5
06:30 | 4105.915 | 3592.615 | 7698.53
07:00 | 4243.83 | 3667.73 | 7911.56
07:30 | 4432.48 | 3904.105 | 8336.585
08:00 | 4621.13 | 4140.48 | 8761.61
08:30 | 4718.76 | 4355.99 | 9074.75
09:00 | 4816.39 | 4571.5 | 9387.89
09:30 | 4780.9 | 4500.265 | 9281.165
10:00 | 4745.41 | 4429.03 | 9174.44
10:30 | 4905.31 | 4384.335 | 9289.645
11:00 | 5065.21 | 4339.64 | 9404.85
11:30 | 5128.84 | 4531.875 | 9660.715
12:00 | 5192.47 | 4724.11 | 9916.58
12:30 | 5243.685 | 4797.365 | 10041.05
13:00 | 5294.9 | 4870.62 | 10165.52
13:30 | 5144.255 | 4775.305 | 9919.56
14:00 | 4993.61 | 4679.99 | 9673.6
14:30 | 4915.095 | 4568.59 | 9483.685
15:00 | 4836.58 | 4457.19 | 9293.77
15:30 | 4849.19 | 4308.42 | 9157.61
16:00 | 4861.8 | 4159.65 | 9021.45
16:30 | 4959.41 | 4195.245 | 9154.655
17:00 | 5057.02 | 4230.84 | 9287.86
17:30 | 5262.51 | 4571.67 | 9834.18
18:00 | 5468 | 4912.5 | 10380.5
18:30 | 5377.5 | 4946 | 10323.5
19:00 | 5287 | 4979.5 | 10266.5
19:30 | 5338.5 | 4978.5 | 10317
20:00 | 5257.5 | 4971.5 | 10229
20:30 | 5144.25 | 4951.515 | 10095.765 |  | Executive Engineer
21:00 | 5031 | 4931.53 | 9962.53 |  | Network Operation Division
21:30 | 4959 | 4809.795 | 9768.795
22:00 | 4887 | 4688.06 | 9575.06
22:30 | 4772.5 | 4576.31 | 9348.81
23:00 | 4658 | 4464.56 | 9122.56

## En-Curve
QF-LDC-12
Date | 31-12-2024 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3094 | 1398.5 | 922 | 0 | 52 | 438 | 26 | 2548 | 0 | 35 | 17 | 0 | 0 | 22 | 0 | DAILY ENERGY CURVE
00:30 | 3039.5 | 1362.5 | 922 | 0 | 50 | 427.5 | 26 | 2379.5 | 0 | 17.5 | 17 | 0 | 0 | 24 | 0 | 31-12-2024
01:00 | 2985 | 1326.5 | 922 | 0 | 48 | 417 | 26 | 2211 | 0 | 0 | 17 | 0 | 0 | 26 | 0
01:30 | 2975 | 1338.5 | 827 | 0 | 46 | 417 | 26 | 2133 | 0 | 0 | 8.5 | 0 | 0 | 27 | 0 |  | Total Energy | 219.3377 |  | MKWHr
02:00 | 2965 | 1350.5 | 732 | 0 | 44 | 417 | 26 | 2055 | 0 | 0 | 0 | 0 | 0 | 28 | 0 |  | Energy not Served | 0 |  | MKWHr
02:30 | 2868 | 1343.5 | 732.5 | 0 | 42 | 418 | 26 | 2031 | 0 | 0 | 0 | 0 | 0 | 30 | 0 |  | Energy Requirement | 219.3377 |  | MKWHr
03:00 | 2771 | 1336.5 | 733 | 0 | 40 | 419 | 26 | 2007 | 0 | 0 | 0 | 0 | 0 | 32 | 0
03:30 | 2725 | 1330.5 | 686 | 0 | 43 | 419 | 26 | 1993 | 0 | 0 | 0 | 0 | 0 | 36 | 0
04:00 | 2679 | 1324.5 | 639 | 0 | 46 | 419 | 26 | 1979 | 0 | 0 | 0 | 0 | 0 | 40 | 0
04:30 | 2678 | 1306 | 639 | 0 | 45 | 418.5 | 26 | 1984 | 0 | 0 | 0 | 0 | 0 | 30.5 | 0
05:00 | 2677 | 1287.5 | 639 | 0 | 44 | 418 | 26 | 1989 | 0 | 0 | 0 | 0 | 0 | 21 | 0
05:30 | 2796 | 1344.5 | 639 | 0 | 42 | 418 | 26 | 2002.5 | 0 | 0 | 0 | 0 | 0 | 25.5 | 0
06:00 | 2915 | 1401.5 | 639 | 0 | 40 | 418 | 26 | 2016 | 0 | 0 | 0 | 0 | 0 | 30 | 0
06:30 | 2933 | 1500 | 686 | 0 | 40 | 418.5 | 26 | 2055 | 4.03 | 1.5 | 5 | 0 | 0 | 29.5 | 0
07:00 | 2951 | 1598.5 | 733 | 0 | 40 | 419 | 26 | 2094 | 8.06 | 3 | 10 | 0 | 0 | 29 | 0
07:30 | 3023.5 | 1635.5 | 827.5 | 0 | 41 | 418 | 26 | 2232 | 44.585 | 15.5 | 43 | 0 | 0 | 30 | 0
08:00 | 3096 | 1672.5 | 922 | 0 | 42 | 417 | 26 | 2370 | 81.11 | 28 | 76 | 0 | 0 | 31 | 0
08:30 | 3090.5 | 1655 | 922.5 | 0 | 43 | 447 | 26 | 2610.5 | 128.25 | 35.5 | 91 | 0 | 0 | 25.5 | 0
09:00 | 3085 | 1637.5 | 923 | 0 | 44 | 477 | 26 | 2851 | 175.39 | 43 | 106 | 0 | 0 | 20 | 0
09:30 | 3010.5 | 1601 | 922.5 | 0 | 47 | 494.5 | 26 | 2788.5 | 224.665 | 50.5 | 98 | 0 | 0 | 18 | 0
10:00 | 2936 | 1564.5 | 922 | 0 | 50 | 512 | 26 | 2726 | 273.94 | 58 | 90 | 0 | 0 | 16 | 0
10:30 | 3010.5 | 1632.25 | 922.5 | 0 | 49 | 499 | 26 | 2679 | 312.895 | 58 | 86 | 0 | 0 | 14.5 | 0
11:00 | 3085 | 1700 | 923 | 0 | 48 | 486 | 26 | 2632 | 351.85 | 58 | 82 | 0 | 0 | 13 | 0
11:30 | 3190 | 1719.25 | 923 | 0 | 49 | 485 | 26 | 2736.5 | 389.965 | 65 | 61.5 | 0 | 0 | 15.5 | 0
12:00 | 3295 | 1738.5 | 923 | 0 | 50 | 484 | 26 | 2841 | 428.08 | 72 | 41 | 0 | 0 | 18 | 0
12:30 | 3298 | 1777 | 922 | 0 | 56 | 498 | 26 | 2874 | 442.05 | 88 | 41 | 0 | 0 | 19 | 0
13:00 | 3301 | 1815.5 | 921 | 0 | 62 | 512 | 26 | 2907 | 456.02 | 104 | 41 | 0 | 0 | 20 | 0
13:30 | 3244.5 | 1744.5 | 921.5 | 0 | 61 | 512.5 | 26 | 2840.5 | 423.06 | 86 | 37 | 0 | 0 | 23 | 0
14:00 | 3188 | 1673.5 | 922 | 0 | 60 | 513 | 26 | 2774 | 390.1 | 68 | 33 | 0 | 0 | 26 | 0
14:30 | 3172.5 | 1635 | 922.5 | 0 | 61 | 513.5 | 26 | 2691 | 332.685 | 68 | 33 | 0 | 0 | 28.5 | 0
15:00 | 3157 | 1596.5 | 923 | 0 | 62 | 514 | 26 | 2608 | 275.27 | 68 | 33 | 0 | 0 | 31 | 0
15:30 | 3176.5 | 1616.75 | 923 | 0 | 57 | 514.5 | 26 | 2513 | 199.36 | 68 | 33 | 0 | 0 | 30.5 | 0
16:00 | 3196 | 1637 | 923 | 0 | 52 | 515 | 26 | 2418 | 123.45 | 68 | 33 | 0 | 0 | 30 | 0
16:30 | 3133 | 1649.25 | 923 | 0 | 54 | 512 | 26 | 2591.5 | 70.405 | 79.5 | 93 | 0 | 0 | 23 | 0
17:00 | 3070 | 1661.5 | 923 | 0 | 56 | 509 | 26 | 2765 | 17.36 | 91 | 153 | 0 | 0 | 16 | 0
17:30 | 3139.5 | 1684.5 | 923 | 0 | 58 | 570 | 26 | 3042.5 | 8.68 | 121.5 | 241.5 | 0 | 0 | 19 | 0
18:00 | 3209 | 1707.5 | 923 | 0 | 60 | 631 | 26 | 3320 | 0 | 152 | 330 | 0 | 0 | 22 | 0
18:30 | 3250 | 1686 | 922.5 | 0 | 62 | 694.5 | 36 | 3256 | 0 | 135.5 | 263.5 | 0 | 0 | 17.5 | 0
19:00 | 3291 | 1664.5 | 922 | 0 | 64 | 758 | 46 | 3192 | 0 | 119 | 197 | 0 | 0 | 13 | 0
19:30 | 3365 | 1745 | 922 | 0 | 54 | 757 | 46 | 3146 | 0 | 101 | 167 | 0 | 0 | 14 | 0
20:00 | 3237 | 1804 | 922 | 0 | 56 | 758 | 46 | 3144 | 0 | 101 | 147 | 0 | 0 | 14 | 0
20:30 | 3199 | 1772.25 | 922 | 0 | 55 | 758.515 | 46 | 3127 | 0 | 92 | 113 | 0 | 0 | 11 | 0
21:00 | 3161 | 1740.5 | 922 | 0 | 54 | 759.03 | 46 | 3110 | 0 | 83 | 79 | 0 | 0 | 8 | 0
21:30 | 3158.5 | 1736 | 921.5 | 0 | 54 | 733.795 | 46 | 2978.5 | 0 | 66.5 | 65 | 0 | 0 | 9 | 0
22:00 | 3156 | 1731.5 | 921 | 0 | 54 | 708.56 | 46 | 2847 | 0 | 50 | 51 | 0 | 0 | 10 | 0
22:30 | 3134 | 1703.5 | 915 | 0 | 53 | 678.31 | 46 | 2738.5 | 0 | 33.5 | 33.5 | 0 | 0 | 13.5 | 0
23:00 | 3112 | 1675.5 | 909 | 0 | 52 | 648.06 | 46 | 2630 | 0 | 17 | 16 | 0 | 0 | 17 | 0
Executive Engineer
Network Operation Division