## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-01-2025 | during | 02-01-2025 | during | 02-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 101.2 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 234.58 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 290 | 291 | 400.37 | 400.37 | 290 | 290
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | 450
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 25.21 | 0 | 0 | 13 | 13 | 25 | 25
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 34 | 54
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 32 | 149.36 | 149.36 | 149 | 149
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 20 | 19 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 0 | 0 | 23 | 23 | Default availability set by nldc
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 26 | 24 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 17 | 34 | 52.19 | 52.19 | 25 | 34
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 0 | 0 | 149 | 149 | 149 | 149
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 105 | 105 | 105 | 100 | 100
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 8 | 104 | 104 | 7 | 17 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 72 | 162 | 162 | 162 | 162
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 25 | 0 | 25 | 0
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 30 | 17 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 180 | 160 | 584 | 584 | 180 | 180
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 718 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
Dhaka Area Total |  |  |  |  | 7178.63 | 6689.44 | 1143 | 1310 | 4405.19 | 4380.19 | 2216 | 2230
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 2 | 25.5 | 25.5 | 8 | 25
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 30 | 50 | 50 | 50 | 50
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 40 | 40 | 40 | 40 | 40
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 209 | 226 | 225 | 225 | 225 | 225
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 85 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 40 | 64 | 64 | 56 | 74 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 35 | 85 | 85 | 50 | 50
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 33 | 33 | 21 | 31 | 0 | 0 | 2 | 8 | Default availability set by nldc
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 8 | 108 | 108 | 20 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4 | 0 | 4 | 0
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 32 | 300 | 300 | 50 | 100
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 17 | 18 | 54.36 | 54.36 | 54.36 | 54.36
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 12 | 110 | 110 | 110 | 110
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 30 | 116 | 116 | 50 | 108 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 72 | 159.86 | 159.86 | 17 | 34
55 | SS Power | Coal | IPP | 2*660 | 1320 | 1224 | 612 | 598 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 66 | 66 | 2 | 8 | 0 | 0 | 2 | 8 | Default availability set by nldc
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1200 | 1200 | 520 | 575 | 575 | 575 | 575 | 575 | U1 S/D 09/Oct/24 (Maintenance Work)
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 22 | 0 | 0 | 0 | 66 | 0 | Default availability set by nldc
Chattogram Area Total |  |  |  |  | 5177.36 | 4987.22 | 1506 | 1798 | 2851.72 | 2829.72 | 2294.36 | 2428.36
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 185 | 180 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 290 | 315 | 356.15 | 356.15 | 320 | 320
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0
62 | Ashuganj 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 33 | 46.94 | 46.94 | 40 | 40
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 130 | 185 | 195 | 195 | 195 | 195
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 10 | 45 | 150 | 150 | 150 | 150
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 24 | 47 | 47 | 30 | 45 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 42 | 20 | 0 | 0 | 40 | 40 | Default availability set by nldc
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 200 | 200 | 200 | 200
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 54 | 90 | 90 | 90 | 90
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 5 | 20.83 | 20.83 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 42 | 113 | 113 | 95 | 100
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 30 | 115 | 115 | 50 | 92
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 17 | 54.5 | 54.5 | 17 | 17
Cumilla Area Total |  |  |  |  | 2893.7 | 2865.98 | 849 | 1055 | 1856.62 | 1856.62 | 1694.2 | 1756.2
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 10 | 10 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 94 | 200 | 200 | 95 | 95
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 18 | 115 | 115 | 115 | 115
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 18.16 | 0 | 23.21 | 0 | 23.21 | 0
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 150 | 0 | 0 | 0 | 0 | 150 | 150 | Default availability set by nldc
Mymensingh Area Total |  |  |  |  | 750 | 749.71 | 139.16 | 134 | 572.21 | 547 | 417.21 | 392
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 0 | 0 | 0 | 30 | 30 | Default availability set by nldc
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | 163
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 44 | 44 | 35 | 35
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 0 | 0 | 2 | 2 | Default availability set by nldc
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 0 | 0 | 0 | 25 | 25 | Default availability set by nldc
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 42 | 42 | 86 | 86 | 55 | 55
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 211 | 206 | 210 | 210 | 205 | 205
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 | 13 | 13 | Default availability set by nldc
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 341 | 341 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 308 | 343 | 350 | 350 | 380 | 380 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 366 | 300 | 383 | 383 | 220 | 220 | air intake filter DP higher due to Fog
Sylhet Area Total |  |  |  |  | 2411 | 2370.57 | 1049 | 1056 | 1577 | 1577 | 1128 | 1128
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 907 | 627 | 1000 | 1000 | 1000 | 1000
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 29 | 42 | 42 | 20 | 35
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 5 | 80 | 80 | 34 | 60
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 312 | 283 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71.1 | 0 | 68 | 0 | 68 | 0
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1105 | 1103 | 1234 | 1234 | 1234 | 1234
** | HVDC(Nepal) | Import | Import | 1*40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0
Khulna Area Total |  |  |  |  | 3743 | 3726.2 | 2395.1 | 2047 | 3274 | 3206 | 2761 | 2734
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 0 | 7 | 10.12 | 10.12 | 10.12 | 10.12
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 130 | 130 | 130 | 134 | 134 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 550 | 510 | 622 | 622 | 622 | 622
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 45 | 150 | 150 | 54 | 150
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 300 | 307 | 307 | 307 | 307
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.49 | 0 | 0.29 | 0 | 0.29 | 0
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1120.49 | 1212 | 1549.41 | 1549.12 | 1457.41 | 1553.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 40 | 41 | 41 | 52 | 52
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 0 | 0 | 71 | 71 | Default availability set by nldc
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 35.09 | 35.09 | Default availability set by nldc
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 33 | 0 | 0 | 26 | 32 | Default availability set by nldc
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 135 | 159 | 214 | 214 | 193 | 193 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 188 | 220 | 220 | 198 | 198 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 190 | 220 | 220 | 198 | 198 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 30 | 30 | 24 | 24
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 8.5 | 8.25 | 8.25 | 8.5 | 8.5
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52 | 52 | 45 | 52
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 98 | 98 | 53 | 95
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 95 | 113
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 1.2 | 0 | 4.2 | 0 | 4.2 | 0
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 754.98 | 680 | 1347.54 | 1347.54 | 1347.54 | 1347.54
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 12.45 | 0 | 25 | 0 | 25 | 0
| Pabna Solar 100 MW | Solar | IPP |  | 100 | 100 | 85 | 0 | 80 | 0 | 80 | 0
Rajshahi Area Total |  |  |  |  | 3575.55 | 3393.2 | 1274.13 | 1412.5 | 2565.99 | 2456.79 | 2568.33 | 2532.13
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 80 | 78 | 75 | 75 | 75 | 75
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 180 | 200 | 200 | 200 | 200 | 200
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 90 | 113
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.9 | 0 | 3 | 0 | 3 | 0
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 34 | 115 | 115 | 115 | 115
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 5 | 0 | 26 | 0 | 26 | 0
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 26 | 0 | 60.69 | 0 | 60.69 | 0
Rangpur Area Total |  |  |  |  | 1030 | 950 | 291.9 | 312 | 592.69 | 503 | 569.69 | 503
System Total |  |  |  |  | 29025.24 | 27997.42 | 9767.78 | 10336.5 | 19244.83 | 18905.44 | 15106.2 | 15256.81
Forecast Scenario (02-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8550 |  | 0 |  | 8550
|  |  |  | 1:00 | 7970 |  | 0 |  | 7970
|  |  |  | 2:00 | 7610 |  | 0 |  | 7610
|  |  |  | 3:00 | 7360 |  | 0 |  | 7360
|  |  |  | 4:00 | 7150 |  | 0 |  | 7150
|  |  |  | 5:00 | 7100 |  | 0 |  | 7100
|  |  |  | 6:00 | 7480 |  | 0 |  | 7480
|  |  |  | 7:00 | 7910 |  | 0 |  | 7910
|  |  |  | 8:00 | 8760 |  | 0 |  | 8760
|  |  |  | 9:00 | 9380 |  | 0 |  | 9380
|  |  |  | 10:00 | 9170 |  | 0 |  | 9170
|  |  |  | 11:00 | 9400 |  | 0 |  | 9400
|  |  |  | 12:00 | 9910 |  | 0 |  | 9910
|  |  |  | 13:00 | 10160 |  | 0 |  | 10160
|  |  |  | 14:00 | 9670 |  | 0 |  | 9670
|  |  |  | 15:00 | 9290 |  | 0 |  | 9290
|  |  |  | 16:00 | 9020 |  | 0 |  | 9020
|  |  |  | 17:00 | 9280 |  | 0 |  | 9280
|  |  |  | 18:00 | 10380 |  | 0 |  | 10380
|  |  |  | 18:30 | 10320 |  | 0 |  | 10320
|  |  |  | 19:00 | 10260 |  | 0 |  | 10260
|  |  |  | 19:30 | 10310 |  | 0 |  | 10310
|  |  |  | 20:00 | 10220 |  | 0 |  | 10220
|  |  |  | 21:00 | 9960 |  | 0 |  | 9960
|  |  |  | 22:00 | 9570 |  | 0 |  | 9570
|  |  |  | 23:00 | 9120 |  | 0 |  | 9120
Probable Maximum Temperature: |  |  | 23.90°C
Probable Maximum Demand at Day Peak: |  |  | 9910.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 10380.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10380.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 214.68 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (01-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 20.70°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 741.89
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 19.3244 | Peak Hour Flow: |  | 627.00 MW at 18:00 hrs.
Energy Flow from West to East |  | 8725634.51 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 13.7819 | Peak Hour Flow: |  | 680.00 MW at 18:00 hrs.
Power Flow during Peak Demand |  | 556 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.1616 | Peak Hour Flow: |  | 54.00 MW at 18:00 hrs.
Maximum Power Flow |  | 924 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 34.2678 | Peak Hour Flow: |  | 1361.00 MW at 18:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## Genlog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-01-2025 | [28 empty] | Date: | 01-01-2025 | [28 empty] | Date: | 01-01-2025 | [28 empty] | Date: | 01-01-2025 | [28 empty] | Date: | 01-01-2025 | [18 empty] | Date: | 01-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | Sonagazi 75 MW (AC) Solar Power Plant | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Bhairob 54.5 MW | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sreepur 150 MW PP | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.00 MW | 105.00 MW | 52.00 MW | 365.00 MW | 260.00 MW | 234.58 MW | 190.00 MW | 108.00 MW | 412.00 MW | 20.00 MW | 718.00 MW | 54.00 MW | 36.09 MW | 20.00 MW | 149.00 MW | 149.00 MW | 300.00 MW | 55.00 MW | 55.00 MW | 162.00 MW | 33.00 MW | 104.00 MW | 450.00 MW | 335.00 MW | 583.00 MW | 583.00 MW | 55.00 MW | 33.00 MW | 335.00 MW | 210.00 MW | 115.00 MW | 35.00 MW | 33.75 MW | 23.00 MW | 105.00 MW | 584.00 MW | 116.00 MW | 300.00 MW | 108.00 MW | 360.00 MW | 66.00 MW | 102.00 MW | 98.00 MW | 54.36 MW | 100.00 MW | 100.00 MW | 7.00 MW | 230.00 MW | 110.00 MW | 33.00 MW | 1150.00 MW | 159.86 MW | 159.86 MW | 50.00 MW | 25.00 MW | 105.00 MW | 225.00 MW | 225.00 MW | 150.00 MW | 150.00 MW | 75.00 MW | 1320.00 MW | 20.00 MW | 51.00 MW | 150.00 MW | 195.00 MW | 400.00 MW | 356.15 MW | 360.00 MW | 45.00 MW | 55.00 MW | 221.00 MW | 54.50 MW | 115.00 MW | 163.00 MW | 200.00 MW | 113.00 MW | 25.00 MW | 114.00 MW | 160.00 MW | 52.20 MW | 52.00 MW | 341.00 MW | 383.00 MW | 400.00 MW | 50.00 MW | 70.00 MW | 90.00 MW | 11.00 MW | 163.00 MW | 25.00 MW | 100.00 MW | 86.00 MW | 66.00 MW | 330.00 MW | 20.00 MW | 231.00 MW | 115.00 MW | 200.00 MW | 210.00 MW | 3.00 MW | 150.00 MW | 50.00 MW | 22.00 MW | - | 1000.00 MW | 410.00 MW | 16.00 MW | 54.00 MW | 109.00 MW | 40.00 MW | 230.00 MW | 230.00 MW | 336.00 MW | 336.00 MW | 105.00 MW | 100.00 MW | 1234.00 MW | 105.00 MW | 1347.54 MW | 35.09 MW | 100.00 MW | 52.00 MW | 71.00 MW | 113.00 MW | 71.00 MW | 104.00 MW | 113.00 MW | 50.00 MW | 52.00 MW | 100.00 MW | 50.00 MW | 68.00 MW | 214.00 MW | 214.00 MW | 220.00 MW | 220.00 MW | 220.00 MW | 220.00 MW | 414.00 MW | 414.00 MW | 6.09 MW | 11.00 MW | 274.00 MW | 170.00 MW | 115.00 MW | 30.00 MW | 113.00 MW | 20.00 MW | 20.00 MW | 8.00 MW | 200.00 MW | 1.00 MW | 110.00 MW | 307.00 MW | 40.00 MW | 194.00 MW | 220.00 MW | 220.00 MW | 1244.00 MW | 150.00 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 23 | 165 | 0 | 0 | 0 | 15 | 22 | 0 | 225 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 42 | 515 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 346 | 0 | 51 | 0 | 108 | 0 | 290 | 0 | 33 | 29 | 181 | 0 | 0 | 40 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 270 | 260 | 348 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 0 | 25 | 0 | 0 | 212 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 4412 | 909 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 545.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 140 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 180 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 100 | 220 | 0 | 350 | 0 | 4068.56 | 8480.56 | 94.03
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 330 | 0 | 0 | 0 | 0 | 23 | 164 | 0 | 0 | 0 | 12 | 22 | 0 | 215 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 37 | 380 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 288 | 0 | 51 | 0 | 108 | 0 | 310 | 0 | 33 | 29 | 181 | 0 | 0 | 40 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 285 | 260 | 307 | 5 | 30 | 0 | 2 | 163 | 13 | 0 | 0 | 25 | 0 | 0 | 213 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 4177 | 910 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767 | 0 | 476.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 199 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 220 | 0 | 280 | 0 | 3927.95 | 8104.95 | 94.02
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 24 | 170 | 0 | 0 | 0 | 12 | 22 | 0 | 210 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 37 | 381 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 290 | 0 | 5 | 0 | 68 | 0 | 310 | 0 | 33 | 23 | 181 | 0 | 0 | 40 | 0 | 0 | 11 | 0 | 42 | 0 | 0 | 295 | 240 | 307 | 0 | 30 | 0 | 2 | 163 | 13 | 0 | 0 | 20 | 0 | 0 | 212 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 4033 | 721 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 420.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 200 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 220 | 0 | 270 | 0 | 3659.73 | 7692.73 | 94.02
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 24 | 170 | 0 | 0 | 0 | 11 | 22 | 0 | 210 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 42 | 382 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 16 | 0 | 290 | 0 | 5 | 0 | 181 | 0 | 0 | 40 | 0 | 0 | 11 | 0 | 40 | 0 | 0 | 270 | 230 | 307 | 0 | 30 | 0 | 2 | 120 | 13 | 0 | 0 | 20 | 0 | 0 | 212 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 3807 | 722 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 416.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 200 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 220 | 0 | 250 | 0 | 3544.72 | 7351.72 | 94.02
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 24 | 162 | 0 | 0 | 0 | 11 | 22 | 0 | 200 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 42 | 381 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 181 | 0 | 0 | 40 | 0 | 0 | 11 | 0 | 38 | 0 | 0 | 280 | 230 | 307 | 0 | 30 | 0 | 2 | 120 | 13 | 0 | 0 | 20 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3692 | 627 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 416.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 200 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 220 | 0 | 250 | 0 | 3391.25 | 7083.25 | 94.02
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 0 | 24 | 162 | 0 | 0 | 0 | 11 | 22 | 0 | 190 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 37 | 382 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 140 | 0 | 0 | 45 | 0 | 0 | 11 | 0 | 38 | 0 | 0 | 300 | 222 | 307 | 0 | 30 | 0 | 2 | 120 | 13 | 0 | 0 | 20 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3671 | 627 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736 | 0 | 417.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 5.5 | 170 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 100 | 180 | 0 | 250 | 0 | 3281.51 | 6952.51 | 94.01
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 28 | 160 | 0 | 0 | 0 | 11 | 22 | 0 | 180 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 42 | 450 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 185 | 0 | 0 | 50 | 0 | 0 | 11 | 0 | 40 | 0 | 0 | 310 | 210 | 307 | 0 | 30 | 0 | 2 | 120 | 13 | 0 | 0 | 20 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3930 | 627 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 746 | 0 | 416.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 130 | 0 | 162 | 0 | 0 | 0 | 0 | 5.5 | 170 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 220 | 0 | 250 | 0 | 3453.48 | 7383.48 | 94.01
07:00 | 0 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 28 | 170 | 0 | 0 | 1 | 15 | 22 | 0 | 180 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 40 | 451 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 0 | 290 | 1 | 0 | 0 | 153 | 0 | 355 | 0 | 30 | 0 | 201 | 0 | 0 | 50 | 0 | 0 | 15 | 0 | 40 | 0 | 0 | 300 | 204 | 307 | 0 | 30 | 0 | 2 | 163 | 13 | 0 | 0 | 20 | 0 | 0 | 213 | 3 | 5 | 0 | 0 | 0 | 0.05 | 0 | 4302.05 | 721 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.47 | 751 | 0 | 417.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.49 | 172 | 0 | 191 | 0 | 188 | 0 | 0 | 0 | 0.01 | 5.5 | 170 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 140 | 0 | 130 | 220 | 0 | 250 | 0 | 3737.53 | 8039.58 | 94.01
08:00 | 0 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 28 | 185 | 0 | 0 | 6 | 17 | 22 | 0 | 180 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 1 | 26 | 0 | 29 | 452 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 3 | 363 | 6 | 29 | 0 | 187 | 0 | 335 | 0 | 27 | 12 | 190 | 0 | 0 | 45 | 0 | 0 | 15 | 0 | 42 | 0 | 0 | 310 | 204 | 307 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 56 | 0 | 0 | 0 | 213 | 35 | 35 | 0 | 0 | 0 | 1.65 | 0 | 4533.65 | 910 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.45 | 895 | 0 | 444.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 7.76 | 169 | 0 | 192 | 0 | 199 | 0 | 0 | 0 | 0.67 | 5.5 | 170 | 78 | 0 | 1 | 0 | 0 | 0 | 0.2 | 9 | 0.03 | 0 | 273 | 0 | 130 | 220 | 0 | 300 | 0 | 4366.52 | 8900.17 | 94.01
09:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 13 | 16 | 22 | 0 | 180 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 21 | 576 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 5 | 442 | 11 | 51 | 0 | 158 | 0 | 370 | 0 | 30 | 29 | 219 | 0 | 0 | 45 | 0 | 0 | 15 | 0 | 42 | 0 | 0 | 200 | 204 | 306 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 212 | 55 | 35 | 0 | 0 | 0 | 4.16 | 22 | 4574.16 | 721 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.19 | 1190 | 0 | 512.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 6.85 | 167 | 0 | 181 | 0 | 198 | 0 | 0 | 0 | 0.78 | 5.5 | 183 | 77 | 0 | 2 | 0 | 0 | 0 | 0.5 | 14 | 0.07 | 0 | 307 | 0 | 130 | 220 | 0 | 450 | 0 | 4764.6 | 9338.76 | 94
10:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 0 | 350 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 20 | 18 | 22 | 0 | 60 | 11 | 15 | 0 | 0 | 1 | 0 | 0 | 12 | 0 | 3 | 3 | 46 | 0 | 21 | 575 | 0 | 0 | 6 | 0 | 0 | 228 | 0 | 0 | 0 | 11 | 530 | 16 | 51 | 10 | 157 | 0 | 285 | 0 | 33 | 29 | 181 | 0 | 0 | 45 | 0 | 12 | 5 | 0 | 50 | 0 | 0 | 0 | 220 | 308 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 42 | 0 | 0 | 0 | 212 | 55 | 8 | 0 | 0 | 0 | 7.1 | 24 | 4263.1 | 627 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.91 | 1239 | 0 | 657.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 10.63 | 167 | 0 | 150 | 0 | 198 | 0 | 0 | 0 | 1.02 | 5.5 | 186 | 77 | 0 | 3 | 0 | 0 | 0 | 1.3 | 23 | 0.19 | 0 | 250 | 0 | 100 | 180 | 0 | 550 | 0 | 4788.31 | 9051.41 | 94
11:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 0 | 320 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 25 | 20 | 20 | 0 | 76 | 17 | 15 | 0 | 0 | 2 | 0 | 0 | 17 | 0 | 12 | 3 | 46 | 0 | 19 | 520 | 0 | 0 | 18 | 0 | 0 | 186 | 0 | 0 | 0 | 18 | 614 | 18 | 43 | 10 | 130 | 0 | 285 | 0 | 32 | 29 | 181 | 0 | 0 | 42 | 0 | 17 | 5 | 0 | 54 | 0 | 0 | 0 | 250 | 308 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 42 | 0 | 0 | 0 | 213 | 75 | 45 | 0 | 0 | 0 | 13.46 | 0 | 4324.46 | 906 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.45 | 1113 | 0 | 752.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 13.23 | 130 | 0 | 130 | 0 | 150 | 0 | 0 | 0 | 1.05 | 5.5 | 174 | 78 | 0 | 4 | 0 | 0 | 0 | 1 | 31 | 0.34 | 0 | 250 | 0 | 100 | 180 | 0 | 540 | 0 | 4949.99 | 9274.45 | 94
12:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 0 | 420 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 26 | 20 | 22 | 0 | 180 | 17 | 0 | 0 | 0 | 2 | 0 | 0 | 17 | 0 | 0 | 4 | 46 | 0 | 21 | 520 | 0 | 0 | 19 | 0 | 0 | 209 | 0 | 0 | 0 | 22 | 612 | 17 | 51 | 10 | 130 | 0 | 290 | 0 | 32 | 29 | 185 | 0 | 0 | 42 | 0 | 17 | 5 | 0 | 58 | 0 | 0 | 0 | 366 | 308 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 42 | 0 | 0 | 0 | 211 | 75 | 45 | 0 | 1 | 0 | 18.16 | 0 | 4686.16 | 907 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.1 | 1105 | 0 | 754.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 12.45 | 135 | 0 | 130 | 0 | 150 | 0 | 0 | 0 | 1.2 | 5.5 | 180 | 80 | 0 | 5 | 0 | 0 | 0 | 0.9 | 26 | 0.49 | 0 | 250 | 0 | 100 | 220 | 0 | 550 | 0 | 5081.62 | 9767.78 | 94
13:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 24 | 20 | 22 | 0 | 180 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 3 | 30 | 0 | 29 | 575 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 40 | 612 | 16 | 51 | 0 | 137 | 0 | 310 | 0 | 32 | 29 | 183 | 0 | 0 | 30 | 0 | 18 | 5 | 0 | 62 | 0 | 0 | 0 | 376 | 310 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 210 | 75 | 45 | 0 | 1 | 0 | 30.01 | 0 | 4811.01 | 908 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.91 | 1103 | 0 | 754.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 11.69 | 172 | 0 | 176 | 0 | 172 | 0 | 0 | 0 | 1.26 | 5.5 | 179 | 80 | 0 | 6 | 0 | 0 | 0 | 1 | 33 | 0.48 | 0 | 307 | 0 | 130 | 220 | 0 | 550 | 0 | 5279.43 | 10090.44 | 93.99
14:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 19 | 21 | 22 | 0 | 180 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 26 | 0 | 20 | 578 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 44 | 560 | 14 | 51 | 0 | 127 | 0 | 295 | 0 | 33 | 29 | 195 | 0 | 0 | 30 | 0 | 24 | 5 | 0 | 58 | 0 | 0 | 0 | 330 | 316 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 42 | 0 | 0 | 0 | 209 | 80 | 53 | 0 | 0 | 0 | 21.38 | 0 | 4629.38 | 907 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.18 | 915 | 0 | 714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 34.67 | 150 | 0 | 209 | 0 | 150 | 0 | 0 | 0 | 2.3 | 5.5 | 200 | 80 | 0 | 6 | 0 | 0 | 0 | 0.9 | 35 | 0.39 | 0 | 249 | 0 | 100 | 180 | 0 | 560 | 0 | 4904.94 | 9534.32 | 93.99
15:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 14 | 20 | 22 | 0 | 180 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 0 | 13 | 500 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 31 | 480 | 10 | 51 | 0 | 118 | 0 | 280 | 0 | 33 | 30 | 181 | 0 | 0 | 30 | 0 | 34 | 5 | 0 | 56 | 0 | 0 | 0 | 346 | 379 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 206 | 96 | 56 | 0 | 0 | 0 | 6.16 | 0 | 4538.16 | 907 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.08 | 911 | 0 | 554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 21.73 | 150 | 0 | 201 | 0 | 150 | 0 | 0 | 0 | 1.93 | 5.5 | 200 | 78 | 0 | 3 | 0 | 0 | 0 | 0.8 | 26 | 0.25 | 0 | 195 | 0 | 130 | 220 | 0 | 540 | 0 | 4666.29 | 9204.45 | 93.99
16:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 6 | 20 | 22 | 0 | 160 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 0 | 18 | 501 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 13 | 450 | 4 | 51 | 0 | 108 | 0 | 290 | 0 | 33 | 29 | 188 | 0 | 4 | 25 | 0 | 34 | 5 | 0 | 54 | 0 | 0 | 0 | 346 | 380 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 206 | 39 | 56 | 0 | 0 | 0 | 3 | 0 | 4443 | 907 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.68 | 816 | 0 | 457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 9.22 | 150 | 0 | 130 | 0 | 210 | 0 | 0 | 0 | 0.79 | 5.5 | 200 | 78 | 0 | 2 | 0 | 0 | 0 | 0.5 | 10 | 0.12 | 0 | 180 | 0 | 130 | 220 | 0 | 540 | 0 | 4388.81 | 8831.81 | 93.98
17:00 | 8 | 85 | 34 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 1 | 15 | 0 | 0 | 16 | 0 | 0 | 9 | 40 | 25 | 0 | 350 | 0 | 0 | 0 | 17 | 26 | 0 | 0 | 0 | 1 | 20 | 22 | 0 | 120 | 5 | 32 | 0 | 0 | 3 | 3 | 16 | 11 | 0 | 12 | 0 | 30 | 1 | 29 | 575 | 32 | 0 | 6 | 0 | 5 | 229 | 0 | 0 | 0 | 2 | 498 | 0 | 51 | 5 | 163 | 0 | 295 | 0 | 33 | 29 | 174 | 9 | 30 | 20 | 5 | 34 | 5 | 0 | 58 | 8 | 4 | 0 | 316 | 309 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 42 | 0 | 0 | 0 | 207 | 18 | 65 | 0 | 0 | 0 | 0.26 | 2 | 4591.26 | 907 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.78 | 925 | 0 | 527 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 7 | 0 | 4 | 5 | 1.26 | 150 | 0 | 130 | 0 | 150 | 0 | 0 | 0 | 0.13 | 5.5 | 200 | 79 | 34 | 0 | 0 | 0 | 0 | 0 | 1 | 0.02 | 0 | 250 | 5 | 100 | 220 | 0 | 530 | 16 | 4585.69 | 9176.95 | 93.98
18:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 17 | 17 | 0 | 0 | 32 | 0 | 0 | 17 | 72 | 25 | 8 | 450 | 0 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 160 | 30 | 32 | 8 | 0 | 8 | 35 | 40 | 18 | 12 | 12 | 0 | 40 | 12 | 31 | 575 | 72 | 0 | 30 | 2 | 17 | 226 | 0 | 0 | 0 | 0 | 598 | 0 | 51 | 45 | 185 | 0 | 315 | 0 | 33 | 29 | 180 | 17 | 30 | 20 | 17 | 42 | 5 | 0 | 54 | 8 | 24 | 0 | 300 | 343 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 206 | 18 | 94 | 0 | 0 | 0 | 0 | 22 | 5353 | 627 | 283 | 0 | 29 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 680 | 0 | 0 | 40 | 0 | 0 | 0 | 92 | 0 | 33 | 0 | 0 | 22 | 0 | 159 | 0 | 188 | 0 | 190 | 0 | 0 | 0 | 0 | 8.5 | 200 | 78 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 7 | 130 | 220 | 0 | 510 | 45 | 4983.5 | 10336.5 | 93.98
19:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 160 | 17 | 15 | 0 | 0 | 13 | 28 | 0 | 17 | 0 | 0 | 0 | 40 | 0 | 33 | 575 | 0 | 0 | 27 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 598 | 0 | 51 | 20 | 185 | 0 | 335 | 0 | 33 | 29 | 230 | 0 | 0 | 20 | 0 | 63 | 5 | 0 | 56 | 0 | 0 | 0 | 310 | 353 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 206 | 18 | 103 | 0 | 0 | 0 | 0 | 22 | 4930 | 627 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1236 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 192 | 0 | 200 | 0 | 0 | 0 | 0 | 8.5 | 200 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 620 | 54 | 5188.5 | 10118.5 | 93.97
19:30 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 115 | 17 | 15 | 0 | 0 | 9 | 29 | 0 | 17 | 0 | 0 | 0 | 40 | 0 | 34 | 576 | 0 | 0 | 19 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 20 | 185 | 0 | 345 | 0 | 33 | 29 | 200 | 0 | 0 | 20 | 0 | 63 | 8 | 0 | 54 | 0 | 0 | 0 | 300 | 366 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 207 | 58 | 103 | 0 | 0 | 0 | 0 | 22 | 4922 | 627 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1235 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 192 | 0 | 200 | 0 | 0 | 0 | 0 | 8.5 | 200 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 622 | 54 | 5185.5 | 10107.5
20:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 115 | 17 | 15 | 0 | 0 | 7 | 29 | 0 | 17 | 0 | 0 | 0 | 40 | 0 | 34 | 575 | 0 | 0 | 19 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 613 | 0 | 51 | 20 | 185 | 0 | 310 | 0 | 34 | 28 | 183 | 0 | 0 | 25 | 0 | 63 | 5 | 0 | 56 | 0 | 0 | 0 | 300 | 344 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 208 | 64 | 65 | 0 | 0 | 0 | 0 | 22 | 4812 | 627 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 193 | 0 | 200 | 0 | 0 | 0 | 0 | 8.5 | 200 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 622 | 54 | 5158.5 | 9970.5 | 93.97
21:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 70 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 17 | 0 | 0 | 0 | 40 | 0 | 34 | 577 | 0 | 0 | 19 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 613 | 0 | 51 | 0 | 189 | 0 | 315 | 0 | 34 | 28 | 185 | 0 | 0 | 20 | 0 | 26 | 17 | 0 | 54 | 0 | 0 | 0 | 280 | 323 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 209 | 64 | 24 | 0 | 0 | 0 | 0 | 0 | 4506 | 909 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1229 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 193 | 0 | 200 | 0 | 0 | 0 | 0 | 8.5 | 200 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 622 | 0 | 5323.5 | 9829.5 | 93.97
22:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 76 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 575 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 189 | 0 | 320 | 0 | 34 | 26 | 181 | 0 | 0 | 20 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 260 | 323 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 209 | 45 | 8 | 0 | 0 | 0 | 0 | 0 | 4375 | 910 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 192 | 0 | 198 | 0 | 0 | 0 | 0 | 8.5 | 200 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 130 | 220 | 0 | 560 | 0 | 5055.5 | 9430.5 | 93.96
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 150 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 524 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 189 | 0 | 325 | 0 | 34 | 28 | 186 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 246 | 323 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 42 | 0 | 0 | 0 | 209 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 4160 | 910 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 188 | 0 | 180 | 0 | 0 | 0 | 0 | 8.5 | 200 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 130 | 220 | 0 | 520 | 0 | 4738.5 | 8898.5 | 93.96
Total KWH | 8064 | 1024176 | 241685 | 0 | 0 | 0 | 0 | 0 | 6904800 | 0 | 0 | 27072 | 196560 | 0 | 23328 | 72000 | 0 | 0 | 27176 | 172800 | 534960 | 7296 | 9459000 | 0 | 0 | 0 | 52861 | 591900 | 1483292 | 0 | 0 | 154804 | 399000 | 528480 | 0 | 3663636 | 149027 | 166855 | 10560 | 0 | 305280 | 95032 | 54174 | 163103 | 11520 | 45120 | 20641 | 789000 | 31780 | 761760 | 12181818.18 | 81963 | 0 | 161760 | 3106.8 | 35963 | 5261585 | 0 | 0 | 0 | 187764 | 11083635 | 112995 | 883685 | 194036 | 2994182 | 0 | 7826000 | 0 | 652968 | 521280 | 4511000 | 31320 | 83520 | 780370 | 27840 | 456960 | 247860 | 0 | 1161600 | 16541 | 26288 | 2575560 | 6509500 | 8123000 | 11232 | 231000 | 0 | 57024 | 3705300 | 122832 | 0 | 707520 | 161376 | 0 | 0 | 5236790 | 908400 | 768000 | 41280 | 2750 | 0 | 101630 | 144720 | 107110695.98 | 19324363 | 6733440 | 0 | 17280 | 2432 | 0 | 0 | 0 | 0 | 0 | 0 | 418320 | 23585450 | 0 | 13781854 | 0 | 0 | 41402 | 0 | 0 | 0 | 301376 | 0 | 29491 | 0 | 523740 | 24226 | 124504 | 3910000 | 0 | 4187036 | 0 | 4369273 | 0 | 0 | 0 | 11460 | 149364 | 4664000 | 1836654 | 55349 | 34316 | 0 | 0 | 0 | 7371.72 | 205130 | 2369 | 0 | 5454000 | 54632 | 2804000 | 5310980 | 0 | 11282909.09 | 204000 | 109450721.81 | 216561417.79

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 01-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 9767.78 | MW | 12:00 Hr. | Energy Generated |  |  | 216561.4178 |  | MWHr
Day Peak Demand |  |  | 9767.78 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MWHr
Evening Peak Generation |  |  | 10336.5 | MW | 18:00 Hr. | Energy Demand |  |  | 216561.4178 |  | MWHr
Evening Peak Demand |  |  | 10336.5 | MW | 18:00 Hr.
Minimum Generation of the Day |  |  | 6952.51 | MW | 05:00 Hr.
Minimum Demand of the Day |  |  | 6952.51 | MW | 05:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 23565.068 | 0 | 1853.018 | 0 | 0 | 154.804 | 0 | 0 | 25572.89 | Gas | 103006.897 | Gas | 358352586.79
Chattogram Zone |  |  | 6023.345 | 23265.4532 | 1009.9638 | 0 | 789 | 321.4 | 0 | 305.28 | 31714.442 | Coal | 70088.4663 | Coal | 513555841.3687
Cumilla Zone |  |  | 18417.345 | 0 | 836.505 | 0 | 0 | 0 | 1161.6 | 0 | 20415.45 | HFO | 6196.1628 | HFO | 116748971.18
Mymensingh Zone |  |  | 41.28 | 0 | 1821.12 | 0 | 0 | 104.38 | 0 | 0 | 1966.78 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 27441.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27441.134 | Hydro | 789 | Hydro | 78900
Khulna Zone |  |  | 6733.44 | 23585.45 | 19.712 | 0 | 0 | 418.32 | 19324.363 | 0 | 50081.285 | Solar | 1907.7947 | Solar | 22012234.152
Barishal Zone |  |  | 8169.612 | 16736.9091 | 204 | 0 | 0 | 2.369 | 0 | 0 | 25112.8901 | Import | 34267.817 | Import | 171864085.27
Rajshahi Zone |  |  | 12615.673 | 0 | 396.495 | 0 | 0 | 659.704 | 13781.854 | 0 | 27453.726 | Wind | 305.28 | Wind | 4396032
Rangpur Zone |  |  | 0 | 6500.654 | 55.349 | 0 | 0 | 246.8177 | 0 | 0 | 6802.8207
Total |  |  | 103006.897 | 70088.4663 | 6196.1628 | 0 | 789 | 1907.7947 | 34267.817 | 305.28 | 216561.4178
Cost of the consumed fuel (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 358352586.79 |  | Hydro | 78900
|  |  | Coal | 513555841.3687 |  | Solar | 22012234.152
|  |  | HFO | 116748971.18 |  | Import | 171864085.27
|  |  | HSD | 0 |  | Wind | 4396032
|  |  |  | Total: | 1187008650.7607 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Rangpur 20 MW GTPP |  |  | 20 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Baghabari 100 MW GTPP |  |  | 100 | 2 | Ashuganj 55 MW PP (Precision) |  |  | 55
| 3 | Barapukuria TPP Unit-2 |  |  | 85 | 3 | Sirajgonj 225MW CCPP Unit-1 GT |  |  | 150
| 4 | Siddhirgonj 210 MW TPP |  |  | 115
| 5 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 734 |  |  |  | Total | 240.09
|  |  | Total Unavailable Capacity |  |  |  | 974.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3687
|  |  | Chattogram |  | 0 |  | 1057
|  |  | Cumilla |  | 0 |  | 875
|  |  | Mymensingh |  | 0 |  | 823
|  |  | Sylhet |  | 0 |  | 364
|  |  | Khulna |  | 0 |  | 1183
|  |  | Barishal |  | 0 |  | 293
|  |  | Rajshahi |  | 0 |  | 931
|  |  | Rangpur |  | 0 |  | 722
|  |  | Total |  | 0 |  | 9935
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:13 |  | Amtoli-Payra(RNPL) CKT-2 is S/D.
08:19 | 18:27 | Baghabari-Sirajganj 230 kV Ckt-1 Scheduled S/D from Baghabari 230/132kV end Due to A/M
08:20 | 15:50 | Magura-Narail 132kV Ckt-1 Scheduled S/D from Magura 132/33kV end Due to Annual
Maintenance and from Narail 132/33kV end Due to Magura ckt-01 and it's associated
equipments annual maintenance work.
08:24 | 15:55 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Annual
maintenance work.
08:25 | 16:01 | Daudkandi-Sonargaon 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to annul
maintenance sonargoan ss end and from Sonargaon 132/33kV end Due to Annual maintenance
work by Siddhirganj
08:35 | 13:07 | Gopalganj 400/132kV S/S 400kV Amtoli Ckt-1 Forced S/D
08:41 | 15:45 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bhandaria 132/33kV end Due to Annual
maintenance.
08:50 | 12:20 | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to Schedule preventive maintenance.
08:54 | 17:27 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end Due to Yearly Ded
line Checking
08:54 | 12:40 | Barapukuria-Bogura 230 kV Ckt-1 Scheduled S/D from Barapukuria 230/132/33kV end. and from
Bogura 400/230kVend.
08:56 | 17:23 | Anowara-Sikalbaha 230 kV Ckt-2 Scheduled S/D from Shikalbaha 230/132kV end.
08:56 | 16:53 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to
Annual Maintenance and from Shahjibazar 132/33kV end Due to Annual Maitenance
08:57 |  | Siddirganj CCPP 335MW was SD due to Gas shortage.
09:22 |  | Summit Bibiana-2 341MW was SD due to gas shortage.
09:29 | 17:38 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 Project Work S/D from Mithapukur
132/33kV end.
09:29 | 17:38 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-2 Project Work S/D from Mithapukur
132/33kV end.
09:29 | 17:22 | Shikalbaha 230/132kV S/S Hathazari-02 Scheduled S/D
09:31 | 17:14 | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-2 Scheduled S/D
09:31 | 17:37 | Mahasthangar-Palashbari 132kV Ckt-2 Project Work S/D from Mahasthangarh 132/33kV end.
09:35 |  | Unique Meghnaghat STG tripped
09:37 | 16:40 | Kodda-Rajendrapur 132kV Ckt-1 Scheduled S/D from Rajendrapur 132/33kV end Due to Yearly
deadline checking of Kodda-Rajendrapur T/L.
09:43 |  | Chhatak 132/33kV S/S Bus-B Scheduled S/D Due to Annual Maintenance
09:45 | 17:37 | Mahasthangar-Palashbari 132kV Ckt-2 Project Work S/D from Palashbari 132/33kV end Due to
project work
09:49 |  | Chhatak 132/33kV S/S T-2 HT Forced S/D Due to DS 412S Maintainnance
09:50 |  | Chhatak 132/33kV S/S T-2 LT Forced S/D Due to Annual Maintainnance 132kv DS Maintenance
09:56 | 20:05 | Sunamganj 132/33kV S/S Tr-1 LT Scheduled S/D
09:56 | 20:01 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D
09:57 | 15:49 | Ghatail 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance
10:08 | 19:59 | Sunamganj 132/33kV S/S Main Bus -2 Scheduled S/D
| 10:43 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT is restored.
12:00 |  | Day peak Generation is 9764 MW
12:17 | 12:39 | Gulshan 132/33kV S/S MT-1 LT Project Work S/D Due to Metering Division Work.
12:18 | 12:37 | Gulshan 132/33kV S/S MT-1 HT Project Work S/D Due to Metering Division Work.
12:30 | 16:08 | KSRM 132/33kV S/S Transformer-02 HT Scheduled S/D Due to Schedule Preventive Maintenance
work.
13:12 | 19:15 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Forced S/D Due to T-2 transformer CT test
both side ( energy meter reading problem )
13:13 | 19:13 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Forced S/D Due to T-2 transformer CT test
both side ( energy meter reading problem )
| 13:46 | Hasnabad 230/132kV S/S Bus-2 is restored.
| 14:47 | Khulshi-MSML 132kV Ckt-2 is restored.
16:14 | 17:23 | KSRM 132/33kV S/S Transformer-03 LT Scheduled S/D Due to schedule Preventive maintenance.
| 17:05 | Gopalganj 400/132kV S/S 230kV Barisal CKT-02 is restored.
| 17:05 | Barishal 230/132kV S/S Gopalgonj CKT-2 is restored.
18:00 |  | Evening Peak Generation: 10336 MW.
22:32 |  | Unique Meghnaghat Power 584 MW CCPP ST was synchronized.
22:38 |  | From NLDC: Chandpur CCPP was shut down.
05:00 |  | Min. Gen. 6826 MW
06:57 |  | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 Project Work S/D from Mithapukur
132/33kV end Due to Project work.
06:57 |  | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-2 Project Work S/D from Mithapukur
132/33kV end Due to Project work.
06:58 |  | Mahasthangar-Palashbari 132kV Ckt-2 Project Work S/D from Mahasthangarh 132/33kV end Due
to Palashbari grid project work . and from Palashbari 132/33kVend.
07:31 |  | Gopalganj 400/132kV S/S 230kV Barisal CKT-02 Scheduled S/D
07:36 |  | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Work on other
side.
07:38 |  | Bhulta-Haripur 230 kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Work on other
side.
07:55 |  | Magura-Narail 132kV Ckt-1 Scheduled S/D from Narail 132/33kV end Due to Narail magura
ckt 01 annual maintenance running. and from Magura 132/33kV end Due to Annual
Maintenance.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 234.58 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Default availability set by nldc
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | Default availability set by nldc
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 291 | 6904800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9459000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | Default availability set by nldc
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 0 | Default availability set by nldc
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 1483292 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 8064 | Default availability set by nldc
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 27072 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149 | 32 | 72000 | Default availability set by nldc
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 27176 | Default availability set by nldc
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 52861 | Default availability set by nldc
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 399000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 528480 | Default availability set by nldc
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 534960 | Default availability set by nldc
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 24 | 591900 | Default availability set by nldc
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 34 | 241685 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Default availability set by nldc
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | Default availability set by nldc
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 23328 | Default availability set by nldc
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1024176 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 8 | 7296 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 172800 | Default availability set by nldc
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 154804 | Default availability set by nldc
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 17 | 196560 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 160 | 3663636 | Machine Problem
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Default availability set by nldc
Dhaka Area Total |  |  |  |  | 6940.42 | 1310 | 25572890
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Default availability set by nldc
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 2 | 3106.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 112995 | Default availability set by nldc
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 30 | 161760 | Default availability set by nldc
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 789000 | Default availability set by nldc
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5261585 | Default availability set by nldc
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 35963 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 54174 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 35 | 95032 | Default availability set by nldc
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 11520 | Default availability set by nldc
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 33 | 31 | 761760 | Default availability set by nldc
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 8 | 10560 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20641 | Default availability set by nldc
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 166855 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 18 | 163103 | Default availability set by nldc
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 12 | 31780 | Default availability set by nldc
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 45120 | Default availability set by nldc
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 30 | 149027 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 72 | 81963 | -
55 | SS Power |  | IPP | 2*660 | 1320 | 598 | 11083635 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 66 | 8 | 305280 | Default availability set by nldc
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 575 | 12181818.18 | U1 S/D 09/Oct/24 (Maintenance Work)
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 187764 | Default availability set by nldc
Chattogram Area Total |  |  |  |  | 5064.22 | 1798 | 31714441.98
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 180 | 4511000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 356.15 | 315 | 7826000 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | -
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.96 | 45 | 33 | 652968 | Default availability set by nldc
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 521280 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 2994182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 883685 | Default availability set by nldc
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 45 | 194036 | Default availability set by nldc
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 24 | 26288 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 20 | 780370 | Default availability set by nldc
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 27840 | Default availability set by nldc
| Import (Tripura) |  | Import | 0 | 160 | 54 | 1161600 | Default availability set by nldc
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 16541 | Default availability set by nldc
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 5 | 247860 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Default availability set by nldc
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 42 | 456960 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 30 | 83520 | -
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 31320 | -
Cumilla Area Total |  |  |  |  | 2881.85 | 1055 | 20415450
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 41280 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 3 | 0 | 2750 | Default availability set by nldc
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 94 | 768000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 18 | 908400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 101630 | Default availability set by nldc
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 144720 | Ready to Dispatch as per NLDC Demand.
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 150 | 0 | 0 | Default availability set by nldc
Mymensingh Area Total |  |  |  |  | 750 | 134 | 1966780
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 231000 | Default availability set by nldc
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Default availability set by nldc
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3705300 | Default availability set by nldc
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Default availability set by nldc
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 11232 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 57024 | Default availability set by nldc
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 161376 | Default availability set by nldc
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 42 | 707520 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Default availability set by nldc
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 206 | 5236790 | Default availability set by nldc
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Default availability set by nldc
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 122832 | Default availability set by nldc
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 2575560 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 343 | 8123000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 300 | 6509500 | -
Sylhet Area Total |  |  |  |  | 2366 | 1056 | 27441134
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Default availability set by nldc
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 627 | 19324363 | Default availability set by nldc
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 17280 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | Default availability set by nldc
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 5 | 2432 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 283 | 6733440 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 418320 | Default availability set by nldc
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | Default availability set by nldc
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234 | 1103 | 23585450 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | Default availability set by nldc
Khulna Area Total |  |  |  |  | 3739 | 2047 | 50081285
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Default availability set by nldc
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 54632 | Default availability set by nldc
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 130 | 2804000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 510 | 11282909.09 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5310980 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 45 | 204000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 300 | 5454000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2369 | Default availability set by nldc
Barishal Area Total |  |  |  |  | 2266 | 1212 | 25112890.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 41402 | Default availability set by nldc
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Default availability set by nldc
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Default availability set by nldc
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 29491 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 159 | 3910000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4187036 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4369273 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 414 | 0 | 0 | Default availability set by nldc
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 24226 | Default availability set by nldc
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 8.5 | 149364 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 301376 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 11460 | Default availability set by nldc
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 680 | 13781854 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 124504 | Default availability set by nldc
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 523740 | Default availability set by nldc
Rajshahi Area Total |  |  |  |  | 3411.72 | 1412.5 | 27453726
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 78 | 1836654 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4664000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Default availability set by nldc
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Default availability set by nldc
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 7371.72 | Default availability set by nldc
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 34 | 55349 | Default availability set by nldc
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 34316 | Default availability set by nldc
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 205130 | Default availability set by nldc
Rangpur Area Total |  |  |  |  | 950 | 312 | 6802820.72
Eastern Grid Total |  |  |  |  | 18002.49 | 5353 | 107110695.98
Western Grid Total |  |  |  |  | 10366.72 | 4983.5 | 109450721.81
National Grid Total |  |  |  |  | 28369.21 | 10336.5 | 216561417.79
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-01-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6806.05 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3129.2 | MW
i) Dhaka area |  |  | 3687.15 |  | MW | i) Khulna area |  |  |  | 1183 | MW
ii) Chattogram area |  |  | 1056.9 |  | MW | ii) Barishal area |  |  |  | 293 | MW
iii) Cumilla area |  |  | 875 |  | MW | iii) Rajshahi area |  |  |  | 931.2 | MW
iv) Mymensingh area |  |  | 823 |  | MW | iv) Rangpur area |  |  |  | 722 | MW
v) Sylhet area |  |  | 364 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9935.25 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 102 | 18:30 | 133 | Rahanpur | 0 | 00:00
2 | AKSML | 107 | 10:00 | 68 | Jashore | 90 | 18:00 | 134 | Rahim | 48 | 12:00
3 | Aftabnagar | 22 | 13:00 | 69 | Jhenaidah | 92 | 18:00 | 135 | Rajbari | 54 | 18:00
4 | Agargaon | 71 | 13:00 | 70 | Joydebpur | 129 | 19:00 | 136 | Rajendrapur | 94 | 10:00
5 | Agrabad | 58 | 18:00 | 71 | Joypurhat | 38 | 20:00 | 137 | Rajshahi | 93 | 13:00
6 | Amnura | 47 | 19:30 | 72 | Juldah | 8 | 21:00 | 138 | Rajshahi-230 | 38 | 13:00
7 | Ashuganj | 59 | 13:00 | 73 | KSRM | 23 | 02:00 | 139 | Ramganj | 90 | 19:00
8 | BSRM | 196 | 09:00 | 74 | Kabirpur | 210 | 18:00 | 140 | Rampur | 22 | 00:00
9 | Bagerhat | 71 | 18:00 | 75 | Kachua | 42 | 19:00 | 141 | Rangamati | 12 | 18:00
10 | Bakulia | 63 | 18:00 | 76 | Kallyanpur | 48 | 09:00 | 142 | Rangpur | 114 | 13:00
11 | Banani | 38 | 13:00 | 77 | Kalurghat | 25 | 12:00 | 143 | Ruppur | 2.4 | 00:00
12 | Bangabhaban | 8 | 10:00 | 78 | Kamrangirchar | 48.4 | 13:00 | 144 | SSM | 10 | 01:00
13 | Barapukuria | 44 | 18:30 | 79 | Kaptai | N/A | N/A | 145 | Saidpur | 88 | 18:00
14 | Barguna | 14 | 19:30 | 80 | Kazla | 81 | 13:00 | 146 | Satkhira | 86 | 18:30
15 | Barishal | 82 | 13:00 | 81 | Keranigonj | 56 | 13:00 | 147 | Satmasjid | 77 | 13:00
16 | Barishal-230 | 60 | 18:00 | 82 | Khagrachori | 24 | 18:00 | 148 | Savar | 170 | 10:00
17 | Baroaulia | 48 | 09:00 | 83 | Khulna | 66 | 13:00 | 149 | SevenRings | 14.44 | 21:00
18 | Baroirhat | 44 | 18:00 | 84 | Khulshi | 134 | 17:00 | 150 | ShahCement | 32 | 11:00
19 | Bashundhara | 113 | 13:00 | 85 | Kishoreganj | 114 | 18:00 | 151 | Shahjadpur | 55 | 19:00
20 | BashundharaCement | 7 | 09:00 | 86 | Kodda | 249 | 10:00 | 152 | Shahjibazar | 68 | 18:00
21 | Beanibazar | 43 | 18:00 | 87 | Kulaura | 26 | 13:00 | 153 | Shahmirpur | 29 | 18:00
22 | Benapole | 44 | 08:00 | 88 | Kurigram | 44 | 08:00 | 154 | Shariatpur | 50 | 20:00
23 | Bhaluka | 108 | 15:00 | 89 | Kushtia | 92 | 18:00 | 155 | Sherpur | 104 | 18:00
24 | Bhandaria | 33.8 | 21:00 | 90 | Lalbag | 64 | 13:00 | 156 | Shikalbaha | 17 | 00:00
25 | Bhangura | 22 | 18:00 | 91 | Lalmonirhat | 41 | 18:00 | 157 | Shitalakhya | 56.8 | 13:00
26 | Bheramara(GK) | 40 | 18:00 | 92 | MI_Cement | 17.7 | 02:00 | 158 | Sholosohor | 28 | 14:00
27 | Bhulta | 255 | 11:00 | 93 | Madanganj | 24 | 00:00 | 159 | Shyampur | 148 | 13:00
28 | Bog-Sherpur | 54 | 18:00 | 94 | Madaripur | 65 | 20:00 | 160 | Siddhirganj | 94 | 14:00
29 | Bogura | 102 | 18:30 | 95 | Madartek | 56.1 | 13:00 | 161 | Sirajganj | 74 | 19:00
30 | Borhanuddin | 54 | 00:00 | 96 | Madunaghat | 32 | 13:00 | 162 | Sonargaon | 68 | 02:00
31 | Brahmanbaria | 105 | 18:00 | 97 | Magura | 43 | 18:00 | 163 | Sreemongol | 49 | 18:00
32 | Cantonment | 78 | 13:00 | 98 | Mahasthangarh | 50 | 18:00 | 164 | Sreepur | 69 | 12:00
33 | Chandpur | 43 | 20:00 | 99 | Manikganj | 85 | 18:30 | 165 | Srinagar | 28.4 | 14:00
34 | Chandraghona | 26 | 18:00 | 100 | Maniknagar | 44 | 13:00 | 166 | Sunamganj | 36 | 21:00
35 | Chapai | 51 | 12:00 | 101 | Matarbari | 33 | 18:00 | 167 | Sylhet | 28 | 14:00
36 | Charsaidpur | 44 | 00:00 | 102 | Matuail | 43 | 10:00 | 168 | Sylhet-132 | 73 | 13:00
37 | Chauddagram | 35 | 19:30 | 103 | Millgate | 71 | 12:00 | 169 | TK | 18.4 | 13:00
38 | Chhatak | 20 | 18:00 | 104 | Mirpur | 79 | 12:00 | 170 | Tangail | 148 | 21:00
39 | Chowmuhani | 132 | 18:00 | 105 | Mirsorai | 8 | 12:00 | 171 | Thakurgaon | 74 | 18:00
40 | Chuadanga | 69 | 13:00 | 106 | Mirzapur | 32 | 18:00 | 172 | Tongi | 98 | 11:00
41 | Coxsbazar | 90 | 18:00 | 107 | Mithapukur | 42 | 18:00 | 173 | Ullahpara | 20 | 18:00
42 | Cumilla(N) | 104 | 18:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 34 | 13:00
43 | Cumilla(S) | 117 | 13:00 | 109 | Mogbazar | 76.6 | 13:00 | 175 | Uttara | 47 | 13:00
44 | Daudkandi | 104 | 18:00 | 110 | Mongla | 30 | 07:00 | 176 | UttaraNew | 42 | 23:00
45 | Dhaka | 32 | 13:00 | 111 | Motijheel | 24 | 13:00 | 177 | Zigatola | 64 | 14:00
46 | Dhamrai | 100 | 19:00 | 112 | Munshiganj | 66 | 13:00
47 | Dhanmondi | 91 | 13:00 | 113 | Mymensingh | 162 | 13:00
48 | Dohazari | 80 | 19:30 | 114 | Naogaon | 82 | 13:00
49 | Faridpur | 107 | 18:00 | 115 | Narail | 38 | 18:00
50 | Fatullah | 76 | 10:00 | 116 | Narinda | 49 | 13:00
51 | Fenchuganj | 25 | 18:00 | 117 | Narshingdi | 151 | 20:00
52 | Feni | 74 | 18:00 | 118 | Natore | 96 | 18:00
53 | GPH | 27 | 11:00 | 119 | Nawabganj | 27.6 | 20:00
54 | Ghatail | 0 | 00:00 | 120 | Netrakona | 104 | 18:00
55 | Ghorashal | 8 | 14:00 | 121 | New | 65.6 | 12:00
56 | Ghorashal-230 | 42 | 18:30 | 122 | Niamatpur | 50 | 13:00
57 | Goalpara | 26 | 13:00 | 123 | Noapara | 33 | 18:00
58 | Gollamari | 48 | 13:00 | 124 | PHP | 3 | 00:00
59 | Gopalganj | 73 | 18:00 | 125 | Pabna | 79 | 18:00
60 | Gulshan | 58 | 13:00 | 126 | Palashbari | 74 | 18:00
61 | Halishahar | 32 | 13:00 | 127 | Panchagarh | 45 | 18:00
62 | HaripurSBU | 150 | 12:00 | 128 | Patuakhali | 53.5 | 21:00
63 | Hasnabad | 63 | 12:00 | 129 | Payra | 20 | 00:00
64 | Hathazari | 52 | 18:00 | 130 | Postogola | 39 | 13:00
65 | Ishurdi | 50 | 18:30 | 131 | Purbachal | 13 | 13:00
66 | Jaldhaka | 59 | 18:00 | 132 | Purbasadipur | 105 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8480.56 | 0 |  | 8480.56
1:00 | 8104.95 | 0 |  | 8104.95
2:00 | 7692.73 | 0 |  | 7692.73
3:00 | 7351.72 | 0 |  | 7351.72
4:00 | 7083.25 | 0 |  | 7083.25
5:00 | 6952.51 | 0 |  | 6952.51
6:00 | 7383.48 | 0 |  | 7383.48
7:00 | 8039.58 | 0 |  | 8039.58
8:00 | 8900.17 | 0 |  | 8900.17
9:00 | 9338.76 | 0 |  | 9338.76
10:00 | 9051.41 | 0 |  | 9051.41
11:00 | 9274.45 | 0 |  | 9274.45
12:00 | 9767.78 | 0 |  | 9767.78
13:00 | 10090.44 | 0 |  | 10090.44
14:00 | 9534.32 | 0 |  | 9534.32
15:00 | 9204.45 | 0 |  | 9204.45
16:00 | 8831.81 | 0 |  | 8831.81
17:00 | 9176.95 | 0 |  | 9176.95
18:00 | 10336.5 | 0 |  | 10336.5
19:00 | 10118.5 | 0 |  | 10118.5
19:30 | 10107.5 | 0 |  | 10107.5
20:00 | 9970.5 | 0 |  | 9970.5
21:00 | 9829.5 | 0 |  | 9829.5
22:00 | 9430.5 | 0 |  | 9430.5
23:00 | 8898.5 | 0 |  | 8898.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2025-01-01 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
Aminbazar | 406 | 05:00 | 387 | 12:00 | Kaliakoir | 378 | 05:00 | 362 | 12:00
Ashuganj | 408 | 5:00 | 395 | 12:00 | Madunaghat | 405 | 03:00 | 394 | 13:00
Bhulta | 399 | 04:00 | 384 | 12:00 | Meghnaghat | 398 | 05:00 | 385 | 12:00
Bibiana | 394 | 04:00 | 386 | 17:00 | Payra | 416 | 05:00 | 409 | 09:00
BIPTC | 409 | 05:00 | 389 | 11:00 | Rahanpur | 416 | 05:00 | 401 | 08:00
Bogura | 410 | 04:00 | 395 | 18:30 | Rampal | 410 | 05:00 | 395 | 13:00
Gopalganj | 411 | 05:00 | 396 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Agargaon | 235 | 03:00 | 219 | 13:00 | Haripur | 238 | 03:00 | 228 | 13:00
AKSML | 234 | 03:00 | 224 | 15:00 | Hasnabad | 234 | 03:00 | 221 | 13:00
Aminbazar | 256 | 16:00 | 220 | 11:00 | Hathazari | 233 | 01:00 | 224 | 05:00
Ashuganj | 237 | 00:00 | 228 | 12:00 | Ishurdi | 244 | 03:00 | 229 | 13:00
Ashuganj-400 | N/A | N/A | N/A | N/A | Jhenaidah | 241 | 03:00 | 225 | 13:00
Baghabari | 242 | 05:00 | 230 | 12:00 | Kaliakoir | 237 | 05:00 | 223 | 12:00
Barapukuria | 226 | 02:00 | 215 | 12:00 | Keranigonj | 235 | 03:00 | 219 | 13:00
Barapukuria-230 | 226 | 02:00 | 215 | 12:00 | Khulna(S) | 241 | 03:00 | 226 | 13:00
Barishal | 244 | 04:00 | 237 | 12:00 | Madunaghat | 231 | 18:00 | 224 | 13:00
Bheramara | 241 | 03:00 | 227 | 13:00 | Madunaghat-400 | 233 | 03:00 | 225 | 13:00
Bhulta | 237 | 04:00 | 224 | 12:00 | Maniknagar | 236 | 04:00 | 223 | 12:00
Bibiana | 228 | 06:00 | 220 | 13:00 | Meghnaghat | 242 | 00:00 | 230 | 13:00
BIPTC | 243 | 03:00 | 227 | 13:00 | Meghnaghat-400 | 239 | 03:00 | 226 | 12:00
Bogura | 239 | 02:00 | 229 | 13:00 | Mirsorai | 233 | 02:00 | 220 | 13:00
Bogura-400 | 239 | 03:00 | 227 | 13:00 | Rajshahi | 243 | 03:00 | 228 | 13:00
Borhanuddin | 247 | 05:00 | 243 | 12:00 | Rampal | 238 | 04:00 | 223 | 13:00
BSRM | 232 | 01:00 | 222 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Cumilla(N) | 232 | 04:00 | 220 | 13:00 | Rampura | 237 | 04:00 | 222 | 12:00
Faridpur | 245 | 03:00 | 233 | 12:00 | Shikalbaha | 232 | 04:00 | 222 | 13:00
Fenchuganj | 232 | 01:00 | 225 | 12:00 | Shyampur | 236 | 03:00 | 223 | 12:00
Ghorashal | 230 | 00:00 | 230 | 00:00 | Siddhirganj | 236 | 00:00 | 223 | 09:00
Ghorashal-230 | 236 | 03:00 | 221 | 13:00 | Sirajgonj | 246 | 05:00 | 238 | 12:00
Gopalganj | 244 | 02:00 | 232 | 12:00 | Sreepur | 239 | 01:00 | 229 | 12:00
GPH | 232 | 01:00 | 221 | 13:00 | Tongi | 235 | 05:00 | 220 | 12:00
132 KV | KV |  | KV |  | 132 KV | KV |  | KV
Aftabnagar | 135 | 02:00 | 125 | 12:00 | Kushtia | 140 | 02:00 | 133 | 13:00
Agargaon | 137 | 03:00 | 127 | 13:00 | Lalbag | 135 | 03:00 | 125 | 13:00
Agrabad | 134 | 01:00 | 128 | 13:00 | Lalmonirhat | 131 | 04:00 | 120 | 18:00
AKS | 131 | 18:00 | 127 | 12:00 | Madanganj | 132 | 03:00 | 124 | 13:00
Aminbazar | 136 | 03:00 | 126 | 11:00 | Madaripur | 135 | 03:00 | 130 | 12:00
Amnura | 141 | 18:00 | 131 | 13:00 | Madartek | 134 | 03:00 | 125 | 12:00
Ashuganj | 140 | 00:00 | 137 | 12:00 | Madunaghat | 134 | 18:00 | 128 | 13:00
Bagerhat | 137 | 03:00 | 130 | 09:00 | Magura | 141 | 01:00 | 131 | 12:00
Bakulia | 133 | 03:00 | 127 | 13:00 | Mahasthangarh | 137 | 03:00 | 129 | 09:00
Banani | 135 | 03:00 | 124 | 12:00 | Manikganj | 132 | 02:00 | 124 | 12:00
Bangabhaban | 136 | 04:00 | 126 | 12:00 | Maniknagar | 135 | 01:00 | 125 | 13:00
Barapukuria | 136 | 02:00 | 127 | 09:00 | Matarbari | 128 | 00:00 | 122 | 19:00
Barguna | 137 | 03:00 | 130 | 13:00 | Matuail | 134 | 02:00 | 126 | 12:00
Barishal | 136 | 02:00 | 130 | 12:00 | Millgate | 134 | 02:00 | 124 | 12:00
Barishal-230 | 134 | 00:00 | 131 | 12:00 | Mirpur | 138 | 06:00 | 126 | 12:00
Baroaulia | 134 | 18:00 | 129 | 12:00 | Mirzapur | 129 | 03:00 | 121 | 12:00
Baroirhat | 131 | 17:00 | 125 | 12:00 | Mithapukur | 134 | 01:00 | 124 | 08:00
Bashundhara | 135 | 03:00 | 125 | 12:00 | MI_Cement | 134 | 03:00 | 126 | 12:00
BashundharaCement | 132 | 03:00 | 124 | 13:00 | Modern | 135 | 01:00 | 125 | 13:00
Beanibazar | 134 | 01:00 | 131 | 12:00 | Mogbazar | 136 | 04:00 | 125 | 12:00
Benapole | 137 | 03:00 | 127 | 13:00 | Mongla | 137 | 02:00 | 128 | 12:00
Bhaluka | 129 | 04:00 | 122 | 12:00 | Motijheel | 136 | 04:00 | 126 | 12:00
Bhandaria | 133 | 04:00 | 129 | 21:00 | Munshiganj | 133 | 04:00 | 126 | 11:00
Bhangura | 141 | 03:00 | 132 | 13:00 | Mymensingh | 133 | 19:30 | 116 | 00:00
Bheramara | 140 | 02:00 | 134 | 12:00 | Naogaon | 136 | 04:00 | 128 | 13:00
Bheramara(GK) | 139 | 00:00 | 135 | 12:00 | Narail | 141 | 03:00 | 129 | 13:00
Bhulta | 126 | 04:00 | 120 | 11:00 | Narinda | 135 | 01:00 | 125 | 13:00
Bog-Sherpur | 138 | 03:00 | 130 | 12:00 | Narshingdi | 130 | 03:00 | 124 | 09:00
Bogura | 138 | 04:00 | 131 | 19:00 | Natore | 137 | 00:00 | 133 | 19:00
Bogura-230 | 138 | 01:00 | 131 | 12:00 | Nawabganj | 135 | 05:00 | 125 | 13:00
Brahmanbaria | 132 | 00:00 | 128 | 10:00 | Netrakona | 130 | 02:00 | 121 | 18:00
Cantonment | 137 | 02:00 | 127 | 13:00 | New | 134 | 02:00 | 126 | 12:00
Chandpur | 128 | 17:00 | 120 | 13:00 | Niamatpur | 140 | 01:00 | 135 | 12:00
Chandraghona | 135 | 03:00 | 129 | 13:00 | Noapara | 139 | 03:00 | 128 | 13:00
Chapai | 139 | 01:00 | 132 | 13:00 | Pabna | 141 | 03:00 | 132 | 13:00
Charsaidpur | 133 | 01:00 | 126 | 12:00 | Palashbari | 132 | 02:00 | 124 | 09:00
Chauddagram | 132 | 01:00 | 126 | 13:00 | Panchagarh | 137 | 04:00 | 118 | 09:00
Chhatak | 134 | 00:00 | 131 | 12:00 | Patuakhali | 136 | 17:00 | 131 | 13:00
Chowmuhani | 125 | 18:00 | 120 | 00:00 | Payra | 138 | 03:00 | 133 | 13:00
Chuadanga | 140 | 04:00 | 127 | 13:00 | PHP | 131 | 02:00 | 122 | 13:00
Coxsbazar | 128 | 01:00 | 122 | 12:00 | Postogola | 136 | 04:00 | 127 | 13:00
Cumilla(N) | 135 | 05:00 | 128 | 13:00 | Purbachal | 135 | 01:00 | 124 | 12:00
Cumilla(S) | 135 | 02:00 | 127 | 13:00 | Purbasadipur | 132 | 04:00 | 118 | 09:00
Daudkandi | 133 | 05:00 | 125 | 12:00 | Rahanpur | 140 | 01:00 | 136 | 13:00
Dhaka | 135 | 03:00 | 125 | 12:00 | Rahanpur-400 | 140 | 00:00 | 136 | 12:00
Dhamrai | 137 | 03:00 | 129 | 12:00 | Rahim | 133 | 02:00 | 124 | 13:00
Dhanmondi | 135 | 04:00 | 127 | 12:00 | Rajbari | 136 | 03:00 | 128 | 13:00
Dohazari | 131 | 00:00 | 126 | 13:00 | Rajendrapur | 136 | 18:00 | 126 | 13:00
Faridpur | 135 | 01:00 | 130 | 12:00 | Rajshahi | 138 | 00:00 | 133 | 12:00
Fatullah | 135 | 03:00 | 126 | 12:00 | Rajshahi-230 | 140 | 02:00 | 130 | 12:00
Fenchuganj | 137 | 00:00 | 134 | 12:00 | Ramganj | 126 | 06:00 | 118 | 12:00
Feni | 130 | 05:00 | 123 | 13:00 | Rampur | 135 | 04:00 | 127 | 13:00
Ghatail | 132 | 19:30 | 119 | 02:00 | Rampura | 135 | 03:00 | 125 | 12:00
Ghorashal | 140 | 07:00 | 138 | 01:00 | Rangamati | 134 | 02:00 | 128 | 12:00
Goalpara | 141 | 03:00 | 131 | 13:00 | Rangpur | 133 | 03:00 | 121 | 09:00
Gollamari | 139 | 03:00 | 131 | 13:00 | Ruppur | 142 | 03:00 | 134 | 20:00
Gopalganj | 138 | 03:00 | 130 | 12:00 | Saidpur | 133 | 05:00 | 120 | 09:00
Gopalganj-400 | 137 | 02:00 | 130 | 12:00 | Satkhira | 137 | 03:00 | 129 | 12:00
Gulshan | 133 | 04:00 | 124 | 12:00 | Satmasjid | 136 | 02:00 | 126 | 13:00
Halishahar | 135 | 06:00 | 128 | 13:00 | Savar | 133 | 00:00 | 126 | 12:00
Haripur | 134 | 04:00 | 125 | 12:00 | SevenRings | 141 | 02:00 | 135 | 12:00
HaripurSBU | 134 | 02:00 | 126 | 12:00 | ShahCement | 133 | 01:00 | 126 | 12:00
Hasnabad | 135 | 01:00 | 127 | 12:00 | Shahjadpur | 142 | 00:00 | 136 | 09:00
Hathazari | 136 | 18:00 | 131 | 12:00 | Shahjibazar | 133 | 00:00 | 130 | 12:00
Ishurdi | 143 | 03:00 | 135 | 13:00 | Shahmirpur | 134 | 03:00 | 129 | 11:00
Jaldhaka | 132 | 03:00 | 118 | 09:00 | Shariatpur | 137 | 03:00 | 130 | 12:00
Jamalpur | 136 | 19:30 | 115 | 00:00 | Sherpur | 135 | 19:30 | 113 | 00:00
Jashore | 138 | 03:00 | 128 | 12:00 | Shikalbaha | 123 | 00:00 | 117 | 13:00
Jhenaidah | 139 | 00:00 | 132 | 13:00 | Shikalbaha-230 | 138 | 02:00 | 129 | 13:00
Jhenaidah-230 | 142 | 03:00 | 131 | 13:00 | Shitalakhya | 134 | 03:00 | 127 | 11:00
Joydebpur | 140 | 17:00 | 130 | 12:00 | Sholosohor | 134 | 03:00 | 128 | 13:00
Joypurhat | 136 | 01:00 | 128 | 12:00 | Shyampur | 131 | 00:00 | 125 | 13:00
Juldah | 133 | 05:00 | 129 | 11:00 | Shyampur-230 | 134 | 03:00 | 125 | 12:00
Kabirpur | 133 | 01:00 | 121 | 12:00 | Siddhirganj | 133 | 01:00 | 127 | 11:00
Kachua | 131 | 17:00 | 124 | 13:00 | Sirajganj | 140 | 03:00 | 130 | 12:00
Kaliakoir | 138 | 02:00 | 124 | 12:00 | Sonargaon | 133 | 05:00 | 127 | 10:00
Kallyanpur | 134 | 04:00 | 127 | 12:00 | Sreemongol | 134 | 03:00 | 130 | 11:00
Kalurghat | 134 | 03:00 | 127 | 13:00 | Sreepur | 130 | 01:00 | 124 | 13:00
Kamrangirchar | 134 | 01:00 | 126 | 12:00 | Srinagar | 135 | 06:00 | 127 | 12:00
Kaptai | 135 | 0.083333 | 126 | 0.5 | SSM | 138 | 18:00 | 132 | 12:00
Kazla | 136 | 04:00 | 125 | 13:00 | Sunamganj | 133 | 01:00 | 130 | 12:00
Keranigonj | 135 | 03:00 | 125 | 13:00 | Sylhet | 135 | 01:00 | 131 | 13:00
Khagrachori | 134 | 03:00 | 127 | 13:00 | Sylhet-132 | 134 | 00:00 | 131 | 12:00
Khulna | 137 | 01:00 | 129 | 13:00 | Tangail | 129 | 17:00 | 120 | 22:00
Khulna(S) | 140 | 02:00 | 131 | 13:00 | Thakurgaon | 133 | 03:00 | 115 | 09:00
Khulshi | 132 | 02:00 | 123 | 08:00 | TK | 134 | 18:00 | 129 | 12:00
Kishoreganj | 134 | 17:00 | 129 | 09:00 | Tongi | 135 | 03:00 | 127 | 12:00
Kodda | 138 | 17:00 | 119 | 12:00 | Ullahpara | 140 | 01:00 | 132 | 11:00
KSRM | 137 | 02:00 | 129 | 12:00 | Ullon | 133 | 00:00 | 125 | 12:00
Kulaura | 138 | 05:00 | 133 | 13:00 | Uttara | 136 | 04:00 | 127 | 12:00
Kurigram | 131 | 03:00 | 119 | 09:00 | UttaraNew | 136 | 02:00 | 125 | 13:00
Zigatola | 135 | 04:00 | 126 | 12:00
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
QF-LDC-11
Date | 01-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4412 | 4068.56 | 8480.56 | DAILY LOAD CURVE
00:30 | 4294.5 | 3998.255 | 8292.755
01:00 | 4177 | 3927.95 | 8104.95 | 01-01-2025
01:30 | 4105 | 3793.84 | 7898.84
02:00 | 4033 | 3659.73 | 7692.73
02:30 | 3920 | 3602.225 | 7522.225
03:00 | 3807 | 3544.72 | 7351.72
03:30 | 3749.5 | 3467.985 | 7217.485
04:00 | 3692 | 3391.25 | 7083.25
04:30 | 3681.5 | 3336.38 | 7017.88
05:00 | 3671 | 3281.51 | 6952.51
05:30 | 3800.5 | 3367.495 | 7167.995
06:00 | 3930 | 3453.48 | 7383.48
06:30 | 4116.025 | 3595.505 | 7711.53
07:00 | 4302.05 | 3737.53 | 8039.58
07:30 | 4417.85 | 4052.025 | 8469.875
08:00 | 4533.65 | 4366.52 | 8900.17
08:30 | 4553.905 | 4565.56 | 9119.465
09:00 | 4574.16 | 4764.6 | 9338.76
09:30 | 4418.63 | 4776.455 | 9195.085
10:00 | 4263.1 | 4788.31 | 9051.41
10:30 | 4293.78 | 4869.15 | 9162.93
11:00 | 4324.46 | 4949.99 | 9274.45
11:30 | 4505.31 | 5015.805 | 9521.115
12:00 | 4686.16 | 5081.62 | 9767.78
12:30 | 4748.585 | 5180.525 | 9929.11
13:00 | 4811.01 | 5279.43 | 10090.44
13:30 | 4720.195 | 5092.185 | 9812.38
14:00 | 4629.38 | 4904.94 | 9534.32
14:30 | 4583.77 | 4785.615 | 9369.385
15:00 | 4538.16 | 4666.29 | 9204.45
15:30 | 4490.58 | 4527.55 | 9018.13
16:00 | 4443 | 4388.81 | 8831.81
16:30 | 4517.13 | 4487.25 | 9004.38
17:00 | 4591.26 | 4585.69 | 9176.95
17:30 | 4972.13 | 4784.595 | 9756.725
18:00 | 5353 | 4983.5 | 10336.5
18:30 | 5141.5 | 5086 | 10227.5
19:00 | 4930 | 5188.5 | 10118.5
19:30 | 4922 | 5185.5 | 10107.5
20:00 | 4812 | 5158.5 | 9970.5
20:30 | 4659 | 5241 | 9900 |  | Executive Engineer
21:00 | 4506 | 5323.5 | 9829.5 |  | Network Operation Division
21:30 | 4440.5 | 5189.5 | 9630
22:00 | 4375 | 5055.5 | 9430.5
22:30 | 4267.5 | 4897 | 9164.5
23:00 | 4160 | 4738.5 | 8898.5

## En-Curve
QF-LDC-12
Date | 01-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3001 | 1514 | 909 | 0 | 48 | 545.56 | 46 | 2371 | 0 | 17 | 0 | 0 | 0 | 29 | 0 | DAILY ENERGY CURVE
00:30 | 2965.5 | 1536.75 | 909.5 | 0 | 46 | 511.005 | 36 | 2255 | 0 | 8.5 | 0 | 0 | 0 | 24.5 | 0 | 01-01-2025
01:00 | 2930 | 1559.5 | 910 | 0 | 44 | 476.45 | 26 | 2139 | 0 | 0 | 0 | 0 | 0 | 20 | 0
01:30 | 2903.5 | 1508.5 | 815.5 | 0 | 43 | 448.34 | 26 | 2135 | 0 | 0 | 0 | 0 | 0 | 19 | 0 |  | Total Energy | 216.5614 |  | MKWHr
02:00 | 2877 | 1457.5 | 721 | 0 | 42 | 420.23 | 26 | 2131 | 0 | 0 | 0 | 0 | 0 | 18 | 0 |  | Energy not Served | 0 |  | MKWHr
02:30 | 2792.5 | 1385.5 | 721.5 | 0 | 41 | 418.225 | 26 | 2118 | 0 | 0 | 0 | 0 | 0 | 19.5 | 0 |  | Energy Requirement | 216.5614 |  | MKWHr
03:00 | 2708 | 1313.5 | 722 | 0 | 40 | 416.22 | 26 | 2105 | 0 | 0 | 0 | 0 | 0 | 21 | 0
03:30 | 2652 | 1280.5 | 674.5 | 0 | 39 | 416.485 | 26 | 2104 | 0 | 0 | 0 | 0 | 0 | 25 | 0
04:00 | 2596 | 1247.5 | 627 | 0 | 38 | 416.75 | 26 | 2103 | 0 | 0 | 0 | 0 | 0 | 29 | 0
04:30 | 2576 | 1230 | 627 | 0 | 38 | 416.88 | 26 | 2074 | 0 | 0 | 0 | 0 | 0 | 30 | 0
05:00 | 2556 | 1212.5 | 627 | 0 | 38 | 417.01 | 26 | 2045 | 0 | 0 | 0 | 0 | 0 | 31 | 0
05:30 | 2678 | 1272 | 627 | 0 | 39 | 416.995 | 26 | 2085.5 | 0 | 0 | 0 | 0 | 0 | 23.5 | 0
06:00 | 2800 | 1331.5 | 627 | 0 | 40 | 416.98 | 26 | 2126 | 0 | 0 | 0 | 0 | 0 | 16 | 0
06:30 | 2939.5 | 1462.5 | 674 | 0 | 40 | 417.02 | 26 | 2128 | 3.51 | 3.5 | 4 | 0 | 0 | 13.5 | 0
07:00 | 3079 | 1593.5 | 721 | 0 | 40 | 417.06 | 26 | 2130 | 7.02 | 7 | 8 | 0 | 0 | 11 | 0
07:30 | 3061.5 | 1653 | 815.5 | 0 | 41 | 430.985 | 26 | 2330.5 | 37.39 | 24 | 39 | 0 | 0 | 11 | 0
08:00 | 3044 | 1712.5 | 910 | 0 | 42 | 444.91 | 26 | 2531 | 67.76 | 41 | 70 | 0 | 0 | 11 | 0
08:30 | 2976.5 | 1650 | 815.5 | 0 | 42 | 478.81 | 36 | 2878 | 98.655 | 46 | 91 | 0 | 0 | 7 | 0
09:00 | 2909 | 1587.5 | 721 | 0 | 42 | 512.71 | 46 | 3225 | 129.55 | 51 | 112 | 0 | 0 | 3 | 0
09:30 | 2788 | 1350.5 | 674 | 0 | 46 | 585.235 | 46 | 3316 | 168.85 | 69 | 149.5 | 0 | 0 | 2 | 0
10:00 | 2667 | 1113.5 | 627 | 0 | 50 | 657.76 | 46 | 3407 | 208.15 | 87 | 187 | 0 | 0 | 1 | 0
10:30 | 2607 | 1088 | 766.5 | 0 | 52 | 705.09 | 46 | 3348 | 238.34 | 87 | 223.5 | 0 | 0 | 1.5 | 0
11:00 | 2547 | 1062.5 | 906 | 0 | 54 | 752.42 | 46 | 3289 | 268.53 | 87 | 260 | 0 | 0 | 2 | 0
11:30 | 2653.5 | 1190.5 | 906.5 | 0 | 56 | 753.7 | 46 | 3293 | 279.415 | 87 | 253.5 | 0 | 0 | 2 | 0
12:00 | 2760 | 1318.5 | 907 | 0 | 58 | 754.98 | 46 | 3297 | 290.3 | 87 | 247 | 0 | 0 | 2 | 0
12:30 | 2849 | 1362.5 | 907.5 | 0 | 60 | 754.785 | 38 | 3351.5 | 304.325 | 87 | 210.5 | 0 | 0 | 4 | 0
13:00 | 2938 | 1406.5 | 908 | 0 | 62 | 754.59 | 30 | 3406 | 318.35 | 87 | 174 | 0 | 0 | 6 | 0
13:30 | 2876.5 | 1356 | 907.5 | 0 | 60 | 734.295 | 28 | 3274 | 312.585 | 87 | 165.5 | 0 | 0 | 11 | 0
14:00 | 2815 | 1305.5 | 907 | 0 | 58 | 714 | 26 | 3142 | 306.82 | 87 | 157 | 0 | 0 | 16 | 0
14:30 | 2850 | 1339 | 907 | 0 | 57 | 634 | 26 | 3023 | 257.385 | 87 | 177.5 | 0 | 0 | 11.5 | 0
15:00 | 2885 | 1372.5 | 907 | 0 | 56 | 554 | 26 | 2904 | 207.95 | 87 | 198 | 0 | 0 | 7 | 0
15:30 | 2903 | 1359.5 | 907 | 0 | 55 | 505.5 | 28 | 2834.5 | 150.13 | 87 | 181.5 | 0 | 0 | 7 | 0
16:00 | 2921 | 1346.5 | 907 | 0 | 54 | 457 | 30 | 2765 | 92.31 | 87 | 165 | 0 | 0 | 7 | 0
16:30 | 2816.5 | 1290.5 | 907 | 0 | 56 | 492 | 30 | 2911 | 52.88 | 151 | 292.5 | 0 | 0 | 5 | 0
17:00 | 2712 | 1234.5 | 907 | 0 | 58 | 527 | 30 | 3057 | 13.45 | 215 | 420 | 0 | 0 | 3 | 0
17:30 | 2788 | 1339 | 767 | 0 | 56 | 603.5 | 35 | 3210.5 | 6.725 | 353 | 592.5 | 0 | 0 | 5.5 | 0
18:00 | 2864 | 1443.5 | 627 | 0 | 54 | 680 | 40 | 3364 | 0 | 491 | 765 | 0 | 0 | 8 | 0
18:30 | 2920 | 1445 | 627 | 0 | 55 | 719.5 | 40 | 3489.5 | 0 | 360.5 | 560.5 | 0 | 0 | 10.5 | 0
19:00 | 2976 | 1446.5 | 627 | 0 | 56 | 759 | 40 | 3615 | 0 | 230 | 356 | 0 | 0 | 13 | 0
19:30 | 2966 | 1405.5 | 627 | 0 | 54 | 756 | 40 | 3630 | 0 | 216 | 404 | 0 | 0 | 9 | 0
20:00 | 2894 | 1401.5 | 627 | 0 | 56 | 755 | 40 | 3603 | 0 | 216 | 371 | 0 | 0 | 7 | 0
20:30 | 2875 | 1387 | 768 | 0 | 55 | 757 | 40 | 3614.5 | 0 | 134 | 260.5 | 0 | 0 | 9 | 0
21:00 | 2856 | 1372.5 | 909 | 0 | 54 | 759 | 40 | 3626 | 0 | 52 | 150 | 0 | 0 | 11 | 0
21:30 | 2844 | 1372.5 | 909.5 | 0 | 53 | 749 | 40 | 3502.5 | 0 | 43.5 | 101.5 | 0 | 0 | 14.5 | 0
22:00 | 2832 | 1372.5 | 910 | 0 | 52 | 739 | 40 | 3379 | 0 | 35 | 53 | 0 | 0 | 18 | 0
22:30 | 2809.5 | 1373.5 | 910 | 0 | 51 | 657 | 40 | 3230 | 0 | 26 | 49 | 0 | 0 | 18.5 | 0
23:00 | 2787 | 1374.5 | 910 | 0 | 50 | 575 | 40 | 3081 | 0 | 17 | 45 | 0 | 0 | 19 | 0
Executive Engineer
Network Operation Division