## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-01-2025 | during | 03-01-2025 | during | 03-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 101.2 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 234.58 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 279 | 286 | 400.37 | 400.37 | 300 | 300
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 280 | 450 | 450 | 450 | 450
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 25.21 | 0 | 0 | 13 | 13 | 13 | 13
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 0 | 0
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 27 | 53.97 | 53.97 | 53.97 | 53.97
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 16 | 149.36 | 149.36 | 149.36 | 149.36
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 18 | 16 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 21 | 18 | 23 | 23 | 23 | 23
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 12 | 33 | 33 | 33 | 33
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 17 | 34 | 52.19 | 52.19 | 52.19 | 52.19
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 16 | 23 | 149 | 149 | 149 | 149
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 70 | 105 | 105 | 105 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 54 | 162 | 162 | 162 | 162
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 5 | 0 | 8 | 0 | 8 | 0
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 36 | 17 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 160 | 320 | 584 | 584 | 350 | 350
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 718 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
Dhaka Area Total |  |  |  |  | 7229.63 | 6740.44 | 1163 | 1198 | 4411.19 | 4411.19 | 2516.52 | 2516.52
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25 | 25 | 25 | 25
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 33 | 0 | 0 | 0 | 0 | Default availability set by nldc
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 227 | 226 | 225 | 225 | 225 | 225
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 33 | 33 | 2 | 14 | 33 | 33 | 33 | 33
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 10 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 1 | 0 | 4 | 0 | 4 | 0
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 10 | 80 | 300 | 300 | 300 | 300
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 1 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 24 | 100 | 100 | 100 | 100
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86
55 | SS Power | Coal | IPP | 2*660 | 1320 | 1224 | 610 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 66 | 66 | 8 | 13 | 66 | 66 | 66 | 66
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1200 | 1200 | 578 | 576 | 575 | 575 | 575 | 575 | U1 S/D 09/Oct/24 (Maintenance Work)
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 21 | 0 | 60 | 0 | 22 | 0
Chattogram Area Total |  |  |  |  | 5177.36 | 4987.22 | 1516 | 1746.36 | 2896.22 | 2814.22 | 2858.22 | 2814.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 182 | 198 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 310 | 350 | 353.35 | 353.35 | 317 | 317
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0
62 | Ashuganj 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 28 | 33 | 46.94 | 46.94 | 40 | 40
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 28 | 55 | 55 | 30 | 30
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 184 | 189 | 195 | 195 | 195 | 195
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 70 | 150 | 150 | 150 | 150
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 40 | 40
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 58 | 160 | 160 | 160 | 160
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 8 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 31 | 106 | 113 | 113 | 113 | 113
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 25 | 115 | 115 | 115 | 115
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5
Cumilla Area Total |  |  |  |  | 2893.7 | 2865.98 | 887 | 1133 | 2111.82 | 2111.82 | 1900.7 | 1900.7
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 2 | 0 | 2 | 0
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 24 | 65 | 200 | 200 | 200 | 200
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 75 | 115 | 115 | 115 | 115
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 11.51 | 0 | 12.48 | 0 | 12.48 | 0
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
Mymensingh Area Total |  |  |  |  | 750 | 749.71 | 81.51 | 162 | 561.48 | 547 | 351.48 | 337
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 44 | 44 | 44 | 44
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 0 | 0 | 2 | 2 | Default availability set by nldc
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 42 | 42 | 86 | 86 | 42 | 42
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 212 | 207 | 210 | 210 | 210 | 210
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 341 | 341 | 0 | 0 | Plant shutdown as per NLDC requirement.
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 378 | 381 | 400 | 400 | 380 | 380 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 346 | 310 | 383 | 383 | 353 | 353
Sylhet Area Total |  |  |  |  | 2411 | 2370.57 | 1143 | 1105 | 1627 | 1627 | 1194 | 1194
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 908 | 626 | 1000 | 1000 | 1000 | 1000
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 80 | 80 | 80 | 80
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 275 | 225 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 76.38 | 0 | 69 | 0 | 69 | 0
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1015 | 1235 | 1234 | 1234 | 1234 | 1234
** | HVDC(Nepal) | Import | Import | 1*40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0
Khulna Area Total |  |  |  |  | 3743 | 3726.2 | 2274.38 | 2086 | 3233 | 3164 | 3123 | 3054
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 130 | 141 | 65 | 65 | 65 | 65 | GT-02 air filter change
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 550 | 622 | 622 | 622 | 622 | 622
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 108 | 150 | 150 | 150 | 150
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.12 | 0 | 0.29 | 0 | 0.29 | 0
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1211.12 | 1405 | 1484.41 | 1484.12 | 1481.29 | 1481
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 142 | 180 | 214 | 214 | 192.6 | 192.6 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 161 | 162 | 220 | 220 | 198 | 198 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 179 | 169 | 220 | 220 | 198 | 198 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 11 | 8.25 | 8.25 | 8.25 | 8.25
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 0 | 0 | 0 | 0 | Substation problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 70 | 98 | 98 | 98 | 98
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 0.51 | 0 | 1.55 | 0 | 1.55 | 0
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 759 | 757.96 | 1347.54 | 1347.54 | 1347.54 | 1347.54
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 9.14 | 0 | 22 | 0 | 22 | 0
| Pabna Solar 100 MW | Solar | IPP |  | 100 | 100 | 92 | 0 | 88 | 0 | 88 | 0
Rajshahi Area Total |  |  |  |  | 3575.55 | 3393.2 | 1348.15 | 1349.96 | 2522.34 | 2410.79 | 2456.94 | 2345.39
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 77 | 76 | 80 | 80 | 80 | 80
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 200 | 205 | 200 | 200 | 200 | 200
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | Default availability set by nldc
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.9 | 0 | 3 | 0 | 3 | 0
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 34 | 35 | 115 | 115 | 115 | 115
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 28 | 0 | 28 | 0
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 30 | 0 | 158.62 | 0 | 54.62 | 0
Rangpur Area Total |  |  |  |  | 1030 | 950 | 349.9 | 316 | 697.62 | 508 | 593.62 | 508
System Total |  |  |  |  | 29076.24 | 28048.42 | 9974.06 | 10501.32 | 19545.08 | 19078.14 | 16475.77 | 16150.83
Forecast Scenario (03-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8540 |  | 0 |  | 8540
|  |  |  | 1:00 | 8020 |  | 0 |  | 8020
|  |  |  | 2:00 | 7600 |  | 0 |  | 7600
|  |  |  | 3:00 | 7430 |  | 0 |  | 7430
|  |  |  | 4:00 | 7180 |  | 0 |  | 7180
|  |  |  | 5:00 | 6980 |  | 0 |  | 6980
|  |  |  | 6:00 | 7250 |  | 0 |  | 7250
|  |  |  | 7:00 | 7330 |  | 0 |  | 7330
|  |  |  | 8:00 | 8280 |  | 0 |  | 8280
|  |  |  | 9:00 | 8140 |  | 0 |  | 8140
|  |  |  | 10:00 | 7780 |  | 0 |  | 7780
|  |  |  | 11:00 | 8020 |  | 0 |  | 8020
|  |  |  | 12:00 | 8940 |  | 0 |  | 8940
|  |  |  | 13:00 | 9290 |  | 0 |  | 9290
|  |  |  | 14:00 | 7900 |  | 0 |  | 7900
|  |  |  | 15:00 | 7290 |  | 0 |  | 7290
|  |  |  | 16:00 | 7130 |  | 0 |  | 7130
|  |  |  | 17:00 | 7620 |  | 0 |  | 7620
|  |  |  | 18:00 | 9030 |  | 0 |  | 9030
|  |  |  | 18:30 | 9060 |  | 0 |  | 9060
|  |  |  | 19:00 | 9090 |  | 0 |  | 9090
|  |  |  | 19:30 | 9020 |  | 0 |  | 9020
|  |  |  | 20:00 | 9010 |  | 0 |  | 9010
|  |  |  | 21:00 | 8930 |  | 0 |  | 8930
|  |  |  | 22:00 | 8580 |  | 0 |  | 8580
|  |  |  | 23:00 | 8250 |  | 0 |  | 8250
Probable Maximum Temperature: |  |  | 16.00°C
Probable Maximum Demand at Day Peak: |  |  | 8940.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 9090.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 9090.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 193.61 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (02-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 16.00°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 716.22
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 19.1229 | Peak Hour Flow: |  | 626.00 MW at 19:00 hrs.
Energy Flow from West to East |  | 2848330636.483 KWHr |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 14.4333 | Peak Hour Flow: |  | 757.96 MW at 19:00 hrs.
Power Flow during Peak Demand |  | 570 MW |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.1981 | Peak Hour Flow: |  | 58.00 MW at 19:00 hrs.
Maximum Power Flow |  | 956 MW |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 34.7543 | Peak Hour Flow: |  | 1441.96 MW at 19:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## yesterdayGen
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-01-2025 | [28 empty] | Date: | 02-01-2025 | [28 empty] | Date: | 02-01-2025 | [28 empty] | Date: | 02-01-2025 | [28 empty] | Date: | 02-01-2025 | [18 empty] | Date: | 02-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | Sonagazi 75 MW (AC) Solar Power Plant | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Bhairob 54.5 MW | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sreepur 150 MW PP | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.00 MW | 105.00 MW | 52.00 MW | 365.00 MW | 260.00 MW | 234.58 MW | 190.00 MW | 108.00 MW | 412.00 MW | 20.00 MW | 718.00 MW | 54.00 MW | 36.09 MW | 20.00 MW | 149.00 MW | 149.00 MW | 300.00 MW | 55.00 MW | 55.00 MW | 162.00 MW | 33.00 MW | 104.00 MW | 450.00 MW | 335.00 MW | 583.00 MW | 583.00 MW | 55.00 MW | 33.00 MW | 335.00 MW | 210.00 MW | 115.00 MW | 35.00 MW | 33.75 MW | 23.00 MW | 105.00 MW | 584.00 MW | 116.00 MW | 300.00 MW | 108.00 MW | 360.00 MW | 66.00 MW | 102.00 MW | 98.00 MW | 54.36 MW | 100.00 MW | 100.00 MW | 7.00 MW | 230.00 MW | 110.00 MW | 33.00 MW | 1150.00 MW | 159.86 MW | 159.86 MW | 50.00 MW | 25.00 MW | 105.00 MW | 225.00 MW | 225.00 MW | 150.00 MW | 150.00 MW | 75.00 MW | 1320.00 MW | 20.00 MW | 51.00 MW | 150.00 MW | 195.00 MW | 400.00 MW | 356.15 MW | 360.00 MW | 45.00 MW | 55.00 MW | 221.00 MW | 54.50 MW | 115.00 MW | 163.00 MW | 200.00 MW | 113.00 MW | 25.00 MW | 114.00 MW | 160.00 MW | 52.20 MW | 52.00 MW | 341.00 MW | 383.00 MW | 400.00 MW | 50.00 MW | 70.00 MW | 90.00 MW | 11.00 MW | 163.00 MW | 25.00 MW | 100.00 MW | 86.00 MW | 66.00 MW | 330.00 MW | 20.00 MW | 231.00 MW | 115.00 MW | 200.00 MW | 210.00 MW | 3.00 MW | 150.00 MW | 50.00 MW | 22.00 MW | - | 1000.00 MW | 410.00 MW | 16.00 MW | 54.00 MW | 109.00 MW | 40.00 MW | 230.00 MW | 230.00 MW | 336.00 MW | 336.00 MW | 105.00 MW | 100.00 MW | 1234.00 MW | 105.00 MW | 1347.54 MW | 35.09 MW | 100.00 MW | 52.00 MW | 71.00 MW | 113.00 MW | 71.00 MW | 104.00 MW | 113.00 MW | 50.00 MW | 52.00 MW | 100.00 MW | 50.00 MW | 68.00 MW | 214.00 MW | 214.00 MW | 220.00 MW | 220.00 MW | 220.00 MW | 220.00 MW | 414.00 MW | 414.00 MW | 6.09 MW | 11.00 MW | 274.00 MW | 170.00 MW | 115.00 MW | 30.00 MW | 113.00 MW | 20.00 MW | 20.00 MW | 8.00 MW | 200.00 MW | 1.00 MW | 110.00 MW | 307.00 MW | 40.00 MW | 194.00 MW | 220.00 MW | 220.00 MW | 1244.00 MW | 150.00 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 170 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 505 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 442 | 0 | 51 | 0 | 189 | 0 | 290 | 0 | 33 | 28 | 181 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 232 | 323 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 209 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 4059 | 911 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 874 | 0 | 482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 187 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 200 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 130 | 220 | 0 | 500 | 0 | 4455.5 | 8514.5 | 93.96
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 170 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 503 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 352 | 0 | 51 | 0 | 110 | 0 | 295 | 0 | 33 | 28 | 190 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 0 | 224 | 323 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3767 | 824 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 187 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 200 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 6 | 130 | 220 | 0 | 420 | 0 | 4028.5 | 7795.5 | 93.95
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 170 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 407 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 355 | 0 | 51 | 0 | 108 | 0 | 280 | 0 | 33 | 29 | 183 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 0 | 216 | 324 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3640 | 721 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 187 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 200 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 130 | 220 | 0 | 320 | 0 | 3800.5 | 7440.5 | 93.95
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 170 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 379 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 305 | 0 | 51 | 0 | 8 | 0 | 280 | 0 | 33 | 18 | 183 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 38 | 0 | 0 | 0 | 216 | 324 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 11 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3421 | 720 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 200 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 130 | 220 | 0 | 290 | 0 | 3698.5 | 7119.5 | 93.95
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 175 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 378 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 51 | 0 | 8 | 0 | 300 | 0 | 33 | 5 | 193 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 38 | 0 | 0 | 0 | 216 | 324 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 11 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3400 | 616 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 200 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 130 | 180 | 0 | 300 | 0 | 3519.5 | 6919.5 | 93.94
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 170 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 379 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 300 | 0 | 51 | 0 | 8 | 0 | 300 | 0 | 33 | 5 | 198 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 38 | 0 | 0 | 0 | 202 | 322 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 11 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3344 | 626 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 200 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 85 | 180 | 0 | 300 | 0 | 3482.5 | 6826.5 | 93.94
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 175 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 407 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 307 | 0 | 51 | 0 | 95 | 0 | 315 | 0 | 33 | 5 | 199 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 40 | 0 | 0 | 0 | 220 | 322 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 11 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3653 | 626 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 773 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 155 | 0 | 158 | 0 | 0 | 0 | 0 | 5.5 | 200 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 6 | 130 | 220 | 0 | 300 | 0 | 3691.5 | 7344.5 | 93.94
07:00 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 175 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 410 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1 | 398 | 0 | 51 | 0 | 158 | 0 | 355 | 0 | 33 | 23 | 220 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 40 | 0 | 0 | 0 | 260 | 322 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 212 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 4009 | 720 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 771 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 153 | 0 | 158 | 0 | 0 | 0 | 0 | 5.5 | 200 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 6 | 130 | 220 | 0 | 390 | 0 | 3894.5 | 7903.5 | 93.93
08:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 1 | 19.5 | 22 | 0 | 170 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 554 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 4 | 460 | 1 | 51 | 0 | 185 | 0 | 356 | 0 | 33 | 27 | 222 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 38 | 0 | 0 | 0 | 320 | 320 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 42 | 0 | 0 | 0 | 212 | 35 | 35 | 0 | 0 | 0 | 1.06 | 0 | 4335.56 | 909 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.35 | 1027 | 0 | 515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1.36 | 168 | 0 | 144 | 0 | 170 | 0 | 0 | 0 | 0.11 | 5.5 | 200 | 80 | 0 | 1 | 0 | 0 | 0 | 0.1 | 4 | 0.03 | 0 | 250 | 4 | 100 | 180 | 0 | 510 | 0 | 4556.45 | 8892.01 | 93.93
09:00 | 0 | 30 | 17 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 1 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 3 | 19 | 22 | 0 | 165 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 577 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 6 | 552 | 3 | 51 | 0 | 185 | 0 | 320 | 0 | 33 | 29 | 182 | 0 | 0 | 0 | 0 | 1 | 15 | 0 | 50 | 0 | 0 | 0 | 340 | 322 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 212 | 47 | 41 | 0 | 0 | 0 | 2.91 | 3 | 4515.91 | 745 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.04 | 1110 | 0 | 744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 3.52 | 153 | 0 | 159 | 0 | 185 | 0 | 0 | 0 | 0.28 | 5.5 | 200 | 70 | 0 | 2 | 0 | 0 | 0 | 0.6 | 12 | 0.07 | 0 | 307 | 3 | 130 | 220 | 0 | 560 | 0 | 4964.01 | 9479.92 | 93.93
10:00 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 0 | 36 | 0 | 0 | 32 | 0 | 0 | 0 | 17 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 6 | 15 | 22 | 0 | 155 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 6 | 577 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 9 | 550 | 15 | 51 | 0 | 189 | 0 | 310 | 0 | 27 | 29 | 183 | 0 | 0 | 0 | 0 | 26 | 13 | 0 | 52 | 0 | 0 | 0 | 316 | 322 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 212 | 38 | 55 | 0 | 0 | 0 | 4.96 | 22 | 4612.96 | 626 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.77 | 1010 | 0 | 753.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 4.85 | 147 | 0 | 160 | 0 | 189 | 0 | 0 | 0 | 0.43 | 5.5 | 200 | 76 | 34 | 3 | 0 | 0 | 0 | 1 | 18 | 0.09 | 0 | 307 | 3 | 130 | 220 | 0 | 570 | 0 | 4871.6 | 9484.56 | 93.92
11:00 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 36 | 0 | 15 | 16 | 0 | 0 | 0 | 42 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 5 | 15 | 21 | 0 | 152 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 575 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 21 | 550 | 18 | 51 | 0 | 184 | 0 | 310 | 0 | 27 | 29 | 183 | 0 | 0 | 0 | 0 | 26 | 13 | 0 | 60 | 0 | 0 | 0 | 316 | 322 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 42 | 0 | 0 | 0 | 213 | 38 | 24 | 0 | 0 | 0 | 11.51 | 22 | 4576.51 | 858 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.34 | 1010 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 8.34 | 144 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 0.5 | 5.5 | 200 | 78 | 34 | 0 | 0 | 0 | 0 | 1.9 | 21 | 0.13 | 0 | 307 | 4 | 130 | 220 | 0 | 570 | 0 | 5094.71 | 9671.22 | 93.92
12:00 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 0 | 0 | 36 | 0 | 16 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 5 | 18 | 21 | 0 | 160 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 1 | 0 | 0 | 1 | 40 | 0 | 2 | 578 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 21 | 610 | 18 | 51 | 0 | 184 | 0 | 310 | 0 | 28 | 29 | 182 | 0 | 0 | 0 | 0 | 31 | 14 | 0 | 58 | 0 | 0 | 0 | 346 | 378 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 212 | 24 | 24 | 0 | 0 | 0 | 11.51 | 22 | 4790.51 | 908 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.38 | 1015 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 9.14 | 142 | 0 | 161 | 0 | 179 | 0 | 0 | 0 | 0.51 | 5.5 | 200 | 77 | 34 | 6 | 0 | 0 | 0 | 2.9 | 30 | 0.12 | 0 | 307 | 4 | 130 | 220 | 0 | 550 | 0 | 5183.55 | 9974.06 | 93.92
13:00 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 279 | 0 | 0 | 0 | 36 | 0 | 16 | 16 | 0 | 0 | 0 | 90 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 5 | 18 | 20 | 0 | 190 | 18 | 30 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 2 | 40 | 0 | 2 | 500 | 0 | 0 | 1 | 0 | 0 | 226 | 0 | 0 | 0 | 31 | 612 | 17 | 51 | 0 | 187 | 0 | 325 | 0 | 31 | 29 | 189 | 0 | 0 | 0 | 0 | 44 | 16 | 0 | 56 | 0 | 0 | 0 | 346 | 380 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 211 | 24 | 24 | 0 | 0 | 0 | 13.31 | 22 | 4896.31 | 909 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.82 | 1064 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 6.06 | 146 | 0 | 178 | 0 | 180 | 0 | 0 | 0 | 0.41 | 5.5 | 200 | 77 | 34 | 9 | 0 | 0 | 0 | 5 | 36 | 0.18 | 0 | 307 | 4 | 130 | 220 | 0 | 550 | 0 | 5248.97 | 10145.28 | 93.92
14:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 36 | 0 | 16 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 5 | 17 | 20 | 0 | 260 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 3 | 40 | 0 | 2 | 502 | 0 | 0 | 13 | 0 | 0 | 226 | 0 | 0 | 0 | 51 | 560 | 14 | 51 | 0 | 187 | 0 | 305 | 0 | 31 | 29 | 194 | 0 | 0 | 0 | 0 | 44 | 16 | 0 | 62 | 0 | 0 | 0 | 346 | 385 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 42 | 0 | 0 | 0 | 212 | 24 | 24 | 0 | 0 | 0 | 23.73 | 22 | 4863.73 | 909 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.14 | 1008 | 0 | 665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 5.46 | 140 | 0 | 140 | 0 | 180 | 0 | 0 | 0 | 0.51 | 5.5 | 200 | 77 | 34 | 14 | 0 | 0 | 0 | 4.2 | 33 | 0.21 | 0 | 250 | 4 | 100 | 180 | 0 | 550 | 0 | 4892.02 | 9755.75 | 93.91
15:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 36 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 390 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 3 | 17 | 20 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 0 | 503 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 21 | 560 | 9 | 51 | 0 | 189 | 0 | 285 | 0 | 32 | 29 | 182 | 0 | 0 | 0 | 0 | 44 | 16 | 0 | 58 | 0 | 0 | 0 | 316 | 382 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 209 | 8 | 8 | 0 | 0 | 0 | 19.16 | 0 | 4622.16 | 909 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.7 | 1010 | 0 | 663.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 3.79 | 140 | 0 | 140 | 0 | 177 | 0 | 0 | 0 | 0.4 | 5.5 | 200 | 77 | 0 | 16 | 0 | 0 | 0 | 3 | 20 | 0.16 | 0 | 250 | 4 | 100 | 180 | 0 | 540 | 0 | 4776.52 | 9398.68 | 93.91
16:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 36 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 360 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 2 | 17 | 20 | 0 | 360 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 6 | 500 | 5 | 51 | 0 | 145 | 0 | 305 | 0 | 33 | 28 | 195 | 0 | 0 | 0 | 0 | 44 | 16 | 0 | 52 | 0 | 0 | 0 | 330 | 382 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 210 | 16 | 8 | 0 | 0 | 0 | 4.7 | 0 | 4527.7 | 910 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.97 | 1007 | 0 | 609.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 1.91 | 145 | 0 | 140 | 0 | 160 | 0 | 0 | 0 | 0.19 | 5.5 | 200 | 76 | 0 | 7 | 0 | 0 | 0 | 1.4 | 12 | 0.12 | 0 | 200 | 4 | 141 | 220 | 0 | 500 | 0 | 4632.27 | 9159.97 | 93.9
17:00 | 0 | 52 | 22 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 0 | 36 | 0 | 16 | 16 | 0 | 0 | 0 | 17 | 25 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 16 | 19 | 0 | 350 | 1 | 10 | 0 | 0 | 3 | 0 | 17 | 5 | 0 | 12 | 0 | 40 | 0 | 0 | 500 | 0 | 0 | 2 | 0 | 0 | 226 | 0 | 0 | 0 | 2 | 500 | 1 | 51 | 1 | 187 | 0 | 285 | 0 | 33 | 28 | 182 | 2 | 0 | 0 | 0 | 58 | 16 | 0 | 46 | 0 | 0 | 0 | 330 | 382 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 205 | 22 | 24 | 0 | 0 | 0 | 0.23 | 1 | 4529.23 | 909 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.28 | 1056 | 0 | 613.7 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 4 | 0 | 0 | 173 | 0 | 174 | 0 | 152 | 0 | 0 | 0 | 0.01 | 5.5 | 205 | 76 | 32 | 1 | 0 | 0 | 0 | 0.3 | 2 | 0.02 | 0 | 200 | 6 | 141 | 220 | 0 | 510 | 5 | 4780.81 | 9310.04 | 93.9
18:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 8 | 36 | 0 | 16 | 32 | 0 | 0 | 0 | 72 | 25 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 16 | 18 | 0 | 350 | 18 | 65 | 7 | 0 | 2 | 0 | 32 | 26 | 12 | 24 | 0 | 40 | 7 | 10 | 576 | 0 | 0 | 24 | 0 | 11 | 226 | 0 | 0 | 0 | 0 | 590 | 0 | 51 | 63 | 187 | 0 | 330 | 0 | 33 | 28 | 197 | 17 | 19 | 0 | 0 | 104 | 16 | 0 | 56 | 0 | 0 | 0 | 340 | 381 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 42 | 0 | 0 | 0 | 208 | 65 | 65 | 0 | 0 | 0 | 0 | 22 | 5276 | 626 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242 | 0 | 799.41 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 176 | 0 | 156 | 0 | 0 | 0 | 0 | 11 | 204 | 77 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 141 | 220 | 0 | 550 | 72 | 5117.41 | 10393.41 | 93.9
19:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 27 | 17 | 0 | 23 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 16 | 18 | 0 | 320 | 35 | 80 | 10 | 0 | 13 | 0 | 0 | 54.36 | 12 | 24 | 0 | 40 | 0 | 14 | 576 | 0 | 0 | 33 | 0 | 17 | 226 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 189 | 0 | 350 | 0 | 33 | 28 | 198 | 17 | 25 | 0 | 0 | 106 | 8 | 0 | 58 | 0 | 0 | 0 | 310 | 381 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 207 | 75 | 65 | 0 | 0 | 0 | 0 | 22 | 5344.36 | 626 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1235 | 0 | 757.96 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 162 | 0 | 169 | 0 | 0 | 0 | 0 | 11 | 205 | 76 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 141 | 220 | 0 | 622 | 108 | 5156.96 | 10501.32 | 93.9
19:30 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 17 | 17 | 0 | 16 | 16 | 0 | 0 | 0 | 17 | 25 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 16 | 18 | 0 | 310 | 35 | 80 | 0 | 0 | 16 | 0 | 0 | 54.36 | 12 | 12 | 0 | 40 | 0 | 20 | 576 | 0 | 0 | 33 | 0 | 17 | 226 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 189 | 0 | 345 | 0 | 33 | 29 | 183 | 17 | 16 | 0 | 0 | 106 | 17 | 0 | 68 | 0 | 0 | 0 | 310 | 381 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 207 | 75 | 65 | 0 | 0 | 0 | 0 | 22 | 5257.36 | 626 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241 | 0 | 759.1 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 167 | 0 | 169 | 0 | 0 | 0 | 0 | 11 | 204 | 77 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 141 | 220 | 0 | 622 | 108 | 5169.1 | 10426.46
20:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 17 | 17 | 0 | 16 | 16 | 0 | 0 | 0 | 17 | 25 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 16 | 20 | 0 | 305 | 35 | 80 | 0 | 0 | 16 | 0 | 0 | 54.36 | 12 | 12 | 0 | 40 | 0 | 24 | 575 | 0 | 0 | 33 | 0 | 17 | 226 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 70 | 158 | 0 | 310 | 0 | 33 | 29 | 191 | 17 | 16 | 0 | 0 | 106 | 17 | 0 | 56 | 0 | 0 | 0 | 300 | 380 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 207 | 75 | 65 | 0 | 0 | 0 | 0 | 22 | 5176.36 | 625 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1244 | 0 | 757.37 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 167 | 0 | 169 | 0 | 0 | 0 | 0 | 11 | 204 | 77 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 622 | 108 | 5160.37 | 10336.73 | 93.9
21:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 280 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 16 | 20 | 0 | 265 | 35 | 30 | 0 | 0 | 14 | 0 | 0 | 54.36 | 0 | 0 | 0 | 40 | 0 | 27 | 576 | 0 | 0 | 33 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 10 | 158 | 0 | 310 | 0 | 33 | 29 | 195 | 17 | 0 | 0 | 0 | 63 | 17 | 0 | 62 | 0 | 0 | 0 | 300 | 380 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 207 | 65 | 35 | 0 | 0 | 0 | 0 | 22 | 4815.36 | 877 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1245 | 0 | 752.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 167 | 0 | 166 | 0 | 0 | 0 | 0 | 8.5 | 204 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 622 | 17 | 5208.14 | 10023.5 | 93.9
22:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 16 | 20 | 0 | 180 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 575 | 0 | 0 | 24 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 128 | 0 | 310 | 0 | 33 | 29 | 201 | 0 | 0 | 0 | 0 | 26 | 17 | 0 | 54 | 0 | 0 | 0 | 266 | 380 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 208 | 24 | 16 | 0 | 0 | 0 | 0 | 22 | 4464 | 915 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1245 | 0 | 676.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 163 | 0 | 166 | 0 | 0 | 0 | 0 | 8.5 | 204 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 622 | 0 | 5140.63 | 9604.63 | 93.9
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 13 | 20 | 0 | 170 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 33 | 576 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 613 | 0 | 51 | 0 | 128 | 0 | 340 | 0 | 33 | 16 | 200 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 56 | 0 | 0 | 0 | 260 | 380 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 42 | 0 | 0 | 0 | 208 | 24 | 16 | 0 | 0 | 0 | 0 | 6 | 4323 | 916 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1119 | 0 | 504.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 138 | 0 | 147 | 0 | 0 | 0 | 0 | 8.5 | 205 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 132 | 220 | 0 | 560 | 0 | 4653.58 | 8976.58 | 93.9
Total KWH | 0 | 884160 | 326400 | 0 | 0 | 0 | 0 | 0 | 6818400 | 0 | 0 | 70164 | 436320 | 0 | 180576 | 259200 | 0 | 0 | 0 | 430560 | 543900 | 0 | 9282500 | 0 | 0 | 0 | 0 | 416900 | 0 | 0 | 0 | 35535 | 367800 | 494640 | 0 | 5230454 | 205745 | 341236 | 18240 | 0 | 184320 | 0 | 64560 | 303917 | 53760 | 73920 | 11520 | 904320 | 27600 | 487200 | 12516363.6 | 0 | 0 | 181920 | 0 | 58545 | 5334378 | 0 | 0 | 0 | 166018 | 11939999 | 98145 | 1233014 | 282690 | 3378909 | 0 | 7850200 | 0 | 788400 | 564960 | 4726000 | 77040 | 105600 | 0 | 0 | 796320 | 387480 | 0 | 1198080 | 0 | 0 | 0 | 6922400 | 8813000 | 0 | 0 | 0 | 57216 | 3844554 | 0 | 0 | 880320 | 0 | 0 | 0 | 5276550 | 682800 | 554400 | 0 | 1550 | 0 | 88470 | 278640 | 107537808.6 | 19122909 | 6342336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465840 | 24356360 | 0 | 14433308 | 0 | 0 | 0 | 0 | 0 | 0 | 270400 | 0 | 0 | 0 | 508680 | 0 | 45000 | 3882818 | 0 | 4016045 | 0 | 4184791 | 0 | 0 | 0 | 3300 | 156582 | 4886000 | 1796509 | 357387 | 63767 | 0 | 0 | 0 | 20892 | 185040 | 1169 | 0 | 5957000 | 135134 | 3010000 | 5260840 | 0 | 12212363.64 | 296400 | 111970870.64 | 219508679.24

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 02-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 9974.06 | MW | 12:00 Hr. | Energy Generated |  |  | 219508.6792 |  | MWHr
Day Peak Demand |  |  | 9974.06 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MWHr
Evening Peak Generation |  |  | 10501.32 | MW | 19:00 Hr. | Energy Demand |  |  | 219508.6792 |  | MWHr
Evening Peak Demand |  |  | 10501.32 | MW | 19:00 Hr.
Minimum Generation of the Day |  |  | 6826.5 | MW | 05:00 Hr.
Minimum Demand of the Day |  |  | 6826.5 | MW | 05:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 23154.594 | 0 | 2587.38 | 0 | 0 | 35.535 | 0 | 0 | 25777.509 | Gas | 100687.721 | Gas | 350202827.5
Chattogram Zone |  |  | 5821.578 | 24456.3626 | 1329.443 | 0 | 904.32 | 275.683 | 0 | 184.32 | 32971.7066 | Coal | 73664.5952 | Coal | 538576086.3224
Cumilla Zone |  |  | 18928.963 | 0 | 1261.65 | 0 | 0 | 0 | 1198.08 | 0 | 21388.693 | HFO | 7618.5 | HFO | 141621884.03
Mymensingh Zone |  |  | 0 | 0 | 1515.84 | 0 | 0 | 90.02 | 0 | 0 | 1605.86 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 25794.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25794.04 | Hydro | 904.32 | Hydro | 90432
Khulna Zone |  |  | 6342.336 | 24356.36 | 0 | 0 | 0 | 465.84 | 19122.909 | 0 | 50287.445 | Solar | 1694.926 | Solar | 19189717.45
Barishal Zone |  |  | 8405.974 | 18169.3636 | 296.4 | 0 | 0 | 1.169 | 0 | 0 | 26872.9066 | Import | 34754.297 | Import | 176700640.31
Rajshahi Zone |  |  | 12240.236 | 0 | 270.4 | 0 | 0 | 556.98 | 14433.308 | 0 | 27500.924 | Wind | 184.32 | Wind | 2654208
Rangpur Zone |  |  | 0 | 6682.509 | 357.387 | 0 | 0 | 269.699 | 0 | 0 | 7309.595
Total |  |  | 100687.721 | 73664.5952 | 7618.5 | 0 | 904.32 | 1694.926 | 34754.297 | 184.32 | 219508.6792
Cost of the consumed fuel (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 350202827.5 |  | Hydro | 90432
|  |  | Coal | 538576086.3224 |  | Solar | 19189717.45
|  |  | HFO | 141621884.03 |  | Import | 176700640.31
|  |  | HSD | 0 |  | Wind | 2654208
|  |  |  | Total: | 1229035795.6124 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Rangpur 20 MW GTPP |  |  | 20 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Baghabari 100 MW GTPP |  |  | 100 | 2 | Ashuganj 55 MW PP (Precision) |  |  | 55
| 3 | Barapukuria TPP Unit-2 |  |  | 85 | 3 | Sirajgonj 225MW CCPP Unit-1 GT |  |  | 150
| 4 | Siddhirgonj 210 MW TPP |  |  | 115
| 5 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 734 |  |  |  | Total | 240.09
|  |  | Total Unavailable Capacity |  |  |  | 974.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3873
|  |  | Chattogram |  | 0 |  | 1100
|  |  | Cumilla |  | 0 |  | 860
|  |  | Mymensingh |  | 0 |  | 824
|  |  | Sylhet |  | 0 |  | 355
|  |  | Khulna |  | 0 |  | 1174
|  |  | Barishal |  | 0 |  | 295
|  |  | Rajshahi |  | 0 |  | 940
|  |  | Rangpur |  | 0 |  | 666
|  |  | Total |  | 0 |  | 10087
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:21 | 13:55 | Aminbazar 400/230/132kV S/S ATR-01 LT Tripped showing IDT NON DIR E/F relays Due to
Unknown
08:21 | 13:52 | Aminbazar 400/230/132kV S/S ATR-01 HT Tripped showing Master Relay relays Due to Unknown
08:33 | 16:58 | Baghabari-Sirajganj 230 kV Ckt-1 Scheduled S/D from Baghabari 230/132kV end Due to Annual
Maintenance and from Sirajgonj 230 end Due to Annual Maintenance
08:45 | 16:45 | Mirpur 132/33kV S/S T2 LT Scheduled S/D Due to Annual Maintenance
08:48 | 16:45 | Mirpur 132/33kV S/S T2 HT Scheduled S/D Due to Annual Maintenance
08:50 | 14:34 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end. and from
Ashuganj 230/132/33kV end Due to As per instruction of NLDC
08:51 | 19:25 | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Barapukuria 230/132/33kV end. and from
Bogura 400/230kV end Due to S/D Taken By ALDC BOGURA.
08:54 | 14:00 | Chhatak 132/33kV S/S Bus-B Scheduled S/D Due to Annual Maintenanse
08:55 | 17:09 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end Due to Yearly
Dead- line checking and from Feni 132/33kV end Due to Yearly maintenance by chowmohani
Grid.
08:57 | 14:15 | Chhatak 132/33kV S/S T-1 HT Scheduled S/D Due to Bus-2 DS Maintenance
08:57 | 15:15 | Chhatak 132/33kV S/S T-1 LT Scheduled S/D
08:58 | 15:40 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Annual
maintenance work
09:02 | 15:43 | Natore-Rajshahi 132kV Ckt-2 Scheduled S/D from Rajshahi 132/33kV end Due to annual
maintenace and from Natore 132/33kV end Due to Dead line checking.
09:04 | 15:56 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to
annual maintenance and from Shahjibazar 132/33kV end Due to Annual Maintenance
09:10 | 16:59 | GPH 230/33kV S/S HATHAZARI Scheduled S/D Due to Line Inspection
09:11 | 16:58 | GPH-Hathazari 230kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to annual
maintenance
09:15 | 17:03 | Rangpur-Saidpur 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to Annual
Maintenance and from Saidpur 132/33kV end Due to Annual maintenance
09:21 | 16:43 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D Due to Annual Maintenance
10:00 | 15:42 | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bhandaria 132/33kV end Due to Annual
mai maintenance
10:11 | 15:58 | Madunaghat 400/230kV S/S Madunaghat-Shikalbaha 230kV Ckt.-2 Scheduled S/D
10:13 |  | Shikalbaha 230/132kV S/S Hathazari-02 Scheduled S/D
10:17 | 17:02 | Daudkandi-Sonargaon 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to Annual
maintenance of sonargoan ss end and from Sonargaon 132/33kV end Due to Annual maintenance
dead line checking
10:23 | 17:20 | Ghatail 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance
11:36 | 17:20 | BIPTC S/S 20DF13 Scheduled S/D Due to Shutdown is taken for painting of fire fighting
pipes
11:56 | 17:38 | BIPTC S/S 400kV Bus-1 Scheduled S/D Due to Shutdown is taken for painting of fire
fighting pipes
12:00 |  | Day peak generation 9971 MW
13:04 | 13:11 | Saidpur 132/33kV S/S TR-4 (414T) LT Scheduled S/D Due to Deferential relay testing.
13:05 | 13:10 | Saidpur 132/33kV S/S TR-4 (414T) HT Scheduled S/D Due to Deferential relay testing.
13:10 | 17:20 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Scheduled S/D from Siddhirganj 132/33kV
end Due to Annual maintenance
13:21 |  | Amtoli 400Kv Switching Station - RNPL P/S Line -2 Close.
| 13:57 | Magura-Narail 132kV Ckt-1 is restored.
14:34 | 17:10 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Scheduled S/D from Ashuganj 230/132/33kV end Due to As
per instruction of NLDC
15:38 |  | Amtoli-RNPL ckt-2 is restored.
15:45 |  | At RNPL PS,unit Transfomer is Charged.
| 17:29 | Mahasthangar-Palashbari 132kV Ckt-2 is restored.
| 17:35 | Barishal 230/132kV S/S Gopalgonj CKT-2 is restored.
| 17:35 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 is restored.
| 17:35 | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-2 is restored.
| 17:36 | Gopalganj 400/132kV S/S 230kV Barisal CKT-02 is restored.
| 18:04 | Niamatpur 132/33kV S/S Transformer-3(426T) HT is restored.
| 18:17 | Niamatpur 132/33kV S/S Transformer-3(426T) LT is restored.
19:00 |  | Evening peak Generation is 10500 MW
22:04 |  | Aminbazar 400/230/132kV S/S ATR-01 HT Tripped showing HV directional Earth
fault 86-1,86-2 master relay operated. relays.
22:04 |  | Aminbazar 400/230/132kV S/S ATR-01 LT Tripped showing 86-1,86-2 master relay operated.
relays.
02:28 |  | Unique Meghnaghat Power 584 MW CCPP tripped.
02:31 |  | Keranigonj 230/132/33kV S/S ATR-3 LT Tripped showing 86.1 Relay Operated relays Due to
Gas Compartment loss of SF6 (E05)
02:31 |  | Keranigonj 230/132/33kV S/S ATR-3 HT Tripped showing 86.1 Relay Operated relays Due to
Gas Compartment loss of SF6(E05)
05:00 |  | Minimum Generation: 6844 MW.
06:03 |  | Bhola 225 MW CCPP GT-2 was shutdown.
06:18 |  | Hathazari 230/132/33kV S/S T-01 LT Scheduled S/D Due to Annual maintenance | [7 empty] | 20.0MW load
interrup.
06:18 |  | Hathazari 230/132/33kV S/S T-01 HT Scheduled S/D Due to Annual maintenance | [7 empty] | 20.0MW load
interrup.
06:20 |  | Hathazari 230/132/33kV S/S T-02 HT Scheduled S/D Due to Annual maintenance | [7 empty] | 20.0MW load
interrup.
06:20 |  | Hathazari 230/132/33kV S/S T-02 LT Scheduled S/D Due to Annual maintenance | [7 empty] | 20.0MW load
interrup.
06:35 |  | Hathazari 230/132/33kV S/S MT-01 LT Scheduled S/D Due to Annual maintenance
06:40 |  | Hathazari 230/132/33kV S/S MT-03 HT Scheduled S/D Due to Annual maintenance
06:40 |  | Hathazari 230/132/33kV S/S MT-03 LT Scheduled S/D Due to Annual maintenance
06:54 |  | Mahasthangar-Palashbari 132kV Ckt-2 Project Work S/D from Palashbari 132/33kV end Due to
Project work and from Mahasthangarh 132/33kV end Due to Polashbari Grid SS project Work.
06:55 |  | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 Forced S/D from Mithapukur 132/33kV
end.
06:56 |  | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-2 Forced S/D from Mithapukur 132/33kV
end.
07:05 |  | Baroaulia-Hathazari 132 kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to
Annual maintenance
07:07 |  | Baroaulia-Hathazari 132 kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to
Annual maintenance
07:10 |  | Hathazari 230/132/33kV S/S 132KV MAIN BUS-02 Scheduled S/D Due to Annual maintenance
07:13 |  | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to
Deadline Checking
07:20 |  | BIPTC S/S 20DF42 Tripped showing Differential 87 relays Due to Capacitor unbalance
07:35 |  | Hathazari 230/132/33kV S/S MT-01 HT Scheduled S/D Due to Annual maintenance
07:38 |  | Hathazari 230/132/33kV S/S MT-02 HT Scheduled S/D Due to Annual maintenance
07:38 |  | Hathazari 230/132/33kV S/S MT-02 LT Scheduled S/D Due to Annual maintenance
07:45 |  | Saidpur 132/33kV S/S TR-3 (424T) HT Scheduled S/D Due to Removal of red hot | [7 empty] | 12.0MW load
interrup.
07:45 |  | Saidpur 132/33kV S/S TR-3 (424T) LT Scheduled S/D Due to Removal of red hot | [7 empty] | 12.0MW load
interrup.
07:46 |  | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
maintenance work
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 234.58 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Default availability set by nldc
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | Default availability set by nldc
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 286 | 6818400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 9282500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | Default availability set by nldc
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Default availability set by nldc
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 27 | 70164 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149 | 16 | 259200 | Default availability set by nldc
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | Default availability set by nldc
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | Default availability set by nldc
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 367800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 494640 | Default availability set by nldc
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 543900 | Default availability set by nldc
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 12 | 416900 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 34 | 326400 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Default availability set by nldc
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | Default availability set by nldc
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 23 | 180576 | Default availability set by nldc
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 884160 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 430560 | Default availability set by nldc
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 35535 | Default availability set by nldc
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 17 | 436320 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 320 | 5230454 | Machine Problem
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | Default availability set by nldc
Dhaka Area Total |  |  |  |  | 6940.42 | 1198 | 25777509
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 98145 | Default availability set by nldc
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 181920 | Default availability set by nldc
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 904320 | Default availability set by nldc
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5334378 | Default availability set by nldc
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 58545 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 64560 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 53760 | Default availability set by nldc
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 33 | 14 | 487200 | Default availability set by nldc
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 10 | 18240 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 11520 | Default availability set by nldc
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 80 | 341236 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 303917 | Default availability set by nldc
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 27600 | Default availability set by nldc
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 73920 | Default availability set by nldc
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 205745 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1320 | 612 | 11939999 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 66 | 13 | 184320 | Default availability set by nldc
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 576 | 12516363.6 | U1 S/D 09/Oct/24 (Maintenance Work)
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 166018 | Default availability set by nldc
Chattogram Area Total |  |  |  |  | 5064.22 | 1746.36 | 32971706.6
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 198 | 4726000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 356.15 | 350 | 7850200 | FGMO
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | -
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.96 | 45 | 33 | 788400 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 28 | 564960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 189 | 3378909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1233014 | Default availability set by nldc
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 70 | 282690 | Default availability set by nldc
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Default availability set by nldc
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | Default availability set by nldc
| Import (Tripura) |  | Import | 0 | 160 | 58 | 1198080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Default availability set by nldc
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 8 | 387480 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Default availability set by nldc
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 106 | 796320 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 25 | 105600 | -
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 77040 | -
Cumilla Area Total |  |  |  |  | 2881.85 | 1133 | 21388693
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 3 | 0 | 1550 | Default availability set by nldc
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 65 | 554400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 75 | 682800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 88470 | Default availability set by nldc
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 278640 | Ready to Dispatch as per NLDC Demand.
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 150 | 0 | 0 | Default availability set by nldc
Mymensingh Area Total |  |  |  |  | 750 | 162 | 1605860
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Default availability set by nldc
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Default availability set by nldc
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3844554 | Default availability set by nldc
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Default availability set by nldc
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 57216 | Default availability set by nldc
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Default availability set by nldc
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 42 | 880320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Default availability set by nldc
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 207 | 5276550 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Default availability set by nldc
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | Default availability set by nldc
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 381 | 8813000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 310 | 6922400 | air intake filter DP higher due to Fog
Sylhet Area Total |  |  |  |  | 2366 | 1105 | 25794040
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Default availability set by nldc
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 626 | 19122909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 225 | 6342336 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 465840 | Default availability set by nldc
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | Default availability set by nldc
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234 | 1235 | 24356360 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | Default availability set by nldc
Khulna Area Total |  |  |  |  | 3739 | 2086 | 50287445
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | Default availability set by nldc
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 135134 | Default availability set by nldc
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 141 | 3010000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 12212363.64 | Partial Shutdown due to maintenance
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5260840 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 108 | 296400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5957000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1169 | Default availability set by nldc
Barishal Area Total |  |  |  |  | 2266 | 1405 | 26872906.64
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Default availability set by nldc
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Default availability set by nldc
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Default availability set by nldc
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Default availability set by nldc
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Default availability set by nldc
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Default availability set by nldc
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 180 | 3882818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 162 | 4016045 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 169 | 4184791 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 414 | 0 | 0 | Default availability set by nldc
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 11 | 156582 | Default availability set by nldc
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Substation problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 70 | 270400 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 3300 | Default availability set by nldc
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 757.96 | 14433308 | Default availability set by nldc
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 45000 | Default availability set by nldc
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 508680 | Default availability set by nldc
Rajshahi Area Total |  |  |  |  | 3411.72 | 1349.96 | 27500924
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 76 | 1796509 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 205 | 4886000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Default availability set by nldc
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 20892 | Default availability set by nldc
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 357387 | Default availability set by nldc
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 63767 | Default availability set by nldc
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 185040 | Default availability set by nldc
Rangpur Area Total |  |  |  |  | 950 | 316 | 7309595
Eastern Grid Total |  |  |  |  | 18002.49 | 5344.36 | 107537808.6
Western Grid Total |  |  |  |  | 10366.72 | 5156.96 | 111970870.64
National Grid Total |  |  |  |  | 28369.21 | 10501.32 | 219508679.24
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7012.14 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3075 | MW
i) Dhaka area |  |  | 3872.74 |  | MW | i) Khulna area |  |  |  | 1174 | MW
ii) Chattogram area |  |  | 1100.4 |  | MW | ii) Barishal area |  |  |  | 295 | MW
iii) Cumilla area |  |  | 860 |  | MW | iii) Rajshahi area |  |  |  | 940 | MW
iv) Mymensingh area |  |  | 824 |  | MW | iv) Rangpur area |  |  |  | 666 | MW
v) Sylhet area |  |  | 355 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10087.14 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 56 | 18:00 | 133 | Purbasadipur | 102 | 13:00
2 | AKSML | 106 | 07:00 | 68 | Jamalpur | 97 | 18:00 | 134 | Rahanpur | 0 | 01:00
3 | Aftabnagar | 24 | 12:00 | 69 | Jashore | 101 | 13:00 | 135 | Rahim | 53 | 18:00
4 | Agargaon | 83 | 13:00 | 70 | Jhenaidah | 92 | 18:00 | 136 | Rajbari | 56 | 18:00
5 | Agrabad | 58 | 18:00 | 71 | Joydebpur | 136 | 12:00 | 137 | Rajendrapur | 98 | 20:00
6 | Amnura | 45 | 13:00 | 72 | Joypurhat | 40 | 19:00 | 138 | Rajshahi | 92 | 13:00
7 | Ashuganj | 57 | 12:00 | 73 | Juldah | 8 | 10:00 | 139 | Rajshahi-230 | 40 | 13:00
8 | BSRM | 193 | 19:00 | 74 | KSRM | 28.5 | 09:00 | 140 | Ramganj | 80 | 13:00
9 | Bagerhat | 71 | 18:00 | 75 | Kabirpur | 232 | 15:00 | 141 | Rampur | 24 | 14:00
10 | Bajitpur | N/A | N/A | 76 | Kachua | 48 | 19:00 | 142 | Rangamati | 12 | 18:00
11 | Bakulia | 63 | 13:00 | 77 | Kallyanpur | 57 | 15:00 | 143 | Rangpur | 109 | 13:00
12 | Banani | 39 | 17:00 | 78 | Kalurghat | 26 | 11:00 | 144 | Ruppur | 2.4 | 10:00
13 | Bangabhaban | 7 | 12:00 | 79 | Kamrangirchar | 53 | 13:00 | 145 | SSM | 14 | 01:00
14 | Barapukuria | 42 | 18:30 | 80 | Kaptai | N/A | N/A | 146 | Saidpur | 86 | 09:00
15 | Barguna | 14 | 20:00 | 81 | Kazla | 82 | 12:00 | 147 | Satkhira | 85 | 18:30
16 | Barishal | 81 | 13:00 | 82 | Keranigonj | 65 | 12:00 | 148 | Satmasjid | 81 | 13:00
17 | Barishal-230 | 60 | 18:00 | 83 | Khagrachori | 26 | 18:00 | 149 | Savar | 174 | 12:00
18 | Baroaulia | 52 | 12:00 | 84 | Khulna | 68 | 13:00 | 150 | SevenRings | 15.16 | 19:00
19 | Baroirhat | 43 | 19:00 | 85 | Khulshi | 139 | 19:00 | 151 | ShahCement | 32 | 00:00
20 | Bashundhara | 119 | 13:00 | 86 | Kishoreganj | 114 | 20:00 | 152 | Shahjadpur | 51 | 18:30
21 | BashundharaCement | 8 | 10:00 | 87 | Kodda | 258 | 18:00 | 153 | Shahjibazar | 74 | 18:00
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 28 | 18:00 | 154 | Shahmirpur | 30 | 18:00
23 | Benapole | 44 | 08:00 | 89 | Kurigram | 46 | 18:00 | 155 | Shariatpur | 52 | 20:00
24 | Bhaluka | 114 | 19:00 | 90 | Kushtia | 102 | 18:00 | 156 | Sherpur | 104 | 18:00
25 | Bhandaria | 35 | 21:00 | 91 | Lalbag | 61 | 13:00 | 157 | Shikalbaha | 22 | 18:00
26 | Bhangura | 22 | 18:00 | 92 | Lalmonirhat | 42 | 18:00 | 158 | Shitalakhya | 59.7 | 12:00
27 | Bheramara(GK) | 41 | 18:00 | 93 | MI_Cement | 17.8 | 14:00 | 159 | Sholosohor | 30 | 12:00
28 | Bhulta | 259 | 12:00 | 94 | Madanganj | 21 | 09:00 | 160 | Shyampur | 164 | 10:00
29 | Bog-Sherpur | 52 | 18:00 | 95 | Madaripur | 70 | 19:30 | 161 | Siddhirganj | 90 | 12:00
30 | Bogura | 101 | 19:00 | 96 | Madartek | 57.37 | 13:00 | 162 | Sirajganj | 64 | 11:00
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 26 | 12:00 | 163 | Sonargaon | 82 | 12:00
32 | Brahmanbaria | 105 | 19:30 | 98 | Magura | 44 | 18:00 | 164 | Sreemongol | 44 | 18:00
33 | Cantonment | 86 | 13:00 | 99 | Mahasthangarh | 48 | 18:30 | 165 | Sreepur | 64 | 11:00
34 | Chandpur | 45 | 20:00 | 100 | Manikganj | 91 | 18:30 | 166 | Srinagar | 29.6 | 20:00
35 | Chandraghona | 25 | 18:00 | 101 | Maniknagar | 42 | 13:00 | 167 | Sunamganj | 36 | 18:00
36 | Chapai | 48 | 12:00 | 102 | Matarbari | 32 | 18:30 | 168 | Sylhet | 28 | 14:00
37 | Charsaidpur | 42 | 11:00 | 103 | Matuail | 46 | 10:00 | 169 | Sylhet-132 | 72 | 13:00
38 | Chauddagram | 39 | 18:30 | 104 | Millgate | 71 | 11:00 | 170 | TK | 15 | 18:00
39 | Chhatak | 21 | 18:30 | 105 | Mirpur | 75 | 14:00 | 171 | Tangail | 132 | 17:00
40 | Chowmuhani | 141 | 20:00 | 106 | Mirsorai | 8 | 19:30 | 172 | Thakurgaon | 76 | 18:30
41 | Chuadanga | 71 | 18:00 | 107 | Mirzapur | 34 | 18:00 | 173 | Tongi | 100 | 11:00
42 | Coxsbazar | 89 | 18:00 | 108 | Mithapukur | 42 | 18:00 | 174 | Ullahpara | 20 | 18:00
43 | Cumilla(N) | 108 | 18:30 | 109 | Modern | 0 | 00:00 | 175 | Ullon | 35 | 14:00
44 | Cumilla(S) | 120 | 13:00 | 110 | Mogbazar | 73.2 | 15:00 | 176 | Uttara | 53 | 13:00
45 | Daudkandi | 104 | 20:00 | 111 | Mongla | 32 | 16:00 | 177 | UttaraNew | 38 | 00:00
46 | Dhaka | 30 | 13:00 | 112 | Motijheel | 23 | 13:00 | 178 | Zigatola | 64 | 13:00
47 | Dhamrai | 114 | 11:00 | 113 | Munshiganj | 78 | 18:30
48 | Dhanmondi | 88 | 13:00 | 114 | Mymensingh | 167 | 13:00
49 | Dohazari | 80 | 18:00 | 115 | Naogaon | 83 | 18:30
50 | Faridpur | 107 | 18:00 | 116 | Narail | 41 | 18:30
51 | Fatullah | 74 | 11:00 | 117 | Narinda | 50 | 13:00
52 | Fenchuganj | 23 | 19:00 | 118 | Narshingdi | 151 | 19:30
53 | Feni | 74 | 13:00 | 119 | Natore | 99 | 18:30
54 | GPH | 26 | 10:00 | 120 | Nawabganj | 37 | 19:30
55 | Ghatail | 0 | 00:00 | 121 | Netrakona | 106 | 18:00
56 | Ghorashal | 9 | 22:00 | 122 | New | 67 | 11:00
57 | Ghorashal-230 | 42 | 17:00 | 123 | Niamatpur | 49 | 19:30
58 | Goalpara | 26 | 13:00 | 124 | Noapara | 34 | 18:30
59 | Gollamari | 44 | 13:00 | 125 | PHP | 7 | 23:00
60 | Gopalganj | 73.8 | 18:30 | 126 | Pabna | 76 | 18:30
61 | Gulshan | 58 | 14:00 | 127 | Palashbari | 73 | 18:00
62 | Halishahar | 57.5 | 15:00 | 128 | Panchagarh | 44 | 18:00
63 | HaripurSBU | 155 | 12:00 | 129 | Patuakhali | 57 | 20:00
64 | Hasnabad | 66 | 15:00 | 130 | Payra | 20 | 18:00
65 | Hathazari | 63 | 13:00 | 131 | Postogola | 40 | 13:00
66 | Ishurdi | 57 | 18:00 | 132 | Purbachal | 14 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 414 | 08:00 | 395 | 11:00 | Kaliakoir | 379 | 04:00 | 357 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 407 | 2:00 | 378 | 12:00 | Madunaghat | 405 | 04:00 | 394 | 13:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 404 | 02:00 | 376 | 12:00 | Meghnaghat | 398 | 03:00 | 386 | 12:00
| Bibiana | 395 | 02:00 | 380 | 12:00 | Payra | 417 | 02:00 | 407 | 13:00
| BIPTC | 409 | 02:00 | 393 | 13:00 | Rahanpur | 416 | 04:00 | 401 | 09:00
| Bogura | 411 | 03:00 | 394 | 13:00 | Rampal | 411 | 02:00 | 398 | 19:30
| Gopalganj | 412 | 05:00 | 398 | 12:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 235 | 04:00 | 222 | 12:00 | Haripur | 237 | 04:00 | 222 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 231 | 04:00 | 223 | 11:00 | Hasnabad | 234 | 02:00 | 221 | 12:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 233 | 03:00 | 220 | 12:00 | Hathazari | 233 | 04:00 | 225 | 12:00
| Ashuganj | 238 | 03:00 | 230 | 16:00 | Ishurdi | 243 | 01:00 | 231 | 13:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 03:00 | 230 | 16:00 | Jhenaidah | 241 | 03:00 | 227 | 12:00
| Baghabari | 243 | 03:00 | 231 | 12:00 | Kaliakoir | 236 | 03:00 | 221 | 12:00 | 230 kV MAX | 247 |  | 247 | 214
| Barapukuria | 227 | 04:00 | 214 | 09:00 | Keranigonj | 234 | 03:00 | 221 | 12:00 | 230 kV MIN | 214 |  | 243 | 220 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 227 | 04:00 | 214 | 09:00 | Khulna(S) | 240 | 03:00 | 229 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 245 | 02:00 | 239 | 13:00 | Madunaghat | 231 | 19:00 | 225 | 12:00 | 132 kV MAX | 142 |  | 142 | 114 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 240 | 01:00 | 229 | 12:00 | Madunaghat-400 | 233 | 04:00 | 226 | 12:00 | 132 kV MIN | 112 |  | 142 | 112 |  |  |  | 400 kV | 7 | [25 empty] | 403
| Bhulta | 239 | 02:00 | 223 | 12:00 | Maniknagar | 238 | 04:00 | 223 | 12:00 | [35 empty] | 6:00
| Bibiana | 230 | 03:00 | 220 | 12:00 | Meghnaghat | 242 | 05:00 | 231 | 12:00 | [35 empty] | 392
| BIPTC | 243 | 01:00 | 230 | 13:00 | Meghnaghat-400 | 238 | 02:00 | 226 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 238 | 02:00 | 231 | 12:00 | Mirsorai | 235 | 03:00 | 220 | 12:00 | ` | [34 empty] | 21:00
| Bogura-400 | 238 | 02:00 | 229 | 13:00 | Rajshahi | 242 | 03:00 | 229 | 13:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 247 | 04:00 | 243 | 14:00 | Rampal | 238 | 02:00 | 227 | 13:00 |  |  |  |  | Ash 400-299274
| BSRM | 232 | 03:00 | 219 | 12:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 234 | 04:00 | 222 | 12:00 | Rampura | 238 | 02:00 | 222 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 244 | 02:00 | 236 | 12:00 | Shikalbaha | 231 | 03:00 | 222 | 11:00 |  | kaptai by call 399528
| Fenchuganj | 232 | 01:00 | 226 | 12:00 | Shyampur | 236 | 03:00 | 223 | 12:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Siddhirganj | 236 | 00:00 | 225 | 11:00
| Ghorashal-230 | 237 | 05:00 | 222 | 13:00 | Sirajgonj | 246 | 02:00 | 205 | 23:00
| Gopalganj | 243 | 02:00 | 235 | 13:00 | Sreepur | 239 | 00:00 | 227 | 13:00
| GPH | 232 | 03:00 | 221 | 12:00 | Tongi | 235 | 04:00 | 222 | 11:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 136 | 03:00 | 125 | 12:00 | Kurigram | 132 | 04:00 | 117 | 09:00 |  | Gopalganj-230 | 599470
| Agargaon | 137 | 03:00 | 128 | 13:00 | Kushtia | 141 | 03:00 | 134 | 13:00
| Agrabad | 133 | 01:00 | 128 | 12:00 | Lalbag | 134 | 02:00 | 126 | 12:00
| AKS | 131 | 00:00 | 126 | 12:00 | Lalmonirhat | 131 | 05:00 | 117 | 18:00
| Aminbazar | 135 | 06:00 | 127 | 11:00 | Madanganj | 132 | 03:00 | 124 | 12:00
| Amnura | 140 | 00:00 | 133 | 09:00 | Madaripur | 134 | 02:00 | 132 | 00:00
| Ashuganj | 140 | 00:00 | 136 | 13:00 | Madartek | 135 | 03:00 | 125 | 12:00
| Bagerhat | 136 | 01:00 | 129 | 18:00 | Madunaghat | 133 | 04:00 | 128 | 12:00
| Bajitpur | 140 | 00:00 | 136 | 13:00 | Magura | 141 | 04:00 | 131 | 13:00
| Bakulia | 135 | 19:00 | 128 | 12:00 | Mahasthangarh | 137 | 03:00 | 129 | 18:00
| Banani | 136 | 05:00 | 125 | 12:00 | Manikganj | 132 | 03:00 | 120 | 12:00
| Bangabhaban | 135 | 01:00 | 126 | 12:00 | Maniknagar | 135 | 03:00 | 126 | 12:00
| Barapukuria | 137 | 04:00 | 126 | 09:00 | Matarbari | 129 | 06:00 | 122 | 13:00
| Barguna | 136 | 02:00 | 132 | 12:00 | Matuail | 133 | 01:00 | 125 | 12:00
| Barishal | 135 | 03:00 | 131 | 12:00 | Millgate | 136 | 03:00 | 123 | 12:00
| Barishal-230 | 137 | 03:00 | 132 | 12:00 | Mirpur | 134 | 05:00 | 127 | 12:00
| Baroaulia | 133 | 01:00 | 128 | 12:00 | Mirzapur | 129 | 05:00 | 120 | 12:00
| Baroirhat | 130 | 07:00 | 123 | 12:00 | Mithapukur | 134 | 02:00 | 124 | 18:00
| Bashundhara | 136 | 03:00 | 123 | 12:00 | MI_Cement | 134 | 03:00 | 125.1 | 12:00
| BashundharaCement | 132 | 03:00 | 124 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 135 | 03:00 | 130 | 12:00 | Mogbazar | 137 | 04:00 | 125 | 13:00
| Benapole | 139 | 03:00 | 127 | 13:00 | Mongla | 138 | 04:00 | 128 | 13:00
| Bhaluka | 130 | 00:00 | 121 | 12:00 | Motijheel | 135 | 01:00 | 126 | 12:00
| Bhandaria | 134 | 05:00 | 129 | 13:00 | Munshiganj | 133 | 04:00 | 125 | 11:00
| Bhangura | 139 | 00:00 | 133 | 12:00 | Mymensingh | 134 | 18:30 | 112 | 08:00
| Bheramara | 140 | 01:00 | 135 | 12:00 | Naogaon | 136 | 03:00 | 129 | 13:00
| Bheramara(GK) | 140 | 01:00 | 135 | 13:00 | Narail | 140 | 04:00 | 130 | 13:00
| Bhulta | 124 | 03:00 | 118 | 12:00 | Narinda | 135 | 7:00 | 126 | 12:00
| Bog-Sherpur | 138 | 02:00 | 131 | 11:00 | Narshingdi | 129 | 01:00 | 122 | 10:00
| Bogura | 138 | 03:00 | 131 | 13:00 | Natore | 139 | 03:00 | 132 | 13:00
| Bogura-230 | 138 | 02:00 | 132 | 12:00 | Nawabganj | 135 | 06:00 | 126 | 12:00
| Brahmanbaria | 133 | 04:00 | 126 | 12:00 | Netrakona | 130 | 00:00 | 121 | 12:00
| Cantonment | 136 | 02:00 | 128 | 12:00 | New | 135 | 02:00 | 125 | 12:00
| Chandpur | 130 | 18:00 | 119 | 12:00 | Niamatpur | 141 | 01:00 | 134 | 12:00
| Chandraghona | 134 | 01:00 | 129 | 12:00 | Noapara | 139 | 03:00 | 130 | 13:00
| Chapai | 138 | 02:00 | 133 | 11:00 | Pabna | 141 | 02:00 | 134 | 12:00
| Charsaidpur | 134 | 04:00 | 125 | 13:00 | Palashbari | 134 | 04:00 | 124 | 18:00
| Chauddagram | 132 | 04:00 | 124 | 12:00 | Panchagarh | 136 | 04:00 | 117 | 09:00
| Chhatak | 134 | 05:00 | 130 | 15:00 | Patuakhali | 137 | 19:00 | 131 | 12:00
| Chowmuhani | 129 | 18:00 | 118 | 12:00 | Payra | 137 | 02:00 | 132 | 15:00
| Chuadanga | 141 | 05:00 | 127 | 13:00 | PHP | 131 | 04:00 | 122 | 12:00
| Coxsbazar | 129 | 02:00 | 123 | 12:00 | Postogola | 136 | 02:00 | 127 | 12:00
| Cumilla(N) | 136 | 05:00 | 127 | 12:00 | Purbachal | 136 | 01:00 | 125 | 12:00
| Cumilla(S) | 133 | 05:00 | 126 | 12:00 | Purbasadipur | 132 | 04:00 | 117 | 09:00
| Daudkandi | 133 | 02:00 | 124 | 12:00 | Rahanpur | 140 | 01:00 | 136 | 09:00
| Dhaka | 136 | 02:00 | 125 | 12:00 | Rahanpur-400 | 141 | 02:00 | 136 | 09:00
| Dhamrai | 136 | 02:00 | 127 | 13:00 | Rahim | 132 | 03:00 | 123 | 13:00
| Dhanmondi | 137 | 02:00 | 126 | 12:00 | Rajbari | 135 | 02:00 | 130 | 12:00
| Dohazari | 132 | 02:00 | 125 | 12:00 | Rajendrapur | 135 | 05:00 | 125 | 13:00
| Faridpur | 136 | 03:00 | 130 | 13:00 | Rajshahi | 139 | 01:00 | 133 | 12:00
| Fatullah | 135 | 05:00 | 126 | 12:00 | Rajshahi-230 | 140 | 04:00 | 130 | 13:00
| Fenchuganj | 138 | 01:00 | 134 | 12:00 | Ramganj | 127 | 18:00 | 117 | 12:00
| Feni | 131 | 05:00 | 124 | 12:00 | Rampur | 134 | 04:00 | 128 | 12:00
| Ghatail | 130 | 20:00 | 114 | 08:00 | Rampura | 135 | 02:00 | 125 | 12:00
| Ghorashal | 140 | 07:00 | 134 | 13:00 | Rangamati | 134 | 04:00 | 128 | 12:00
| Goalpara | 140 | 02:00 | 130 | 13:00 | Rangpur | 133 | 03:00 | 119 | 09:00
| Gollamari | 139 | 03:00 | 131 | 13:00 | Ruppur | 142 | 01:00 | 136 | 11:00
| Gopalganj | 137 | 02:00 | 131 | 12:00 | Saidpur | 133 | 04:00 | 122 | 08:00
| Gopalganj-400 | 137 | 02:00 | 132 | 12:00 | Satkhira | 139 | 03:00 | 129 | 18:30
| Gulshan | 134 | 07:00 | 125 | 12:00 | Satmasjid | 136 | 02:00 | 128 | 12:00
| Halishahar | 132 | 00:00 | 125 | 12:00 | Savar | 134 | 05:00 | 125 | 12:00
| Haripur | 133 | 04:00 | 125 | 12:00 | SevenRings | 141 | 02:00 | 133 | 12:00
| HaripurSBU | 133 | 04:00 | 123 | 13:00 | ShahCement | 134 | 04:00 | 125 | 13:00
| Hasnabad | 135 | 04:00 | 127 | 11:00 | Shahjadpur | 142 | 00:00 | 138 | 07:00
| Hathazari | 136 | 00:00 | 131 | 12:00 | Shahjibazar | 136 | 01:00 | 129 | 12:00
| Ishurdi | 142 | 01:00 | 136 | 12:00 | Shahmirpur | 133 | 04:00 | 128 | 11:00
| Jaldhaka | 132 | 04:00 | 118 | 09:00 | Shariatpur | 137 | 04:00 | 131 | 13:00
| Jamalpur | 136 | 19:00 | 116 | 16:00 | Sherpur | 135 | 17:00 | 112 | 15:00
| Jashore | 138 | 01:00 | 129 | 13:00 | Shikalbaha | 122 | 18:30 | 117 | 12:00
| Jhenaidah | 140 | 04:00 | 132 | 12:00 | Shikalbaha-230 | 135 | 04:00 | 129 | 12:00
| Jhenaidah-230 | 141 | 01:00 | 132 | 13:00 | Shitalakhya | 134 | 03:00 | 125.1 | 12:00
| Joydebpur | 140 | 02:00 | 132 | 12:00 | Sholosohor | 134 | 03:00 | 128 | 12:00
| Joypurhat | 137 | 02:00 | 129 | 13:00 | Shyampur | 132 | 05:00 | 125 | 13:00
| Juldah | 134 | 05:00 | 128 | 12:00 | Shyampur-230 | 133 | 02:00 | 125 | 12:00
| Kabirpur | 134 | 03:00 | 121 | 12:00 | Siddhirganj | 134 | 04:00 | 125 | 12:00
| Kachua | 131 | 03:00 | 121 | 13:00 | Sirajganj | 140 | 03:00 | 131 | 12:00
| Kaliakoir | 138 | 03:00 | 123 | 12:00 | Sonargaon | 129 | 01:00 | 125 | 16:00
| Kallyanpur | 135 | 02:00 | 130 | 11:00 | Sreemongol | 135 | 03:00 | 130 | 00:00
| Kalurghat | 134 | 04:00 | 129 | 12:00 | Sreepur | 131 | 04:00 | 123 | 13:00
| Kamrangirchar | 134 | 02:00 | 127 | 12:00 | Srinagar | 135 | 04:00 | 126 | 12:00
| Kaptai | 136 | 5:00 | 131 | 10:00 | SSM | 138 | 04:00 | 134 | 10:00
| Kazla | 135 | 03:00 | 125 | 13:00 | Sunamganj | 132 | 00:00 | 129 | 18:00
| Keranigonj | 135 | 03:00 | 127 | 12:00 | Sylhet | 135 | 02:00 | 131 | 12:00
| Khagrachori | 134 | 04:00 | 127 | 12:00 | Sylhet-132 | 134 | 01:00 | 132 | 12:00
| Khulna | 138 | 04:00 | 130 | 13:00 | Tangail | 129 | 10:00 | 118 | 07:00
| Khulna(S) | 140 | 03:00 | 132 | 13:00 | Thakurgaon | 133 | 03:00 | 114 | 09:00
| Khulshi | 132 | 02:00 | 127 | 12:00 | TK | 134 | 03:00 | 130 | 09:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 133 | 00:00 | 127 | 12:00 | Tongi | 135 | 04:00 | 127 | 11:00 |  |  | Nos | Nos | Nos
| Kodda | 136 | 20:00 | 119 | 16:00 | Ullahpara | 140 | 01:00 | 132 | 11:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 134 | 02:00 | 128 | 12:00 | Ullon | 134 | 05:00 | 126 | 12:00
| Kulaura | 137 | 03:00 | 133 | 12:00 | Uttara | 135 | 02:00 | 127 | 12:00
| Zigatola | 135 | 04:00 | 126 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8514.5 | 0 |  | 8514.5
1:00 | 7795.5 | 0 |  | 7795.5
2:00 | 7440.5 | 0 |  | 7440.5
3:00 | 7119.5 | 0 |  | 7119.5
4:00 | 6919.5 | 0 |  | 6919.5
5:00 | 6826.5 | 0 |  | 6826.5
6:00 | 7344.5 | 0 |  | 7344.5
7:00 | 7903.5 | 0 |  | 7903.5
8:00 | 8892.01 | 0 |  | 8892.01
9:00 | 9479.92 | 0 |  | 9479.92
10:00 | 9484.56 | 0 |  | 9484.56
11:00 | 9671.22 | 0 |  | 9671.22
12:00 | 9974.06 | 0 |  | 9974.06
13:00 | 10145.28 | 0 |  | 10145.28
14:00 | 9755.75 | 0 |  | 9755.75
15:00 | 9398.68 | 0 |  | 9398.68
16:00 | 9159.97 | 0 |  | 9159.97
17:00 | 9310.04 | 0 |  | 9310.04
18:00 | 10393.41 | 0 |  | 10393.41
19:00 | 10501.32 | 0 |  | 10501.32
19:30 | 10426.46 | 0 |  | 10426.46
20:00 | 10336.73 | 0 |  | 10336.73
21:00 | 10023.5 | 0 |  | 10023.5
22:00 | 9604.63 | 0 |  | 9604.63
23:00 | 8976.58 | 0 |  | 8976.58
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4059 | 4455.5 | 8514.5 | DAILY LOAD CURVE
00:30 | 3913 | 4242 | 8155
01:00 | 3767 | 4028.5 | 7795.5 | 02-01-2025
01:30 | 3703.5 | 3914.5 | 7618
02:00 | 3640 | 3800.5 | 7440.5
02:30 | 3530.5 | 3749.5 | 7280
03:00 | 3421 | 3698.5 | 7119.5
03:30 | 3410.5 | 3609 | 7019.5
04:00 | 3400 | 3519.5 | 6919.5
04:30 | 3372 | 3501 | 6873
05:00 | 3344 | 3482.5 | 6826.5
05:30 | 3498.5 | 3587 | 7085.5
06:00 | 3653 | 3691.5 | 7344.5
06:30 | 3831 | 3793 | 7624
07:00 | 4009 | 3894.5 | 7903.5
07:30 | 4172.28 | 4225.475 | 8397.755
08:00 | 4335.56 | 4556.45 | 8892.01
08:30 | 4425.735 | 4760.23 | 9185.965
09:00 | 4515.91 | 4964.01 | 9479.92
09:30 | 4564.435 | 4917.805 | 9482.24
10:00 | 4612.96 | 4871.6 | 9484.56
10:30 | 4594.735 | 4983.155 | 9577.89
11:00 | 4576.51 | 5094.71 | 9671.22
11:30 | 4683.51 | 5139.13 | 9822.64
12:00 | 4790.51 | 5183.55 | 9974.06
12:30 | 4843.41 | 5216.26 | 10059.67
13:00 | 4896.31 | 5248.97 | 10145.28
13:30 | 4880.02 | 5070.495 | 9950.515
14:00 | 4863.73 | 4892.02 | 9755.75
14:30 | 4742.945 | 4834.27 | 9577.215
15:00 | 4622.16 | 4776.52 | 9398.68
15:30 | 4574.93 | 4704.395 | 9279.325
16:00 | 4527.7 | 4632.27 | 9159.97
16:30 | 4528.465 | 4706.54 | 9235.005
17:00 | 4529.23 | 4780.81 | 9310.04
17:30 | 4902.615 | 4949.11 | 9851.725
18:00 | 5276 | 5117.41 | 10393.41
18:30 | 5310.18 | 5137.185 | 10447.365
19:00 | 5344.36 | 5156.96 | 10501.32
19:30 | 5257.36 | 5169.1 | 10426.46
20:00 | 5176.36 | 5160.37 | 10336.73
20:30 | 4995.86 | 5184.255 | 10180.115 |  | Executive Engineer
21:00 | 4815.36 | 5208.14 | 10023.5 |  | Network Operation Division
21:30 | 4639.68 | 5174.385 | 9814.065
22:00 | 4464 | 5140.63 | 9604.63
22:30 | 4393.5 | 4897.105 | 9290.605
23:00 | 4323 | 4653.58 | 8976.58

## En-Curve
QF-LDC-12
Date | 02-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2701 | 1431.5 | 911 | 0 | 48 | 482 | 40 | 2847 | 0 | 0 | 35 | 0 | 0 | 19 | 0 | DAILY ENERGY CURVE
00:30 | 2705 | 1353 | 867.5 | 0 | 44 | 448.5 | 40 | 2664 | 0 | 0 | 17.5 | 0 | 0 | 15.5 | 0 | 02-01-2025
01:00 | 2709 | 1274.5 | 824 | 0 | 40 | 415 | 40 | 2481 | 0 | 0 | 0 | 0 | 0 | 12 | 0
01:30 | 2693 | 1274 | 772.5 | 0 | 39 | 415 | 40 | 2373 | 0 | 0 | 0 | 0 | 0 | 11.5 | 0 |  | Total Energy | 219.5087 |  | MKWHr
02:00 | 2677 | 1273.5 | 721 | 0 | 38 | 415 | 40 | 2265 | 0 | 0 | 0 | 0 | 0 | 11 | 0 |  | Energy not Served | 0 |  | MKWHr
02:30 | 2636.5 | 1205.5 | 720.5 | 0 | 38 | 415.5 | 40 | 2215.5 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 |  | Energy Requirement | 219.5087 |  | MKWHr
03:00 | 2596 | 1137.5 | 720 | 0 | 38 | 416 | 40 | 2166 | 0 | 0 | 0 | 0 | 0 | 6 | 0
03:30 | 2591 | 1090.5 | 668 | 0 | 38 | 415.5 | 40 | 2165.5 | 0 | 0 | 0 | 0 | 0 | 11 | 0
04:00 | 2586 | 1043.5 | 616 | 0 | 38 | 415 | 40 | 2165 | 0 | 0 | 0 | 0 | 0 | 16 | 0
04:30 | 2558.5 | 1026 | 621 | 0 | 38 | 415 | 40 | 2164.5 | 0 | 0 | 0 | 0 | 0 | 10 | 0
05:00 | 2531 | 1008.5 | 626 | 0 | 38 | 415 | 40 | 2164 | 0 | 0 | 0 | 0 | 0 | 4 | 0
05:30 | 2611.5 | 1146.5 | 626 | 0 | 39 | 415 | 40 | 2204.5 | 0 | 0 | 0 | 0 | 0 | 3 | 0
06:00 | 2692 | 1284.5 | 626 | 0 | 40 | 415 | 40 | 2245 | 0 | 0 | 0 | 0 | 0 | 2 | 0
06:30 | 2751 | 1340.5 | 673 | 0 | 40 | 416 | 40 | 2336 | 1 | 6.5 | 16 | 0 | 0 | 4 | 0
07:00 | 2810 | 1396.5 | 720 | 0 | 40 | 417 | 40 | 2427 | 2 | 13 | 32 | 0 | 0 | 6 | 0
07:30 | 2809 | 1373.75 | 814.5 | 0 | 39 | 466 | 40 | 2754 | 21.505 | 23.5 | 51 | 0 | 0 | 5.5 | 0
08:00 | 2808 | 1351 | 909 | 0 | 38 | 515 | 40 | 3081 | 41.01 | 34 | 70 | 0 | 0 | 5 | 0
08:30 | 2819.5 | 1384.25 | 827 | 0 | 44 | 629.5 | 40 | 3228.5 | 67.215 | 56.5 | 86.5 | 0 | 0 | 3 | 0
09:00 | 2831 | 1417.5 | 745 | 0 | 50 | 744 | 40 | 3376 | 93.42 | 79 | 103 | 0 | 0 | 1 | 0
09:30 | 2811.5 | 1412.5 | 685.5 | 0 | 51 | 748.98 | 40 | 3333 | 141.26 | 89 | 165.5 | 0 | 0 | 4 | 0
10:00 | 2792 | 1407.5 | 626 | 0 | 52 | 753.96 | 40 | 3290 | 189.1 | 99 | 228 | 0 | 0 | 7 | 0
10:30 | 2766 | 1380 | 742 | 0 | 56 | 754.48 | 40 | 3290 | 217.41 | 91 | 232.5 | 0 | 0 | 8.5 | 0
11:00 | 2740 | 1352.5 | 858 | 0 | 60 | 755 | 40 | 3290 | 245.72 | 83 | 237 | 0 | 0 | 10 | 0
11:30 | 2794.5 | 1379.5 | 883 | 0 | 59 | 757 | 40 | 3313.5 | 259.64 | 83 | 244.5 | 0 | 0 | 9 | 0
12:00 | 2849 | 1406.5 | 908 | 0 | 58 | 759 | 40 | 3337 | 273.56 | 83 | 252 | 0 | 0 | 8 | 0
12:30 | 2870 | 1423.5 | 908.5 | 0 | 57 | 759 | 40 | 3323.5 | 278.67 | 83 | 312.5 | 0 | 0 | 4 | 0
13:00 | 2891 | 1440.5 | 909 | 0 | 56 | 759 | 40 | 3310 | 283.78 | 83 | 373 | 0 | 0 | 0 | 0
13:30 | 2846 | 1433.5 | 909 | 0 | 59 | 712 | 40 | 3228.5 | 285.015 | 93 | 344.5 | 0 | 0 | 0 | 0
14:00 | 2801 | 1426.5 | 909 | 0 | 62 | 665 | 40 | 3147 | 286.25 | 103 | 316 | 0 | 0 | 0 | 0
14:30 | 2764 | 1453 | 909 | 0 | 60 | 664.485 | 40 | 3143.5 | 235.23 | 94 | 214 | 0 | 0 | 0 | 0
15:00 | 2727 | 1479.5 | 909 | 0 | 58 | 663.97 | 40 | 3140 | 184.21 | 85 | 112 | 0 | 0 | 0 | 0
15:30 | 2766 | 1475 | 909.5 | 0 | 55 | 636.575 | 40 | 3062 | 133.75 | 85 | 116 | 0 | 0 | 0.5 | 0
16:00 | 2805 | 1470.5 | 910 | 0 | 52 | 609.18 | 40 | 2984 | 83.29 | 85 | 120 | 0 | 0 | 1 | 0
16:30 | 2808 | 1446.5 | 909.5 | 0 | 49 | 611.44 | 40 | 3015.5 | 49.065 | 122 | 182 | 0 | 0 | 2 | 0
17:00 | 2811 | 1422.5 | 909 | 0 | 46 | 613.7 | 40 | 3047 | 14.84 | 159 | 244 | 0 | 0 | 3 | 0
17:30 | 2852 | 1408.75 | 767.5 | 0 | 51 | 706.555 | 40 | 3296.5 | 7.42 | 198.5 | 521 | 0 | 0 | 2.5 | 0
18:00 | 2893 | 1395 | 626 | 0 | 56 | 799.41 | 40 | 3546 | 0 | 238 | 798 | 0 | 0 | 2 | 0
18:30 | 2880.5 | 1400.5 | 626 | 0 | 57 | 778.685 | 40 | 3589.5 | 0 | 214 | 853.68 | 0 | 0 | 7.5 | 0
19:00 | 2868 | 1406 | 626 | 0 | 58 | 757.96 | 40 | 3633 | 0 | 190 | 909.36 | 0 | 0 | 13 | 0
19:30 | 2852 | 1412 | 626 | 0 | 68 | 759.1 | 40 | 3639 | 0 | 190 | 824.36 | 0 | 0 | 16 | 0
20:00 | 2805 | 1382 | 625 | 0 | 56 | 757.37 | 40 | 3641 | 0 | 190 | 824.36 | 0 | 0 | 16 | 0
20:30 | 2807 | 1362.25 | 751 | 0 | 59 | 755.005 | 40 | 3642 | 0 | 137.5 | 611.36 | 0 | 0 | 15 | 0
21:00 | 2809 | 1342.5 | 877 | 0 | 62 | 752.64 | 40 | 3643 | 0 | 85 | 398.36 | 0 | 0 | 14 | 0
21:30 | 2789 | 1321.5 | 896 | 0 | 58 | 714.385 | 40 | 3642.5 | 0 | 73.5 | 263.68 | 0 | 0 | 15.5 | 0
22:00 | 2769 | 1300.5 | 915 | 0 | 54 | 676.13 | 40 | 3642 | 0 | 62 | 129 | 0 | 0 | 17 | 0
22:30 | 2742.5 | 1289 | 915.5 | 0 | 55 | 590.105 | 33 | 3521 | 0 | 39.5 | 87.5 | 0 | 0 | 17.5 | 0
23:00 | 2716 | 1277.5 | 916 | 0 | 56 | 504.08 | 26 | 3400 | 0 | 17 | 46 | 0 | 0 | 18 | 0
Executive Engineer
Network Operation Division