## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-01-2025 | [28 empty] | Date: | 06-01-2025 | [28 empty] | Date: | 06-01-2025 | [28 empty] | Date: | 06-01-2025 | [28 empty] | Date: | 06-01-2025 | [18 empty] | Date: | 06-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.000 MW | 365.000 MW | 260.000 MW | 234.580 MW | 190.000 MW | 108.000 MW | 412.000 MW | 20.000 MW | 718.000 MW | 54.000 MW | 36.090 MW | 20.000 MW | 149.000 MW | 149.000 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 150.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 66.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 33.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.000 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1320.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 400.000 MW | 356.150 MW | 360.000 MW | 55.000 MW | 221.000 MW | 45.000 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 50.000 MW | 70.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 3.000 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.000 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 52.000 MW | 71.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 414.000 MW | 414.000 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 380 | 0 | 0 | 0 | 0 | 22.5 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 90 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 32 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 51 | 0 | 88 | 0 | 255 | 0 | 29 | 181 | 39 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 300 | 346 | 379 | 0 | 0 | 30 | 2 | 120 | 13 | 0 | 30 | 0 | 0 | 0 | 213 | 0 | 18 | 19 | 12 | 0 | 0 | 0 | 4473.5 | 918 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 908 | 0 | 421.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 174 | 0 | 0 | 0 | 0 | 5.5 | 220 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 490 | 0 | 4283.76 | 8757.26 | 93.74
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 0 | 9 | 22 | 0 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 32 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 51 | 0 | 88 | 0 | 255 | 0 | 29 | 182 | 39 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 270 | 346 | 379 | 0 | 0 | 30 | 2 | 120 | 13 | 0 | 30 | 0 | 0 | 0 | 212 | 0 | 18 | 19 | 12 | 0 | 0 | 0 | 4310 | 913 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 0 | 423.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 167 | 0 | 0 | 0 | 0 | 2.5 | 200 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 220 | 0 | 400 | 0 | 4011.9 | 8321.9 | 93.73
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 0 | 9.9 | 22 | 0 | 60 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 32 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 51 | 0 | 88 | 0 | 255 | 0 | 29 | 182 | 39 | 0 | 50 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 275 | 346 | 381 | 0 | 0 | 30 | 2 | 120 | 13 | 0 | 30 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 4013.9 | 726 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 421.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 165 | 0 | 163 | 0 | 0 | 0 | 0 | 2.5 | 200 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 180 | 0 | 320 | 0 | 3653.91 | 7667.81 | 93.73
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 0 | 9.9 | 22 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 24 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 16 | 0 | 255 | 0 | 5 | 192 | 5 | 0 | 70 | 0 | 0 | 15 | 0 | 42 | 0 | 0 | 0 | 290 | 360 | 380 | 0 | 0 | 30 | 2 | 120 | 13 | 0 | 5 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 3799.9 | 725 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 420.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 167 | 0 | 164 | 0 | 0 | 0 | 0 | 2.5 | 200 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 180 | 0 | 300 | 0 | 3557.09 | 7356.99 | 93.73
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 24 | 270 | 0 | 0 | 0 | 0 | 9.9 | 22 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 27 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 8 | 0 | 255 | 0 | 5 | 181 | 5 | 0 | 50 | 0 | 0 | 15 | 0 | 40 | 0 | 0 | 0 | 285 | 346 | 380 | 0 | 0 | 30 | 2 | 120 | 13 | 0 | 5 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 3759.9 | 631 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 418.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 167 | 0 | 165 | 0 | 0 | 0 | 0 | 2.5 | 200 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 100 | 180 | 0 | 250 | 0 | 3384.72 | 7144.62 | 93.73
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 25 | 270 | 0 | 0 | 0 | 0 | 9.9 | 22 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 27 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 8 | 0 | 255 | 0 | 5 | 190 | 5 | 0 | 50 | 0 | 0 | 15 | 0 | 40 | 0 | 0 | 0 | 285 | 346 | 310 | 0 | 0 | 30 | 2 | 120 | 13 | 0 | 5 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 3720.9 | 632 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 419.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 149 | 0 | 150 | 0 | 0 | 0 | 0 | 2.5 | 200 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 250 | 0 | 3361.84 | 7082.74 | 93.72
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 25 | 335 | 0 | 0 | 0 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 27 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 92 | 0 | 255 | 0 | 5 | 196 | 30 | 0 | 50 | 0 | 0 | 15 | 0 | 42 | 0 | 0 | 0 | 300 | 352 | 352 | 0 | 0 | 30 | 2 | 163 | 13 | 0 | 5 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 3951.5 | 632 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 422.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 156 | 0 | 163 | 0 | 0 | 0 | 0 | 2.5 | 200 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 250 | 0 | 3582.88 | 7534.38 | 93.72
07:00 | 0 | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 25 | 335 | 0 | 0 | 1 | 0 | 10.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 19 | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 1 | 37 | 0 | 187 | 0 | 0 | 0 | 14 | 205 | 39 | 0 | 70 | 0 | 0 | 15 | 0 | 42 | 0 | 2 | 0 | 295 | 382 | 380 | 0 | 0 | 30 | 2 | 163 | 13 | 0 | 83 | 0 | 0 | 0 | 212 | 0 | 8 | 7 | 20 | 0 | 0 | 0 | 4234.5 | 783 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 901 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 124 | 0 | 170 | 0 | 181 | 0 | 0 | 0 | 0.05 | 2.5 | 205 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.01 | 0 | 241 | 5 | 140 | 220 | 0 | 340 | 0 | 4148.16 | 8382.66 | 93.72
08:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 25 | 335 | 0 | 0 | 7 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 26 | 0 | 2 | 576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 433 | 4 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 189 | 39 | 0 | 50 | 0 | 0 | 15 | 0 | 42 | 0 | 29 | 0 | 285 | 346 | 380 | 0 | 0 | 30 | 2 | 163 | 13 | 0 | 83 | 0 | 0 | 0 | 212 | 0 | 45 | 45 | 19 | 1 | 0 | 0 | 4471 | 912 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.64 | 1052 | 0 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10.89 | 123 | 0 | 165 | 0 | 166 | 0 | 0 | 0 | 0.56 | 2.5 | 205 | 75 | 0 | 5 | 0 | 0 | 0 | 1.4 | 56 | 0.09 | 0 | 291 | 6 | 140 | 220 | 0 | 510 | 0 | 4871.08 | 9342.08 | 93.72
09:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 33 | 0 | 1 | 48 | 0 | 0 | 0 | 0 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 25 | 335 | 0 | 0 | 14 | 0 | 22.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 2 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 10 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 181 | 35 | 0 | 50 | 0 | 0 | 15 | 0 | 46 | 0 | 39 | 0 | 280 | 346 | 380 | 0 | 0 | 30 | 2 | 120 | 13 | 0 | 83 | 0 | 0 | 0 | 212 | 0 | 55 | 67 | 10 | 1 | 0 | 0 | 4662.5 | 631 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 1150 | 0 | 562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 28.53 | 134 | 0 | 155 | 0 | 156 | 0 | 0 | 0 | 2.44 | 2.5 | 205 | 75 | 0 | 17 | 0 | 0 | 0 | 1.5 | 97 | 0.19 | 0 | 307 | 4 | 140 | 180 | 0 | 600 | 0 | 4871.16 | 9533.66 | 93.71
10:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 36 | 0 | 15 | 48 | 0 | 0 | 17 | 0 | 25 | 0 | 420 | 0 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 19 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 2 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 17 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 181 | 31 | 0 | 50 | 0 | 0 | 13 | 0 | 56 | 0 | 55 | 0 | 280 | 346 | 382 | 0 | 0 | 30 | 2 | 120 | 13 | 0 | 83 | 0 | 0 | 0 | 214 | 0 | 56 | 55 | 10 | 2 | 0 | 0 | 4690 | 631 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 1165 | 0 | 465.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 41.35 | 159 | 0 | 158 | 0 | 157 | 0 | 0 | 0 | 3.52 | 2.5 | 204 | 75 | 0 | 17 | 0 | 0 | 0 | 2.5 | 100 | 0.41 | 0 | 200 | 3 | 80 | 180 | 0 | 500 | 0 | 4608.36 | 9298.36 | 93.71
11:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 35 | 36 | 0 | 15 | 48 | 0 | 0 | 17 | 0 | 25 | 0 | 420 | 0 | 0 | 0 | 0 | 19.5 | 335 | 0 | 0 | 29 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 2 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 18 | 51 | 0 | 182 | 0 | 0 | 0 | 29 | 181 | 34 | 0 | 50 | 0 | 0 | 13 | 0 | 58 | 0 | 61 | 0 | 285 | 346 | 382 | 0 | 0 | 29 | 2 | 120 | 13 | 0 | 83 | 0 | 0 | 0 | 214 | 0 | 56 | 18 | 10 | 1 | 0 | 0 | 4725.5 | 776 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 1075 | 0 | 467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 48.97 | 150 | 0 | 156 | 0 | 155 | 0 | 0 | 0 | 4.25 | 2.5 | 205 | 75 | 0 | 30 | 0 | 0 | 0 | 3.7 | 99 | 0.51 | 0 | 200 | 3 | 80 | 180 | 0 | 500 | 0 | 4701.93 | 9427.43 | 93.71
12:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 35 | 34 | 0 | 15 | 48 | 0 | 0 | 17 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 19.5 | 333 | 0 | 0 | 30 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 2 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 19 | 51 | 0 | 184 | 0 | 0 | 0 | 28 | 186 | 36 | 0 | 50 | 0 | 0 | 13 | 0 | 66 | 0 | 66 | 0 | 290 | 346 | 382 | 0 | 0 | 30 | 2 | 163 | 13 | 0 | 83 | 0 | 0 | 0 | 214 | 0 | 47 | 18 | 10 | 2 | 0 | 0 | 4826.5 | 913 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 1163 | 0 | 510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 51.15 | 159 | 0 | 171 | 0 | 169 | 0 | 0 | 0 | 4.7 | 2.5 | 205 | 73 | 0 | 33 | 0 | 0 | 0 | 3 | 74 | 0.52 | 0 | 250 | 3 | 140 | 220 | 0 | 500 | 0 | 5150.87 | 9977.37 | 93.71
13:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 35 | 36 | 0 | 15 | 48 | 0 | 0 | 17 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 19.5 | 334 | 0 | 0 | 29 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 3 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 18 | 51 | 0 | 184 | 0 | 0 | 0 | 29 | 187 | 33 | 0 | 50 | 10 | 8 | 13 | 0 | 66 | 0 | 61 | 0 | 290 | 346 | 385 | 0 | 0 | 30 | 2 | 163 | 0 | 0 | 83 | 0 | 0 | 0 | 214 | 0 | 49 | 18 | 5 | 1 | 0 | 3 | 4923.5 | 914 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 1239 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 55.13 | 192 | 0 | 171 | 0 | 170 | 0 | 0 | 0 | 4.68 | 2.5 | 205 | 74 | 0 | 20 | 0 | 0 | 0 | 3 | 99 | 0.51 | 0 | 250 | 4 | 140 | 220 | 0 | 550 | 0 | 5370.82 | 10294.32 | 93.7
14:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 35 | 19 | 0 | 15 | 48 | 0 | 0 | 17 | 12 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 19.5 | 331 | 0 | 0 | 7 | 0 | 22.3 | 22 | 0 | 80 | 3 | 15 | 0 | 0 | 5 | 0 | 0 | 5 | 2 | 10 | 1 | 46 | 0 | 2 | 575 | 17 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 611 | 16 | 51 | 1 | 184 | 0 | 0 | 0 | 27 | 186 | 35 | 1 | 50 | 17 | 18 | 13 | 0 | 70 | 0 | 58 | 0 | 275 | 346 | 385 | 0 | 0 | 30 | 2 | 120 | 13 | 0 | 83 | 0 | 0 | 0 | 214 | 4 | 48 | 19 | 6 | 0 | 0 | 14 | 5124.8 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 602 | 0 | 740.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 37.52 | 194 | 0 | 160 | 0 | 206 | 0 | 0 | 0 | 1.08 | 2.5 | 205 | 74 | 20 | 13 | 0 | 0 | 0 | 1.7 | 85 | 0.22 | 0 | 307 | 4 | 140 | 220 | 0 | 580 | 7 | 4650.07 | 9774.87 | 93.7
15:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 35 | 36 | 0 | 15 | 48 | 0 | 0 | 17 | 17 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 19.5 | 333 | 0 | 0 | 14 | 0 | 22 | 22 | 0 | 80 | 17 | 15 | 6 | 0 | 5 | 0 | 0 | 17 | 12 | 12 | 2 | 46 | 12 | 2 | 575 | 0 | 0 | 16 | 0 | 17 | 0 | 0 | 0 | 0 | 612 | 12 | 51 | 10 | 185 | 0 | 0 | 0 | 29 | 182 | 36 | 0 | 50 | 17 | 27 | 13 | 0 | 58 | 0 | 39 | 0 | 275 | 316 | 323 | 0 | 0 | 30 | 2 | 120 | 13 | 0 | 83 | 0 | 0 | 0 | 214 | 17 | 58 | 18 | 6 | 1 | 0 | 18 | 5145.5 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.9 | 604 | 0 | 753.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 11.05 | 194 | 0 | 130 | 0 | 180 | 0 | 0 | 0 | 1.71 | 2.5 | 205 | 70 | 0 | 11 | 0 | 0 | 0 | 1.9 | 81 | 0.15 | 0 | 250 | 3 | 100 | 180 | 0 | 560 | 17 | 4369.88 | 9515.38 | 93.7
16:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 35 | 36 | 0 | 15 | 48 | 0 | 0 | 17 | 17 | 25 | 5 | 450 | 0 | 0 | 0 | 10 | 19.5 | 280 | 0 | 0 | 8 | 0 | 22 | 22 | 0 | 80 | 17 | 15 | 12 | 0 | 0 | 0 | 0 | 17 | 12 | 12 | 1 | 46 | 17 | 2 | 501 | 0 | 0 | 19 | 0 | 17 | 0 | 0 | 0 | 0 | 580 | 7 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 182 | 38 | 0 | 50 | 17 | 26 | 13 | 0 | 54 | 2 | 21 | 0 | 285 | 346 | 385 | 5 | 0 | 30 | 2 | 163 | 13 | 0 | 83 | 0 | 0 | 0 | 212 | 17 | 59 | 18 | 8 | 0 | 0 | 18 | 5119.5 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 604 | 0 | 705.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 11.07 | 140 | 0 | 194 | 0 | 130 | 0 | 0 | 0 | 1.14 | 2.5 | 205 | 70 | 0 | 4 | 0 | 0 | 0 | 1.1 | 19 | 0.15 | 0 | 200 | 3 | 100 | 220 | 0 | 560 | 17 | 4144.64 | 9264.14 | 93.7
17:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 43 | 36 | 0 | 15 | 48 | 0 | 6 | 17 | 54 | 25 | 14 | 350 | 0 | 0 | 0 | 17 | 19.5 | 335 | 0 | 0 | 1 | 0 | 21 | 22 | 0 | 136 | 22 | 65 | 17 | 0 | 0 | 29 | 39 | 54.36 | 37 | 14 | 0 | 30 | 17 | 9 | 503 | 17 | 0 | 19 | 5 | 17 | 0 | 0 | 0 | 0 | 580 | 1 | 51 | 6 | 128 | 0 | 0 | 0 | 29 | 181 | 38 | 0 | 50 | 19 | 42 | 13 | 17 | 62 | 8 | 3 | 21 | 280 | 316 | 383 | 5 | 0 | 30 | 2 | 120 | 13 | 0 | 41 | 0 | 0 | 0 | 212 | 17 | 59 | 18 | 11 | 0 | 0 | 23 | 5269.86 | 913 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 601 | 0 | 661.05 | 0 | 0 | 15 | 0 | 0 | 0 | 34 | 0 | 10 | 0 | 5 | 0 | 1.76 | 170 | 0 | 160 | 0 | 170 | 0 | 0 | 0 | 0.16 | 2.5 | 205 | 72 | 34 | 1 | 0 | 0 | 0 | 0.3 | 4 | 0.03 | 0 | 200 | 3 | 100 | 180 | 0 | 550 | 54 | 4175.8 | 9445.66 | 93.69
18:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 54 | 36 | 0 | 15 | 82 | 35 | 30 | 17 | 125 | 25 | 13 | 450 | 0 | 0 | 0 | 17 | 24 | 330 | 0 | 0 | 0 | 53 | 21 | 22 | 0 | 164 | 35 | 90 | 48 | 0 | 0 | 63 | 49 | 54.36 | 40 | 50 | 0 | 26 | 17 | 13 | 575 | 53 | 0 | 19 | 8 | 17 | 0 | 0 | 0 | 0 | 600 | 0 | 51 | 37 | 185 | 0 | 0 | 0 | 29 | 182 | 38 | 26 | 50 | 49 | 70 | 13 | 17 | 64 | 8 | 0 | 39 | 285 | 346 | 383 | 16 | 0 | 30 | 2 | 163 | 13 | 0 | 84 | 5 | 0 | 0 | 212 | 23 | 58 | 18 | 11 | 0 | 0 | 22 | 6215.36 | 630 | 33 | 0 | 34 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 0 | 721.76 | 0 | 0 | 49 | 0 | 11 | 0 | 98 | 30 | 22 | 0 | 0 | 0 | 0 | 182 | 0 | 199 | 0 | 204 | 0 | 0 | 0 | 0 | 5.5 | 204 | 72 | 50 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 7 | 140 | 220 | 0 | 590 | 135 | 4572.26 | 10787.62 | 93.69
19:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 54 | 36 | 0 | 15 | 64 | 15 | 0 | 0 | 144 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 330 | 0 | 0 | 0 | 35 | 22 | 22 | 0 | 280 | 35 | 130 | 0 | 0 | 0 | 71 | 49 | 54.36 | 62 | 50 | 0 | 26 | 0 | 14 | 575 | 10 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 88 | 187 | 0 | 0 | 0 | 29 | 182 | 40 | 4 | 50 | 17 | 96 | 17 | 0 | 56 | 0 | 0 | 0 | 275 | 346 | 383 | 40 | 0 | 30 | 2 | 163 | 13 | 0 | 84 | 25 | 0 | 0 | 215 | 28 | 59 | 18 | 11 | 0 | 0 | 22 | 6162.36 | 631 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 0 | 756.62 | 0 | 0 | 49 | 0 | 0 | 0 | 98 | 0 | 30 | 0 | 0 | 0 | 0 | 201 | 0 | 204 | 0 | 209 | 0 | 0 | 0 | 0 | 5.5 | 204 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 7 | 140 | 220 | 0 | 610 | 100 | 4591.12 | 10753.48 | 93.69
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 17 | 36 | 0 | 15 | 64 | 0 | 0 | 0 | 144 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 327 | 0 | 0 | 0 | 35 | 22 | 22 | 0 | 280 | 35 | 130 | 0 | 0 | 0 | 37 | 0 | 54.36 | 62 | 50 | 0 | 26 | 0 | 18 | 575 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 110 | 187 | 0 | 0 | 0 | 29 | 218 | 40 | 17 | 50 | 0 | 98 | 17 | 0 | 56 | 0 | 0 | 0 | 300 | 386 | 385 | 43 | 0 | 30 | 2 | 163 | 13 | 0 | 84 | 25 | 0 | 0 | 217 | 28 | 59 | 18 | 11 | 0 | 0 | 22 | 6150.36 | 631 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 0 | 757.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 201 | 0 | 199 | 0 | 0 | 0 | 0 | 5.5 | 204 | 74 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 610 | 100 | 4360.6 | 10510.96
20:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 17 | 36 | 0 | 15 | 64 | 0 | 0 | 0 | 144 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 35 | 22 | 22 | 0 | 280 | 35 | 130 | 0 | 0 | 0 | 37 | 0 | 54.36 | 62 | 50 | 0 | 26 | 0 | 14 | 575 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 110 | 187 | 0 | 0 | 0 | 29 | 184 | 40 | 16 | 50 | 0 | 97 | 17 | 0 | 56 | 0 | 0 | 0 | 285 | 346 | 383 | 43 | 0 | 30 | 2 | 163 | 13 | 0 | 84 | 25 | 0 | 0 | 215 | 17 | 59 | 18 | 17 | 0 | 0 | 22 | 6050.36 | 630 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 708 | 0 | 754.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 202 | 0 | 199 | 0 | 0 | 0 | 0 | 5.5 | 185 | 72 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 610 | 100 | 4504.95 | 10555.31 | 93.69
21:00 | 0 | 51 | 8 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 17 | 25 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 300 | 0 | 0 | 0 | 17 | 22 | 22 | 0 | 280 | 35 | 65 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 26 | 0 | 22 | 575 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 80 | 187 | 0 | 0 | 0 | 29 | 182 | 40 | 0 | 50 | 0 | 54 | 17 | 0 | 60 | 0 | 0 | 0 | 280 | 346 | 383 | 15 | 0 | 29 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 45 | 18 | 16 | 0 | 0 | 21 | 5169 | 913 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 883 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 202 | 0 | 202 | 0 | 0 | 0 | 0 | 5.5 | 172 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 560 | 54 | 4986.5 | 10155.5 | 93.68
22:00 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 300 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 29 | 555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 182 | 41 | 0 | 50 | 0 | 0 | 17 | 0 | 60 | 0 | 0 | 0 | 270 | 346 | 380 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 24 | 18 | 11 | 0 | 0 | 0 | 4730 | 913 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 823 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 204 | 0 | 201 | 0 | 0 | 0 | 0 | 5.5 | 204 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 7 | 140 | 180 | 0 | 590 | 0 | 4925.5 | 9655.5 | 93.68
23:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 19.5 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 29 | 503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 0 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 182 | 41 | 0 | 50 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 290 | 316 | 380 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 24 | 18 | 11 | 0 | 0 | 0 | 4535.5 | 914 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 742 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 188 | 0 | 201 | 0 | 0 | 0 | 0 | 5.5 | 203 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 180 | 0 | 620 | 0 | 4623.5 | 9159 | 93.68
Total KWH | 0 | 1011840 | 420960 | 0 | 0 | 0 | 0 | 0 | 7185600 | 0 | 0 | 401400 | 523080 | 0 | 196992 | 811200 | 45415 | 65457 | 169285 | 570240 | 524520 | 32640 | 9337000 | 0 | 0 | 0 | 69285 | 548500 | 7670294 | 0 | 0 | 149624 | 133200 | 430800 | 519840 | 0 | 2380000 | 222055 | 541964 | 123840 | 0 | 45120 | 181873 | 105984 | 311901 | 228480 | 215040 | 21719 | 776760 | 81130 | 385440 | 12109090.9 | 92000 | 0 | 149760 | 15638.4 | 85309 | 0 | 0 | 0 | 0 | 11683635 | 119340 | 1024109 | 388072 | 3479273 | 0 | 1656900 | 0 | 591360 | 4599000 | 801504 | 63360 | 1242710 | 180480 | 499800 | 359440 | 35340 | 1254720 | 23813 | 424873 | 68608 | 6912000 | 8390400 | 9355000 | 175608 | 0 | 688080 | 55344 | 3581100 | 338688 | 0 | 1384320 | 147072 | 0 | 0 | 5333960 | 138240 | 862800 | 448800 | 276480 | 11000 | 0 | 173040 | 115658545.3 | 18891636 | 5617728 | 0 | 45600 | 2560 | 0 | 0 | 0 | 0 | 0 | 0 | 442080 | 20014542 | 0 | 13816364 | 0 | 0 | 75748 | 0 | 22272 | 0 | 186720 | 17664 | 34890 | 0 | 571420 | 0 | 300000 | 3577045 | 0 | 4366373 | 0 | 4423900 | 0 | 0 | 0 | 25560 | 85230 | 4900000 | 1726254 | 211981 | 154084 | 7296 | 0 | 0 | 18707.52 | 656640 | 2934 | 37632 | 5520000 | 133836 | 2931000 | 5126750 | 0 | 12334545.45 | 471600 | 106750591.97 | 222409137.27

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-01-2025 | during | 07-01-2025 | during | 07-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 234.58 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 341 | 312 | 400.37 | 400.37 | 370 | 370 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 25.21 | 0 | 0 | 13 | 13 | 13 | 13 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 333 | 330 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 82 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 22 | 21 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 19.5 | 24 | 33 | 33 | 33 | 33
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 34 | 34 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 35 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 15 | 15 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 13 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 125 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 27 | 0 | 27 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 34 | 36 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 164 | 584 | 584 | 350 | 350 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 53 | 0 | 0 | 51 | 51 | -
Dhaka Area Total |  |  |  |  | 7379.63 | 5770.24 | 1475.5 | 1929 | 4604.99 | 4577.99 | 2991.52 | 2964.52
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 115 | 115 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 26 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 49 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 63 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 40 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 33 | 0 | 2 | 13 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 48 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.81 | 0 | 3.81 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 90 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 53 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1320 | 1224 | 425 | 600 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 66 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1200 | 1200 | 575 | 575 | 575 | 575 | 575 | 575 | U1 S/D 09/Oct/24 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 5102.36 | 4879.22 | 1071 | 1757.36 | 2742.53 | 2719.72 | 2742.53 | 2719.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 186 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 36 | 38 | 46.94 | 46.94 | 40 | 40 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 28 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 184 | 185 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 37 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 39 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 49 | 200 | 200 | 200 | 200 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 66 | 64 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 26 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2914.2 | 2886.48 | 680 | 858 | 1738.97 | 1678.97 | 1599.2 | 1539.2
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 11 | 210 | 210 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 18 | 18 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 58 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 23 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654.5 | 654.21 | 77 | 132 | 645.4 | 601.5 | 455.4 | 411.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | -
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 16 | 44 | 44 | 0 | 0 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 5 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 84 | 83 | 83 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 214 | 212 | 210 | 210 | 210 | 210 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 0 | 0 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 382 | 383 | 380 | 380 | 380 | 380 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 346 | 346 | 383 | 383 | 353 | 353 | FGMO
Sylhet Area Total |  |  |  |  | 2411 | 2370.57 | 1523 | 1539 | 1656.5 | 1656.5 | 1541 | 1541
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 913 | 630 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 34 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 10 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 340 | 33 | 410 | 410 | 350 | 350 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1163 | 586 | 1234 | 1234 | 617 | 617 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3743 | 3686.2 | 2490 | 1293 | 3239 | 3169 | 2562 | 2492
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 3 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 135 | 135 | 145 | 145 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 590 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 135 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.52 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1113.52 | 1415 | 2176.12 | 2176.12 | 2146.12 | 2146.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 49 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 22 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 159 | 182 | 214 | 214 | 192.6 | 192.6 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 199 | 220 | 220 | 198 | 198 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 169 | 204 | 220 | 220 | 198 | 198 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52 | 52 | 52 | 52 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 98 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 11 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 30 | 113 | 113 | 113 | 113 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.7 | 0 | 4.5 | 0 | 4.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 510 | 721.76 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.15 | 0 | 45 | 0 | 45 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 100 | 100 | 92 | 0 | 90 | 0 | 90 | 0 | -
Rajshahi Area Total |  |  |  |  | 3575.55 | 3393.2 | 1159.35 | 1522.26 | 2662.04 | 2522.54 | 2596.64 | 2457.14
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 73 | 72 | 75 | 75 | 75 | 75 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 205 | 204 | 200 | 200 | 200 | 200 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 16 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3 | 0 | 4 | 0 | 4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 74 | 0 | 108.24 | 0 | 108.24 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 388 | 342 | 665.24 | 523 | 665.24 | 523
System Total |  |  |  |  | 29076.24 | 26855.22 | 9977.37 | 10787.62 | 20130.79 | 19625.34 | 17299.65 | 16794.2
Forecast Scenario (07-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8510 |  | 0 |  | 8510
|  |  |  | 1:00 | 7950 |  | 0 |  | 7950
|  |  |  | 2:00 | 7450 |  | 0 |  | 7450
|  |  |  | 3:00 | 7250 |  | 0 |  | 7250
|  |  |  | 4:00 | 6900 |  | 0 |  | 6900
|  |  |  | 5:00 | 6870 |  | 0 |  | 6870
|  |  |  | 6:00 | 7370 |  | 0 |  | 7370
|  |  |  | 7:00 | 8000 |  | 0 |  | 8000
|  |  |  | 8:00 | 8950 |  | 0 |  | 8950
|  |  |  | 9:00 | 9340 |  | 0 |  | 9340
|  |  |  | 10:00 | 9410 |  | 0 |  | 9410
|  |  |  | 11:00 | 9430 |  | 0 |  | 9430
|  |  |  | 12:00 | 10050 |  | 0 |  | 10050
|  |  |  | 13:00 | 10260 |  | 0 |  | 10260
|  |  |  | 14:00 | 9860 |  | 0 |  | 9860
|  |  |  | 15:00 | 9300 |  | 0 |  | 9300
|  |  |  | 16:00 | 9150 |  | 0 |  | 9150
|  |  |  | 17:00 | 9310 |  | 0 |  | 9310
|  |  |  | 18:00 | 10840 |  | 0 |  | 10840
|  |  |  | 18:30 | 10600 |  | 0 |  | 10600
|  |  |  | 19:00 | 10540 |  | 0 |  | 10540
|  |  |  | 19:30 | 10580 |  | 0 |  | 10580
|  |  |  | 20:00 | 10420 |  | 0 |  | 10420
|  |  |  | 21:00 | 10310 |  | 0 |  | 10310
|  |  |  | 22:00 | 9760 |  | 0 |  | 9760
|  |  |  | 23:00 | 9020 |  | 0 |  | 9020
Probable Maximum Temperature: |  |  | 25.70°C
Probable Maximum Demand at Day Peak: |  |  | 10050.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 10840.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10840.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 216.25 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (06-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 29.50°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 771.94
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 18.8916 | Peak Hour Flow: |  | 630.00 MW at 18:00 hrs.
Energy Flow from West to East |  | 10651654.636 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 13.8164 | Peak Hour Flow: |  | 721.76 MW at 18:00 hrs.
Power Flow during Peak Demand |  | 330 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.2547 | Peak Hour Flow: |  | 64.00 MW at 18:00 hrs.
Maximum Power Flow |  | 920 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 33.9627 | Peak Hour Flow: |  | 1415.76 MW at 18:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 06-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 9977.37 | MW | 12:00 Hr. | Energy Generated |  |  | 222409.1373 |  | MWHr
Day Peak Demand |  |  | 10002.37 | MW | 12:00 Hr. | Energy Unserverd |  |  | 199 |  | MWHr
Evening Peak Generation |  |  | 10787.62 | MW | 18:00 Hr. | Energy Demand |  |  | 222608.1373 |  | MWHr
Evening Peak Demand |  |  | 10787.62 | MW | 18:00 Hr.
Minimum Generation of the Day |  |  | 7082.74 | MW | 05:00 Hr.
Minimum Demand of the Day |  |  | 7082.74 | MW | 05:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 28596.554 | 0 | 4450.994 | 0 | 0 | 149.624 | 0 | 0 | 33197.172 | Gas | 105636.204 | Gas | 369827188.16
Chattogram Zone |  |  | 385.44 | 23792.7259 | 2354.9744 | 0 | 776.76 | 141.059 | 0 | 45.12 | 27496.0793 | Coal | 68288.0673 | Coal | 497717687.9235
Cumilla Zone |  |  | 13754.296 | 0 | 1259.473 | 0 | 0 | 424.873 | 1254.72 | 0 | 16693.362 | HFO | 10802.2844 | HFO | 200130536.83
Mymensingh Zone |  |  | 276.48 | 0 | 1622.88 | 0 | 0 | 11 | 0 | 0 | 1910.36 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 36361.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36361.572 | Hydro | 776.76 | Hydro | 77676
Khulna Zone |  |  | 5617.728 | 20014.542 | 48.16 | 0 | 0 | 442.08 | 18891.636 | 0 | 45014.146 | Solar | 2897.9815 | Solar | 35997260.702
Barishal Zone |  |  | 8191.586 | 17854.5455 | 509.232 | 0 | 0 | 2.934 | 0 | 0 | 26558.2974 | Import | 33962.72 | Import | 171817250.24
Rajshahi Zone |  |  | 12452.548 | 0 | 337.294 | 0 | 0 | 896.98 | 13816.364 | 0 | 27503.186 | Wind | 45.12 | Wind | 649728
Rangpur Zone |  |  | 0 | 6626.254 | 219.277 | 0 | 0 | 829.4315 | 0 | 0 | 7674.9625
Total |  |  | 105636.204 | 68288.0673 | 10802.2844 | 0 | 776.76 | 2897.9815 | 33962.72 | 45.12 | 222409.1373
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 369827188.16 |  | Hydro | 77676
|  |  | Coal | 497717687.9235 |  | Solar | 35997260.702
|  |  | HFO | 200130536.83 |  | Import | 171817250.24
|  |  | HSD | 0 |  | Wind | 649728
|  |  |  | Total: | 1276217327.8555 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Barapukuria TPP Unit-2 |  |  | 85
| 3 | Siddhirgonj 210 MW TPP |  |  | 115
| 4 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 5 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 714 |  |  |  | Total | 35.09
|  |  | Total Unavailable Capacity |  |  |  | 749.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (18:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3996
|  |  | Chattogram |  | 0 |  | 1089
|  |  | Cumilla |  | 0 |  | 880
|  |  | Mymensingh |  | 0 |  | 867
|  |  | Sylhet |  | 0 |  | 368
|  |  | Khulna |  | 0 |  | 1214
|  |  | Barishal |  | 0 |  | 297
|  |  | Rajshahi |  | 0 |  | 985
|  |  | Rangpur |  | 0 |  | 703
|  |  | Total |  | 0 |  | 10399
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:06 | 16:01 | Madartek-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual
maintenance.
08:07 | 16:58 | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual maintenance
08:17 |  | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Scheduled S/D Due to For ALDC maintenance
work
08:21 | 17:13 | Gopalganj(N)-Rampal Ckt-1 Scheduled S/D from Rampal 400/230kV end Due to For ALDC
maintenance work
08:29 | 14:05 | Juldah-Sikalbaha 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to Dead Line
Chack and from Shikalbaha 230/132kV end Due to Annual Maintenance
08:30 | 17:54 | Mithapukur-Palashbari 132kV Ckt-1 Scheduled S/D from Mithapukur 132/33kV end Due to
Yearly Maintenance
08:33 | 15:41 | Baghabari-Sirajganj 230 kV Ckt-2 Scheduled S/D from Baghabari 230/132kV end.
08:35 | 17:13 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Scheduled S/D Due to Annual Maintenance
08:40 | 17:53 | Mithapukur-Palashbari 132kV Ckt-1 Scheduled S/D from Palashbari 132/33kV end Due to
Annual maintenance
08:43 | 15:55 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Main Bus 2 Replacement work
08:43 | 15:55 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Main Bus 2 Replacement work
08:44 | 17:21 | Haripur-Siddirganj 132kV Ckt-1 Scheduled S/D from Siddhirganj 132/33kV end Due to Annual
maintenance and from Haripur 230/132kVend.
08:44 | 17:19 | Haripur-Siddirganj 230kV Ckt-2 Scheduled S/D from Siddhirganj 132/33kV end Due to Annual
maintenance
08:46 | 17:21 | Haripur-Siddirganj 132kV Ckt-2 Scheduled S/D from Haripur 230/132kV end.
08:48 | 15:44 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to Tr2 - 132 - KV LA Change
Works.
08:48 | 15:44 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Scheduled S/D Due to Tr2 - 132 - KV LA Change
Works.
08:48 | 15:46 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to Tr2 - 132 - KV LA Change
Works.
08:48 | 15:46 | Sreemongol 132/33kV S/S 132/33kv T-2 LT Scheduled S/D Due to Tr2 - 132 - KV LA Change
Works.
08:55 | 13:37 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to request for nesco bus | [7 empty] | 10.0MW load
interrup.
08:55 | 13:37 | Ishurdi 132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to None | [7 empty] | 10.0MW load
interrup.
08:56 | 17:07 | Hathazari-Madunaghat 132kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to
dead line check
09:02 | 17:07 | Madunaghat 400/230kV S/S Madunaghat-Hathazari 230kV Ckt.-1 Scheduled S/D Due to Shut Down
Taken by Old Madunaghat Grid
09:02 | 19:14 | Kallyanpur 132/33kV S/S GT-2 (132kV) LT Scheduled S/D Due to Annual Maintenance
09:02 | 19:12 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to Annaul Maintenance
09:04 | 16:09 | Kodda-Rajendrapur 132kV Ckt-2 Scheduled S/D from Rajendrapur 132/33kV end Due to
Kodda-Rajendrapur Ckt-02 shutdown due to deadline checking.
09:05 | 15:50 | Savar 132/33kV S/S Transfer Bus Scheduled S/D Due to Main Bus 2 Replacement work
09:06 | 17:07 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end. and
from Shahjibazar 132/33kV end Due to Annual Maintenece
09:10 | 15:11 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Scheduled S/D Due to Annual maintenance
09:10 | 15:12 | Jashore 132/33kV S/S JH-1(L2) Scheduled S/D Due to Annual Maintenance
09:10 |  | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D from Chowmuhani 132/33kV end Due to Yearly
deadline checking and from Feni 132/33kV end Due to For annual maintenance by Chawmuhani
s/s.
09:14 | 17:15 | Khulna(S) 230/132kV S/S TR-1 LT Scheduled S/D Due to Annual Maintenance work.
09:15 | 17:14 | Khulna(S) 230/132kV S/S TR-1 HT Scheduled S/D Due to Annual Maintenance work.
09:19 | 15:24 | Tangail 132/33kV S/S Kaliakair-1 Scheduled S/D Due to Annual Maintenance
09:40 | 18:08 | Haripur-Madanganj 132kV Ckt-1 Scheduled S/D from Madanganj 132/33kV end Due to Annual
Maintenance and from Haripur 230/132kVend.
09:40 | 16:12 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Annual Maintenance
09:44 | 16:13 | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to AM
09:49 | 15:21 | Madunaghat 400/230kV S/S Madunaghat-Banskhali 400kV Ckt.-1 Scheduled S/D
09:50 | 14:25 | Fenchuganj 230/132/33kV S/S TR-01 LT Scheduled S/D Due to Annual Maintenance.
09:53 | 14:21 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to Annual Maintenance.
09:54 | 12:04 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Daudkandi 132/33kV end Due to Annual
Maintenance work.
09:55 | 15:59 | Sunamganj 132/33kV S/S Main Bus -1 Scheduled S/D Due to Due to Annual Maintenance
09:58 | 15:40 | Savar 132/33kV S/S Bus-A Scheduled S/D Due to Annual maintenance work
10:04 | 20:24 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end
Due to CB troubleshooting.
10:48 | 19:04 | Madunaghat 400/230kV S/S Madunaghat-Meghnaghat 400kV Ckt.-2 Scheduled S/D
10:52 | 12:07 | Bajitpur 132/33kV S/S Tr-2(414T) HT Forced S/D Due to 33 kV Incomer PT OIL refill.
10:53 | 19:03 | Madunaghat-Meghnaghat 400kV Ckt-2 Project Work S/D from Meghnaghat 400/230kV end Due to
FF system, DFDR, SAS, SCADA and CVT HF point modification.
11:27 | 13:08 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintenance work. and from Aminbazar 400/230/132kV end Due to Dead line checking
11:38 | 12:27 | Niamatpur 132/33kV S/S Transformer-3(426T) LT Forced S/D Due to T-3,33 kV PT metering
core replacement.
11:38 | 12:26 | Niamatpur 132/33kV S/S Transformer-3(426T) HT Forced S/D Due to T-3,33 kV PT metering
core replacement.
12:00 |  | Day peak Generation is 9975 MW
12:05 | 14:24 | Cumilla(N)-Daudkandi 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to Annual
maintenance work
12:11 | 13:07 | Bajitpur 132/33kV S/S Tr-1(404T) HT Forced S/D Due to 33 kV incomer PT OIL refill.
13:10 | 18:48 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Dead line checking and from Meghnaghat 400/230kV end Due to Maintenance work.
13:12 | 13:16 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing BCPU relays Due to df/dt | [7 empty] | 36.0MW load
interrup.
13:12 | 13:16 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing BCPU relays Due to df/dt | [7 empty] | 14.0MW load
interrup.
| 14:17 | Haripur 230/132kV S/S Ullon (Maniknagar-2) is restored.
14:43 | 15:57 | Benapole 132/33kV S/S Transformer-1(406T) LT Forced S/D Due to Kazirhat Feeder Source DS | [7 empty] | 20.0MW load
|  | Red Hot | [7 empty] | interrup.
14:44 | 15:56 | Benapole 132/33kV S/S Transformer-1(406T) HT Forced S/D Due to Kazirhat Feeder Source DS | [7 empty] | 20.0MW load
|  | Red Hot | [7 empty] | interrup.
| 15:08 | Shyampur 230/132kV S/S 230 kV APR (D04) is restored.
15:09 |  | Unique Meghnaghat Power 584 MW CCPP ST was sync.
| 15:12 | APR-Hasnabad 230kV Ckt-2 is restored.
15:21 |  | Unique Meghnaghat Power 584 MW CCPP ST tripped.
15:42 | 16:59 | Baghabari-Sirajganj 230 kV Ckt-1 Forced S/D from Baghabari 230/132kV end Due to L1
আইসোলেটর এর B ফেজ এ রেডহট
16:43 |  | Unique Meghnaghat Power 584 MW CCPP ST was sync.
| 17:23 | Dhamrai-Kaliakoir 132 kV Ckt-1 is restored.
| 17:38 | Mymensingh 132/33kV S/S 50 MW Solar Plant is restored.
17:55 |  | Bheramara 410MW GT was sync.
18:00 |  | Evening Peak Generation: 10786 MW.
| 19:18 | Bhulta-Rampura 230 kV Ckt-1 is restored.
| 19:18 | Bhulta-Rampura 230 kV Ckt-1 is restored.
19:51 |  | Bheramara 410MW ST was sync.
20:07 |  | Rampal 1320 MW (BIFPCL) unit-2 was sync.
21:09 |  | Payra 1320 MW unit-2 was sync.
04:30 |  | Rampal 1320 MW (BIFPCL) Unit-1 was shut down due to the shortage of coal.
05:00 |  | Min. Gen. 7151 MW
07:19 |  | Barishal 132/33kV S/S 132 kv GTPS Scheduled S/D Due to Annual maintenance
07:21 |  | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to AM
07:22 |  | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Annual Maintenance & Deed line
work.
07:28 |  | Barishal 132/33kV S/S 132 kv Summit power Scheduled S/D Due to Annual maintenance
07:30 |  | A full interruption occurred at the Narshingdi and Bhulta substations (approximately 205
MW) from 07:30 hours due to the tripping of the Haripur-Narshingdi 132 kV line, caused by
a loop tearing in the switchyard of the Narshingdi Substation. Bhulta is now taking load
following the switching of the Haripur-Bhulta 132 kV circuit. Narshingdi remains in
full interruption.
07:30 |  | Haripur-Narsingdi 132kV Ckt-1 Tripped from Haripur 230/132kV end showing E/F relays.
07:31 | 07:51 | Bhulta-Haripur 132 kV Ckt-1 Tripped from Bhulta 132/33kV end showing MCGG, MVAJ, MVAX | [7 empty] | 150.0MW load
|  | relays Due to Overecurrent fault at Narsingdi side | [7 empty] | interrup. Bhulta
132/33kV end
07:46 |  | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end.
07:46 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end.
07:49 |  | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to
Annual Maintenance (Deep Cleaning of Insulator)
07:53 |  | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Scheduled S/D
07:54 |  | Gopalganj(N)-Rampal Ckt-1 Scheduled S/D from Rampal 400/230kV end Due to For ALDC
maintenance work purpose
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 234.58 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 312 | 7185600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9337000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 65457 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7670294 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 401400 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149 | 82 | 811200 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 169285 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 69285 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 430800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 519840 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 524520 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 24 | 548500 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 34 | 420960 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 35 | 45415 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 15 | 196992 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1011840 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 13 | 32640 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 125 | 570240 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 149624 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 36 | 523080 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 164 | 2380000 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 150 | 53 | 133200 | -
Dhaka Area Total |  |  |  |  | 7090.42 | 1929 | 33197172
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 15638.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119340 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 149760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 26 | 776760 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 85309 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 49 | 105984 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 63 | 181873 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 40 | 228480 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 33 | 13 | 385440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 48 | 123840 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 21719 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 90 | 541964 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 311901 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 81130 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 215040 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 222055 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 53 | 92000 | -
55 | SS Power |  | IPP | 2*660 | 1320 | 600 | 11683635 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 66 | 0 | 45120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 575 | 12109090.9 | U1 S/D 09/Oct/24 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4989.22 | 1757.36 | 27496079.3
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 182 | 4599000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 356.15 | 0 | 1656900 | ST Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 45 | 38 | 801504 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 591360 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 3479273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1024109 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 37 | 388072 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 39 | 68608 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1242710 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 49 | 180480 | -
| Import (Tripura) |  | Import | 0 | 160 | 64 | 1254720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 23813 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 13 | 359440 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 35340 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 70 | 499800 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 26 | 63360 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 424873 | -
Cumilla Area Total |  |  |  |  | 2902.35 | 858 | 16693362
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 276480 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 3 | 0 | 11000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 448800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 862800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 0 | Annual Maintenance on going
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 173040 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 23 | 138240 | -
Mymensingh Area Total |  |  |  |  | 654.5 | 132 | 1910360
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 688080 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3581100 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | -
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 16 | 175608 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 55344 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 5 | 147072 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1384320 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 212 | 5333960 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 338688 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6912000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 383 | 9355000 | machine problem
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 346 | 8390400 | FGMO
Sylhet Area Total |  |  |  |  | 2366 | 1539 | 36361572
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 630 | 18891636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 45600 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 10 | 2560 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 33 | 5617728 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 442080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234 | 586 | 20014542 | U#2 under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739 | 1293 | 45014146
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 37632 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 133836 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 140 | 2931000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 590 | 12334545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5126750 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 135 | 471600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5520000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2934 | -
Barishal Area Total |  |  |  |  | 2266 | 1415 | 26558297.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 49 | 75748 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 34890 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 182 | 3577045 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 199 | 4366373 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 204 | 4423900 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 414 | 0 | 0 | schedule outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 85230 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Substation problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 186720 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 11 | 22272 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 30 | 17664 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25560 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 721.76 | 13816364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 300000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 571420 | -
Rajshahi Area Total |  |  |  |  | 3411.72 | 1522.26 | 27503186
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 72 | 1726254 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 204 | 4900000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 16 | 7296 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 18707.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 211981 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 154084 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 656640 | -
Rangpur Area Total |  |  |  |  | 950 | 342 | 7674962.52
Eastern Grid Total |  |  |  |  | 18002.49 | 6215.36 | 115658545.3
Western Grid Total |  |  |  |  | 10366.72 | 4572.26 | 106750591.97
National Grid Total |  |  |  |  | 28369.21 | 10787.62 | 222409137.27
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-01-2025
Zone Total Scenario at Evening Peak Hour (18:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7199.72 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3199 | MW
i) Dhaka area |  |  | 3995.52 |  | MW | i) Khulna area |  |  |  | 1214 | MW
ii) Chattogram area |  |  | 1089.2 |  | MW | ii) Barishal area |  |  |  | 297 | MW
iii) Cumilla area |  |  | 880 |  | MW | iii) Rajshahi area |  |  |  | 985 | MW
iv) Mymensingh area |  |  | 867 |  | MW | iv) Rangpur area |  |  |  | 703 | MW
v) Sylhet area |  |  | 368 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10398.72 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 54 | 18:00 | 133 | Purbasadipur | 99 | 18:30
2 | AKSML | 99 | 10:00 | 68 | Jamalpur | 98 | 08:00 | 134 | Rahanpur | 0 | 00:00
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 101 | 13:00 | 135 | Rahim | 39 | 11:00
4 | Agargaon | 77 | 13:00 | 70 | Jhenaidah | 96 | 18:00 | 136 | Rajbari | 60 | 18:30
5 | Agrabad | 68 | 18:00 | 71 | Joydebpur | 132 | 18:30 | 137 | Rajendrapur | 98 | 09:00
6 | Amnura | 45 | 12:00 | 72 | Joypurhat | 40 | 18:30 | 138 | Rajshahi | 93 | 13:00
7 | Ashuganj | 56 | 13:00 | 73 | Juldah | 9 | 17:00 | 139 | Rajshahi-230 | 50 | 13:00
8 | BSRM | 193 | 13:00 | 74 | KSRM | 36 | 07:00 | 140 | Ramganj | 82 | 18:00
9 | Bagerhat | 74 | 18:30 | 75 | Kabirpur | 231 | 18:00 | 141 | Rampur | 27 | 18:30
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 53 | 21:00 | 142 | Rangamati | 12 | 18:00
11 | Bakulia | 64 | 13:00 | 77 | Kallyanpur | 62 | 18:00 | 143 | Rangpur | 103 | 18:00
12 | Banani | 39.4 | 12:00 | 78 | Kalurghat | 28 | 11:00 | 144 | Ruppur | 4.2 | 09:00
13 | Bangabhaban | 8 | 11:00 | 79 | Kamrangirchar | 53 | 13:00 | 145 | SSM | 12 | 06:00
14 | Barapukuria | 50 | 18:00 | 80 | Kaptai | N/A | N/A | 146 | Saidpur | 87 | 09:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 86 | 13:00 | 147 | Satkhira | 82 | 20:00
16 | Barishal | 92 | 13:00 | 82 | Keranigonj | 55 | 19:00 | 148 | Satmasjid | 82 | 13:00
17 | Barishal-230 | 54 | 20:00 | 83 | Khagrachori | 22 | 18:30 | 149 | Savar | 190 | 12:00
18 | Baroaulia | 46 | 10:00 | 84 | Khulna | 74 | 13:00 | 150 | SevenRings | 12.37 | 17:00
19 | Baroirhat | 46 | 18:00 | 85 | Khulshi | 142 | 17:00 | 151 | ShahCement | 33 | 11:00
20 | Bashundhara | 129 | 13:00 | 86 | Kishoreganj | 114 | 18:30 | 152 | Shahjadpur | 53 | 18:00
21 | BashundharaCement | 7 | 23:00 | 87 | Kodda | 271 | 18:30 | 153 | Shahjibazar | 72 | 20:00
22 | Beanibazar | 42 | 18:00 | 88 | Kulaura | 27 | 13:00 | 154 | Shahmirpur | 43 | 16:00
23 | Benapole | 57 | 18:00 | 89 | Kurigram | 46 | 08:00 | 155 | Shariatpur | 55 | 20:00
24 | Bhaluka | 116 | 18:00 | 90 | Kushtia | 106 | 18:00 | 156 | Sherpur | 114 | 18:00
25 | Bhandaria | 35 | 20:00 | 91 | Lalbag | 65 | 18:00 | 157 | Shikalbaha | 22 | 19:00
26 | Bhangura | 22 | 18:00 | 92 | Lalmonirhat | 40 | 18:00 | 158 | Shitalakhya | 62.9 | 12:00
27 | Bheramara(GK) | 41 | 18:30 | 93 | MI_Cement | 18.1 | 19:00 | 159 | Sholosohor | 32 | 18:30
28 | Bhulta | 237.5 | 16:00 | 94 | Madanganj | 28 | 11:00 | 160 | Shyampur | 118 | 13:00
29 | Bog-Sherpur | 54 | 09:00 | 95 | Madaripur | 64 | 19:00 | 161 | Siddhirganj | 106 | 12:00
30 | Bogura | 109 | 18:30 | 96 | Madartek | 58.46 | 13:00 | 162 | Sirajganj | 72 | 19:00
31 | Borhanuddin | 52 | 20:00 | 97 | Madunaghat | 37 | 18:00 | 163 | Sonargaon | 79 | 12:00
32 | Brahmanbaria | 108 | 19:00 | 98 | Magura | 46 | 18:00 | 164 | Sreemongol | 49 | 18:00
33 | Cantonment | 80 | 18:00 | 99 | Mahasthangarh | 50 | 18:30 | 165 | Sreepur | 62 | 12:00
34 | Chandpur | 43 | 18:00 | 100 | Manikganj | 102 | 18:00 | 166 | Srinagar | 29.4 | 14:00
35 | Chandraghona | 26 | 18:00 | 101 | Maniknagar | 48 | 13:00 | 167 | Sunamganj | 38 | 19:00
36 | Chapai | 45 | 09:00 | 102 | Matarbari | 36 | 18:00 | 168 | Sylhet | 28 | 12:00
37 | Charsaidpur | 38 | 02:00 | 103 | Matuail | 46 | 09:00 | 169 | Sylhet-132 | 73 | 13:00
38 | Chauddagram | 41 | 13:00 | 104 | Millgate | 75 | 12:00 | 170 | TK | 21.4 | 19:30
39 | Chhatak | 22 | 18:00 | 105 | Mirpur | 103 | 13:00 | 171 | Tangail | 132 | 08:00
40 | Chowmuhani | 144 | 20:00 | 106 | Mirsorai | 8 | 17:00 | 172 | Thakurgaon | 74 | 18:30
41 | Chuadanga | 71 | 18:00 | 107 | Mirzapur | 28 | 18:30 | 173 | Tongi | 90 | 11:00
42 | Coxsbazar | 99 | 18:00 | 108 | Mithapukur | 40 | 18:00 | 174 | Ullahpara | 28 | 18:00
43 | Cumilla(N) | 105 | 18:00 | 109 | Modern | 0 | 00:00 | 175 | Ullon | 35 | 14:00
44 | Cumilla(S) | 135 | 14:00 | 110 | Mogbazar | 80 | 13:00 | 176 | Uttara | 58 | 13:00
45 | Daudkandi | 102 | 20:00 | 111 | Mongla | 30 | 00:00 | 177 | UttaraNew | 34 | 13:00
46 | Dhaka | 34 | 13:00 | 112 | Motijheel | 25 | 13:00 | 178 | Zigatola | 70 | 13:00
47 | Dhamrai | 82 | 18:00 | 113 | Munshiganj | 68 | 21:00
48 | Dhanmondi | 96 | 13:00 | 114 | Mymensingh | 180 | 18:00
49 | Dohazari | 66 | 18:00 | 115 | Naogaon | 86 | 13:00
50 | Faridpur | 109 | 18:00 | 116 | Narail | 43 | 18:30
51 | Fatullah | 78 | 11:00 | 117 | Narinda | 51 | 13:00
52 | Fenchuganj | 25 | 18:00 | 118 | Narshingdi | 153 | 19:30
53 | Feni | 72 | 18:00 | 119 | Natore | 104 | 18:00
54 | GPH | 24 | 10:00 | 120 | Nawabganj | 35 | 13:00
55 | Ghatail | 34 | 19:00 | 121 | Netrakona | 113 | 18:30
56 | Ghorashal | 8 | 00:00 | 122 | New | 70.7 | 12:00
57 | Ghorashal-230 | 54 | 18:00 | 123 | Niamatpur | 56 | 08:00
58 | Goalpara | 26 | 13:00 | 124 | Noapara | 35 | 18:30
59 | Gollamari | 46 | 18:00 | 125 | PHP | 6 | 03:00
60 | Gopalganj | 76.2 | 18:30 | 126 | Pabna | 83 | 18:00
61 | Gulshan | 64 | 13:00 | 127 | Palashbari | 74 | 18:00
62 | Halishahar | 46 | 11:00 | 128 | Panchagarh | 44 | 18:00
63 | HaripurSBU | 167 | 16:00 | 129 | Patuakhali | 55.5 | 20:00
64 | Hasnabad | 56 | 11:00 | 130 | Payra | 14 | 14:00
65 | Hathazari | 51 | 13:00 | 131 | Postogola | 40 | 13:00
66 | Ishurdi | 60 | 18:30 | 132 | Purbachal | 15 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8757.26 | 0 |  | 8757.26
1:00 | 8321.9 | 0 |  | 8321.9
2:00 | 7667.81 | 0 |  | 7667.81
3:00 | 7356.99 | 0 |  | 7356.99
4:00 | 7144.62 | 0 |  | 7144.62
5:00 | 7082.74 | 0 |  | 7082.74
6:00 | 7534.38 | 0 |  | 7534.38
7:00 | 8382.66 | 0 |  | 8382.66
8:00 | 9342.08 | 0 |  | 9342.08
9:00 | 9533.66 | 0 |  | 9533.66
10:00 | 9298.36 | 0 |  | 9298.36
11:00 | 9427.43 | 0 |  | 9427.43
12:00 | 9977.37 | 24 |  | 10002.37
13:00 | 10294.32 | 55 |  | 10351.32
14:00 | 9774.87 | 75 |  | 9852.87
15:00 | 9515.38 | 45 |  | 9562.38
16:00 | 9264.14 | 0 |  | 9264.14
17:00 | 9445.66 | 0 |  | 9445.66
18:00 | 10787.62 | 0 |  | 10787.62
19:00 | 10753.48 | 0 |  | 10753.48
19:30 | 10510.96 | 0 |  | 10510.96
20:00 | 10555.31 | 0 |  | 10555.31
21:00 | 10155.5 | 0 |  | 10155.5
22:00 | 9655.5 | 0 |  | 9655.5
23:00 | 9159 | 0 |  | 9159
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4473.5 | 4283.76 | 8757.26 | DAILY LOAD CURVE
00:30 | 4391.75 | 4147.83 | 8539.58
01:00 | 4310 | 4011.9 | 8321.9 | 06-01-2025
01:30 | 4161.95 | 3832.905 | 7994.855
02:00 | 4013.9 | 3653.91 | 7667.81
02:30 | 3906.9 | 3605.5 | 7512.4
03:00 | 3799.9 | 3557.09 | 7356.99
03:30 | 3779.9 | 3470.905 | 7250.805
04:00 | 3759.9 | 3384.72 | 7144.62
04:30 | 3740.4 | 3373.28 | 7113.68
05:00 | 3720.9 | 3361.84 | 7082.74
05:30 | 3836.2 | 3472.36 | 7308.56
06:00 | 3951.5 | 3582.88 | 7534.38
06:30 | 4093 | 3865.52 | 7958.52
07:00 | 4234.5 | 4148.16 | 8382.66
07:30 | 4352.75 | 4509.62 | 8862.37
08:00 | 4471 | 4871.08 | 9342.08
08:30 | 4566.75 | 4871.12 | 9437.87
09:00 | 4662.5 | 4871.16 | 9533.66
09:30 | 4676.25 | 4739.76 | 9416.01
10:00 | 4690 | 4608.36 | 9298.36
10:30 | 4707.75 | 4655.145 | 9362.895
11:00 | 4725.5 | 4701.93 | 9427.43
11:30 | 4776 | 4926.4 | 9702.4
12:00 | 4826.5 | 5150.87 | 9977.37
12:30 | 4875 | 5260.845 | 10135.845
13:00 | 4923.5 | 5370.82 | 10294.32
13:30 | 5024.15 | 5010.445 | 10034.595
14:00 | 5124.8 | 4650.07 | 9774.87
14:30 | 5135.15 | 4509.975 | 9645.125
15:00 | 5145.5 | 4369.88 | 9515.38
15:30 | 5132.5 | 4257.26 | 9389.76
16:00 | 5119.5 | 4144.64 | 9264.14
16:30 | 5194.68 | 4160.22 | 9354.9
17:00 | 5269.86 | 4175.8 | 9445.66
17:30 | 5742.61 | 4374.03 | 10116.64
18:00 | 6215.36 | 4572.26 | 10787.62
18:30 | 6188.86 | 4581.69 | 10770.55
19:00 | 6162.36 | 4591.12 | 10753.48
19:30 | 6150.36 | 4360.6 | 10510.96
20:00 | 6050.36 | 4504.95 | 10555.31
20:30 | 5609.68 | 4745.725 | 10355.405 |  | Executive Engineer
21:00 | 5169 | 4986.5 | 10155.5 |  | Network Operation Division
21:30 | 4949.5 | 4956 | 9905.5
22:00 | 4730 | 4925.5 | 9655.5
22:30 | 4632.75 | 4774.5 | 9407.25
23:00 | 4535.5 | 4623.5 | 9159

## En-Curve
QF-LDC-12
Date | 06-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2943 | 1466 | 918 | 0 | 48 | 421.26 | 26 | 2847 | 0 | 17 | 54 | 0 | 0 | 17 | 0 | DAILY ENERGY CURVE
00:30 | 2931.5 | 1457.25 | 915.5 | 0 | 46 | 422.33 | 26 | 2661.5 | 0 | 8.5 | 54 | 0 | 0 | 17 | 0 | 06-01-2025
01:00 | 2920 | 1448.5 | 913 | 0 | 44 | 423.4 | 26 | 2476 | 0 | 0 | 54 | 0 | 0 | 17 | 0
01:30 | 2910.5 | 1378.45 | 819.5 | 0 | 43 | 422.405 | 26 | 2355.5 | 0 | 0 | 27 | 0 | 0 | 12.5 | 0 |  | Total Energy | 222.4091 |  | MKWHr
02:00 | 2901 | 1308.4 | 726 | 0 | 42 | 421.41 | 26 | 2235 | 0 | 0 | 0 | 0 | 0 | 8 | 0 |  | Energy not Served | 0.199 |  | MKWHr
02:30 | 2869.5 | 1228.4 | 725.5 | 0 | 42 | 421 | 26 | 2196 | 0 | 0 | 0 | 0 | 0 | 4 | 0 |  | Energy Requirement | 222.6081 |  | MKWHr
03:00 | 2838 | 1148.4 | 725 | 0 | 42 | 420.59 | 26 | 2157 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2776 | 1178.4 | 678 | 0 | 41 | 419.405 | 26 | 2132 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2714 | 1208.4 | 631 | 0 | 40 | 418.22 | 26 | 2107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2672.5 | 1217.9 | 631.5 | 0 | 40 | 418.78 | 26 | 2107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2631 | 1227.4 | 632 | 0 | 40 | 419.34 | 26 | 2107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2791 | 1288.7 | 632 | 0 | 41 | 420.86 | 26 | 2109 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:00 | 2951 | 1350 | 632 | 0 | 42 | 422.38 | 26 | 2111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2912.5 | 1450 | 707.5 | 0 | 42 | 421.19 | 26 | 2355.5 | 5.83 | 30.5 | 7.5 | 0 | 0 | 0 | 0
07:00 | 2874 | 1550 | 783 | 0 | 42 | 420 | 26 | 2600 | 11.66 | 61 | 15 | 0 | 0 | 0 | 0
07:30 | 2828 | 1554.75 | 847.5 | 0 | 42 | 489.5 | 26 | 2871 | 79.12 | 72 | 52.5 | 0 | 0 | 0 | 0
08:00 | 2782 | 1559.5 | 912 | 0 | 42 | 559 | 26 | 3142 | 146.58 | 83 | 90 | 0 | 0 | 0 | 0
08:30 | 2764.5 | 1517.75 | 771.5 | 0 | 44 | 560.5 | 36 | 3292 | 221.12 | 107.5 | 123 | 0 | 0 | 0 | 0
09:00 | 2747 | 1476 | 631 | 0 | 46 | 562 | 46 | 3442 | 295.66 | 132 | 156 | 0 | 0 | 0 | 0
09:30 | 2750 | 1476.25 | 631 | 0 | 51 | 513.54 | 46 | 3308.5 | 340.22 | 132 | 167.5 | 0 | 0 | 0 | 0
10:00 | 2753 | 1476.5 | 631 | 0 | 56 | 465.08 | 46 | 3175 | 384.78 | 132 | 179 | 0 | 0 | 0 | 0
10:30 | 2772.5 | 1475.25 | 703.5 | 0 | 57 | 466.04 | 46 | 3115 | 417.605 | 132 | 178 | 0 | 0 | 0 | 0
11:00 | 2792 | 1474 | 776 | 0 | 58 | 467 | 46 | 3055 | 450.43 | 132 | 177 | 0 | 0 | 0 | 0
11:30 | 2849.5 | 1533.5 | 844.5 | 0 | 62 | 488.5 | 46 | 3123 | 451.9 | 132 | 171.5 | 0 | 0 | 0 | 12
12:00 | 2907 | 1593 | 913 | 0 | 66 | 510 | 46 | 3191 | 453.37 | 132 | 166 | 0 | 0 | 0 | 24
12:30 | 2919.5 | 1588 | 913.5 | 0 | 66 | 535 | 46 | 3292 | 454.845 | 142 | 178.5 | 0 | 0 | 0.5 | 39.5
13:00 | 2932 | 1583 | 914 | 0 | 66 | 560 | 46 | 3393 | 456.32 | 152 | 191 | 0 | 0 | 1 | 55
13:30 | 2777 | 1599.15 | 914 | 0 | 68 | 650.025 | 46 | 3173.5 | 406.42 | 152 | 245.5 | 0 | 0 | 3 | 65
14:00 | 2622 | 1615.3 | 914 | 0 | 70 | 740.05 | 46 | 2954 | 356.52 | 152 | 300 | 0 | 0 | 5 | 75
14:30 | 2527.5 | 1596.15 | 914 | 0 | 64 | 746.86 | 46 | 2915 | 315.615 | 152 | 363 | 0 | 0 | 5 | 60
15:00 | 2433 | 1577 | 914 | 0 | 58 | 753.67 | 46 | 2876 | 274.71 | 152 | 426 | 0 | 0 | 5 | 45
15:30 | 2433.5 | 1626 | 913.5 | 0 | 56 | 729.675 | 46 | 2798 | 196.085 | 152 | 436.5 | 0 | 0 | 2.5 | 22.5
16:00 | 2434 | 1675 | 913 | 0 | 54 | 705.68 | 46 | 2720 | 117.46 | 152 | 447 | 0 | 0 | 0 | 0
16:30 | 2461.5 | 1562.5 | 913 | 0 | 58 | 683.365 | 38 | 2715.5 | 69.355 | 238.5 | 615.18 | 0 | 0 | 0 | 0
17:00 | 2489 | 1450 | 913 | 0 | 62 | 661.05 | 30 | 2711 | 21.25 | 325 | 783.36 | 0 | 0 | 0 | 0
17:30 | 2573 | 1621.25 | 771.5 | 0 | 63 | 691.405 | 28 | 2822.5 | 10.625 | 464 | 1071.36 | 0 | 0 | 0 | 0
18:00 | 2657 | 1792.5 | 630 | 0 | 64 | 721.76 | 26 | 2934 | 0 | 603 | 1359.36 | 0 | 0 | 0 | 0
18:30 | 2706.5 | 1861.5 | 630.5 | 0 | 60 | 739.19 | 26 | 2949 | 0 | 547 | 1250.86 | 0 | 0 | 0 | 0
19:00 | 2756 | 1930.5 | 631 | 0 | 56 | 756.62 | 26 | 2964 | 0 | 491 | 1142.36 | 0 | 0 | 0 | 0
19:30 | 2824 | 1962.5 | 631 | 0 | 56 | 757.1 | 26 | 2974 | 0 | 231 | 1049.36 | 0 | 0 | 0 | 0
20:00 | 2809 | 1943.5 | 630 | 0 | 56 | 754.45 | 26 | 3069 | 0 | 231 | 1036.36 | 0 | 0 | 0 | 0
20:30 | 2872 | 1839 | 771.5 | 0 | 58 | 755.225 | 26 | 3125 | 0 | 169.5 | 739.18 | 0 | 0 | 0 | 0
21:00 | 2935 | 1734.5 | 913 | 0 | 60 | 756 | 26 | 3181 | 0 | 108 | 442 | 0 | 0 | 0 | 0
21:30 | 2951 | 1691.5 | 913 | 0 | 60 | 756.5 | 26 | 3161.5 | 0 | 95.5 | 250.5 | 0 | 0 | 0 | 0
22:00 | 2967 | 1648.5 | 913 | 0 | 60 | 757 | 26 | 3142 | 0 | 83 | 59 | 0 | 0 | 0 | 0
22:30 | 2901.5 | 1655.75 | 913.5 | 0 | 57 | 708.5 | 26 | 3011 | 0 | 75 | 59 | 0 | 0 | 0 | 0
23:00 | 2836 | 1663 | 914 | 0 | 54 | 660 | 26 | 2880 | 0 | 67 | 59 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour |  | a
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 406 | 04:00 | 374 | 13:00 | Kaliakoir | 374 | 04:00 | 340 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 409 | 2:00 | 372 | 13:00 | Madunaghat | 411 | 19:00 | 379 | 13:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 408 | 04:00 | 373 | 12:00 | Meghnaghat | 400 | 04:00 | 368 | 13:00
| Bibiana | 393 | 09:00 | 384 | 12:00 | Payra | 417 | 04:00 | 402 | 11:00
| BIPTC | 408 | 02:00 | 389 | 12:00 | Rahanpur | 414 | 04:00 | 400 | 13:00
| Bogura | 409 | 02:00 | 393 | 13:00 | Rampal | 408 | 02:00 | 387 | 13:00
| Gopalganj | 411 | 04:00 | 386 | 13:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 239 | 06:00 | 218 | 11:00 | Haripur | 234 | 02:00 | 218 | 13:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 235 | 17:00 | 214 | 12:00 | Hasnabad | 232 | 01:00 | 211 | 13:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 232 | 03:00 | 210 | 12:00 | Hathazari | 239 | 18:30 | 213 | 13:00
| Ashuganj | 238 | 01:00 | 222 | 13:00 | Ishurdi | 243 | 03:00 | 226 | 14:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 01:00 | 222 | 13:00 | Jhenaidah | 242 | 04:00 | 222 | 14:00
| Baghabari | 243 | 04:00 | 227 | 14:00 | Kaliakoir | 234 | 03:00 | 214 | 12:00 | 230 kV MAX | 248 |  | 248 | 210
| Barapukuria | 224 | 00:00 | 219 | 08:00 | Keranigonj | 232 | 04:00 | 210 | 13:00 | 230 kV MIN | 210 |  | 244 | 210 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 224 | 00:00 | 219 | 08:00 | Khulna(S) | 240 | 04:00 | 225 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 244 | 03:00 | 232 | 13:00 | Madunaghat | 238 | 18:30 | 216 | 11:00 | 132 kV MAX | 143 |  | 143 | 112 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 243 | 04:00 | 223 | 14:00 | Madunaghat-400 | 237 | 18:30 | 216 | 13:00 | 132 kV MIN | 112 |  | 142 | 112 |  |  |  | 400 kV | 7 | [25 empty] | 403
| Bhulta | 236 | 04:00 | 217 | 12:00 | Maniknagar | 237 | 04:00 | 218 | 12:00 | [35 empty] | 6:00
| Bibiana | 229 | 00:00 | 219 | 13:00 | Meghnaghat | 240 | 04:00 | 225 | 14:00 | [35 empty] | 392
| BIPTC | 245 | 04:00 | 224 | 14:00 | Meghnaghat-400 | 235 | 05:00 | 218 | 13:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 240 | 04:00 | 229 | 13:00 | Mirsorai | 236 | 18:00 | 211 | 13:00 | ` | [34 empty] | 21:00
| Bogura-400 | 238 | 04:00 | 228 | 12:00 | Rajshahi | 244 | 04:00 | 223 | 14:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 248 | 04:00 | 241 | 12:00 | Rampal | 237 | 04:00 | 223 | 12:00 |  |  |  |  | Ash 400-299274
| BSRM | 234 | 18:00 | 212 | 13:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 231 | 02:00 | 215 | 12:00 | Rampura | 237 | 04:00 | 216 | 13:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 243 | 02:00 | 228 | 13:00 | Shikalbaha | 237 | 18:30 | 216 | 11:00 |  | kaptai by call 399528
| Fenchuganj | 231 | 18:30 | 224 | 13:00 | Shyampur | 233 | 04:00 | 215 | 12:00
| Ghorashal | 240 | 00:00 | 235 | 01:00 | Siddhirganj | 231 | 00:00 | 220 | 12:00
| Ghorashal-230 | 235 | 02:00 | 215 | 13:00 | Sirajgonj | 247 | 04:00 | 236 | 13:00
| Gopalganj | 244 | 04:00 | 224 | 13:00 | Sreepur | 235 | 04:00 | 222 | 12:00
| GPH | 236 | 18:00 | 212 | 13:00 | Tongi | 229 | 23:00 | 214 | 11:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 136 | 01:00 | 123 | 12:00 | Kurigram | 130 | 04:00 | 118 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 139 | 04:00 | 124 | 13:00 | Kushtia | 140 | 02:00 | 128 | 14:00
| Agrabad | 137 | 18:00 | 121 | 12:00 | Lalbag | 137 | 00:00 | 122 | 13:00
| AKS | 135 | 19:00 | 122 | 12:00 | Lalmonirhat | 131 | 05:00 | 120 | 21:00
| Aminbazar | 141 | 03:00 | 122 | 13:00 | Madanganj | 132 | 18:00 | 122 | 12:00
| Amnura | 139 | 00:00 | 130 | 14:00 | Madaripur | 135 | 23:00 | 130 | 12:00
| Ashuganj | 141 | 05:00 | 134 | 12:00 | Madartek | 136 | 04:00 | 123 | 12:00
| Bagerhat | 138 | 05:00 | 126 | 12:00 | Madunaghat | 137 | 18:30 | 123 | 11:00
| Bajitpur | 135 | 00:00 | 130 | 12:00 | Magura | 142 | 03:00 | 126 | 14:00
| Bakulia | 135 | 17:00 | 123 | 12:00 | Mahasthangarh | 136 | 03:00 | 129 | 08:00
| Banani | 136 | 01:00 | 121 | 13:00 | Manikganj | 130 | 02:00 | 119 | 12:00
| Bangabhaban | 134 | 02:00 | 123 | 13:00 | Maniknagar | 134 | 01:00 | 124 | 12:00
| Barapukuria | 134 | 00:00 | 129 | 08:00 | Matarbari | 129 | 17:00 | 116 | 12:00
| Barguna | 137 | 02:00 | 129 | 13:00 | Matuail | 134 | 09:00 | 128 | 08:00
| Barishal | 136 | 02:00 | 129 | 12:00 | Millgate | 134 | 03:00 | 120 | 12:00
| Barishal-230 | 137 | 04:00 | 130 | 12:00 | Mirpur | 139 | 04:00 | 125 | 12:00
| Baroaulia | 136 | 18:00 | 125 | 12:00 | Mirzapur | 131 | 04:00 | 121 | 12:00
| Baroirhat | 132 | 18:30 | 120 | 12:00 | Mithapukur | 134 | 02:00 | 125 | 13:00
| Bashundhara | 136 | 01:00 | 120 | 12:00 | MI_Cement | 134 | 05:00 | 123 | 13:00
| BashundharaCement | 132 | 18:00 | 122 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 134 | 02:00 | 130 | 12:00 | Mogbazar | 139 | 05:00 | 123 | 12:00
| Benapole | 139 | 03:00 | 122 | 13:00 | Mongla | 137 | 06:00 | 127 | 14:00
| Bhaluka | 129 | 05:00 | 117 | 12:00 | Motijheel | 134 | 01:00 | 123 | 13:00
| Bhandaria | 133 | 05:00 | 128 | 12:00 | Munshiganj | 133 | 04:00 | 122 | 13:00
| Bhangura | 141 | 04:00 | 132 | 12:00 | Mymensingh | 134 | 09:00 | 115 | 12:00
| Bheramara | 141 | 04:00 | 128 | 14:00 | Naogaon | 136 | 03:00 | 127 | 13:00
| Bheramara(GK) | 139 | 00:00 | 129 | 14:00 | Narail | 140 | 04:00 | 128 | 14:00
| Bhulta | 125 | 03:00 | 117 | 14:00 | Narinda | 134 | 7:00 | 125 | 11:00
| Bog-Sherpur | 136 | 01:00 | 130 | 12:00 | Narshingdi | 125 | 04:00 | 116 | 13:00
| Bogura | 137 | 05:00 | 130 | 13:00 | Natore | 138 | 01:00 | 129 | 14:00
| Bogura-230 | 138 | 04:00 | 130 | 13:00 | Nawabganj | 137 | 00:00 | 123 | 12:00
| Brahmanbaria | 136 | 01:00 | 121 | 13:00 | Netrakona | 130 | 04:00 | 117 | 08:00
| Cantonment | 139 | 04:00 | 124 | 13:00 | New | 138 | 09:00 | 121 | 12:00
| Chandpur | 129 | 17:00 | 118 | 14:00 | Niamatpur | 140 | 01:00 | 134 | 12:00
| Chandraghona | 137 | 18:00 | 124 | 12:00 | Noapara | 139 | 05:00 | 125 | 14:00
| Chapai | 139 | 03:00 | 133 | 12:00 | Pabna | 140 | 01:00 | 130 | 14:00
| Charsaidpur | 134 | 03:00 | 123 | 13:00 | Palashbari | 132 | 03:00 | 124 | 08:00
| Chauddagram | 132 | 03:00 | 119 | 12:00 | Panchagarh | 135 | 04:00 | 121 | 08:00
| Chhatak | 134 | 01:00 | 131 | 11:00 | Patuakhali | 138 | 18:00 | 130 | 12:00
| Chowmuhani | 128 | 17:00 | 112 | 13:00 | Payra | 138 | 18:00 | 132 | 12:00
| Chuadanga | 140 | 03:00 | 123 | 14:00 | PHP | 131 | 18:00 | 116 | 13:00
| Coxsbazar | 127 | 00:00 | 117 | 12:00 | Postogola | 135 | 00:00 | 126 | 12:00
| Cumilla(N) | 134 | 02:00 | 123 | 12:00 | Purbachal | 137 | 04:00 | 122 | 13:00
| Cumilla(S) | 133 | 04:00 | 122 | 12:00 | Purbasadipur | 131 | 03:00 | 120 | 08:00
| Daudkandi | 132 | 01:00 | 118 | 13:00 | Rahanpur | 140 | 02:00 | 135 | 14:00
| Dhaka | 136 | 02:00 | 123 | 12:00 | Rahanpur-400 | 140 | 00:00 | 135 | 13:00
| Dhamrai | 136 | 04:00 | 122 | 12:00 | Rahim | 132 | 03:00 | 121 | 13:00
| Dhanmondi | 137 | 02:00 | 126 | 16:00 | Rajbari | 135 | 02:00 | 127 | 13:00
| Dohazari | 134 | 18:00 | 123 | 12:00 | Rajendrapur | 134 | 04:00 | 123 | 13:00
| Faridpur | 135 | 02:00 | 128 | 13:00 | Rajshahi | 138 | 01:00 | 131 | 14:00
| Fatullah | 136 | 05:00 | 123 | 13:00 | Rajshahi-230 | 141 | 04:00 | 129 | 12:00
| Fenchuganj | 138 | 22:00 | 133 | 13:00 | Ramganj | 128 | 18:30 | 115 | 14:00
| Feni | 130 | 05:00 | 120 | 12:00 | Rampur | 137 | 18:30 | 122 | 13:00
| Ghatail | 131 | 09:00 | 119 | 11:00 | Rampura | 136 | 01:00 | 122 | 13:00
| Ghorashal | 139 | 01:00 | 134 | 13:00 | Rangamati | 136 | 18:00 | 123 | 12:00
| Goalpara | 140 | 01:00 | 126 | 13:00 | Rangpur | 132 | 06:00 | 124 | 12:00
| Gollamari | 139 | 03:00 | 128 | 13:00 | Ruppur | 141 | 01:00 | 133 | 15:00
| Gopalganj | 138 | 04:00 | 127 | 13:00 | Saidpur | 135 | 04:00 | 123 | 12:00
| Gopalganj-400 | 137 | 04:00 | 128 | 12:00 | Satkhira | 139 | 01:00 | 127 | 13:00
| Gulshan | 135 | 03:00 | 123 | 12:00 | Satmasjid | 138 | 01:00 | 124 | 13:00
| Halishahar | 138 | 19:00 | 119 | 12:00 | Savar | 137 | 01:00 | 122 | 13:00
| Haripur | 133 | 18:00 | 121 | 13:00 | SevenRings | 141 | 04:00 | 131 | 12:00
| HaripurSBU | 133 | 18:00 | 121 | 13:00 | ShahCement | 134 | 03:00 | 123 | 13:00
| Hasnabad | 136 | 03:00 | 126 | 12:00 | Shahjadpur | 140 | 00:00 | 135 | 11:00
| Hathazari | 137 | 19:00 | 126 | 13:00 | Shahjibazar | 136 | 08:00 | 127 | 13:00
| Ishurdi | 143 | 04:00 | 132 | 14:00 | Shahmirpur | 137 | 18:00 | 124 | 12:00
| Jaldhaka | 131 | 04:00 | 120 | 08:00 | Shariatpur | 137 | 04:00 | 128 | 12:00
| Jamalpur | 135 | 09:00 | 120 | 02:00 | Sherpur | 132 | 09:00 | 115 | 08:00
| Jashore | 138 | 02:00 | 124 | 13:00 | Shikalbaha | 126 | 18:00 | 112 | 12:00
| Jhenaidah | 139 | 06:00 | 128 | 14:00 | Shikalbaha-230 | 139 | 18:30 | 122 | 12:00
| Jhenaidah-230 | 142 | 04:00 | 129 | 14:00 | Shitalakhya | 133.8 | 06:00 | 123 | 13:00
| Joydebpur | 140 | 03:00 | 130 | 12:00 | Sholosohor | 135 | 19:30 | 122 | 13:00
| Joypurhat | 136 | 01:00 | 127 | 13:00 | Shyampur | 133 | 01:00 | 125 | 12:00
| Juldah | 136 | 17:00 | 122 | 12:00 | Shyampur-230 | 135 | 04:00 | 125 | 12:00
| Kabirpur | 134 | 09:00 | 119 | 12:00 | Siddhirganj | 134 | 09:00 | 128 | 12:00
| Kachua | 130 | 17:00 | 118 | 13:00 | Sirajganj | 140 | 05:00 | 130 | 12:00
| Kaliakoir | 138 | 04:00 | 123 | 12:00 | Sonargaon | 130 | 18:00 | 115 | 09:00
| Kallyanpur | 134 | 04:00 | 121 | 13:00 | Sreemongol | 136 | 02:00 | 130 | 12:00
| Kalurghat | 136 | 18:00 | 123 | 13:00 | Sreepur | 130 | 04:00 | 120 | 12:00
| Kamrangirchar | 136 | 02:00 | 120 | 13:00 | Srinagar | 136 | 06:00 | 123 | 12:00
| Kaptai | 138 | 18:00 | 126 | 1:00 | SSM | 138 | 18:00 | 128 | 13:00
| Kazla | 134 | 03:00 | 123 | 13:00 | Sunamganj | 133 | 05:00 | 129 | 13:00
| Keranigonj | 138 | 00:00 | 122 | 13:00 | Sylhet | 134 | 01:00 | 130 | 13:00
| Khagrachori | 136 | 18:00 | 123 | 12:00 | Sylhet-132 | 134 | 00:00 | 131 | 12:00
| Khulna | 138 | 04:00 | 127 | 13:00 | Tangail | 130 | 09:00 | 118 | 15:00
| Khulna(S) | 140 | 04:00 | 129 | 12:00 | Thakurgaon | 132 | 04:00 | 118 | 08:00
| Khulshi | 136 | 18:00 | 121 | 12:00 | TK | 137 | 18:00 | 124 | 11:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 132 | 18:00 | 126 | 12:00 | Tongi | 134 | 04:00 | 123 | 11:00 |  |  | Nos | Nos | Nos
| Kodda | 135 | 20:00 | 119 | 12:00 | Ullahpara | 139 | 03:00 | 132 | 12:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 137 | 18:00 | 123 | 13:00 | Ullon | 137 | 02:00 | 122 | 13:00
| Kulaura | 136 | 00:00 | 131 | 13:00 | Uttara | 141 | 04:00 | 125 | 13:00
| Zigatola | 135 | 04:00 | 126 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.