## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-01-2025 | during | 08-01-2025 | during | 08-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 234.58 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 325 | 313 | 400.37 | 400.37 | 370 | 370 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 32 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 18 | 17 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 19 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 28 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 16 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 30 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 15 | 15 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 90 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 36 | 36 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 220 | 584 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 35 | 72 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 7401.63 | 5842.27 | 1652 | 1773 | 4431.19 | 4403.19 | 2591.52 | 2563.52
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 26 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 36 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 33 | 0 | 2 | 4 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.79 | 0 | 3.79 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 80 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 35 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 36 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1320 | 1224 | 612 | 612 | 1224 | 1224 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 66 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1200 | 1200 | 502 | 575 | 1150 | 1150 | 575 | 575 | Partial Shutdown due to maintenance
Chattogram Area Total |  |  |  |  | 5102.36 | 4879.22 | 1185 | 1471 | 3814.51 | 3791.72 | 2627.51 | 2604.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 38 | 36 | 46.94 | 46.94 | 42 | 42 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 185 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 100 | 145 | 145 | 145 | 145 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 54 | 56 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 55 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 34 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 680 | 796 | 1738.97 | 1673.97 | 1621.2 | 1556.2
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 6 | 9 | 210 | 210 | 25 | 25 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 18 | 19 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 80 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41 | 0 | 38 | 0 | 38 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654.5 | 654.21 | 122 | 130 | 641.3 | 601.5 | 456.3 | 416.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 29 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 15 | 15 | 44 | 44 | 44 | 44 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 25 | 25 | 0 | 0 | 25 | 25 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 50 | 83 | 86 | 83 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 217 | 216 | 210 | 210 | 210 | 210 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 0 | 0 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 370 | 381 | 385 | 385 | 357 | 357 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 346 | 340 | 383 | 383 | 353 | 353 | FGMO
Sylhet Area Total |  |  |  |  | 2411 | 2370.57 | 1526 | 1514 | 1661.5 | 1664.5 | 1587 | 1590
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 913 | 632 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 327 | 322 | 410 | 410 | 350 | 350 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 64 | 0 | 60 | 0 | 60 | 0 | Low irradiation
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 583 | 603 | 1234 | 1234 | 617 | 617 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3743 | 3686.2 | 1887 | 1557 | 3226 | 3166 | 2549 | 2489
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 140 | 135 | 135 | 145 | 145 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 750 | 1072 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 220 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1294 | 1781 | 2176.12 | 2176.12 | 2186.12 | 2186.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 150 | 188 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 197 | 197 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 199 | 200 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 3 | 5.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 16 | 52 | 52 | 52 | 52 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 68 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4 | 0 | 3.35 | 0 | 3.35 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 611 | 755.45 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48 | 0 | 51 | 0 | 51 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 100 | 100 | 90 | 0 | 92 | 0 | 92 | 0 | -
Rajshahi Area Total |  |  |  |  | 3575.55 | 3393.2 | 1302 | 1429.95 | 2668.89 | 2522.54 | 2668.89 | 2522.54
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 70 | 72 | 72 | 75 | 75 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 175 | 210 | 200 | 200 | 200 | 200 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 70 | 0 | 78.49 | 0 | 115.49 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 349 | 280 | 633.29 | 520 | 673.29 | 523
System Total |  |  |  |  | 29109.24 | 26938.25 | 9997 | 10731.95 | 20991.77 | 20519.54 | 16960.83 | 16451.6
Forecast Scenario (08-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8750 |  | 0 |  | 8750
|  |  |  | 1:00 | 8320 |  | 0 |  | 8320
|  |  |  | 2:00 | 7660 |  | 0 |  | 7660
|  |  |  | 3:00 | 7350 |  | 0 |  | 7350
|  |  |  | 4:00 | 7140 |  | 0 |  | 7140
|  |  |  | 5:00 | 7080 |  | 0 |  | 7080
|  |  |  | 6:00 | 7530 |  | 0 |  | 7530
|  |  |  | 7:00 | 8380 |  | 0 |  | 8380
|  |  |  | 8:00 | 9340 |  | 0 |  | 9340
|  |  |  | 9:00 | 9530 |  | 0 |  | 9530
|  |  |  | 10:00 | 9290 |  | 0 |  | 9290
|  |  |  | 11:00 | 9420 |  | 0 |  | 9420
|  |  |  | 12:00 | 10000 |  | 0 |  | 10000
|  |  |  | 13:00 | 10350 |  | 0 |  | 10350
|  |  |  | 14:00 | 9850 |  | 0 |  | 9850
|  |  |  | 15:00 | 9560 |  | 0 |  | 9560
|  |  |  | 16:00 | 9260 |  | 0 |  | 9260
|  |  |  | 17:00 | 9440 |  | 0 |  | 9440
|  |  |  | 18:00 | 10780 |  | 0 |  | 10780
|  |  |  | 18:30 | 10765 |  | 0 |  | 10765
|  |  |  | 19:00 | 10750 |  | 0 |  | 10750
|  |  |  | 19:30 | 10510 |  | 0 |  | 10510
|  |  |  | 20:00 | 10550 |  | 0 |  | 10550
|  |  |  | 21:00 | 10150 |  | 0 |  | 10150
|  |  |  | 22:00 | 9650 |  | 0 |  | 9650
|  |  |  | 23:00 | 9159 |  | 0 |  | 9159
Probable Maximum Temperature: |  |  | 23.60°C
Probable Maximum Demand at Day Peak: |  |  | 10000.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 10780.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10780.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 219.289 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (07-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 26.20°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 810.37
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 19.5127 | Peak Hour Flow: |  | 632.00 MW at 19:00 hrs.
Energy Flow from West to East |  | 11485181.92 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 13.5764 | Peak Hour Flow: |  | 755.45 MW at 19:00 hrs.
Power Flow during Peak Demand |  | 330 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.2586 | Peak Hour Flow: |  | 56.00 MW at 19:00 hrs.
Maximum Power Flow |  | 920 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 34.3477 | Peak Hour Flow: |  | 1443.45 MW at 19:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-01-2025 | [28 empty] | Date: | 07-01-2025 | [28 empty] | Date: | 07-01-2025 | [28 empty] | Date: | 07-01-2025 | [28 empty] | Date: | 07-01-2025 | [18 empty] | Date: | 07-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.000 MW | 365.000 MW | 260.000 MW | 234.580 MW | 190.000 MW | 108.000 MW | 412.000 MW | 20.000 MW | 718.000 MW | 54.000 MW | 36.090 MW | 20.000 MW | 149.000 MW | 149.000 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 150.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 66.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 33.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.000 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1320.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 400.000 MW | 356.150 MW | 360.000 MW | 55.000 MW | 221.000 MW | 45.000 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 50.000 MW | 70.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 3.000 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 40.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.000 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 52.000 MW | 71.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.000 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 414.000 MW | 414.000 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 18 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 23 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 51 | 0 | 178 | 0 | 0 | 0 | 29 | 182 | 41 | 0 | 50 | 0 | 0 | 17 | 0 | 56 | 0 | 0 | 0 | 280 | 316 | 380 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 16 | 0 | 12 | 0 | 0 | 0 | 4369 | 913 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 6 | 204 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 590 | 0 | 4270 | 8639 | 93.68
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 24 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 51 | 0 | 53 | 0 | 0 | 0 | 29 | 181 | 41 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 285 | 316 | 380 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 3971 | 912 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 3 | 204 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 570 | 0 | 4184 | 8155 | 93.67
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 32 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 28 | 182 | 5 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 280 | 346 | 320 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 3725 | 726 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 732 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 3 | 175 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 550 | 0 | 3865 | 7590 | 93.67
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 32 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 5 | 182 | 5 | 0 | 70 | 0 | 0 | 15 | 0 | 48 | 0 | 0 | 0 | 290 | 315 | 322 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 3703 | 725 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 736 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 3 | 175 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 550 | 0 | 3865 | 7568 | 93.67
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 32 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 5 | 182 | 5 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 275 | 316 | 323 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 5 | 25 | 0 | 0 | 215 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 3597 | 633 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 3 | 175 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 540 | 0 | 3725 | 7322 | 93.67
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 0 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 32 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 5 | 182 | 5 | 0 | 70 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 285 | 316 | 323 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 5 | 24 | 0 | 0 | 214 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 3702 | 633 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 3 | 175 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 550 | 0 | 3450 | 7152 | 93.66
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 30 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 9 | 0 | 125 | 0 | 0 | 0 | 6 | 186 | 27 | 0 | 50 | 0 | 0 | 16 | 0 | 44 | 0 | 0 | 0 | 290 | 370 | 380 | 15 | 0 | 29 | 2 | 163 | 13 | 0 | 50 | 24 | 0 | 0 | 215 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 4078 | 633 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 502 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 0 | 3 | 175 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 6 | 140 | 220 | 0 | 560 | 0 | 3701 | 7779 | 93.66
07:00 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 25 | 250 | 0 | 0 | 1 | 0 | 14 | 22 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 25 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 1 | 40 | 0 | 185 | 0 | 0 | 0 | 27 | 214 | 37 | 0 | 50 | 0 | 0 | 16 | 0 | 46 | 0 | 2 | 0 | 290 | 382 | 380 | 15 | 0 | 29 | 2 | 163 | 13 | 0 | 50 | 24 | 0 | 0 | 215 | 0 | 0 | 0 | 22 | 0 | 1 | 0 | 4370 | 725 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 500 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 184 | 0 | 192 | 0 | 175 | 0 | 0 | 0 | 1 | 3 | 175 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 249 | 6 | 140 | 220 | 0 | 590 | 0 | 4002 | 8372 | 93.66
08:00 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 5 | 0 | 19 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 26 | 0 | 5 | 577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 5 | 51 | 0 | 120 | 0 | 0 | 0 | 28 | 189 | 42 | 0 | 50 | 0 | 0 | 16 | 0 | 44 | 0 | 16 | 0 | 280 | 346 | 380 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 46 | 18 | 11 | 0 | 9 | 0 | 4341 | 914 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 555 | 0 | 610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 9 | 192 | 0 | 196 | 0 | 191 | 0 | 0 | 0 | 1 | 3 | 175 | 75 | 0 | 5 | 0 | 0 | 0 | 1 | 28 | 0 | 0 | 270 | 5 | 100 | 220 | 0 | 710 | 0 | 4599 | 8940 | 93.66
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 320 | 0 | 0 | 0 | 0 | 25 | 300 | 0 | 0 | 13 | 0 | 18 | 15 | 0 | 230 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 2 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 13 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 181 | 39 | 0 | 50 | 0 | 0 | 16 | 0 | 50 | 0 | 36 | 0 | 290 | 316 | 380 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 46 | 18 | 10 | 1 | 12 | 0 | 4699 | 915 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 560 | 0 | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 25 | 193 | 0 | 192 | 0 | 198 | 0 | 0 | 0 | 3 | 3 | 174 | 75 | 0 | 9 | 0 | 0 | 0 | 3 | 76 | 0 | 0 | 270 | 4 | 140 | 220 | 0 | 770 | 0 | 4826 | 9525 | 93.65
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 23 | 0 | 17 | 0 | 25 | 0 | 320 | 0 | 0 | 0 | 0 | 25 | 300 | 0 | 0 | 19 | 0 | 13 | 15 | 0 | 230 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 11 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 17 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 220 | 39 | 0 | 50 | 0 | 5 | 11 | 0 | 54 | 0 | 49 | 0 | 285 | 376 | 380 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 216 | 0 | 55 | 18 | 10 | 2 | 28 | 0 | 4774 | 632 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 567 | 0 | 610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 36 | 192 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 4 | 3 | 175 | 71 | 0 | 19 | 0 | 0 | 0 | 4 | 83 | 0 | 0 | 220 | 4 | 140 | 180 | 0 | 730 | 0 | 4377 | 9151 | 93.65
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 10 | 0 | 15 | 32 | 30 | 0 | 17 | 0 | 25 | 0 | 320 | 0 | 0 | 0 | 0 | 25 | 335 | 0 | 0 | 22 | 0 | 13 | 15 | 0 | 245 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 7 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603 | 19 | 51 | 0 | 184 | 0 | 0 | 0 | 29 | 182 | 39 | 0 | 50 | 0 | 17 | 11 | 0 | 54 | 0 | 60 | 0 | 285 | 316 | 381 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 216 | 0 | 75 | 18 | 6 | 2 | 29 | 0 | 4950 | 742 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 606 | 0 | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 41 | 165 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 4 | 3 | 175 | 70 | 0 | 27 | 0 | 0 | 0 | 5 | 79 | 0 | 0 | 220 | 4 | 140 | 180 | 0 | 730 | 0 | 4563 | 9513 | 93.65
12:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 36 | 0 | 15 | 16 | 30 | 0 | 17 | 0 | 25 | 0 | 370 | 0 | 0 | 0 | 0 | 25 | 335 | 0 | 0 | 24 | 35 | 18 | 15 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 46 | 0 | 2 | 502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 19 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 183 | 38 | 0 | 50 | 0 | 17 | 11 | 0 | 54 | 0 | 62 | 0 | 295 | 346 | 370 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 217 | 0 | 55 | 18 | 6 | 2 | 41 | 0 | 5165 | 913 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 583 | 0 | 611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 48 | 150 | 0 | 197 | 0 | 199 | 0 | 0 | 0 | 4 | 3 | 175 | 70 | 0 | 28 | 0 | 0 | 0 | 6 | 70 | 0 | 0 | 220 | 4 | 100 | 220 | 0 | 750 | 0 | 4832 | 9997 | 93.65
13:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 36 | 0 | 15 | 16 | 30 | 0 | 17 | 0 | 25 | 0 | 420 | 0 | 0 | 0 | 0 | 25 | 335 | 0 | 0 | 23 | 35 | 18 | 15 | 0 | 300 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 10 | 577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 19 | 51 | 0 | 179 | 0 | 0 | 0 | 29 | 182 | 38 | 0 | 50 | 0 | 17 | 11 | 0 | 66 | 0 | 59 | 0 | 295 | 340 | 382 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 217 | 0 | 56 | 18 | 5 | 1 | 22 | 0 | 5297 | 913 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 604 | 0 | 610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 47 | 150 | 0 | 208 | 0 | 207 | 0 | 0 | 0 | 4 | 3 | 175 | 70 | 0 | 28 | 0 | 0 | 0 | 5 | 50 | 0 | 0 | 307 | 4 | 140 | 220 | 0 | 860 | 0 | 5063 | 10360 | 93.64
14:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 36 | 0 | 15 | 16 | 30 | 0 | 17 | 0 | 25 | 0 | 370 | 0 | 0 | 0 | 0 | 25 | 270 | 0 | 0 | 10 | 35 | 18 | 15 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 10 | 577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 16 | 51 | 0 | 177 | 0 | 0 | 0 | 29 | 183 | 36 | 0 | 50 | 0 | 17 | 11 | 0 | 62 | 0 | 48 | 0 | 260 | 340 | 383 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 55 | 18 | 5 | 1 | 23 | 0 | 4956 | 914 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 600 | 0 | 610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 38 | 150 | 0 | 198 | 0 | 188 | 0 | 0 | 0 | 4 | 3 | 175 | 70 | 0 | 21 | 0 | 0 | 0 | 4 | 92 | 0 | 0 | 250 | 4 | 140 | 180 | 0 | 870 | 0 | 4864 | 9820 | 93.64
15:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 17 | 0 | 15 | 16 | 30 | 0 | 17 | 0 | 25 | 0 | 370 | 0 | 0 | 0 | 0 | 25 | 270 | 0 | 0 | 10 | 35 | 18 | 15 | 0 | 300 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 2 | 505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 12 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 203 | 37 | 0 | 50 | 0 | 17 | 11 | 0 | 54 | 0 | 16 | 0 | 280 | 370 | 385 | 15 | 0 | 50 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 55 | 19 | 5 | 1 | 21 | 0 | 4911 | 913 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 516 | 0 | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 26 | 150 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 2 | 3 | 175 | 68 | 0 | 15 | 0 | 0 | 0 | 3 | 77 | 0 | 0 | 200 | 3 | 140 | 180 | 0 | 850 | 0 | 4492 | 9403 | 93.64
16:00 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 23 | 0 | 15 | 16 | 30 | 0 | 0 | 0 | 25 | 0 | 370 | 0 | 0 | 0 | 0 | 28 | 270 | 0 | 0 | 7 | 35 | 18 | 15 | 0 | 300 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 2 | 502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 7 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 194 | 40 | 0 | 50 | 0 | 17 | 11 | 0 | 56 | 0 | 18 | 0 | 295 | 370 | 385 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 55 | 18 | 5 | 0 | 9 | 0 | 4865 | 913 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 520 | 0 | 517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 150 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 1 | 3 | 175 | 68 | 0 | 7 | 0 | 0 | 0 | 2 | 40 | 0 | 0 | 200 | 4 | 140 | 180 | 0 | 850 | 0 | 4348 | 9213 | 93.64
17:00 | 0 | 56 | 16 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 36 | 0 | 15 | 16 | 30 | 0 | 0 | 17 | 25 | 0 | 360 | 0 | 0 | 0 | 0 | 28 | 300 | 0 | 0 | 0 | 35 | 17 | 15 | 0 | 270 | 3 | 15 | 0 | 0 | 0 | 0 | 18 | 17 | 8 | 12 | 0 | 46 | 0 | 5 | 509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 51 | 2 | 185 | 0 | 0 | 0 | 29 | 183 | 38 | 0 | 50 | 0 | 17 | 11 | 0 | 56 | 0 | 0 | 0 | 290 | 340 | 344 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 62 | 28 | 5 | 0 | 1.18 | 0 | 4858.18 | 913 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 513 | 0 | 547.36 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 4 | 0 | 0 | 164 | 0 | 179 | 0 | 179 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 5 | 140 | 220 | 0 | 860 | 3 | 4585.86 | 9444.04 | 93.63
18:00 | 0 | 70 | 17 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 22 | 36 | 0 | 22 | 48 | 30 | 0 | 0 | 72 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 35 | 17 | 15 | 0 | 250 | 18 | 80 | 0 | 0 | 0 | 0 | 25 | 54.36 | 36 | 36 | 0 | 26 | 0 | 7 | 575 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 53 | 185 | 0 | 0 | 0 | 29 | 193 | 42 | 21 | 50 | 0 | 28 | 17 | 0 | 58 | 0 | 0 | 0 | 280 | 350 | 381 | 15 | 0 | 29 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 4 | 78 | 28 | 5 | 0 | 0 | 14 | 5648.36 | 631 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 660.87 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 8 | 0 | 0 | 0 | 190 | 0 | 194 | 0 | 200 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 140 | 220 | 0 | 970 | 35 | 4861.37 | 10509.73 | 93.63
19:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 35 | 36 | 0 | 15 | 32 | 0 | 0 | 0 | 90 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 72 | 17 | 19 | 0 | 220 | 35 | 80 | 0 | 0 | 0 | 0 | 0 | 35 | 36 | 36 | 0 | 26 | 0 | 4 | 575 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 100 | 185 | 0 | 0 | 0 | 29 | 183 | 36 | 34 | 50 | 0 | 55 | 17 | 0 | 56 | 0 | 0 | 0 | 280 | 340 | 381 | 15 | 0 | 29 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 216 | 0 | 80 | 19 | 9 | 0 | 0 | 22 | 5684 | 632 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 603 | 0 | 755.45 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 16 | 0 | 0 | 0 | 188 | 0 | 197 | 0 | 200 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1072 | 35 | 5047.95 | 10731.95 | 93.63
19:30 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 36 | 0 | 0 | 32 | 0 | 0 | 0 | 17 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 72 | 19 | 22 | 0 | 190 | 35 | 80 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 26 | 0 | 15 | 575 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 100 | 185 | 0 | 0 | 0 | 29 | 213 | 39 | 0 | 50 | 0 | 57 | 17 | 0 | 58 | 0 | 0 | 0 | 300 | 390 | 384 | 15 | 0 | 29 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 80 | 19 | 9 | 0 | 0 | 22 | 5532 | 632 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 0 | 754.67 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 8 | 0 | 0 | 0 | 188 | 0 | 197 | 0 | 201 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1082 | 35 | 5056.17 | 10588.17
20:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 36 | 0 | 0 | 32 | 0 | 0 | 0 | 17 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 72 | 21 | 22 | 0 | 190 | 35 | 80 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 26 | 0 | 16 | 575 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 100 | 185 | 0 | 0 | 0 | 29 | 183 | 39 | 0 | 50 | 0 | 58 | 17 | 0 | 60 | 0 | 0 | 0 | 295 | 340 | 381 | 15 | 0 | 29 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 80 | 19 | 10 | 0 | 0 | 22 | 5451 | 632 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 0 | 755.34 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 197 | 0 | 200 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1082 | 35 | 5047.84 | 10498.84 | 93.63
21:00 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 42 | 21 | 22 | 0 | 180 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 26 | 0 | 18 | 575 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 60 | 185 | 0 | 0 | 0 | 29 | 182 | 36 | 0 | 50 | 0 | 45 | 17 | 0 | 58 | 0 | 0 | 0 | 260 | 340 | 381 | 15 | 0 | 29 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 216 | 0 | 35 | 19 | 11 | 0 | 0 | 22 | 5107 | 871 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611 | 0 | 756.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 160 | 0 | 200 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1102 | 0 | 5161.28 | 10268.28 | 93.62
22:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 35 | 14 | 22 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 22 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 595 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 182 | 33 | 0 | 50 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 265 | 340 | 380 | 15 | 0 | 30 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 216 | 0 | 24 | 19 | 11 | 0 | 0 | 22 | 4837 | 913 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 659.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 7 | 140 | 220 | 0 | 1112 | 0 | 4927.55 | 9764.55 | 93.62
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 24 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 182 | 39 | 0 | 50 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 275 | 340 | 380 | 15 | 0 | 30 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 24 | 19 | 10 | 0 | 0 | 0 | 4577 | 914 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 510.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 1152 | 0 | 4586.86 | 9163.86 | 93.62
Total KWH | 0 | 768000 | 281760 | 0 | 0 | 0 | 0 | 0 | 7477200 | 0 | 0 | 66240 | 434880 | 0 | 201744 | 472320 | 306109 | 0 | 109774 | 177120 | 501480 | 32640 | 8976500 | 0 | 0 | 0 | 0 | 594200 | 7078567 | 0 | 0 | 137427 | 474000 | 384600 | 423360 | 0 | 6102727.27 | 140509 | 296073 | 0 | 0 | 37920 | 0 | 39272 | 154810 | 66240 | 65280 | 20762 | 804240 | 12545 | 354720 | 12174545.46 | 0 | 0 | 124320 | 0 | 0 | 0 | 0 | 0 | 0 | 11361817 | 121230 | 1023927 | 359636 | 3479273 | 0 | 0 | 0 | 596640 | 4616000 | 817488 | 59520 | 1225140 | 0 | 327600 | 354590 | 0 | 1258560 | 0 | 360264 | 0 | 6910500 | 8159800 | 9244000 | 417168 | 0 | 682080 | 58224 | 3520882 | 344400 | 0 | 1070400 | 587808 | 0 | 0 | 5336800 | 16560 | 914400 | 312000 | 249600 | 10250 | 207310 | 114240 | 113409991.73 | 19512727 | 7499808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344880 | 14632725 | 0 | 13576364 | 0 | 0 | 0 | 0 | 0 | 0 | 264848 | 0 | 0 | 22147 | 486750 | 0 | 275252 | 4112818 | 0 | 4235191 | 0 | 4317236 | 0 | 0 | 0 | 23700 | 85464 | 4577000 | 1625890 | 40569 | 155678 | 0 | 0 | 0 | 27786.36 | 650160 | 34 | 0 | 5498000 | 139563 | 2993000 | 5101920 | 0 | 19799272.73 | 133200 | 110131983.09 | 223541974.82

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 07-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 9997 | MW | 12:00 Hr. | Energy Generated |  |  | 223541.9748 |  | MWHr
Day Peak Demand |  |  | 9997 | MW | 12:00 Hr. | Energy Unserverd |  |  | 60 |  | MWHr
Evening Peak Generation |  |  | 10731.95 | MW | 19:00 Hr. | Energy Demand |  |  | 223601.9748 |  | MWHr
Evening Peak Demand |  |  | 10731.95 | MW | 19:00 Hr.
Minimum Generation of the Day |  |  | 7152 | MW | 05:00 Hr.
Minimum Demand of the Day |  |  | 7152 | MW | 05:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 31538.6343 | 0 | 3324.587 | 0 | 0 | 137.427 | 0 | 0 | 35000.6483 | Gas | 109073.0743 | Gas | 382033231.7705
Chattogram Zone |  |  | 354.72 | 23536.3625 | 899.049 | 0 | 804.24 | 141.992 | 0 | 37.92 | 25774.2835 | Coal | 69669.2502 | Coal | 498478679.4539
Cumilla Zone |  |  | 12113.058 | 0 | 746.756 | 0 | 0 | 360.264 | 1258.56 | 0 | 14478.638 | HFO | 6788.356 | HFO | 119452892.98
Mymensingh Zone |  |  | 249.6 | 0 | 1357.2 | 0 | 0 | 217.56 | 0 | 0 | 1824.36 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 36332.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36332.062 | Hydro | 804.24 | Hydro | 80424
Khulna Zone |  |  | 7499.808 | 14632.725 | 0 | 0 | 0 | 344.88 | 19512.727 | 0 | 41990.14 | Solar | 2821.4834 | Solar | 37430678.576
Barishal Zone |  |  | 8234.483 | 25297.2727 | 133.2 | 0 | 0 | 0.034 | 0 | 0 | 33664.9897 | Import | 34347.651 | Import | 171726919.73
Rajshahi Zone |  |  | 12750.709 | 0 | 286.995 | 0 | 0 | 785.702 | 13576.364 | 0 | 27399.77 | Wind | 37.92 | Wind | 546048
Rangpur Zone |  |  | 0 | 6202.89 | 40.569 | 0 | 0 | 833.6244 | 0 | 0 | 7077.0834
Total |  |  | 109073.0743 | 69669.2502 | 6788.356 | 0 | 804.24 | 2821.4834 | 34347.651 | 37.92 | 223541.9748
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 382033231.7705 |  | Hydro | 80424
|  |  | Coal | 498478679.4539 |  | Solar | 37430678.576
|  |  | HFO | 119452892.98 |  | Import | 171726919.73
|  |  | HSD | 0 |  | Wind | 546048
|  |  |  | Total: | 1209748874.5104 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Barapukuria TPP Unit-2 |  |  | 85
| 3 | Khulna 330 MW CCPP GT |  |  | 220
| 4 | Khulna 330 MW CCPP ST |  |  | 110
| 5 | Siddhirgonj 210 MW TPP |  |  | 115
| 6 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 7 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1044 |  |  |  | Total | 35.09
|  |  | Total Unavailable Capacity |  |  |  | 1079.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3944
|  |  | Chattogram |  | 0 |  | 1083
|  |  | Cumilla |  | 0 |  | 895
|  |  | Mymensingh |  | 0 |  | 870
|  |  | Sylhet |  | 0 |  | 371
|  |  | Khulna |  | 0 |  | 1186
|  |  | Barishal |  | 0 |  | 295
|  |  | Rajshahi |  | 0 |  | 984
|  |  | Rangpur |  | 0 |  | 651
|  |  | Total |  | 0 |  | 10279
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:14 | 17:00 | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual maintenance
08:14 | 17:00 | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual maintenance
08:14 | 17:00 | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual maintenance
08:18 | 15:41 | Mithapukur-Palashbari 132kV Ckt-1 Scheduled S/D from Mithapukur 132/33kV end Due to
Annual Maintenance.
08:22 | 17:22 | Pabna 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance
08:22 | 17:22 | Pabna 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance
08:28 | 16:10 | Bogura 230/132kV S/S Bogura (W) CKT-1 Scheduled S/D Due to Annual Maintenance
08:28 | 16:10 | Bogura 400/230kV S/S Bogura 230 kV Ckt-1 Scheduled S/D Due to Deadline check
08:30 | 15:40 | Mithapukur-Palashbari 132kV Ckt-1 Scheduled S/D from Palashbari 132/33kV end.
08:32 | 17:06 | Bogura-Mahasthangar (New)) 132 kV Ckt-1 Scheduled S/D from Mahasthangarh 132/33kV end Due
to Annual Maintenance Work. and from Bogura 132/33kV end Due to annual maintenance
08:35 | 14:39 | Juldah-Sikalbaha 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to Annual
maintenance
08:41 | 13:32 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Scheduled S/D Due to Annual Maintenance
08:41 | 13:32 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to Annual Maintenance
08:52 | 16:26 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Dhamrai 132/33kV end Due to Annual
maintenance
08:55 | 17:03 | Kallyanpur 132/33kV S/S GT-2 (132kV) LT Scheduled S/D Due to Annual Maintenance
08:56 | 17:02 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to annual maintenance
08:56 | 17:13 | Kodda-Rajendrapur 132kV Ckt-2 Scheduled S/D from Rajendrapur 132/33kV end Due to Due to
deadline checking. and from Kodda 132/33kV end Due to Dead line checking
08:56 | 16:44 | Madunaghat 400/230kV S/S Madunaghat-Banskhali 400kV Ckt.-1 Scheduled S/D Due to Annual
maintenance.
08:59 | 16:27 | Baghabari-Sirajganj 230 kV Ckt-2 Scheduled S/D from Baghabari 230/132kV end Due to A/M
09:04 | 10:59 | Noapara 132/33kV S/S BUS A Scheduled S/D Due to Due to annual maintenance
09:07 | 15:08 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Scheduled S/D Due to Annual Maintenance
09:07 | 15:08 | Jashore 132/33kV S/S JH-2(L1) Scheduled S/D
09:13 | 15:41 | Haripur-Madanganj 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to From Other
End. and from Madanganj 132/33kV end Due to Annual Maintenance
09:14 | 19:05 | Haripur-Siddirganj 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to From Other
End. and from Siddhirganj 132/33kV end Due to Annual Maintenance work.
09:14 | 19:05 | Haripur-Siddirganj 132kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to From Other
End.
09:15 | 19:02 | Haripur-Siddirganj 230kV Ckt-2 Scheduled S/D from Siddhirganj 132/33kV end Due to Annual
Maintenance work
09:17 | 17:05 | Tangail 132/33kV S/S Kaliakair-2 Scheduled S/D Due to Dead line cheaking
09:20 | 16:16 | Chowmuhani-Feni 132 kV Ckt-2 Scheduled S/D from Chowmuhani 132/33kV end Due to Yearly
maintenance and from Feni 132/33kVend.
09:24 | 17:04 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2A(E04) Scheduled S/D Due to Tangail Grid
Maintenance Work
09:25 | 17:04 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2B(E03) Scheduled S/D Due to Tangail Grid
Maintenance work
09:47 | 15:19 | Madunaghat-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Project work.
09:48 | 15:54 | Madunaghat 400/230kV S/S Madunaghat-Meghnaghat 400kV Ckt.-1 Scheduled S/D
09:48 | 11:09 | Matuail-Siddhirganj 132kV Ckt-1 Scheduled S/D from Siddhirganj 132/33kV end Due to
Annual maintenance work by matuail end. and from Matuail 132/33kV end Due to winter
maintenance work
| 10:01 | Daudkandi 132/33kV S/S Transformer-1 HT is restored.
10:08 | 11:49 | Bogura 230/132kV S/S Confidance UN-2 Scheduled S/D
10:09 | 15:57 | Madunaghat 400/230kV S/S Madunaghat-Hathazari 230kV Ckt.-1 Scheduled S/D
10:12 | 15:21 | Tongi 230/132/33kV S/S T-2 LT Scheduled S/D Due to SPS installation
10:12 | 15:58 | Hathazari 230/132/33kV S/S Shikolbaha-01 Scheduled S/D Due to dead line check
10:13 | 15:21 | Tongi 230/132/33kV S/S T-2 HT Scheduled S/D Due to SPS installation
| 10:14 | Haripur-Narsingdi 132kV Ckt-1 is restored.
10:16 | 13:02 | Daudkandi 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual Maintenance
10:16 | 13:01 | Daudkandi 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual maintenance
10:20 |  | Kulaura 132/33kV S/S 132 kV Bus-B Scheduled S/D Due to Annual maintenance.
10:42 | 14:55 | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to U/G Cable Checking
10:43 | 13:45 | Sylhet 132/33kV S/S T1 HT Scheduled S/D Due to U/G Cable Abnormal Sound Checking
10:44 |  | Maniknagar-Matuail 132kV Ckt-1 Forced S/D from Matuail 132/33kV end Due to for circuit
tripping from maniknagar end
11:03 | 11:58 | HVDC Bheramera- Ishwardi 230kV Ckt-3 Scheduled S/D from Ishurdi 230/132kV end Due to DC
E/F locator installation
11:04 | 15:12 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end.
12:13 | 12:37 | HVDC Bheramera-Ishwardi 230kV Ckt-4 Scheduled S/D from Ishurdi 230/132kV end Due to dc
earth fault locator installation
13:08 | 15:25 | Daudkandi 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Relay test by SPMD cumilla
13:09 | 15:24 | Daudkandi 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Relay test by SPMD cumilla
13:15 | 13:29 | Baghabari-Ishurdi 230 kV Ckt-1 Scheduled S/D from Ishurdi 230/132kV end Due to dc earth
fault locator installation
13:29 | 13:34 | Baghabari-Ishurdi 230 kV Ckt-2 Scheduled S/D from Ishurdi 230/132kV end Due to dc earth
fault locator installation
| 13:33 | BIPTC S/S 20DF13 is restored.
| 14:40 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT is restored.
| 14:40 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT is restored.
15:51 | 22:27 | Tongi 230/132/33kV S/S T-3 HT Scheduled S/D Due to Relay Test
15:51 | 22:27 | Tongi 230/132/33kV S/S T-3 LT Scheduled S/D Due to Relay Test
| 16:09 | Gopalganj(N)-Rampal Ckt-1 is restored.
| 16:09 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 is restored.
| 16:21 | Barishal 132/33kV S/S 132 kv Summit power is restored.
| 16:24 | Barishal 132/33kV S/S 132 kv GTPS is restored.
16:41 |  | Jhenidah(O) - Chuadanga Ckt-2 Close .
| 16:55 | Kaliakoir 400/230/132kV S/S Bibiyana1 is restored.
| 16:56 | Bibiyana-Kaliakoir 400 kV Ckt-1 is restored.
| 17:42 | Aminbazar-Kaliakoir 230kV Ckt-2 is restored.
| 17:42 | Aminbazar-Kaliakoir 230kV Ckt-1 is restored.
19:00 |  | Evening Peak generation = 10,731MW
| 19:07 | Bhulta-Haripur 230 kV Ckt-2 is restored.
| 19:07 | Bhulta-Haripur 230 kV Ckt-2 is restored.
| 19:10 | Aminbazar-Airport(Old) 230kV Ckt-1 is restored.
23:04 | 23:19 | Pabna 132/33kV S/S T-3 LT Tripped showing 51N trip relays Due to Chatmohar 33 kv Fault | [7 empty] | 24.0MW load
interrup.
23:04 | 23:19 | Pabna 132/33kV S/S T-2 LT Tripped showing INST. E/F. relays Due to Chatmohar 33 kv | [7 empty] | 12.0MW load
interrup.
01:00 |  | Unique Meghnaghat Power 584 MW CCPP was shutdown.
05:00 |  | Minimum Generation: 7238 MW.
07:21 | 07:41 | Cumilla(N) 230/132/33kV S/S 132KV T-05 LT Tripped showing 50N/51N OC ABC phase 33KV 87N | [7 empty] | 16.0MW load
|  | REF Lockout relays. | [7 empty] | interrup.
07:21 | 07:41 | Cumilla(N) 230/132/33kV S/S 132KV T-05 HT Tripped showing 50N/51N OC ABC phase 33KV 87N | [7 empty] | 16.0MW load
|  | REF Lockout relays Due to PBS 33KV faulty feeder trialed | [7 empty] | interrup.
07:22 |  | Kabirpur -Kodda 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to 132 kv Kadda
Ckt-2 Re conducting work.
07:31 |  | Barishal 132/33kV S/S 132 kv GTPS Scheduled S/D Due to Annual Maintenance Work
07:45 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
NLDC.
07:46 |  | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
NLDC.
07:53 |  | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Scheduled S/D
07:54 |  | Gopalganj(N)-Rampal Ckt-1 Scheduled S/D from Rampal 400/230kV end Due to Due to Khulna
ALDC Demand(Maintenance Work)
07:57 |  | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual maintenance
07:58 |  | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual maintenance
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 234.58 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 313 | 7477200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 360 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8976500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7078567 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 66240 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149 | 32 | 472320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 109774 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 384600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 19 | 423360 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 501480 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 28 | 594200 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 281760 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 306109 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 15 | 201744 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 768000 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 32640 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 177120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 137427 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 36 | 434880 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 220 | 6102727.27 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 718 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 150 | 72 | 474000 | -
Dhaka Area Total |  |  |  |  | 7112.42 | 1773 | 35000648.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 121230 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 124320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 26 | 804240 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 39272 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 36 | 66240 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 33 | 4 | 354720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 80 | 296073 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 35 | 154810 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 12545 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 65280 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 140509 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1320 | 612 | 11361817 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 66 | 0 | 37920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 575 | 12174545.46 | Partial Shutdown due to maintenance
Chattogram Area Total |  |  |  |  | 4989.22 | 1471 | 25774283.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221 | 183 | 4616000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 356.15 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 45 | 36 | 817488 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 596640 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 3479273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1023927 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 359636 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1225140 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 56 | 1258560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 354590 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 55 | 327600 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 59520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 360264 | -
Cumilla Area Total |  |  |  |  | 2913.35 | 796 | 14478638
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 9 | 249600 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 3 | 0 | 10250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 312000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 80 | 914400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 207310 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 114240 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 16560 | -
Mymensingh Area Total |  |  |  |  | 654.5 | 130 | 1824360
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 682080 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3520882 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | -
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 15 | 417168 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 58224 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 587808 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 1070400 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 216 | 5336800 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 344400 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6910500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 381 | 9244000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 340 | 8159800 | FGMO
Sylhet Area Total |  |  |  |  | 2366 | 1514 | 36332062
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 632 | 19512727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 322 | 7499808 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 344880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234 | 603 | 14632725 | -
** | HVDC(Nepal) |  | Import | 1*40 | 40 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3739 | 1557 | 41990140
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 139563 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 140 | 2993000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1072 | 19799272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5101920 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 133200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5498000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 34 | -
Barishal Area Total |  |  |  |  | 2266 | 1781 | 33664989.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 188 | 4112818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 197 | 4235191 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 200 | 4317236 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 414 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 85464 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 16 | 22147 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 68 | 264848 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 755.45 | 13576364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 275252 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 486750 | -
Rajshahi Area Total |  |  |  |  | 3411.72 | 1429.95 | 27399770
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 70 | 1625890 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4577000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 27786.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 40569 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 155678 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 650160 | -
Rangpur Area Total |  |  |  |  | 950 | 280 | 7077083.36
Eastern Grid Total |  |  |  |  | 18035.49 | 5684 | 113409991.73
Western Grid Total |  |  |  |  | 10366.72 | 5047.95 | 110131983.09
National Grid Total |  |  |  |  | 28402.21 | 10731.95 | 223541974.82
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7163.38 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3116.8 | MW
i) Dhaka area |  |  | 3944.38 |  | MW | i) Khulna area |  |  |  | 1186.4 | MW
ii) Chattogram area |  |  | 1083 |  | MW | ii) Barishal area |  |  |  | 295 | MW
iii) Cumilla area |  |  | 895 |  | MW | iii) Rajshahi area |  |  |  | 984.4 | MW
iv) Mymensingh area |  |  | 870 |  | MW | iv) Rangpur area |  |  |  | 651 | MW
v) Sylhet area |  |  | 371 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10280.18 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 54 | 18:00 | 133 | Purbasadipur | 102 | 18:00
2 | AKSML | 107 | 00:00 | 68 | Jamalpur | 93 | 18:00 | 134 | Rahanpur | 0 | 00:00
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 99 | 13:00 | 135 | Rahim | 34 | 12:00
4 | Agargaon | 78 | 13:00 | 70 | Jhenaidah | 94 | 18:00 | 136 | Rajbari | 56 | 18:00
5 | Agrabad | 64 | 18:00 | 71 | Joydebpur | 128 | 12:00 | 137 | Rajendrapur | 94 | 13:00
6 | Amnura | 43 | 08:00 | 72 | Joypurhat | 40 | 20:00 | 138 | Rajshahi | 94 | 20:00
7 | Ashuganj | 56 | 00:00 | 73 | Juldah | 10 | 00:00 | 139 | Rajshahi-230 | 52 | 13:00
8 | BSRM | 192 | 07:00 | 74 | KSRM | 30 | 13:00 | 140 | Ramganj | 80 | 19:30
9 | Bagerhat | 71 | 18:30 | 75 | Kabirpur | 220 | 18:00 | 141 | Rampur | 26 | 18:30
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 44 | 18:00 | 142 | Rangamati | 12 | 18:00
11 | Bakulia | 65 | 18:00 | 77 | Kallyanpur | 70 | 13:00 | 143 | Rangpur | 107 | 18:00
12 | Banani | 38 | 13:00 | 78 | Kalurghat | 28 | 10:00 | 144 | Ruppur | 2.8 | 00:00
13 | Bangabhaban | 8 | 10:00 | 79 | Kamrangirchar | 54.67 | 13:00 | 145 | SSM | 2 | 00:00
14 | Barapukuria | 48 | 18:30 | 80 | Kaptai | N/A | N/A | 146 | Saidpur | 85 | 18:30
15 | Barguna | 14 | 19:00 | 81 | Kazla | 83 | 12:00 | 147 | Satkhira | 86 | 18:00
16 | Barishal | 93 | 13:00 | 82 | Keranigonj | 61 | 18:30 | 148 | Satmasjid | 83 | 13:00
17 | Barishal-230 | 60 | 18:00 | 83 | Khagrachori | 24 | 18:00 | 149 | Savar | 195 | 12:00
18 | Baroaulia | 50 | 08:00 | 84 | Khulna | 69 | 13:00 | 150 | SevenRings | 12.03 | 21:00
19 | Baroirhat | 44 | 18:00 | 85 | Khulshi | 141 | 18:00 | 151 | ShahCement | 31 | 10:00
20 | Bashundhara | 130 | 13:00 | 86 | Kishoreganj | 114 | 18:00 | 152 | Shahjadpur | 54 | 18:00
21 | BashundharaCement | 12 | 13:00 | 87 | Kodda | 264 | 19:00 | 153 | Shahjibazar | 73 | 21:00
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 27 | 19:30 | 154 | Shahmirpur | 38 | 01:00
23 | Benapole | 50 | 08:00 | 89 | Kurigram | 43 | 08:00 | 155 | Shariatpur | 52 | 20:00
24 | Bhaluka | 114 | 19:00 | 90 | Kushtia | 108 | 18:00 | 156 | Sherpur | 104 | 08:00
25 | Bhandaria | 35 | 21:00 | 91 | Lalbag | 64 | 17:00 | 157 | Shikalbaha | 20 | 13:00
26 | Bhangura | 22 | 19:00 | 92 | Lalmonirhat | 41 | 18:00 | 158 | Shitalakhya | 61.8 | 12:00
27 | Bheramara(GK) | 41 | 18:00 | 93 | MI_Cement | 15.7 | 00:00 | 159 | Sholosohor | 32 | 11:00
28 | Bhulta | 252 | 12:00 | 94 | Madanganj | 30 | 13:00 | 160 | Shyampur | 148 | 10:00
29 | Bog-Sherpur | 54 | 08:00 | 95 | Madaripur | 66 | 21:00 | 161 | Siddhirganj | 111 | 12:00
30 | Bogura | 108 | 18:00 | 96 | Madartek | 58.03 | 13:00 | 162 | Sirajganj | 74 | 19:00
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 38 | 17:00 | 163 | Sonargaon | 79 | 18:00
32 | Brahmanbaria | 108 | 18:30 | 98 | Magura | 45 | 18:30 | 164 | Sreemongol | 52 | 18:00
33 | Cantonment | 84 | 13:00 | 99 | Mahasthangarh | 48 | 18:00 | 165 | Sreepur | 60 | 10:00
34 | Chandpur | 43 | 19:30 | 100 | Manikganj | 106 | 20:00 | 166 | Srinagar | 29.6 | 14:00
35 | Chandraghona | 26 | 18:00 | 101 | Maniknagar | 48 | 13:00 | 167 | Sunamganj | 40 | 18:00
36 | Chapai | 47 | 13:00 | 102 | Matarbari | 35 | 18:00 | 168 | Sylhet | 30 | 18:00
37 | Charsaidpur | 38 | 20:00 | 103 | Matuail | 44 | 14:00 | 169 | Sylhet-132 | 76 | 18:00
38 | Chauddagram | 40 | 13:00 | 104 | Millgate | 70 | 15:00 | 170 | TK | 21.4 | 18:00
39 | Chhatak | 20 | 19:00 | 105 | Mirpur | 95.5 | 14:00 | 171 | Tangail | 130 | 19:00
40 | Chowmuhani | 146 | 19:00 | 106 | Mirsorai | 8 | 18:00 | 172 | Thakurgaon | 76 | 18:30
41 | Chuadanga | 72 | 13:00 | 107 | Mirzapur | 28 | 17:00 | 173 | Tongi | 102 | 12:00
42 | Coxsbazar | 97 | 18:00 | 108 | Mithapukur | 42 | 18:00 | 174 | Ullahpara | 27 | 18:00
43 | Cumilla(N) | 116 | 18:30 | 109 | Modern | 0 | 00:00 | 175 | Ullon | 38 | 21:00
44 | Cumilla(S) | 122 | 14:00 | 110 | Mogbazar | 66.5 | 18:30 | 176 | Uttara | 58 | 13:00
45 | Daudkandi | 98 | 21:00 | 111 | Mongla | 22 | 18:00 | 177 | UttaraNew | 33 | 12:00
46 | Dhaka | 32 | 13:00 | 112 | Motijheel | 26 | 13:00 | 178 | Zigatola | 67 | 15:00
47 | Dhamrai | 84 | 18:30 | 113 | Munshiganj | 70 | 13:00
48 | Dhanmondi | 81.5 | 13:00 | 114 | Mymensingh | 177 | 13:00
49 | Dohazari | 64 | 18:00 | 115 | Naogaon | 84 | 18:00
50 | Faridpur | 108 | 19:00 | 116 | Narail | 41 | 18:30
51 | Fatullah | 78 | 10:00 | 117 | Narinda | 49 | 13:00
52 | Fenchuganj | 24 | 18:30 | 118 | Narshingdi | 154 | 18:30
53 | Feni | 67 | 13:00 | 119 | Natore | 105 | 18:00
54 | GPH | 20 | 05:00 | 120 | Nawabganj | 34.6 | 20:00
55 | Ghatail | 30 | 07:00 | 121 | Netrakona | 113 | 19:30
56 | Ghorashal | 8 | 00:00 | 122 | New | 69 | 12:00
57 | Ghorashal-230 | 48 | 00:00 | 123 | Niamatpur | 58 | 13:00
58 | Goalpara | 26 | 13:00 | 124 | Noapara | 35 | 19:30
59 | Gollamari | 50 | 13:00 | 125 | PHP | 7 | 01:00
60 | Gopalganj | 75.5 | 18:30 | 126 | Pabna | 82 | 18:00
61 | Gulshan | 66 | 13:00 | 127 | Palashbari | 73 | 18:00
62 | Halishahar | 46 | 14:00 | 128 | Panchagarh | 43 | 18:00
63 | HaripurSBU | 157 | 11:00 | 129 | Patuakhali | 54 | 19:00
64 | Hasnabad | 62 | 15:00 | 130 | Payra | 14 | 18:00
65 | Hathazari | 56 | 13:00 | 131 | Postogola | 40 | 12:00
66 | Ishurdi | 58 | 18:00 | 132 | Purbachal | 14 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8639 | 0 |  | 8639
1:00 | 8155 | 0 |  | 8155
2:00 | 7590 | 0 |  | 7590
3:00 | 7568 | 0 |  | 7568
4:00 | 7322 | 0 |  | 7322
5:00 | 7152 | 0 |  | 7152
6:00 | 7779 | 0 |  | 7779
7:00 | 8372 | 0 |  | 8372
8:00 | 8940 | 0 |  | 8940
9:00 | 9525 | 25 |  | 9551.13
10:00 | 9151 | 20 |  | 9171.9
11:00 | 9513 | 15 |  | 9528.68
12:00 | 9997 | 0 |  | 9997
13:00 | 10360 | 0 |  | 10360
14:00 | 9820 | 0 |  | 9820
15:00 | 9403 | 0 |  | 9403
16:00 | 9213 | 0 |  | 9213
17:00 | 9444.04 | 0 |  | 9444.04
18:00 | 10509.73 | 0 |  | 10509.73
19:00 | 10731.95 | 0 |  | 10731.95
19:30 | 10588.17 | 0 |  | 10588.17
20:00 | 10498.84 | 0 |  | 10498.84
21:00 | 10268.28 | 0 |  | 10268.28
22:00 | 9764.55 | 0 |  | 9764.55
23:00 | 9163.86 | 0 |  | 9163.86
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4369 | 4270 | 8639 | DAILY LOAD CURVE
00:30 | 4170 | 4227 | 8397
01:00 | 3971 | 4184 | 8155 | 07-01-2025
01:30 | 3848 | 4024.5 | 7872.5
02:00 | 3725 | 3865 | 7590
02:30 | 3714 | 3865 | 7579
03:00 | 3703 | 3865 | 7568
03:30 | 3650 | 3795 | 7445
04:00 | 3597 | 3725 | 7322
04:30 | 3649.5 | 3587.5 | 7237
05:00 | 3702 | 3450 | 7152
05:30 | 3890 | 3575.5 | 7465.5
06:00 | 4078 | 3701 | 7779
06:30 | 4224 | 3851.5 | 8075.5
07:00 | 4370 | 4002 | 8372
07:30 | 4355.5 | 4300.5 | 8656
08:00 | 4341 | 4599 | 8940
08:30 | 4520 | 4712.5 | 9232.5
09:00 | 4699 | 4826 | 9525
09:30 | 4736.5 | 4601.5 | 9338
10:00 | 4774 | 4377 | 9151
10:30 | 4862 | 4470 | 9332
11:00 | 4950 | 4563 | 9513
11:30 | 5057.5 | 4697.5 | 9755
12:00 | 5165 | 4832 | 9997
12:30 | 5231 | 4947.5 | 10178.5
13:00 | 5297 | 5063 | 10360
13:30 | 5126.5 | 4963.5 | 10090
14:00 | 4956 | 4864 | 9820
14:30 | 4933.5 | 4678 | 9611.5
15:00 | 4911 | 4492 | 9403
15:30 | 4888 | 4420 | 9308
16:00 | 4865 | 4348 | 9213
16:30 | 4861.59 | 4466.93 | 9328.52
17:00 | 4858.18 | 4585.86 | 9444.04
17:30 | 5253.27 | 4723.615 | 9976.885
18:00 | 5648.36 | 4861.37 | 10509.73
18:30 | 5666.18 | 4954.66 | 10620.84
19:00 | 5684 | 5047.95 | 10731.95
19:30 | 5532 | 5056.17 | 10588.17
20:00 | 5451 | 5047.84 | 10498.84
20:30 | 5279 | 5104.56 | 10383.56 |  | Executive Engineer
21:00 | 5107 | 5161.28 | 10268.28 |  | Network Operation Division
21:30 | 4972 | 5044.415 | 10016.415
22:00 | 4837 | 4927.55 | 9764.55
22:30 | 4707 | 4757.205 | 9464.205
23:00 | 4577 | 4586.86 | 9163.86

## En-Curve
QF-LDC-12
Date | 07-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2734 | 1637 | 913 | 0 | 56 | 491 | 26 | 2700 | 0 | 49 | 33 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2732 | 1572 | 912.5 | 0 | 50 | 455 | 26 | 2592 | 0 | 32.5 | 25 | 0 | 0 | 0 | 0 | 07-01-2025
01:00 | 2730 | 1507 | 912 | 0 | 44 | 419 | 26 | 2484 | 0 | 16 | 17 | 0 | 0 | 0 | 0
01:30 | 2668 | 1462 | 819 | 0 | 46 | 419.5 | 26 | 2415.5 | 0 | 8 | 8.5 | 0 | 0 | 0 | 0 |  | Total Energy | 223.542 |  | MKWHr
02:00 | 2606 | 1417 | 726 | 0 | 48 | 420 | 26 | 2347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Energy not Served | 0.06 |  | MKWHr
02:30 | 2600 | 1409.5 | 725.5 | 0 | 48 | 420.5 | 26 | 2349.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Energy Requirement | 223.602 |  | MKWHr
03:00 | 2594 | 1402 | 725 | 0 | 48 | 421 | 26 | 2352 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2571.5 | 1372.5 | 679 | 0 | 48 | 420.5 | 26 | 2327.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2549 | 1343 | 633 | 0 | 48 | 420 | 26 | 2303 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2514.5 | 1387 | 633 | 0 | 46 | 420 | 26 | 2210.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2480 | 1431 | 633 | 0 | 44 | 420 | 26 | 2118 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2623 | 1538.5 | 633 | 0 | 44 | 419 | 26 | 2178 | 0 | 4 | 0 | 0 | 0 | 0 | 0
06:00 | 2766 | 1646 | 633 | 0 | 44 | 418 | 26 | 2238 | 0 | 8 | 0 | 0 | 0 | 0 | 0
06:30 | 2827.5 | 1676 | 679 | 0 | 45 | 434 | 26 | 2361.5 | 6.5 | 20 | 0 | 0 | 0 | 0 | 0
07:00 | 2889 | 1706 | 725 | 0 | 46 | 450 | 26 | 2485 | 13 | 32 | 0 | 0 | 0 | 0 | 0
07:30 | 2864.5 | 1606.5 | 819.5 | 0 | 45 | 530 | 26 | 2623.5 | 58.5 | 50 | 32 | 0 | 0 | 0.5 | 0
08:00 | 2840 | 1507 | 914 | 0 | 44 | 610 | 26 | 2762 | 104 | 68 | 64 | 0 | 0 | 1 | 0
08:30 | 2863.5 | 1591.5 | 914.5 | 0 | 47 | 611 | 36 | 2843 | 178 | 75 | 71.5 | 0 | 0 | 1.5 | 12.5
09:00 | 2887 | 1676 | 915 | 0 | 50 | 612 | 46 | 2924 | 252 | 82 | 79 | 0 | 0 | 2 | 25
09:30 | 2891.5 | 1631.5 | 773.5 | 0 | 52 | 611 | 46 | 2844 | 299 | 82 | 106 | 0 | 0 | 1.5 | 22.5
10:00 | 2896 | 1587 | 632 | 0 | 54 | 610 | 46 | 2764 | 346 | 82 | 133 | 0 | 0 | 1 | 20
10:30 | 2859.5 | 1613.5 | 687 | 0 | 54 | 609 | 46 | 2834.5 | 388 | 82 | 157.5 | 0 | 0 | 1 | 17.5
11:00 | 2823 | 1640 | 742 | 0 | 54 | 608 | 46 | 2905 | 430 | 82 | 182 | 0 | 0 | 1 | 15
11:30 | 2860.5 | 1718 | 827.5 | 0 | 54 | 609.5 | 46 | 2908.5 | 446 | 99.5 | 185 | 0 | 0 | 0.5 | 7.5
12:00 | 2898 | 1796 | 913 | 0 | 54 | 611 | 46 | 2912 | 462 | 117 | 188 | 0 | 0 | 0 | 0
12:30 | 2929.5 | 1822 | 913 | 0 | 60 | 610.5 | 46 | 3058.5 | 427.5 | 117 | 188.5 | 0 | 0 | 6 | 0
13:00 | 2961 | 1848 | 913 | 0 | 66 | 610 | 46 | 3205 | 393 | 117 | 189 | 0 | 0 | 12 | 0
13:30 | 2875.5 | 1763 | 913.5 | 0 | 64 | 610 | 46 | 3123.5 | 377.5 | 117 | 188.5 | 0 | 0 | 11.5 | 0
14:00 | 2790 | 1678 | 914 | 0 | 62 | 610 | 46 | 3042 | 362 | 117 | 188 | 0 | 0 | 11 | 0
14:30 | 2774.5 | 1687.5 | 913.5 | 0 | 58 | 586.5 | 46 | 2928 | 312.5 | 117 | 179 | 0 | 0 | 9 | 0
15:00 | 2759 | 1697 | 913 | 0 | 54 | 563 | 46 | 2814 | 263 | 117 | 170 | 0 | 0 | 7 | 0
15:30 | 2745 | 1706.5 | 913 | 0 | 55 | 540 | 46 | 2814.5 | 201.5 | 117 | 164 | 0 | 0 | 5.5 | 0
16:00 | 2731 | 1716 | 913 | 0 | 56 | 517 | 46 | 2815 | 140 | 117 | 158 | 0 | 0 | 4 | 0
16:30 | 2777 | 1714.75 | 913 | 0 | 56 | 532.18 | 46 | 2839.5 | 77.09 | 159.5 | 211.5 | 0 | 0 | 2 | 0
17:00 | 2823 | 1713.5 | 913 | 0 | 56 | 547.36 | 46 | 2864 | 14.18 | 202 | 265 | 0 | 0 | 0 | 0
17:30 | 2898.5 | 1771 | 772 | 0 | 57 | 604.115 | 36 | 3104 | 7.09 | 232.5 | 494.68 | 0 | 0 | 0 | 0
18:00 | 2974 | 1828.5 | 631 | 0 | 58 | 660.87 | 26 | 3344 | 0 | 263 | 724.36 | 0 | 0 | 0 | 0
18:30 | 2969 | 1814.5 | 631.5 | 0 | 57 | 708.16 | 26 | 3396.5 | 0 | 260.5 | 757.68 | 0 | 0 | 0 | 0
19:00 | 2964 | 1800.5 | 632 | 0 | 56 | 755.45 | 26 | 3449 | 0 | 258 | 791 | 0 | 0 | 0 | 0
19:30 | 3050 | 1806.5 | 632 | 0 | 58 | 754.67 | 26 | 3465 | 0 | 239 | 557 | 0 | 0 | 0 | 0
20:00 | 2967 | 1804.5 | 632 | 0 | 60 | 755.34 | 26 | 3465 | 0 | 239 | 550 | 0 | 0 | 0 | 0
20:30 | 2941 | 1761.5 | 751.5 | 0 | 59 | 756.06 | 26 | 3476 | 0 | 190 | 422.5 | 0 | 0 | 0 | 0
21:00 | 2915 | 1718.5 | 871 | 0 | 58 | 756.78 | 26 | 3487 | 0 | 141 | 295 | 0 | 0 | 0 | 0
21:30 | 2873 | 1717 | 892 | 0 | 58 | 707.915 | 26 | 3424.5 | 0 | 129.5 | 188.5 | 0 | 0 | 0 | 0
22:00 | 2831 | 1715.5 | 913 | 0 | 58 | 659.05 | 26 | 3362 | 0 | 118 | 82 | 0 | 0 | 0 | 0
22:30 | 2822 | 1712 | 913.5 | 0 | 55 | 584.705 | 26 | 3204.5 | 0 | 75.5 | 71 | 0 | 0 | 0 | 0
23:00 | 2813 | 1708.5 | 914 | 0 | 52 | 510.36 | 26 | 3047 | 0 | 33 | 60 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 407 | 04:00 | 382 | 13:00 | Kaliakoir | 375 | 04:00 | 345 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 409 | 2:00 | 372 | 13:00 | Madunaghat | 407 | 04:00 | 383 | 12:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 401 | 06:00 | 377 | 12:00 | Meghnaghat | 401 | 04:00 | 378 | 12:00
| Bibiana | 394 | 05:00 | 384 | 14:00 | Payra | 418 | 03:00 | 409 | 13:00
| BIPTC | 409 | 04:00 | 391 | 12:00 | Rahanpur | 414 | 04:00 | 400 | 13:00
| Bogura | 409 | 04:00 | 393 | 13:00 | Rampal | 413 | 05:00 | 389 | 13:00
| Gopalganj | 413 | 04:00 | 392 | 13:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 233 | 04:00 | 214 | 13:00 | Haripur | 235 | 04:00 | 219 | 13:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 233 | 00:00 | 215 | 12:00 | Hasnabad | 230 | 00:00 | 215 | 13:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 231 | 03:00 | 216 | 12:00 | Hathazari | 233 | 03:00 | 218 | 12:00
| Ashuganj | 237 | 04:00 | 223 | 13:00 | Ishurdi | 242 | 03:00 | 228 | 13:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 01:00 | 222 | 13:00 | Jhenaidah | 240 | 03:00 | 223 | 13:00
| Baghabari | 241 | 07:00 | 229 | 12:00 | Kaliakoir | 235 | 04:00 | 218 | 12:00 | 230 kV MAX | 247 |  | 247 | 213
| Barapukuria | 226 | 06:00 | 217 | 08:00 | Keranigonj | 232 | 04:00 | 214 | 13:00 | 230 kV MIN | 213 |  | 242 | 213 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 226 | 06:00 | 217 | 08:00 | Khulna(S) | 240 | 03:00 | 224 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 246 | 04:00 | 237 | 13:00 | Madunaghat | 230 | 17:00 | 218 | 13:00 | 132 kV MAX | 142 |  | 142 | 113 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 240 | 03:00 | 225 | 13:00 | Madunaghat-400 | 234 | 03:00 | 217 | 13:00 | 132 kV MIN | 109 |  | 141 | 109 |  |  |  | 400 kV | 7 | [25 empty] | 403
| Bhulta | 234 | 01:00 | 220 | 12:00 | Maniknagar | 234 | 03:00 | 219 | 13:00 | [35 empty] | 6:00
| Bibiana | 227 | 00:00 | 221 | 12:00 | Meghnaghat | 240 | 03:00 | 228 | 13:00 | [35 empty] | 392
| BIPTC | 241 | 03:00 | 226 | 13:00 | Meghnaghat-400 | 235 | 04:00 | 221 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 238 | 04:00 | 229 | 13:00 | Mirsorai | 232 | 02:00 | 213 | 13:00 | ` | [34 empty] | 21:00
| Bogura-400 | 238 | 04:00 | 228 | 08:00 | Rajshahi | 241 | 04:00 | 226 | 13:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 247 | 01:00 | 241 | 13:00 | Rampal | 238 | 03:00 | 223 | 13:00 |  |  |  |  | Ash 400-299274
| BSRM | 232 | 02:00 | 213 | 13:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 230 | 01:00 | 217 | 12:00 | Rampura | 236 | 04:00 | 220 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 245 | 05:00 | 233 | 13:00 | Shikalbaha | 232 | 03:00 | 214 | 12:00 |  | kaptai by call 399528
| Fenchuganj | 230 | 03:00 | 224 | 13:00 | Shyampur | 233 | 04:00 | 217 | 12:00
| Ghorashal | 235 | 00:00 | 235 | 00:00 | Siddhirganj | 235 | 03:00 | 221 | 12:00
| Ghorashal-230 | 234 | 04:00 | 218 | 13:00 | Sirajgonj | 245 | 02:00 | 236 | 12:00
| Gopalganj | 244 | 04:00 | 233 | 12:00 | Sreepur | 235 | 01:00 | 226 | 09:00
| GPH | 233 | 04:00 | 214 | 12:00 | Tongi | 234 | 04:00 | 220 | 07:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 135 | 03:00 | 124 | 12:00 | Kurigram | 132 | 04:00 | 119 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 139 | 04:00 | 126 | 13:00 | Kushtia | 139 | 03:00 | 131 | 13:00
| Agrabad | 133 | 02:00 | 122 | 12:00 | Lalbag | 136 | 04:00 | 124 | 13:00
| AKS | 132 | 01:00 | 121 | 13:00 | Lalmonirhat | 130 | 03:00 | 120 | 12:00
| Aminbazar | 140 | 05:00 | 128 | 08:00 | Madanganj | 131 | 00:00 | 122 | 12:00
| Amnura | 141 | 03:00 | 132 | 08:00 | Madaripur | 136 | 00:00 | 130 | 12:00
| Ashuganj | 141 | 02:00 | 135 | 08:00 | Madartek | 135 | 04:00 | 123 | 16:00
| Bagerhat | 137 | 04:00 | 127 | 13:00 | Madunaghat | 134 | 20:00 | 124 | 12:00
| Bajitpur | 134 | 00:00 | 128 | 12:00 | Magura | 141 | 03:00 | 129 | 12:00
| Bakulia | 133 | 19:00 | 122 | 13:00 | Mahasthangarh | 136 | 04:00 | 126 | 13:00
| Banani | 135 | 01:00 | 125 | 12:00 | Manikganj | 131 | 04:00 | 120 | 12:00
| Bangabhaban | 134 | 04:00 | 123 | 11:00 | Maniknagar | 134 | 06:00 | 123 | 11:00
| Barapukuria | 136 | 06:00 | 128 | 08:00 | Matarbari | 126 | 02:00 | 116 | 12:00
| Barguna | 137 | 07:00 | 130 | 13:00 | Matuail | 133 | 17:00 | 125 | 10:00
| Barishal | 135 | 00:00 | 129 | 13:00 | Millgate | 133 | 03:00 | 121 | 12:00
| Barishal-230 | 137 | 03:00 | 131 | 13:00 | Mirpur | 138 | 00:00 | 128 | 12:00
| Baroaulia | 133 | 03:00 | 126 | 11:00 | Mirzapur | 133 | 17:00 | 120 | 07:00
| Baroirhat | 131 | 01:00 | 120 | 12:00 | Mithapukur | 135 | 04:00 | 124 | 08:00
| Bashundhara | 135 | 03:00 | 122 | 12:00 | MI_Cement | 134 | 03:00 | 123 | 12:00
| BashundharaCement | 131 | 00:00 | 122 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 135 | 04:00 | 130 | 12:00 | Mogbazar | 136 | 04:00 | 125 | 12:00
| Benapole | 136 | 04:00 | 124 | 13:00 | Mongla | 136 | 04:00 | 127 | 13:00
| Bhaluka | 129 | 04:00 | 119 | 09:00 | Motijheel | 134 | 04:00 | 123 | 11:00
| Bhandaria | 135 | 06:00 | 128 | 13:00 | Munshiganj | 132 | 01:00 | 123 | 11:00
| Bhangura | 137 | 00:00 | 132 | 12:00 | Mymensingh | 134 | 17:00 | 111 | 07:00
| Bheramara | 138 | 02:00 | 132 | 12:00 | Naogaon | 136 | 05:00 | 128 | 08:00
| Bheramara(GK) | 139 | 01:00 | 132 | 13:00 | Narail | 139 | 04:00 | 129 | 12:00
| Bhulta | 127 | 08:00 | 113 | 12:00 | Narinda | 134 | 06:00 | 123 | 11:00
| Bog-Sherpur | 137 | 04:00 | 129 | 12:00 | Narshingdi | 130 | 19:30 | 115 | 09:00
| Bogura | 137 | 04:00 | 130 | 13:00 | Natore | 138 | 02:00 | 131 | 12:00
| Bogura-230 | 137 | 03:00 | 130 | 13:00 | Nawabganj | 135 | 02:00 | 125 | 12:00
| Brahmanbaria | 134 | 00:00 | 123 | 10:00 | Netrakona | 127 | 06:00 | 112 | 12:00
| Cantonment | 139 | 04:00 | 126 | 13:00 | New | 133 | 03:00 | 121 | 12:00
| Chandpur | 126 | 00:00 | 116 | 13:00 | Niamatpur | 139 | 03:00 | 134 | 12:00
| Chandraghona | 134 | 03:00 | 125 | 12:00 | Noapara | 139 | 03:00 | 127 | 12:00
| Chapai | 138 | 03:00 | 132 | 13:00 | Pabna | 140 | 04:00 | 132 | 12:00
| Charsaidpur | 134 | 04:00 | 123 | 12:00 | Palashbari | 134 | 05:00 | 123 | 09:00
| Chauddagram | 131 | 03:00 | 120 | 12:00 | Panchagarh | 137 | 04:00 | 121 | 08:00
| Chhatak | 134 | 04:00 | 130 | 13:00 | Patuakhali | 136 | 19:00 | 131 | 12:00
| Chowmuhani | 126 | 02:00 | 114 | 13:00 | Payra | 138 | 02:00 | 134 | 12:00
| Chuadanga | 140 | 04:00 | 123 | 13:00 | PHP | 130 | 03:00 | 117 | 13:00
| Coxsbazar | 123 | 00:00 | 116 | 12:00 | Postogola | 136 | 02:00 | 126 | 12:00
| Cumilla(N) | 134 | 01:00 | 125 | 13:00 | Purbachal | 135 | 03:00 | 125 | 12:00
| Cumilla(S) | 133 | 05:00 | 123 | 12:00 | Purbasadipur | 131 | 03:00 | 119 | 08:00
| Daudkandi | 131 | 04:00 | 121 | 12:00 | Rahanpur | 140 | 06:00 | 135 | 08:00
| Dhaka | 135 | 05:00 | 125 | 12:00 | Rahanpur-400 | 140 | 01:00 | 136 | 08:00
| Dhamrai | 136 | 04:00 | 125 | 12:00 | Rahim | 131 | 04:00 | 122 | 12:00
| Dhanmondi | 135 | 04:00 | 126 | 12:00 | Rajbari | 136 | 04:00 | 128 | 13:00
| Dohazari | 131 | 02:00 | 123 | 11:00 | Rajendrapur | 134 | 18:00 | 121 | 13:00
| Faridpur | 138 | 04:00 | 130 | 12:00 | Rajshahi | 138 | 01:00 | 131 | 12:00
| Fatullah | 135 | 04:00 | 126 | 12:00 | Rajshahi-230 | 139 | 01:00 | 129 | 08:00
| Fenchuganj | 138 | 23:00 | 134 | 12:00 | Ramganj | 125 | 01:00 | 117 | 14:00
| Feni | 128 | 03:00 | 121 | 12:00 | Rampur | 134 | 04:00 | 123 | 13:00
| Ghatail | 131 | 17:00 | 115 | 08:00 | Rampura | 135 | 04:00 | 125 | 12:00
| Ghorashal | 139 | 04:00 | 135 | 09:00 | Rangamati | 134 | 05:00 | 123 | 12:00
| Goalpara | 139 | 04:00 | 129 | 12:00 | Rangpur | 132 | 05:00 | 122 | 09:00
| Gollamari | 139 | 03:00 | 129 | 13:00 | Ruppur | 140 | 03:00 | 134 | 09:00
| Gopalganj | 138 | 04:00 | 129 | 13:00 | Saidpur | 132 | 03:00 | 122 | 08:00
| Gopalganj-400 | 137 | 03:00 | 130 | 13:00 | Satkhira | 138 | 06:00 | 126 | 13:00
| Gulshan | 134 | 06:00 | 124 | 12:00 | Satmasjid | 139 | 04:00 | 127 | 13:00
| Halishahar | 132 | 02:00 | 119 | 12:00 | Savar | 138 | 03:00 | 129 | 09:00
| Haripur | 133 | 01:00 | 122 | 13:00 | SevenRings | 140 | 03:00 | 131 | 12:00
| HaripurSBU | 131 | 04:00 | 122 | 13:00 | ShahCement | 134 | 04:00 | 123 | 12:00
| Hasnabad | 136 | 03:00 | 126 | 12:00 | Shahjadpur | 140 | 20:00 | 135 | 12:00
| Hathazari | 135 | 00:00 | 127 | 12:00 | Shahjibazar | 134 | 00:00 | 126 | 08:00
| Ishurdi | 141 | 03:00 | 134 | 12:00 | Shahmirpur | 133 | 18:30 | 122 | 20:00
| Jaldhaka | 131 | 03:00 | 119 | 08:00 | Shariatpur | 137 | 04:00 | 129 | 13:00
| Jamalpur | 134 | 17:00 | 113 | 07:00 | Sherpur | 133 | 17:00 | 109 | 07:00
| Jashore | 138 | 02:00 | 124 | 13:00 | Shikalbaha | 124 | 04:00 | 113 | 12:00
| Jhenaidah | 140 | 04:00 | 130 | 12:00 | Shikalbaha-230 | 135 | 03:00 | 123 | 12:00
| Jhenaidah-230 | 141 | 03:00 | 130 | 13:00 | Shitalakhya | 134 | 03:00 | 123 | 12:00
| Joydebpur | 136 | 18:00 | 128 | 11:00 | Sholosohor | 133 | 01:00 | 123 | 12:00
| Joypurhat | 136 | 02:00 | 127 | 08:00 | Shyampur | 132 | 00:00 | 126 | 12:00
| Juldah | 132 | 18:00 | 123 | 12:00 | Shyampur-230 | 136 | 04:00 | 125 | 09:00
| Kabirpur | 132 | 06:00 | 121 | 12:00 | Siddhirganj | 134 | 18:30 | 128 | 09:00
| Kachua | 129 | 03:00 | 118 | 13:00 | Sirajganj | 139 | 04:00 | 131 | 08:00
| Kaliakoir | 137 | 03:00 | 125 | 08:00 | Sonargaon | 130 | 00:00 | 122 | 15:00
| Kallyanpur | 132 | 00:00 | 125 | 12:00 | Sreemongol | 135 | 03:00 | 128 | 10:00
| Kalurghat | 134 | 18:00 | 123 | 12:00 | Sreepur | 129 | 02:00 | 122 | 09:00
| Kamrangirchar | 133 | 00:00 | 123 | 13:00 | Srinagar | 133 | 23:00 | 124 | 00:00
| Kaptai | N/A | N/A | N/A | N/A | SSM | 138 | 00:00 | 130 | 09:00
| Kazla | 134 | 04:00 | 123 | 13:00 | Sunamganj | 134 | 06:00 | 130 | 13:00
| Keranigonj | 136 | 04:00 | 125 | 12:00 | Sylhet | 135 | 02:00 | 131 | 12:00
| Khagrachori | 134 | 03:00 | 122 | 13:00 | Sylhet-132 | 134 | 00:00 | 131 | 12:00
| Khulna | 139 | 04:00 | 127 | 13:00 | Tangail | 129 | 17:00 | 117 | 07:00
| Khulna(S) | 142 | 04:00 | 129 | 13:00 | Thakurgaon | 133 | 04:00 | 118 | 08:00
| Khulshi | 131 | 04:00 | 122 | 12:00 | TK | 133 | 03:00 | 125 | 12:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 133 | 00:00 | 126 | 08:00 | Tongi | 135 | 04:00 | 125 | 12:00 |  |  | Nos | Nos | Nos
| Kodda | 135 | 20:00 | 122 | 07:00 | Ullahpara | 139 | 03:00 | 131 | 12:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 134 | 00:00 | 123 | 13:00 | Ullon | 136 | 04:00 | 124 | 13:00
| Kulaura | 137 | 04:00 | 133 | 12:00 | Uttara | 140 | 02:00 | 127 | 13:00
| Zigatola | 135 | 04:00 | 126 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.