## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-01-2025 | during | 09-01-2025 | during | 09-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 234.58 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 263 | 306 | 400.37 | 400.37 | 300 | 300 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 95 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 64 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 20 | 20 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 22 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 30 | 30 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 34 | 25 | 52.19 | 52.19 | 34 | 34 | machine problem
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 32 | 32 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 90 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 17 | 17 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 17 | 36 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 7401.63 | 5842.27 | 1364 | 1580 | 4603.99 | 4585.99 | 2749.33 | 2731.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 17 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 26 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 56 | 70 | 56 | 70 | temp problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 33 | 0 | 2 | 18 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 55 | 55 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 3.75 | 0 | 3.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 17 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 35 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1320 | 1224 | 500 | 612 | 1224 | 1224 | 612 | 612 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 66 | 60 | 4 | 11 | 66 | 66 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1200 | 1200 | 575 | 575 | 1150 | 1150 | 575 | 575 | Partial Shutdown due to maintenance
Chattogram Area Total |  |  |  |  | 5102.36 | 4873.22 | 1214 | 1342 | 3987.47 | 3978.72 | 2566.47 | 2557.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 182 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 40 | 46.94 | 46.94 | 46.94 | 46.94 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 185 | 185 | 195 | 195 | 185 | 185 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 10 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 60 | 57 | 160 | 160 | 54 | 54 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 16 | 9 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 44 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 12 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 654 | 675 | 1728.97 | 1678.97 | 1480.14 | 1430.14
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 8 | 210 | 210 | 25 | 25 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 18 | 19 | 200 | 200 | 18 | 18 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 69 | 115 | 115 | 55 | 55 | Machine Problem
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 20.08 | 0 | 22.1 | 0 | 22.1 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654.5 | 654.21 | 134.08 | 96 | 625.4 | 601.5 | 198.4 | 174.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 15 | 40 | 44 | 44 | 20 | 20 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 0 | 2.5 | 2.5 | 2 | 2 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 25 | 25 | 0 | 0 | 25 | 25 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 86 | 86 | 86 | 50 | 50 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 214 | 216 | 210 | 210 | 210 | 210 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 25 | 25 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 270 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 317 | 347 | 380 | 380 | 380 | 380 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 372 | 386 | 383 | 383 | 290 | 290 | -
Sylhet Area Total |  |  |  |  | 2411 | 2370.57 | 1433 | 1576 | 1684.5 | 1684.5 | 1524 | 1524
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 914 | 915 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 307 | 285 | 410 | 410 | 310 | 310 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 42.82 | 0 | 63.5 | 0 | 63.5 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 371 | 614 | 1234 | 1234 | 617 | 617 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3743 | 3686.2 | 1634.82 | 1814 | 3232.5 | 3169 | 2075.5 | 2012
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 135 | 135 | 145 | 145 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1090 | 1192 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1778 | 1883 | 2176.12 | 2176.12 | 2186.12 | 2186.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 20 | 20 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 186 | 186 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 209 | 201 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 210 | 204 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 8.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 52 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 1.55 | 0 | 4.25 | 0 | 4.25 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 756 | 757.65 | 1347.54 | 1347.54 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 25.13 | 0 | 20 | 0 | 20 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 100 | 100 | 68 | 0 | 88 | 0 | 88 | 0 | -
Rajshahi Area Total |  |  |  |  | 3575.55 | 3393.2 | 1461.18 | 1409.15 | 2634.99 | 2522.74 | 1961.25 | 1849
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 71 | 73 | 72 | 72 | 75 | 75 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 210 | 210 | 200 | 200 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.6 | 0 | 4 | 0 | 4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 3 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 24 | 0 | 65.41 | 0 | 65.41 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 309.6 | 333 | 629.41 | 530 | 602.41 | 503
System Total |  |  |  |  | 29109.24 | 26932.25 | 9982.68 | 10708.15 | 21303.35 | 20927.54 | 15343.62 | 14967.81
Forecast Scenario (09-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8630 |  | 0 |  | 8630
|  |  |  | 1:00 | 8150 |  | 0 |  | 8150
|  |  |  | 2:00 | 7590 |  | 0 |  | 7590
|  |  |  | 3:00 | 7560 |  | 0 |  | 7560
|  |  |  | 4:00 | 7320 |  | 0 |  | 7320
|  |  |  | 5:00 | 7150 |  | 0 |  | 7150
|  |  |  | 6:00 | 7770 |  | 0 |  | 7770
|  |  |  | 7:00 | 8370 |  | 0 |  | 8370
|  |  |  | 8:00 | 8940 |  | 0 |  | 8940
|  |  |  | 9:00 | 9550 |  | 0 |  | 9550
|  |  |  | 10:00 | 9170 |  | 0 |  | 9170
|  |  |  | 11:00 | 9520 |  | 0 |  | 9520
|  |  |  | 12:00 | 9990 |  | 0 |  | 9990
|  |  |  | 13:00 | 10360 |  | 0 |  | 10360
|  |  |  | 14:00 | 9820 |  | 0 |  | 9820
|  |  |  | 15:00 | 9400 |  | 0 |  | 9400
|  |  |  | 16:00 | 9210 |  | 0 |  | 9210
|  |  |  | 17:00 | 9440 |  | 0 |  | 9440
|  |  |  | 18:00 | 10510 |  | 0 |  | 10510
|  |  |  | 18:30 | 10600 |  | 0 |  | 10600
|  |  |  | 19:00 | 10730 |  | 0 |  | 10730
|  |  |  | 19:30 | 10580 |  | 0 |  | 10580
|  |  |  | 20:00 | 10490 |  | 0 |  | 10490
|  |  |  | 21:00 | 10260 |  | 0 |  | 10260
|  |  |  | 22:00 | 9760 |  | 0 |  | 9760
|  |  |  | 23:00 | 9160 |  | 0 |  | 9160
Probable Maximum Temperature: |  |  | 23.60°C
Probable Maximum Demand at Day Peak: |  |  | 9990.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 10730.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10730.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 218.85 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (08-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 21.00°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 823.24
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 17.4771 | Peak Hour Flow: |  | 915.00 MW at 19:00 hrs.
Energy Flow from West to East |  | 11453145.547 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 14.6983 | Peak Hour Flow: |  | 757.65 MW at 19:00 hrs.
Power Flow during Peak Demand |  | 679 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.2355 | Peak Hour Flow: |  | 57.00 MW at 19:00 hrs.
Maximum Power Flow |  | 1000 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 33.4109 | Peak Hour Flow: |  | 1729.65 MW at 19:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 08-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 9982.68 | MW | 12:00 Hr. | Energy Generated |  |  | 218686.724 |  | MWHr
Day Peak Demand |  |  | 9982.68 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MWHr
Evening Peak Generation |  |  | 10708.15 | MW | 19:00 Hr. | Energy Demand |  |  | 218686.724 |  | MWHr
Evening Peak Demand |  |  | 10708.15 | MW | 19:00 Hr.
Minimum Generation of the Day |  |  | 7238.5 | MW | 05:00 Hr.
Maximum Generation of the Day |  |  | 10708.15 | MW | 19:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 27529.731 | 0 | 4159.805 | 0 | 0 | 9.203 | 0 | 0 | 31698.739 | Gas | 105423.7937 | Gas | 375489883.8924
Chattogram Zone |  |  | 444.403 | 23132.7263 | 703.834 | 0 | 715.08 | 128.803 | 0 | 115.68 | 25240.5263 | Coal | 70085.2204 | Coal | 507386201.235
Cumilla Zone |  |  | 13110.03 | 0 | 594.843 | 0 | 0 | 103.082 | 1235.52 | 0 | 15043.475 | HFO | 7384.807 | HFO | 137018030.77
Mymensingh Zone |  |  | 213.12 | 0 | 1612.92 | 0 | 0 | 139.84 | 0 | 0 | 1965.88 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 35636.8487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35636.8487 | Hydro | 715.08 | Hydro | 71508
Khulna Zone |  |  | 7282.944 | 10523.64 | 0 | 0 | 0 | 275.04 | 17477.09 | 0 | 35558.714 | Solar | 1551.2378 | Solar | 18833358.254
Barishal Zone |  |  | 8186.551 | 29973.8182 | 116.4 | 0 | 0 | 0.305 | 0 | 0 | 38277.0742 | Import | 33410.905 | Import | 175567034.85
Rajshahi Zone |  |  | 13020.166 | 0 | 90.224 | 0 | 0 | 604.99 | 14698.295 | 0 | 28413.675 | Wind | 115.68 | Wind | 1665792
Rangpur Zone |  |  | 0 | 6455.036 | 106.781 | 0 | 0 | 289.9748 | 0 | 0 | 6851.7918
Total |  |  | 105423.7937 | 70085.2204 | 7384.807 | 0 | 715.08 | 1551.2378 | 33410.905 | 115.68 | 218686.724
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 375489883.8924 |  | Hydro | 71508
|  |  | Coal | 507386201.235 |  | Solar | 18833358.254
|  |  | HFO | 137018030.77 |  | Import | 175567034.85
|  |  | HSD | 0 |  | Wind | 1665792
|  |  |  | Total: | 1216031809.0014 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Barapukuria TPP Unit-2 |  |  | 85
| 3 | Khulna 330 MW CCPP GT |  |  | 220
| 4 | Khulna 330 MW CCPP ST |  |  | 110
| 5 | Siddhirgonj 210 MW TPP |  |  | 115
| 6 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 7 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1044 |  |  |  | Total | 35.09
|  |  | Total Unavailable Capacity |  |  |  | 1079.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3918
|  |  | Chattogram |  | 0 |  | 1004
|  |  | Cumilla |  | 0 |  | 879
|  |  | Mymensingh |  | 0 |  | 865
|  |  | Sylhet |  | 0 |  | 365
|  |  | Khulna |  | 0 |  | 1195
|  |  | Barishal |  | 0 |  | 297
|  |  | Rajshahi |  | 0 |  | 989
|  |  | Rangpur |  | 0 |  | 669
|  |  | Total |  | 0 |  | 10181
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:22 | 18:07 | Kabirpur-Kaliakoir 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Annual
maintenance
08:24 | 16:07 | Bogura 230/132kV S/S Bogura (W) CKT-2 Scheduled S/D Due to Bogura 400/230 kv (W) S/S
প্রান্ত থেকে S/D নেওয়া হয়।
08:24 | 16:05 | Bogura 400/230kV S/S Bogura 230 kV Ckt-2 Scheduled S/D Due to Dead line Check and Annual
maintenance
08:24 | 16:05 | Bogura 400/230kV S/S Bogura 230 kV Ckt-2 Scheduled S/D Due to Dead line Check and Annual
maintenance
08:30 | 11:05 | Noapara 132/33kV S/S BUS A Scheduled S/D Due to Due to annual maintenance
08:35 | 16:20 | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to annual
maintenance and from Chauddagram 132/33kV end Due to Yearly Maintenance.
08:47 | 15:05 | Mithapukur-Palashbari 132kV Ckt-2 Scheduled S/D from Palashbari 132/33kV end Due to
বার্ষিক সংরক্ষণ কাজ and from Mithapukur 132/33kV end Due to Annual Maintenance
08:58 | 16:36 | Madunaghat 400/230kV S/S Madunaghat-Banskhali 400kV Ckt.-1 Scheduled S/D Due to Annual
Maintenance
09:00 | 16:46 | Cumilla(N)-Kachua 132 kV Ckt-2 Scheduled S/D from Kachua 132/33kV end Due to Annual
Maintanance.
09:01 | 16:45 | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance.
09:04 | 16:31 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Scheduled S/D Due to Annual maintenance
09:04 | 16:32 | Jashore 132/33kV S/S JH-2(L1) Scheduled S/D Due to Annual Maintenance
09:08 | 17:26 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to
Annual maintenance.
09:08 | 13:51 | Kodda 132/33kV S/S Bus-1 Scheduled S/D Due to Annual maintenance
09:08 | 15:53 | Bogura-Mahasthangar (New)) 132 kV Ckt-1 Scheduled S/D from Mahasthangarh 132/33kV end Due
to Annul Maintenance work . and from Bogura 132/33kV end Due to Annual maintanance
09:09 |  | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Annual Maintenance
09:10 | 17:35 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Scheduled S/D Due to Annual
Maintenance and Dead Line checking
09:10 | 17:18 | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to AM
09:11 | 17:34 | Haripur 230/132kV S/S Madanganj-2 Scheduled S/D Due to From other End.
09:14 | 15:49 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2A(E04) Scheduled S/D Due to Line Maintenance
09:14 | 13:52 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to Annual Maintenance
09:14 | 13:52 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to Annual Maintenance
09:16 | 15:49 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2B(E03) Scheduled S/D Due to Line Maintenance.
09:28 | 15:46 | Hathazari 230/132/33kV S/S Shikolbaha-02 Scheduled S/D Due to annual maintenance
09:29 | 16:28 | Fenchuganj 230/132/33kV S/S 230 KV Bus-2 Scheduled S/D Due to Annual Maintence
09:30 | 15:44 | Madunaghat 400/230kV S/S Madunaghat-Hathazari 230kV Ckt.-2 Scheduled S/D Due to Annual
Maintenance
09:37 | 18:21 | BIPTC S/S Baharampur-2 Scheduled S/D Due to Annual Maintenance
09:43 | 20:30 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Scheduled S/D Due to RTS different testing
purpose
09:43 | 20:30 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D Due to RTS different testing
purpose
09:43 | 17:25 | Ishurdi 132/33kV S/S 230/132 kV T01 Incoming Scheduled S/D
09:43 | 17:23 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Scheduled S/D
09:47 |  | Kodda-Rajendrapur 132kV Ckt-2 Scheduled S/D from Rajendrapur 132/33kV end Due to Yearly
deadline checking of kodda-2 ckt. and from Kodda 132/33kV end Due to Dead line checking
10:01 | 13:40 | Savar 132/33kV S/S Main Bus Scheduled S/D Due to Annual maintenance work.
10:03 | 10:32 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Annual maintenance work.
10:03 | 10:32 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenance work.
10:06 | 19:29 | Cumilla(S) 132/33kV S/S Tripura Ckt-2 Scheduled S/D Due to S/D taken by NLDC INDIA
10:11 |  | Anwara 300 MW PP (United) Running with remarks:- NLDC load demand 15 MW at 10:08 hrs. by
Mr. Shawkat & Plant synchronized at 10:11 hrs.
10:11 | 15:56 | Haripur-Siddirganj 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Work on
other end. and from Siddhirganj 132/33kV end Due to Annual maintenance work
10:11 | 15:56 | Haripur-Siddirganj 132kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Work on
other end.
10:11 |  | Anwara 300 MW PP (United) Synchronized
10:12 | 15:51 | Haripur-Siddirganj 230kV Ckt-2 Scheduled S/D from Siddhirganj 132/33kV end Due to Annual
maintenance work
10:17 | 11:50 | Bashundhara-Tongi 132 kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by Basundhara end side.
10:25 |  | Ashuganj 150MW PP (Midland) Synchronized
10:26 | 13:39 | Daudkandi 132/33kV S/S Transformer-3 LT Scheduled S/D Due to annual maintenance of spmd
work
10:27 | 13:38 | Daudkandi 132/33kV S/S Transformer-3 HT Scheduled S/D Due to annual maintenance of spmd
work
10:28 | 16:41 | Baghabari-Sirajganj 230 kV Ckt-2 Scheduled S/D from Baghabari 230/132kV end Due to Annual
Maintenance and from Sirajgonj 230 end Due to Annual Maintenance Work
10:34 | 12:29 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenance work.
10:34 | 12:29 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenance work
10:35 | 18:12 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end.
10:41 |  | Anlima Energy Ltd. Synchronized
10:43 | 12:09 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to Annual maintenance
work
11:48 | 17:44 | BIPTC S/S 20D10A 20MVA HT Scheduled S/D Due to Annual Maintenance
11:52 |  | Chandraghona-Rangamati 132 kV Ckt-1 Scheduled S/D from Rangamati 132/33kV end Due to
Relay testing and from Chandraghona 132/33kV end Due to SPMD RELAY TEST
12:00 |  | Day Peak generation = 9,982MW
12:10 |  | Kodda 300 MW PP Unit-2 (Summit) Synchronized
12:13 | 12:58 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Annual maintenance
work.
12:30 | 13:18 | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintenance work.
12:30 | 13:18 | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintenance work.
12:56 | 14:15 | Chandraghona-Rangamati 132 kV Ckt-2 Scheduled S/D from Chandraghona 132/33kV end Due to
Spmd relay test
12:58 |  | Anwara 300 MW PP (United) Shutdown
12:58 |  | Anwara 300 MW PP (United) Shutdown with remarks:- NLDC load demand 00 MW at 12:51 hours
by Mr. Shawkat and plant unloaded at 12:58 hours.
13:02 |  | Anlima Energy Ltd. Shutdown
13:05 |  | Ashuganj 150MW PP (Midland) Shutdown
| 14:16 | Chandraghona-Rangamati 132 kV Ckt-2 is restored.
14:25 | 15:27 | Khagrachari-Rangamati 132kV Ckt-1 Project Work S/D from Khagrachori 132/33kV end Due to
Relay test in Rangamati sub station
| 14:34 | Barishal 132/33kV S/S 132 kv GTPS is restored.
15:31 | 16:16 | Khagrachari-Rangamati 132kV Ckt-2 Project Work S/D from Khagrachori 132/33kV end Due to
Relay test in Rangamati sub station
| 15:57 | Gopalganj(N)-Rampal Ckt-1 is restored.
| 15:58 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 is restored.
16:00 |  | Meghnaghat CCPP(Summit) GT-1 Synchronized with remarks:- NLDC asked for GT-1 start.
16:00 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT1
16:20 |  | Ashuganj 150MW PP (Midland) Synchronized
16:37 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ghorashal 230kV end showing Distance
Protection Relay relays Due to 230kV Ghorashal-ishwardi line-2 , C Phase conductor is
Torn from Midspan joint of span 3-4 and from Ishurdi 230/132kV end showing Siemens relays
Due to Ghorashal end conductor cut off.
16:40 |  | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- NLDC asked for GT-2 startup.
16:40 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2
| 16:43 | Dhamrai 132/33kV S/S Transformer-1 HT is restored.
| 16:43 | Dhamrai 132/33kV S/S Transformer-1 LT is restored.
| 16:48 | Kulaura 132/33kV S/S 132 kV Bus-B is restored.
17:01 |  | Anwara 300 MW PP (United) Running with remarks:- NLDC load demand 80 MW by Mr. Swakshar
& Plant synchronized at 17:01 hrs
17:01 |  | Anwara 300 MW PP (United) Synchronized
17:06 |  | Anlima Energy Ltd. Synchronized
17:47 |  | Kodda 300 MW PP Unit-2 (Summit) Shutdown
| 18:32 | Kabirpur -Kodda 132kV Ckt-1 is restored.
18:33 |  | Meghnaghat CCPP(Summit) ST Synchronized with remarks:- ST synch at 18:33 hrs
18:33 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- ST
19:05 |  | Anwara 300 MW PP (United) Shutdown with remarks:- NLDC load demand 00 MW at 19:05 hours
by Mr. Swakshar and plant unloaded at 19:23 hours
19:15 |  | Anlima Energy Ltd. Shutdown
19:20 |  | Ashuganj 150MW PP (Midland) Shutdown
19:23 |  | Anwara 300 MW PP (United) Shutdown
20:24 | 20:44 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing DIR O/C & E/F Relay relays Due to Over | [7 empty] | 38.0MW load
|  | current trip. DIR E/F trip. | [7 empty] | interrup.
22:40 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Forced S/D from Ghorashal 230kV end Due to Conductor
emergency maintenance due to conductor rupture.
00:01 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:- CCPP put into FGMO at 23:20 hrs (8th
Jan 2025)
| 00:49 | Rampal 400/230kV S/S Bus Reactor is restored.
01:44 |  | Ashuganj 51 MW PP (Midland) Partially Running with remarks:- NLDC demand 05 MW at 01:29.
05:00 |  | Minimum Generation is 7157 MW
06:15 |  | Kabirpur -Kodda 132kV Ckt-1 Project Work S/D from Kabirpur 132/33kV end Due to Conductor
changing work purpose
06:20 |  | Ashuganj 51 MW PP (Midland) Running with remarks:- NLDC demand 51 MW
07:40 |  | Agargaon 230/132kV S/S Auxiliary Tr-1 LT Scheduled S/D Due to Annual maintenance.
07:43 |  | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) LT Scheduled S/D Due to Annual
maintenance.
07:44 |  | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT Scheduled S/D Due to Annual
maintenance.
07:44 |  | Agargaon 230/132kV S/S Auxiliary Tr-1 HT Scheduled S/D Due to Annual maintenance.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 306 | 6501600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10100300 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 95 | 1007651 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7820840 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 26280 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 757440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 351373 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 34633 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 381000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 500400 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 525240 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 30 | 692700 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 25 | 496800 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 90327 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 32 | 469872 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1275840 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 56160 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 9203 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 36 | 357480 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 72 | 243600 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 1580 | 31698739
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 110565 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 202560 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 26 | 715080 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 77203 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 0 | 18 | 367200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 18238 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 160582 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 217517 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 11520 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 111655 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 10739999 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 11 | 115680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12392727.27 | Partial Shutdown due to maintenance
Chattogram Area Total |  |  |  |  | 4873.22 | 1342 | 25240526.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4614000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 40 | 900216 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 692160 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 4114909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1210375 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 10 | 247563 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1231220 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 57 | 1235520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 347150 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 169680 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 44 | 177600 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 103082 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 675 | 15043475
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 8 | 213120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 336000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 988800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 132440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 207120 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 81000 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 96 | 1965880
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 0 | 95000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 602040 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3801272.72 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 40 | 486360 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 48336 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 25 | 568896 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1319040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 216 | 4367040 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 328464 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 6875500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 347 | 8942000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 386 | 8202900 | FGMO
Sylhet Area Total |  |  |  |  | 2370.57 | 1576 | 35636848.72
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 915 | 17477090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 285 | 7282944 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 275040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 614 | 10523640 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1814 | 35558714
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 139421 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2833000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1192 | 24453818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5214130 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 116400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5520000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 305 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1883 | 38277074.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 186 | 4087727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 201 | 4363282 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 204 | 4453309 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 8.5 | 115848 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 52 | 90224 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Liquid fuel shortage
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 16620 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 757.65 | 14698295 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 208500 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 379870 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1409.15 | 28413675
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 73 | 1666036 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4789000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 10236.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 106781 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 25578 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 254160 | -
Rangpur Area Total |  |  |  |  | 950 | 333 | 6851791.84
Eastern Grid Total |  |  |  |  | 16637.75 | 5269 | 109585468.99
Western Grid Total |  |  |  |  | 10294.5 | 5439.15 | 109101255.02
National Grid Total |  |  |  |  | 26932.25 | 10708.15 | 218686724.01
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7030.9 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3149.4 | MW
i) Dhaka area |  |  | 3917.9 |  | MW | i) Khulna area |  |  |  | 1194.8 | MW
ii) Chattogram area |  |  | 1004 |  | MW | ii) Barishal area |  |  |  | 296.8 | MW
iii) Cumilla area |  |  | 879 |  | MW | iii) Rajshahi area |  |  |  | 988.8 | MW
iv) Mymensingh area |  |  | 865 |  | MW | iv) Rangpur area |  |  |  | 669 | MW
v) Sylhet area |  |  | 365 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10180.3 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 51 | 18:00 | 133 | Purbasadipur | 102 | 18:00
2 | AKSML | 108 | 03:00 | 68 | Jamalpur | 91 | 18:30 | 134 | Rahanpur | 0 | 00:00
3 | Aftabnagar | 26 | 12:00 | 69 | Jashore | 101 | 13:00 | 135 | Rahim | 39 | 08:00
4 | Agargaon | 72 | 13:00 | 70 | Jhenaidah | 94 | 18:00 | 136 | Rajbari | 56 | 18:00
5 | Agrabad | 62 | 18:00 | 71 | Joydebpur | 116 | 11:00 | 137 | Rajendrapur | 94 | 19:00
6 | Amnura | 42 | 08:00 | 72 | Joypurhat | 42 | 19:00 | 138 | Rajshahi | 94 | 08:00
7 | Ashuganj | 55 | 12:00 | 73 | Juldah | 10 | 11:00 | 139 | Rajshahi-230 | 44 | 21:00
8 | BSRM | 187 | 05:00 | 74 | KSRM | 27 | 23:00 | 140 | Ramganj | 80 | 18:00
9 | Bagerhat | 71 | 20:00 | 75 | Kabirpur | 233 | 12:00 | 141 | Rampur | 25 | 14:00
10 | Bajitpur | 0 | 03:00 | 76 | Kachua | 51 | 19:30 | 142 | Rangamati | 12 | 18:00
11 | Bakulia | 65 | 18:00 | 77 | Kallyanpur | 66 | 12:00 | 143 | Rangpur | 111 | 18:00
12 | Banani | 39.2 | 13:00 | 78 | Kalurghat | 30 | 15:00 | 144 | Ruppur | 4 | 11:00
13 | Bangabhaban | 8 | 11:00 | 79 | Kamrangirchar | 53.7 | 13:00 | 145 | SSM | 12 | 01:00
14 | Barapukuria | 43 | 18:00 | 80 | Kaptai | N/A | N/A | 146 | Saidpur | 88 | 09:00
15 | Barguna | 14 | 18:00 | 81 | Kazla | 87 | 13:00 | 147 | Satkhira | 88 | 08:00
16 | Barishal | 80 | 12:00 | 82 | Keranigonj | 60 | 13:00 | 148 | Satmasjid | 84 | 13:00
17 | Barishal-230 | 62 | 18:00 | 83 | Khagrachori | 24 | 18:00 | 149 | Savar | 178 | 15:00
18 | Baroaulia | 49 | 12:00 | 84 | Khulna | 72 | 13:00 | 150 | SevenRings | 17.82 | 23:00
19 | Baroirhat | 45 | 18:00 | 85 | Khulshi | 117 | 22:00 | 151 | ShahCement | 25 | 06:00
20 | Bashundhara | 120 | 12:00 | 86 | Kishoreganj | 112 | 19:30 | 152 | Shahjadpur | 54 | 19:30
21 | BashundharaCement | 12 | 01:00 | 87 | Kodda | 276 | 11:00 | 153 | Shahjibazar | 76 | 18:30
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 27 | 18:00 | 154 | Shahmirpur | 34 | 16:00
23 | Benapole | 46 | 08:00 | 89 | Kurigram | 46 | 18:00 | 155 | Shariatpur | 52 | 20:00
24 | Bhaluka | 114 | 18:30 | 90 | Kushtia | 100 | 18:30 | 156 | Sherpur | 106 | 18:30
25 | Bhandaria | 36 | 21:00 | 91 | Lalbag | 68 | 13:00 | 157 | Shikalbaha | 14 | 12:00
26 | Bhangura | 22 | 18:00 | 92 | Lalmonirhat | 41 | 18:00 | 158 | Shitalakhya | 66.6 | 12:00
27 | Bheramara(GK) | 40 | 18:00 | 93 | MI_Cement | 17.5 | 02:00 | 159 | Sholosohor | 33 | 12:00
28 | Bhulta | 259 | 12:00 | 94 | Madanganj | 29 | 11:00 | 160 | Shyampur | 152 | 12:00
29 | Bog-Sherpur | 54 | 18:00 | 95 | Madaripur | 68 | 20:00 | 161 | Siddhirganj | 113 | 12:00
30 | Bogura | 107 | 19:30 | 96 | Madartek | 54.5 | 13:00 | 162 | Sirajganj | 74 | 18:30
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 37 | 18:00 | 163 | Sonargaon | 84 | 11:00
32 | Brahmanbaria | 109 | 20:00 | 98 | Magura | 45 | 18:30 | 164 | Sreemongol | 51 | 18:00
33 | Cantonment | 76 | 13:00 | 99 | Mahasthangarh | 50 | 18:30 | 165 | Sreepur | 61 | 12:00
34 | Chandpur | 40 | 18:30 | 100 | Manikganj | 102 | 18:00 | 166 | Srinagar | 29.2 | 21:00
35 | Chandraghona | 24 | 18:30 | 101 | Maniknagar | 46 | 13:00 | 167 | Sunamganj | 36 | 20:00
36 | Chapai | 48 | 13:00 | 102 | Matarbari | 35 | 18:00 | 168 | Sylhet | 28 | 13:00
37 | Charsaidpur | 39 | 10:00 | 103 | Matuail | 44 | 09:00 | 169 | Sylhet-132 | 73 | 18:00
38 | Chauddagram | 40 | 18:00 | 104 | Millgate | 69 | 18:00 | 170 | TK | 21 | 18:30
39 | Chhatak | 20 | 18:00 | 105 | Mirpur | 93 | 12:00 | 171 | Tangail | 128 | 19:00
40 | Chowmuhani | 143 | 19:30 | 106 | Mirsorai | 8 | 18:00 | 172 | Thakurgaon | 75 | 18:30
41 | Chuadanga | 67 | 18:00 | 107 | Mirzapur | 30 | 08:00 | 173 | Tongi | 104 | 15:00
42 | Coxsbazar | 93 | 19:30 | 108 | Mithapukur | 42 | 18:00 | 174 | Ullahpara | 25 | 08:00
43 | Cumilla(N) | 108 | 18:30 | 109 | Modern | 0 | 00:00 | 175 | Ullon | 34 | 14:00
44 | Cumilla(S) | 122 | 14:00 | 110 | Mogbazar | 76.5 | 13:00 | 176 | Uttara | 53 | 13:00
45 | Daudkandi | 108 | 18:00 | 111 | Mongla | 24 | 11:00 | 177 | UttaraNew | 32 | 12:00
46 | Dhaka | 32 | 13:00 | 112 | Motijheel | 25 | 13:00 | 178 | Zigatola | 66 | 14:00
47 | Dhamrai | 78 | 18:30 | 113 | Munshiganj | 68 | 13:00
48 | Dhanmondi | 87 | 13:00 | 114 | Mymensingh | 174 | 18:30
49 | Dohazari | 66 | 18:00 | 115 | Naogaon | 82 | 20:00
50 | Faridpur | 110 | 18:30 | 116 | Narail | 42 | 18:00
51 | Fatullah | 78 | 12:00 | 117 | Narinda | 51 | 13:00
52 | Fenchuganj | 24 | 18:00 | 118 | Narshingdi | 150 | 18:30
53 | Feni | 66 | 18:30 | 119 | Natore | 102 | 18:00
54 | GPH | 26 | 22:00 | 120 | Nawabganj | 36 | 20:00
55 | Ghatail | 26 | 08:00 | 121 | Netrakona | 116 | 07:00
56 | Ghorashal | 8 | 18:00 | 122 | New | 63 | 10:00
57 | Ghorashal-230 | 51 | 09:00 | 123 | Niamatpur | 59 | 09:00
58 | Goalpara | 26 | 13:00 | 124 | Noapara | 35 | 18:00
59 | Gollamari | 50 | 13:00 | 125 | PHP | 8 | 16:00
60 | Gopalganj | 74.2 | 18:30 | 126 | Pabna | 82 | 18:30
61 | Gulshan | 58 | 13:00 | 127 | Palashbari | 71 | 18:00
62 | Halishahar | 57 | 10:00 | 128 | Panchagarh | 42 | 18:00
63 | HaripurSBU | 163 | 09:00 | 129 | Patuakhali | 54 | 21:00
64 | Hasnabad | 54 | 17:00 | 130 | Payra | 14 | 18:00
65 | Hathazari | 50 | 13:00 | 131 | Postogola | 35 | 13:00
66 | Ishurdi | 58 | 19:00 | 132 | Purbachal | 15 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8698.14 | 0 |  | 8698.14
1:00 | 8228.5 | 0 |  | 8228.5
2:00 | 7832.5 | 0 |  | 7832.5
3:00 | 7526.5 | 0 |  | 7526.5
4:00 | 7267.5 | 0 |  | 7267.5
5:00 | 7238.5 | 0 |  | 7238.5
6:00 | 7572.5 | 0 |  | 7572.5
7:00 | 8180 | 0 |  | 8180
8:00 | 9128.29 | 0 |  | 9128.29
9:00 | 9719.68 | 0 |  | 9719.68
10:00 | 9475.15 | 0 |  | 9475.15
11:00 | 9500.96 | 0 |  | 9500.96
12:00 | 9982.68 | 0 |  | 9982.68
13:00 | 10044.26 | 0 |  | 10044.26
14:00 | 9456.32 | 0 |  | 9456.32
15:00 | 9358.19 | 0 |  | 9358.19
16:00 | 9122.26 | 0 |  | 9122.26
17:00 | 9362.46 | 0 |  | 9362.46
18:00 | 10509.25 | 0 |  | 10509.25
19:00 | 10708.15 | 0 |  | 10708.15
19:30 | 10489.35 | 0 |  | 10489.35
20:00 | 10454.7 | 0 |  | 10454.7
21:00 | 10167.84 | 0 |  | 10167.84
22:00 | 9896.27 | 0 |  | 9896.27
23:00 | 9182.95 | 0 |  | 9182.95
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4341 | 4357.14 | 8698.14 | DAILY LOAD CURVE
00:30 | 4209 | 4254.32 | 8463.32
01:00 | 4077 | 4151.5 | 8228.5 | 08-01-2025
01:30 | 4021 | 4009.5 | 8030.5
02:00 | 3965 | 3867.5 | 7832.5
02:30 | 3909.5 | 3770 | 7679.5
03:00 | 3854 | 3672.5 | 7526.5
03:30 | 3842.5 | 3554.5 | 7397
04:00 | 3831 | 3436.5 | 7267.5
04:30 | 3817.5 | 3435.5 | 7253
05:00 | 3804 | 3434.5 | 7238.5
05:30 | 3862.5 | 3543 | 7405.5
06:00 | 3921 | 3651.5 | 7572.5
06:30 | 4035.75 | 3840.5 | 7876.25
07:00 | 4150.5 | 4029.5 | 8180
07:30 | 4339.64 | 4314.505 | 8654.145
08:00 | 4528.78 | 4599.51 | 9128.29
08:30 | 4589.34 | 4834.645 | 9423.985
09:00 | 4649.9 | 5069.78 | 9719.68
09:30 | 4611.985 | 4985.43 | 9597.415
10:00 | 4574.07 | 4901.08 | 9475.15
10:30 | 4550.935 | 4937.12 | 9488.055
11:00 | 4527.8 | 4973.16 | 9500.96
11:30 | 4663.44 | 5078.38 | 9741.82
12:00 | 4799.08 | 5183.6 | 9982.68
12:30 | 4821.545 | 5191.925 | 10013.47
13:00 | 4844.01 | 5200.25 | 10044.26
13:30 | 4762.935 | 4987.355 | 9750.29
14:00 | 4681.86 | 4774.46 | 9456.32
14:30 | 4680.72 | 4726.535 | 9407.255
15:00 | 4679.58 | 4678.61 | 9358.19
15:30 | 4675.365 | 4564.86 | 9240.225
16:00 | 4671.15 | 4451.11 | 9122.26
16:30 | 4736.75 | 4505.61 | 9242.36
17:00 | 4802.35 | 4560.11 | 9362.46
17:30 | 5098.855 | 4837 | 9935.855
18:00 | 5395.36 | 5113.89 | 10509.25
18:30 | 5332.18 | 5276.52 | 10608.7
19:00 | 5269 | 5439.15 | 10708.15
19:30 | 5133 | 5356.35 | 10489.35
20:00 | 5126 | 5328.7 | 10454.7
20:30 | 5039 | 5272.27 | 10311.27 |  | Executive Engineer
21:00 | 4952 | 5215.84 | 10167.84 |  | Network Operation Division
21:30 | 4949 | 5083.055 | 10032.055
22:00 | 4946 | 4950.27 | 9896.27
22:30 | 4820.5 | 4719.11 | 9539.61
23:00 | 4695 | 4487.95 | 9182.95

## En-Curve
QF-LDC-12
Date | 08-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2727 | 1693.5 | 913 | 0 | 50 | 415.64 | 26 | 2802 | 0 | 17 | 54 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2694 | 1614.5 | 913 | 0 | 47 | 415.82 | 26 | 2709 | 0 | 8.5 | 35.5 | 0 | 0 | 0 | 0 | 08-01-2025
01:00 | 2661 | 1535.5 | 913 | 0 | 44 | 416 | 26 | 2616 | 0 | 0 | 17 | 0 | 0 | 0 | 0
01:30 | 2669.5 | 1534 | 819.5 | 0 | 43 | 416 | 26 | 2513.5 | 0 | 0 | 8.5 | 0 | 0 | 0.5 | 0 |  | Total Energy | 218.6867 |  | MKWHr
02:00 | 2678 | 1532.5 | 726 | 0 | 42 | 416 | 26 | 2411 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | Energy not Served | 0 |  | MKWHr
02:30 | 2669 | 1527 | 726.5 | 0 | 42 | 416.5 | 26 | 2272 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 |  | Energy Requirement | 218.6867 |  | MKWHr
03:00 | 2660 | 1521.5 | 727 | 0 | 42 | 417 | 26 | 2133 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2642 | 1504.5 | 680 | 0 | 41 | 416.5 | 26 | 2086 | 0 | 0 | 0 | 0 | 0 | 1 | 0
04:00 | 2624 | 1487.5 | 633 | 0 | 40 | 416 | 26 | 2039 | 0 | 0 | 0 | 0 | 0 | 2 | 0
04:30 | 2619 | 1479.5 | 632.5 | 0 | 40 | 416.5 | 26 | 2038 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0
05:00 | 2614 | 1471.5 | 632 | 0 | 40 | 417 | 26 | 2037 | 0 | 0 | 0 | 0 | 0 | 1 | 0
05:30 | 2639.5 | 1479.5 | 632 | 0 | 42 | 445 | 26 | 2140.5 | 0 | 0 | 0 | 0 | 0 | 1 | 0
06:00 | 2665 | 1487.5 | 632 | 0 | 44 | 473 | 26 | 2244 | 0 | 0 | 0 | 0 | 0 | 1 | 0
06:30 | 2733 | 1481.25 | 679 | 0 | 43 | 497 | 26 | 2352.5 | 2 | 46 | 15.5 | 0 | 0 | 1 | 0
07:00 | 2801 | 1475 | 726 | 0 | 42 | 521 | 26 | 2461 | 4 | 92 | 31 | 0 | 0 | 1 | 0
07:30 | 2823 | 1505.75 | 820 | 0 | 42 | 565.5 | 26 | 2653.5 | 16.395 | 132 | 69 | 0 | 0 | 1 | 0
08:00 | 2845 | 1536.5 | 914 | 0 | 42 | 610 | 26 | 2846 | 28.79 | 172 | 107 | 0 | 0 | 1 | 0
08:30 | 2870.5 | 1555 | 914 | 0 | 47 | 655.5 | 36 | 3002.5 | 56.985 | 172 | 114 | 0 | 0 | 0.5 | 0
09:00 | 2896 | 1573.5 | 914 | 0 | 52 | 701 | 46 | 3159 | 85.18 | 172 | 121 | 0 | 0 | 0 | 0
09:30 | 2816.5 | 1542.5 | 914 | 0 | 52 | 701.5 | 46 | 3102.5 | 112.915 | 172 | 137.5 | 0 | 0 | 0 | 0
10:00 | 2737 | 1511.5 | 914 | 0 | 52 | 702 | 46 | 3046 | 140.65 | 172 | 154 | 0 | 0 | 0 | 0
10:30 | 2724 | 1467 | 914.5 | 0 | 54 | 726 | 46 | 3028.5 | 156.055 | 180 | 192 | 0 | 0 | 0 | 0
11:00 | 2711 | 1422.5 | 915 | 0 | 56 | 750 | 46 | 3011 | 171.46 | 188 | 230 | 0 | 0 | 0 | 0
11:30 | 2795 | 1451.5 | 914.5 | 0 | 58 | 753 | 46 | 3067.5 | 195.82 | 188 | 270.5 | 0 | 0 | 2 | 0
12:00 | 2879 | 1480.5 | 914 | 0 | 60 | 756 | 46 | 3124 | 220.18 | 188 | 311 | 0 | 0 | 4 | 0
12:30 | 2870.5 | 1487.5 | 914 | 0 | 61.5 | 758.5 | 46 | 3122.5 | 256.97 | 188 | 303.5 | 0 | 0 | 4.5 | 0
13:00 | 2862 | 1494.5 | 914 | 0 | 63 | 761 | 46 | 3121 | 293.76 | 188 | 296 | 0 | 0 | 5 | 0
13:30 | 2759.5 | 1457.5 | 914.5 | 0 | 63.5 | 737.5 | 36 | 3033 | 275.79 | 180 | 279.5 | 0 | 0 | 13.5 | 0
14:00 | 2657 | 1420.5 | 915 | 0 | 64 | 714 | 26 | 2945 | 257.82 | 172 | 263 | 0 | 0 | 22 | 0
14:30 | 2690.5 | 1425 | 914 | 0 | 61 | 712.71 | 26 | 2900 | 216.545 | 172 | 271 | 0 | 0 | 18.5 | 0
15:00 | 2724 | 1429.5 | 913 | 0 | 58 | 711.42 | 26 | 2855 | 175.27 | 172 | 279 | 0 | 0 | 15 | 0
15:30 | 2740.5 | 1438 | 913 | 0 | 57.5 | 659.375 | 26 | 2810.5 | 129.35 | 172 | 279 | 0 | 0 | 15 | 0
16:00 | 2757 | 1446.5 | 913 | 0 | 57 | 607.33 | 26 | 2766 | 83.43 | 172 | 279 | 0 | 0 | 15 | 0
16:30 | 2770.5 | 1496 | 913 | 0 | 57 | 645.53 | 26 | 2802 | 50.58 | 178.75 | 289.5 | 0 | 0 | 13.5 | 0
17:00 | 2784 | 1545.5 | 913 | 0 | 57 | 683.73 | 26 | 2838 | 17.73 | 185.5 | 300 | 0 | 0 | 12 | 0
17:30 | 2840 | 1586 | 913.5 | 0 | 56.5 | 717.56 | 26 | 3041 | 8.865 | 223.25 | 511.18 | 0 | 0 | 12 | 0
18:00 | 2896 | 1626.5 | 914 | 0 | 56 | 751.39 | 26 | 3244 | 0 | 261 | 722.36 | 0 | 0 | 12 | 0
18:30 | 2919 | 1686.5 | 914.5 | 0 | 56.5 | 754.52 | 26 | 3413.5 | 0 | 264 | 562.68 | 0 | 0 | 11.5 | 0
19:00 | 2942 | 1746.5 | 915 | 0 | 57 | 757.65 | 26 | 3583 | 0 | 267 | 403 | 0 | 0 | 11 | 0
19:30 | 2950 | 1768.5 | 914 | 0 | 56 | 758.85 | 26 | 3615 | 0 | 195 | 201 | 0 | 0 | 5 | 0
20:00 | 3009 | 1750.5 | 915 | 0 | 54 | 760.2 | 26 | 3590 | 0 | 169 | 175 | 0 | 0 | 6 | 0
20:30 | 2966 | 1764.5 | 914.5 | 0 | 54 | 725.27 | 26 | 3556.5 | 0 | 139.5 | 158 | 0 | 0 | 7 | 0
21:00 | 2923 | 1778.5 | 914 | 0 | 54 | 690.34 | 26 | 3523 | 0 | 110 | 141 | 0 | 0 | 8 | 0
21:30 | 2880.5 | 1868 | 913.5 | 0 | 54 | 651.055 | 26 | 3390.5 | 0 | 101.5 | 141 | 0 | 0 | 6 | 0
22:00 | 2838 | 1957.5 | 913 | 0 | 54 | 611.77 | 26 | 3258 | 0 | 93 | 141 | 0 | 0 | 4 | 0
22:30 | 2793 | 1904 | 913.5 | 0 | 56 | 589.61 | 26 | 3088 | 0 | 63 | 100.5 | 0 | 0 | 6 | 0
23:00 | 2748 | 1850.5 | 914 | 0 | 58 | 567.45 | 26 | 2918 | 0 | 33 | 60 | 0 | 0 | 8 | 0
Executive Engineer
Network Operation Division

## daily_load
SN | S/S Name | 0:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00
1 | AKS 132/33kV Grid Sub-Station | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | AKSML 230/33kV Grid Sub-Station | 40 | 65 | 69 | 108 | 32 | 49 | 27 | 92 | 4 | 39 | 2 | 49 | 30 | 97 | 104 | 98 | 32 | 22 | 25 | 20 | 1 | 2 | 6 | 9 | 18 | 106
3 | Aftabnagar 132/33kV Grid Sub-Station | 18 | 16 | 16 | 16 | 14 | 14 | 16 | 16 | 20 | 20 | 22 | 22 | 26 | 26 | 24 | 22 | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 20
4 | Agargaon 230/132kV Grid Sub-Station | 51 | 44 | 41 | 39 | 38 | 38 | 40 | 43 | 50 | 56 | 61 | 65 | 67 | 72 | 71 | 67 | 61 | 63 | 67 | 66 | 65 | 64 | 65 | 61 | 62 | 57
5 | Agrabad 132/33kV Grid Sub-Station | 44 | 40 | 38 | 38 | 36 | 36 | 36 | 38 | 42 | 42 | 48 | 56 | 58 | 58 | 54 | 56 | 56 | 60 | 62 | 62 | 60 | 60 | 58 | 58 | 52 | 48
6 | Amnura 132/33kV Grid Sub-Station | 29 | 29 | 27 | 27 | 27 | 27 | 29 | 32 | 42 | 42 | 39 | 39 | 42 | 42 | 35 | 32 | 30 | 31 | 39 | 41 | 41 | 40 | 40 | 38 | 36 | 33
7 | Ashuganj 230/132/33kV Sub-Station | 51 | 52 | 49 | 46 | 44 | 44 | 46 | 45 | 47 | 47 | 49 | 51 | 55 | 54 | 33 | 47 | 54 | 47 | 52 | 52 | 50 | 48 | 50 | 49 | 50 | 48
8 | BIPTC | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data
9 | BSRM 230/33kV Grid Sub-Station | 184 | 146 | 143 | 159 | 180 | 187 | 170 | 156 | 117 | 158 | 172 | 167 | 152 | 173 | 146 | 170 | 132 | 134 | 162 | 181 | 162 | 181 | 151 | 146 | 131 | 99
10 | Bagerhat 132/33kV Grid Sub-Station | 49 | 49 | 49 | 49 | 46 | 46 | 46 | 49 | 55 | 55 | 52 | 52 | 55 | 58 | 52 | 49 | 49 | 52 | 70 | 70 | 68 | 68 | 71 | 64 | 61 | 55
11 | Bajitpur 132/33kV Grid Sub-Station | No Data | No Data | No Data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Bakulia 132/33kV Grid Sub-Station | 50 | 46 | 43 | 41 | 39 | 38 | 37 | 32 | 43 | 49 | 52 | 54 | 59 | 62 | 60 | 62 | 58 | 62 | 65 | 60 | 61 | 59 | 59 | 59 | 57 | 48
13 | Banani 132/33kV Grid Sub-Station | 22.8 | 20 | 19.4 | 19 | 18.4 | 18.4 | 20.4 | 20.8 | 23.4 | 28.2 | 33.6 | 36.6 | 37 | 39.2 | 38.2 | 37 | 35.6 | 36 | 37.4 | 36 | 36 | 34 | 34 | 32 | 30 | 26
14 | Bangabhaban 132/33kV Grid Sub-Station | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 6 | 6 | 8 | 7 | 7 | 8 | 8 | 8 | 6 | 6 | 5 | 5 | 4 | 4 | 3 | 3 | 2
15 | Barapukuria 230/132/33kV Grid Sub-Station | 32 | 31 | 31 | 31 | 31 | 30 | 30 | 31 | 36 | 40 | 39 | 35 | 37 | 38 | 35 | 32 | 30 | 31 | 43 | 43 | 42 | 41 | 42 | 39 | 38 | 35
16 | Barguna 132/33kV Grid Sub-Station | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 10 | 10 | 6 | 8 | 8 | 10 | 8 | 8 | 8 | 8 | 8 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12
17 | Barishal 132/33kV Grid Sub-Station | 59 | 56 | 56 | 53 | 52 | 52 | 52 | 55 | 62 | 67 | 67 | 77 | 80 | 75 | 78 | 69 | 64 | 64 | 77 | 75 | 76 | 76 | 75 | 77 | 72 | 64
18 | Barishal 230/132kV Grid Sub-Station | 48 | 42 | 40 | 38 | 26 | 32 | 42 | 44 | 48 | 48 | 50 | 38 | 40 | 44 | 56 | 48 | 42 | 44 | 62 | 62 | 60 | 60 | 62 | 60 | 56 | 50
19 | Baroaulia 132/33kV Grid Sub-Station | 39 | 39 | 39 | 36 | 36 | 36 | 36 | 42 | 45 | 48 | 48 | 48 | 49 | 48 | 41 | 46 | 39 | 36 | 40 | 40 | 39 | 37 | 38 | 41 | 40 | 37
20 | Baroirhat 132/33kV Grid Sub-Station | 31 | 29 | 29 | 28 | 28 | 27 | 29 | 30 | 34 | 34 | 35 | 37 | 39 | 40 | 38 | 34 | 34 | 38 | 45 | 43 | 41 | 43 | 43 | 42 | 40 | 36
21 | Bashundhara 132/33kV Grid Sub-Station | 86 | 76 | 69 | 64 | 62 | 62 | 62 | 70 | 83 | 103 | 109 | 112 | 120 | 120 | 116 | 111 | 106 | 107 | 115 | 110 | 110 | 107 | 107 | 107 | 102 | 91
22 | BashundharaCement 132/33kV Sub-Station | 7 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 12 | 12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
23 | Beanibazar 132/33kV Grid Sub-Station | 34 | 30 | 28 | 26 | 28 | 30 | 30 | 30 | 30 | 34 | 34 | 34 | 34 | 36 | 32 | 32 | 32 | 36 | 44 | 40 | 40 | 40 | 42 | 42 | 38 | 36
24 | Benapole 132/33kV Grid Sub-Station | 30 | 24 | 24 | 24 | 24 | 26 | 28 | 44 | 46 | 46 | 38 | 41 | 42 | 41 | 38 | 32 | 29 | 32 | 41 | 42 | 42 | 39 | 41 | 39 | 37 | 31
25 | Bhaluka 132/33kV Grid Sub-Station | 88 | 88 | 84 | 80 | 78 | 76 | 82 | 86 | 100 | 92 | 94 | 98 | 72 | 80 | 78 | 88 | 74 | 70 | 98 | 114 | 108 | 108 | 102 | 100 | 96 | 90
26 | Bhandaria 132/33kV Grid Sub-Station | 28 | 28 | 28 | 26 | 26 | 26 | 25 | 24 | 22 | 22 | 22 | 24 | 26 | 27 | 26 | 23 | 21 | 21 | 33 | 33 | 32 | 34 | 34 | 36 | 35 | 31
27 | Bhangura 132/33kV Grid Sub-Station | 16 | 14 | 14 | 14 | 14 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 16 | 18 | 16 | 14 | 14 | 16 | 22 | 22 | 20 | 20 | 20 | 20 | 18 | 16
28 | Bheramara(GK) 132/33kV Grid Sub-Station | 28 | 27 | 25 | 25 | 24 | 24 | 26 | 32 | 35 | 33 | 30 | 29 | 31 | 33 | 30 | 28 | 28 | 30 | 40 | 40 | 38 | 38 | 38 | 37 | 34 | 32
29 | Bhulta 132/33kV Grid Sub-Station | 215 | 198 | 202 | 206 | 202 | 202 | 204 | 198.5 | 228 | 222 | 252 | 248 | 259 | 242 | 249 | 251 | 253 | 237 | 210 | 232 | 232 | 234 | 240 | 230 | 216 | 191
30 | Bog-Sherpur 132/33kV Grid Sub-Station | 48 | 46 | 46 | 44 | 42 | 44 | 44 | 44 | 50 | 52 | 46 | 48 | 48 | 50 | 44 | 42 | 44 | 42 | 54 | 54 | 52 | 50 | 50 | 50 | 48 | 48
31 | Bogura 132/33kV Grid Sub-Station | 79 | 81 | 79 | 76 | 76 | 70 | 79 | 90 | 99 | 104 | 93 | 92 | 97 | 93 | 91 | 90 | 89 | 92 | 102 | 104 | 102 | 107 | 104 | 100 | 92 | 88
32 | Borhanuddin 230/33kV Grid Sub-Station | 47 | 46 | 45 | 44 | 40 | 42 | 42 | 33 | 41 | 41 | 38 | 38 | 42 | 43 | 44 | 34 | 37 | 36 | 49 | 49 | 49 | 50 | 52 | 53 | 52 | 48
33 | Brahmanbaria 132/33kV Grid Sub-Station | 87 | 83 | 82 | 80 | 78 | 77 | 80 | 78 | 79 | 85 | 87 | 87 | 89 | 84 | 87 | 80 | 80 | 86 | 105 | 107 | 107 | 107 | 109 | 109 | 100 | 85
34 | Cantonment 132/33kV GIS Grid Sub-Station | 52 | 46 | 42 | 40 | 39 | 40 | 44 | 48 | 54 | 58 | 64 | 68 | 72 | 76 | 74 | 70 | 68 | 64 | 74 | 74 | 72 | 72 | 70 | 68 | 66 | 58
35 | Chandpur 132/33kV Grid Sub-Station | 37 | 36 | 35 | 34 | 34 | 33 | 33 | 33 | 32 | 30 | 30 | 30 | 32 | 35 | 33 | 30 | 30 | 31 | 39 | 40 | 39 | 38 | 38 | 37 | 34 | 34
36 | Chandraghona 132/33kV Grid Sub-Station | 17 | 16 | 16 | 15 | 15 | 15 | 16 | 18 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 19 | 22 | 23 | 24 | 23 | 24 | 23 | 23 | 20 | 18
37 | Chapai 132/33kV Grid Sub-Station | 37 | 31 | 31 | 31 | 31 | 31 | 36 | 40 | 37 | 42 | 42 | 45.5 | 47 | 48 | 37 | 32 | 32 | 32 | 40 | 42 | 41 | 41 | 41 | 41 | 41 | 40
38 | Charsaidpur 132/33kV Sub-Station | 27 | 36 | 37 | 37 | 36 | 36 | 36 | 38 | 38 | 36 | 39 | 39 | 36 | 35 | 35 | 27 | 26 | 37 | 36 | 37 | 37 | 37 | 37 | 39 | 38 | 39
39 | Chauddagram 132/33kV Grid Sub-Station | 32 | 30 | 30 | 28 | 28 | 29 | 31 | 32 | 34 | 34 | 35 | 36 | 38 | 35 | 35 | 32 | 32 | 37 | 40 | 36 | 39 | 40 | 40 | 39 | 38 | 35
40 | Chhatak 132/33kV Grid Sub-Station | 16 | 14 | 14 | 14 | 14 | 13 | 13 | 13 | 16 | 16 | 16 | 16 | 15 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 19 | 18 | 17
41 | Chowmuhani 132/33kV Grid Sub-Station | 124 | 118 | 112 | 112 | 112 | 113 | 113 | 116 | 116 | 108 | 106 | 106 | 109 | 108 | 110 | 106 | 110 | 119 | 133 | 126 | 138 | 143 | 143 | 139 | 134 | 125
42 | Chuadanga 132/33kV Grid Sub-Station | 44 | 39 | 39 | 37 | 37 | 38 | 42 | 56 | 57 | 56 | 50 | 50 | 58 | 64 | 54 | 52 | 34 | 55 | 67 | 67 | 66 | 63 | 62 | 60 | 57 | 50
43 | Coxsbazar 132/33kV Grid Sub-Station | 82 | 82 | 82 | 82 | 82 | 82 | 83 | 80 | 78 | 75 | 80 | 82 | 78 | 80 | 74 | 71 | 62 | 57 | 92 | 91 | 92 | 93 | 92 | 92 | 87 | 83
44 | Cumilla(N) 230/132/33kV Grid Sub-Station | 77 | 75 | 72 | 70 | 70 | 69 | 83 | 78 | 87 | 91 | 81 | 96 | 96 | 102 | 96 | 83 | 77 | 76 | 102 | 108 | 92 | 96 | 101 | 92 | 84 | 85
45 | Cumilla(S) 132/33kV Grid Sub-Station | 96 | 87 | 85 | 85 | 81 | 80 | 87 | 89 | 94 | 105 | 110 | 113 | 116 | 117 | 122 | 109 | 115 | 117 | 117 | 115 | 115 | 113 | 108 | 107 | 105 | 107
46 | Daudkandi 132/33kV Grid Sub-Station | 76 | 74 | 74 | 70 | 70 | 74 | 76 | 86 | 72 | 84 | 84 | 84 | 88 | 92 | 74 | 80 | 82 | 90 | 108 | 108 | 102 | 104 | 104 | 102 | 94 | 90
47 | Dhaka University 132/33kV Grid Sub-Station | 12 | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 16 | 20 | 26 | 30 | 30 | 32 | 30 | 30 | 30 | 28 | 28 | 26 | 26 | 24 | 22 | 20 | 16 | 14
48 | Dhamrai 132/33kV Grid Sub-Station | 64 | 64 | 62 | 60 | 60 | 62 | 66 | 68 | 57 | 56 | 56 | 52 | 55 | 54 | 54 | 54 | 55 | 70 | 76 | 78 | 76 | 74 | 76 | 72 | 68 | 68
49 | Dhanmondi 132/33kV Grid Sub-Station | 47.7 | 42.4 | 40 | 39 | 36 | 34.7 | 37.5 | 39 | 46.7 | 55.8 | 65 | 77 | 84 | 87 | 86 | 83 | 84 | 83 | 86 | 85 | 81 | 81 | 78 | 73 | 64 | 56
50 | Dohazari 132/33kV Grid Sub-Station | 48 | 46 | 42 | 42 | 42 | 44 | 46 | 46 | 46 | 47 | 50 | 48 | 52 | 59 | 52 | 44 | 47 | 49 | 66 | 66 | 64 | 61 | 58 | 57 | 57 | 52
51 | Faridpur 132/33kV Grid Sub-Station | 88 | 82 | 76 | 72 | 70 | 69 | 76 | 83 | 87 | 83 | 81 | 83 | 82 | 81 | 83 | 77 | 77 | 76 | 106 | 110 | 110 | 110 | 108 | 106 | 106 | 93
52 | Fatullah 132/33kV Grid Sub-Station | 60 | 57 | 53 | 50 | 51 | 46 | 47 | 48 | 48 | 69 | 74 | 76 | 78 | 68 | 68 | 74 | 75 | 72 | 72 | 72 | 70 | 64 | 61 | 61 | 61 | 59
53 | Fenchuganj 230/132/33kV Grid Sub-Station | 17 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 16 | 18 | 18 | 19 | 19 | 16 | 6 | 14 | 17 | 18 | 24 | 24 | 24 | 24 | 24 | 23 | 22 | 19
54 | Feni 132/33kV Grid Sub-Station | 50 | 49 | 48 | 48 | 46 | 46 | 45 | 45 | 45 | 47 | 46 | 54 | 62 | 64 | 59 | 58 | 54 | 61 | 65 | 66 | 66 | 66 | 66 | 66 | 56 | 56
55 | GPH 230/33kV Grid Sub-Station | 19 | 7 | 17 | 18 | 18 | 13 | 19 | 10 | 17 | 15 | 13 | 15 | 9 | 12 | 19 | 18 | 17 | 18 | 12 | 22 | 24 | 24 | 22 | 25 | 26 | 26
56 | Ghatail 132/33kV Grid Sub-Station | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 22 | 26 | 24 | 20 | 20 | 18 | 22 | 20 | 20 | 22 | 18 | 26 | 24 | 24 | 24 | 24 | 24 | 22 | 20
57 | Ghorashal 230/132/33kV Sub-Station | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6
58 | Ghorashal 230kV Switching Sub-Station | 46 | 46 | 42 | 43 | 38 | 33 | 39 | 42 | 46 | 51 | 38 | 33 | 40 | 39 | 38 | 38 | 32 | 23 | 34 | 32 | 31 | 32 | 31 | 40 | 46 | 46
59 | Goalpara 132/33kV Grid Sub-Station | 18 | 16 | 16 | 14 | 14 | 14 | 14 | 18 | 20 | 20 | 20 | 22 | 24 | 26 | 22 | 18 | 16 | 16 | 22 | 24 | 24 | 24 | 24 | 24 | 22 | 20
60 | Gollamari 132/33kV Grid Sub-Station | 38 | 38 | 36 | 34 | 32 | 30 | 32 | 36 | 42 | 42 | 40 | 42 | 46 | 50 | 46 | 38 | 36 | 38 | 46 | 44 | 44 | 44 | 44 | 42 | 42 | 42
61 | Gopalganj 132/33kV Grid Sub-Station | 53 | 48 | 44 | 43 | 42 | 42 | 47 | 58 | 65 | 57.6 | 52.4 | 51.8 | 57.4 | 54.8 | 54.6 | 48 | 47 | 50 | 70 | 74.2 | 70.8 | 71.4 | 68.4 | 64.4 | 63 | 58
62 | Gulshan 132/33kV Grid Sub-Station | 34 | 30 | 30 | 30 | 28 | 28 | 28 | 30 | 38 | 44 | 52 | 54 | 56 | 58 | 56 | 56 | 56 | 54 | 54 | 52 | 52 | 48 | 48 | 42 | 40 | 34
63 | Halishahar 132/33kV Grid Sub-Station | 25 | 24 | 24 | 24.5 | 25 | 25.5 | 26 | 26 | 45 | 56 | 57 | 38 | 46.5 | 39.5 | 38.5 | 42 | 39 | 46 | 26 | 34 | 35 | 32 | 46 | 25.5 | 26 | 24.5
64 | HaripurSBU 132/33kV Sub-Station | 131 | 130 | 132 | 135 | 138 | 142 | 140 | 147 | 150 | 163 | 139 | 132 | 133 | 123 | 119 | 124 | 127 | 130 | 125 | 137 | 147 | 142 | 144 | 135 | 160 | 158
65 | Hasnabad 132/33kV Grid Substation | 42 | 40 | 39 | 39 | 37 | 36 | 36 | 36 | 40 | 44 | 46 | 50 | 51 | 52 | 52 | 52 | 53 | 54 | 54 | 53 | 53 | 52 | 52 | 51 | 49 | 43
66 | Hathazari 230/132/33kV Grid Sub-Station | 36 | 36 | 36 | 34 | 32 | 31 | 31 | 38 | 37 | 37 | 43 | 43 | 47 | 50 | 48 | 32 | 35 | 39 | 46 | 49 | 48 | 48 | 48 | 45 | 43 | 41
67 | Ishurdi 132/33kV Grid Sub-Station | 44 | 42 | 39 | 39 | 38 | 41 | 43 | 43 | 47 | 49 | 45 | 47 | 49 | 52 | 50 | 49 | 49 | 48 | 56 | 57 | 58 | 57 | 56 | 54 | 51 | 49
68 | Jaldhaka 132/33kV Grid Sub-Station | 34 | 32 | 32 | 30 | 30 | 30 | 30 | 34 | 40 | 44 | 41 | 39 | 38 | 38 | 35 | 32 | 31 | 36 | 51 | 49 | 51 | 47 | 45 | 44 | 43 | 40
69 | Jamalpur 132/33kV Grid Sub-Station | 64 | 60 | 58 | 56 | 55 | 56 | 60 | 72 | 88 | 84 | 62 | 62 | 64 | 68 | 70 | 60 | 60 | 66 | 90 | 91 | 84 | 90 | 90 | 85 | 78 | 70
70 | Jashore 132/33kV Grid Sub-Station | 65 | 70 | 68 | 68 | 68 | 70 | 71 | 86 | 98 | 95 | 91 | 91 | 93 | 101 | 97 | 77 | 75 | 73 | 92 | 94 | 93 | 93 | 92 | 89 | 83 | 77
71 | Jhenaidah 132/33kV Grid Sub-Station | 60 | 54 | 54 | 50 | 50 | 50 | 59 | 70 | 85 | 85 | 70 | 64 | 68 | 75 | 71 | 64 | 62 | 65 | 94 | 94 | 88 | 85 | 85 | 78 | 71 | 65
72 | Joydebpur 132/33kV Grid Sub-Station | 91 | 81 | 81 | 81 | 81 | 81 | 84 | 112 | 113 | 113 | 107 | 116 | 115 | 95 | 97 | 102 | 111 | 108 | 115 | 110 | 105 | 106 | 104 | 102 | 95 | 83
73 | Joypurhat 132/33kV Grid Sub-Station | 32 | 32 | 32 | 30 | 30 | 28 | 27 | 32 | 38 | 35 | 33 | 30 | 34 | 34 | 30 | 27 | 26 | 30 | 40 | 40 | 42 | 42 | 42 | 40 | 40 | 35
74 | Juldah 132/33kV Grid Sub-Station | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 6 | 7 | 7 | 9
75 | KSRM 132/33kV Grid Sub-Station | 12 | 13 | 19 | 20 | 16 | 12 | 15 | 20 | 23 | 14 | 17 | 18 | 17 | 17 | 5 | 21 | 15 | 15 | 20 | 10 | 10 | 12 | 12 | 18 | 21 | 27
76 | Kabirpur 132/33kV Grid Sub-Station | 171 | 168 | 163 | 158 | 152 | 146 | 159 | 186 | 220 | 215 | 216 | 227 | 233 | 194 | 195 | 206 | 217 | 224 | 231 | 226 | 215 | 208 | 201 | 195 | 182 | 162
77 | Kachua 132/33kV Grid Sub-Station | 33 | 30 | 27 | 27 | 26 | 25 | 29 | 29 | 29 | 38 | 36 | 34 | 33 | 32 | 41 | 38 | 38 | 41 | 50 | 49 | 48 | 51 | 51 | 49 | 47 | 41
78 | Kallyanpur 132/33kV Grid Sub-Station | 45 | 42 | 39 | 39 | 39 | 39 | 39 | 42 | 51 | 57 | 60 | 60 | 66 | 66 | 63 | 63 | 66 | 57 | 63 | 60 | 60 | 60 | 60 | 57 | 57 | 51
79 | Kalurghat 132/33kV Grid Sub-Station | 20 | 16 | 16 | 14 | 14 | 14 | 16 | 14 | 20 | 22 | 26 | 28 | 29 | 26 | 25 | 30 | 28 | 26 | 25 | 24 | 26 | 24 | 22 | 22 | 22 | 18
80 | Kamrangirchar 132/33kV Grid Sub-Station | 40.91 | 38.67 | 37.78 | 37.06 | 36.1 | 34.45 | 33.71 | 33.1 | 35.74 | 42.04 | 45.08 | 50.2 | 52.3 | 53.7 | 48.6 | 44.5 | 45.9 | 50.2 | 50.7 | 50.7 | 49.9 | 49.9 | 48.5 | 46.3 | 45 | 43.5
81 | Kaptai 132/33kV Sub-Station | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data
82 | Kazla 132/33kV Grid Sub-Station | 66 | 61 | 59 | 57 | 54 | 54 | 56 | 55 | 59 | 75 | 72 | 80 | 85 | 87 | 81 | 79 | 77 | 71 | 61 | 64 | 62 | 64 | 59 | 61 | 60 | 57
83 | Keranigonj 230/132/33kV Grid Sub-Station | 45 | 41 | 37 | 37 | 35 | 34 | 37 | 37 | 40 | 52 | 53 | 55 | 56 | 60 | 56 | 51 | 52 | 56 | 58 | 59 | 56 | 57 | 55 | 54 | 51 | 48
84 | Khagrachori 132/33kV Grid Sub-Station | 14 | 14 | 12 | 12 | 10 | 10 | 12 | 16 | 18 | 20 | 18 | 18 | 18 | 18 | 18 | 14 | 16 | 18 | 24 | 22 | 20 | 20 | 20 | 20 | 18 | 16
85 | Khulna (C) 132/33kV Grid Sub-Station | 48 | 41 | 38 | 38 | 37 | 38 | 38 | 47 | 55 | 57 | 56 | 57 | 64 | 72 | 65 | 52 | 48 | 50 | 63 | 64 | 65 | 65 | 61 | 62 | 56 | 53
86 | Khulshi 132/33kV Grid Sub-Station | 114 | 105 | 98 | 86 | 84 | 81 | 82 | 91 | 85 | 82 | 88 | 89 | 92 | 98 | 92 | 94 | 91 | 92 | 95 | 89 | 87 | 84 | 88 | 87 | 117 | 115
87 | Kishoreganj 132/33kV Grid Sub-Station | 96 | 93 | 90 | 88 | 94 | 82 | 80 | 90 | 96 | 87 | 82 | 81 | 78 | 86 | 85 | 67 | 67 | 77 | 97 | 104 | 105 | 112 | 108 | 105 | 107 | 100
88 | Kodda 132/33kV Grid Sub-Station | 200 | 188 | 185 | 183 | 179 | 174 | 180 | 192 | 248 | 264 | 262 | 276 | 240 | 190 | 215 | 246 | 247 | 260 | 263 | 266 | 262 | 255 | 250 | 240 | 226 | 220
89 | Kulaura 132/33kV Grid Sub-Station | 20 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 21 | 22 | 24 | 24 | 24 | 22 | 20 | 27 | 26 | 26 | 26 | 25 | 25 | 24 | 20
90 | Kurigram 132/33kV Grid Sub-Station | 30 | 24 | 20 | 20 | 20 | 22 | 27 | 33 | 44 | 39 | 30 | 28 | 30 | 30 | 28 | 26 | 22 | 34 | 46 | 42 | 40 | 36 | 36 | 34 | 34 | 32
91 | Kushtia 132/33kV Grid Sub-Station | 80 | 74 | 66 | 66 | 60 | 60 | 64 | 76 | 86 | 84 | 76 | 78 | 80 | 82 | 80 | 70 | 71 | 80 | 98 | 100 | 94 | 92 | 88 | 82 | 78 | 76
92 | Lalbag 132/33kV Grid Sub-Station | 57 | 56 | 52 | 51 | 48 | 48 | 48 | 50 | 50 | 53 | 59 | 63 | 65 | 68 | 64 | 62 | 64 | 65 | 66 | 65 | 65 | 64 | 63 | 59 | 60 | 59
93 | Lalmonirhat 132/33kV Grid Sub-Station | 30 | 22 | 20 | 20 | 22 | 22 | 24 | 28 | 31 | 32 | 32 | 26 | 26 | 24 | 19 | 24 | 23 | 28 | 41 | 40 | 40 | 30 | 37 | 32 | 28 | 28
94 | MI_Cement 132/33kV Grid Sub-Station | 15 | 17.3 | 17.5 | 17.3 | 17.3 | 17.2 | 16.8 | 15.1 | 15 | 14.7 | 11 | 12 | 12 | 15.5 | 15.1 | 15.3 | 15.4 | 10.3 | 15.8 | 15.5 | 15.6 | 15.5 | 15.9 | 14.7 | 15 | 15.2
95 | Madanganj 132/33kV Grid Sub-Station | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 23 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 28 | 26 | 27 | 27 | 29 | 29 | 29 | 27 | 29 | 29 | 26
96 | Madaripur 132/33kV Grid Sub-Station | 58 | 56 | 51 | 50 | 50 | 46 | 45 | 47 | 50 | 52 | 53 | 57 | 58 | 57 | 50 | 53 | 51 | 52 | 60 | 63 | 65 | 67 | 68 | 68 | 64 | 60
97 | Madartek 132/33kV Grid Sub-Station | 41.99 | 38.96 | 35.61 | 33.82 | 32.44 | 32.02 | 34.61 | 38.08 | 42.95 | 46.77 | 45.81 | 48 | 52.2 | 54.5 | 52.72 | 48.1 | 44.88 | 44.7 | 51.9 | 52 | 52.3 | 52.5 | 52.8 | 51.2 | 48.8 | 45.88
98 | Madunaghat 132/33kV Grid Sub-Station | 24 | 23 | 22 | 21 | 21 | 21 | 21 | 27 | 28 | 28 | 30 | 32 | 33 | 33 | 33 | 29 | 33 | 33 | 37 | 35 | 35 | 34 | 34 | 32 | 31 | 26
99 | Magura 132/33kV Grid Sub-Station | 30 | 27 | 25 | 24 | 23 | 23 | 26 | 33 | 41 | 38 | 31 | 31 | 31 | 36 | 34 | 32 | 30 | 31 | 44 | 45 | 42 | 41 | 40 | 39 | 36 | 32
100 | Mahasthangarh 132/33kV Grid Sub-Station | 36 | 34 | 26 | 30 | 28 | 28 | 30 | 34 | 40 | 42 | 38 | 34 | 36 | 36 | 34 | 34 | 32 | 34 | 48 | 50 | 46 | 44 | 46 | 44 | 42 | 40
101 | Manikganj 132/33kV Grid Sub-Station | 88 | 84 | 80 | 80 | 80 | 78 | 80 | 81 | 86 | 96 | 92 | 94 | 96 | 90 | 88 | 89 | 89 | 88 | 102 | 102 | 102 | 102 | 102 | 100 | 96 | 92
102 | Maniknagar 132/33kV Grid Sub-Station | 28 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 30 | 34 | 40 | 40 | 42 | 46 | 44 | 40 | 38 | 38 | 40 | 38 | 38 | 36 | 34 | 34 | 34 | 30
103 | Matarbari 132/33kV Sub-Station | 26 | 25 | 24 | 21 | 18 | 22 | 21 | 32 | 28 | 25 | 28 | 28 | 28 | 30 | 30 | 20 | 23 | 24 | 35 | 32 | 32 | 32 | 32 | 30 | 30 | 28
104 | Matuail 132/33kV Grid Sub-Station | 36 | 32 | 35 | 34 | 32 | 32 | 32 | 36 | 37 | 44 | 44 | 44 | 44 | 36 | 40 | 44 | 42 | 42 | 38 | 38 | 36 | 35 | 33 | 34 | 35 | 40
105 | Millgate Tongi 132/33kV Grid Sub-Station | 44 | 43 | 41 | 40 | 39 | 40 | 44 | 43 | 59 | 62 | 54 | 61 | 65 | 54 | 58 | 68 | 67 | 63 | 69 | 66 | 65 | 64 | 59 | 60 | 57 | 57
106 | Mirpur 132/33kV Grid Sub-Station | 64.5 | 52 | 47.5 | 47.5 | 47.5 | 47.5 | 52 | 56.5 | 62 | 74 | 84 | 87 | 93 | 91 | 91 | 90.5 | 83 | 84 | 91 | 90 | 88 | 88 | 87 | 85 | 76 | 70
107 | Mirsorai 230/33kV Grid Sub-Station | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 7 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 6
108 | Mirzapur 132/33kV GIS Grid Sub-Station | 26 | 26 | 24 | 24 | 24 | 24 | 24 | 28 | 30 | 26 | 22 | 22 | 24 | 24 | 22 | 22 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 28 | 26 | 26
109 | Mithapukur 132/33kV Grid Sub-Station | 30 | 28 | 28 | 24 | 24 | 22 | 22 | 26 | 36 | 30 | 29 | 24 | 26 | 26 | 26 | 24 | 24 | 28 | 42 | 39 | 36 | 34 | 34 | 32 | 32 | 31
110 | Modern Steel 132/11kV Grid Sub-Station | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | Mogbazar 132/33kV Grid Sub-Station | 50.9 | 49.3 | 46.9 | 35.1 | 43.7 | 42.6 | 41.9 | 48.2 | 55.1 | 62.1 | 68.9 | 73.9 | 74.2 | 76.5 | 67.5 | 75.9 | 71.4 | 73 | 72.6 | 71.7 | 70.2 | 69.2 | 68 | 61.7 | 57.6 | 56.8
112 | Mongla 132/33kV Grid Sub-Station | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 20 | 18 | 19 | 23 | 24 | 24 | 22 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 14 | 16
113 | Motijheel 132/33kV Grid Sub-Station | 15 | 13 | 11 | 11 | 11 | 11 | 11 | 12 | 15 | 17 | 20 | 22 | 24 | 25 | 23 | 22 | 22 | 22 | 24 | 22 | 22 | 22 | 21 | 21 | 19 | 17
114 | Munshiganj 132/33kV Grid Sub-Station | 58 | 58 | 58 | 56 | 56 | 54 | 52 | 52 | 58 | 58 | 58 | 58 | 64 | 68 | 62 | 60 | 58 | 55 | 57 | 60 | 62 | 62 | 64 | 66 | 64 | 60
115 | Mymensingh 132/33kV Grid Sub-Station | 144 | 141 | 139 | 134 | 132 | 129 | 128 | 124 | 135 | 139 | 151 | 152 | 155 | 164 | 168 | 143 | 142 | 151 | 171 | 174 | 171 | 166 | 166 | 159 | 161 | 149
116 | Naogaon 132/33kV Grid Sub-Station | 68 | 64 | 61 | 58 | 55 | 54 | 56 | 62 | 76 | 76 | 70 | 74 | 75 | 77 | 70 | 65 | 61 | 60 | 78 | 81 | 81 | 81 | 82 | 76 | 73 | 73
117 | Narail 132/33kV Grid Sub-Station | 27 | 26 | 24 | 25 | 24 | 24 | 23 | 30 | 38 | 31 | 25 | 25 | 29 | 32 | 27 | 26 | 25 | 27 | 42 | 41 | 39 | 38 | 36 | 35 | 32 | 29
118 | Narinda 132/33kV Grid Sub-Station | 30 | 27 | 25 | 23 | 20 | 18 | 18 | 21 | 24 | 28 | 39 | 43 | 49 | 51 | 49 | 46.5 | 46 | 46 | 44 | 44.5 | 44.5 | 43 | 41.5 | 40 | 34 | 32
119 | Narshingdi 132/33kV Grid Sub-Station | 139 | 128 | 120 | 119 | 117 | 117 | 118 | 118 | 113 | 125 | 129 | 113 | 121 | 134 | 117 | 117 | 121 | 120 | 133 | 150 | 147 | 147 | 148 | 148 | 142 | 138
120 | Natore 132/33kV Grid Sub-Station | 79 | 76 | 75 | 73 | 70 | 68 | 70 | 75 | 88 | 87 | 81 | 77 | 78 | 86 | 82 | 73 | 75 | 78 | 102 | 102 | 100 | 98 | 100 | 96 | 91 | 86
121 | Nawabganj 132/33kV Grid Sub-Station | 26.4 | 25.6 | 24.6 | 24 | 23.5 | 23.1 | 22.6 | 22.4 | 24 | 25.4 | 25.2 | 25.2 | 28.2 | 34 | 33 | 27.2 | 22.8 | 24.4 | 30 | 31.6 | 32.4 | 33.6 | 36 | 34.1 | 33 | 28.6
122 | Netrakona 132/33kV Grid Sub-Station | 87 | 85 | 82 | 80 | 80 | 76 | 82 | 116 | 96 | 94 | 85 | 82 | 92 | 95 | 83 | 85 | 94 | 100 | 92 | 111 | 109 | 109 | 106 | 107 | 103 | 95
123 | New Tongi 132/33kV Grid Sub-Station | 49.3 | 46.7 | 45.3 | 43.8 | 43 | 42.7 | 42.2 | 47.2 | 54.5 | 62 | 63 | 62 | 61 | 54 | 53 | 56 | 55 | 54 | 55.5 | 55.5 | 54 | 54 | 54 | 52.5 | 49 | 47
124 | Niamatpur 132/33kV Grid Sub-Station | 40 | 39 | 37 | 36 | 36 | 36 | 38 | 41 | 54 | 59 | 55 | 53 | 53 | 59 | 51 | 44 | 44 | 43 | 52 | 52 | 52 | 51 | 50 | 50 | 48 | 43
125 | Noapara 132/33kV Grid Sub-Station | 25 | 24 | 20 | 18 | 17 | 17 | 23 | 29 | 32 | 30 | 28 | 28 | 30 | 30 | 29 | 25 | 24 | 25 | 35 | 34 | 35 | 35 | 34 | 32 | 30 | 25
126 | PHP 132/33kV Sub-Station | 6 | 4 | 4 | 6 | 5 | 7 | 3 | 4 | 6 | 6 | 7 | 7 | 6 | 4 | 6 | 7 | 8 | 8 | 5 | 4 | 3 | 3 | 4 | 4 | 6 | 5
127 | Pabna 132/33kV Grid Sub-Station | 54 | 56 | 52 | 50 | 47 | 47 | 52 | 60 | 69 | 65 | 59 | 62 | 63 | 67 | 62 | 60 | 60 | 66 | 76 | 82 | 78 | 77 | 76 | 73 | 68 | 62
128 | Palashbari 132/33kV Grid Sub-Station | 53 | 50 | 50 | 47 | 47 | 42 | 42 | 52 | 62 | 57 | 49 | 48 | 48 | 56 | 49 | 45 | 44 | 50 | 71 | 69 | 66 | 65 | 65 | 61 | 58 | 54
129 | Panchagarh 132/33kV Grid Sub-Station | 28 | 27 | 24 | 22 | 22 | 22 | 22 | 27 | 34 | 36 | 33 | 29 | 33 | 31 | 30 | 28 | 28 | 32 | 42 | 41 | 40 | 37 | 35 | 32 | 32 | 29
130 | Patuakhali 132/33kV Grid Sub-Station | 45 | 43.5 | 42 | 40 | 39 | 39 | 40.5 | 40.5 | 40.5 | 35 | 36 | 39 | 39 | 39 | 38 | 33.3 | 33.3 | 35 | 51.6 | 51.6 | 51.8 | 53.9 | 53.9 | 54 | 52.1 | 48.3
131 | Payra 400/132/33kV Grid Sub-Station | 12 | 12 | 10 | 10 | 8 | 8 | 10 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12
132 | Postogola 132/33kV Grid Sub-Station | 29 | 26 | 24 | 23 | 21 | 21 | 20 | 21 | 22 | 25 | 30 | 32 | 34 | 35 | 33 | 31 | 32 | 32 | 32 | 33 | 33 | 32 | 34 | 32 | 32 | 32
133 | Purbachal 132/33kV Grid Sub-Station | 11 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 11 | 11 | 11 | 12 | 14 | 15 | 14 | 13 | 12 | 13 | 15 | 14 | 14 | 14 | 14 | 14 | 13 | 6
134 | Purbasadipur 132/33kV Grid Sub-Station | 79 | 79 | 70 | 70 | 63 | 63 | 63 | 83 | 95 | 96 | 92 | 94 | 99 | 98 | 90 | 82 | 77 | 78 | 102 | 96 | 97 | 95 | 95 | 90 | 87 | 86
135 | Rahanpur 132/33kV Grid Sub-Station | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | Rahim Steel 132/33kV Sub-Station | 15 | 15 | 12 | 17 | 19 | 22 | 17 | 29 | 39 | 28 | 37 | 28 | 29 | 32 | 21 | 19 | 21 | 17 | 19 | 9 | 9 | 9 | 8 | 14 | 13 | 19
137 | Rajbari 132/33kV Grid Sub-Station | 40 | 38 | 36 | 34 | 32 | 32 | 34 | 38 | 44 | 42 | 38 | 38 | 38 | 40 | 40 | 36 | 36 | 42 | 56 | 56 | 54 | 52 | 52 | 50 | 46 | 44
138 | Rajendrapur 132/33kV Grid Sub-Station | 82 | 78 | 74 | 72 | 70 | 70 | 72 | 82 | 88 | 92 | 90 | 88 | 90 | 90 | 82 | 84 | 86 | 86 | 88 | 92 | 94 | 92 | 92 | 88 | 84 | 80
139 | Rajshahi 132/33kV Grid Sub-Station | 78 | 70 | 64 | 61 | 61 | 61 | 61 | 66 | 94 | 90 | 84 | 70 | 82 | 90 | 80 | 46 | 55 | 56 | 81 | 82 | 81 | 81 | 80 | 81 | 79 | 72
140 | Rajshahi 230/132/33kV Grid Sub-Station | 28 | 28 | 27 | 26 | 26 | 25 | 26 | 27 | 9 | 9 | 9 | 16 | 32 | 36 | 30 | 25 | 35 | 26 | 37 | 38 | 42 | 43 | 43 | 44 | 42 | 39
141 | Ramganj 132/33kV Grid Sub-Station | 64 | 62 | 60 | 58 | 56 | 54 | 60 | 60 | 60 | 64 | 60 | 60 | 60 | 66 | 66 | 56 | 64 | 64 | 80 | 76 | 80 | 80 | 76 | 78 | 76 | 68
142 | Rampur 230/132/33 kV GIS Grid Sub-Station | 22 | 20 | 19 | 18 | 17 | 17 | 17 | 16 | 17 | 19 | 20 | 21 | 22 | 24 | 25 | 25 | 24 | 23 | 25 | 25 | 25 | 24 | 24 | 23 | 23 | 22
143 | Rangamati 132/33kV Grid Sub-Station | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 8 | 10 | 8 | 8 | 8 | 10 | 10 | 8 | 8 | 8 | 9 | 12 | 12 | 11 | 10 | 10 | 9 | 8 | 6
144 | Rangpur 132/33kV Grid Sub-Station | 75 | 73 | 68 | 65 | 63 | 60 | 57 | 76 | 85 | 94 | 90 | 86 | 90 | 89 | 86 | 78 | 76 | 81 | 111 | 108 | 103 | 94 | 88 | 84 | 83 | 76
145 | Ruppur 132/11kV Grid Sub-Station | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.6 | 3 | 3.4 | 3.8 | 4 | 3.6 | 3 | 3.4 | 3.8 | 4 | 3.6 | 3.2 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
146 | SSM 132/33kV Grid Sub-Station | 10 | 12 | 10 | 12 | 12 | 10 | 8 | 10 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4
147 | Saidpur 132/33kV Grid Sub-Station | 53 | 50 | 48 | 46 | 46 | 51 | 53 | 68 | 82 | 88 | 87 | 85 | 79 | 79 | 72 | 73 | 68 | 71 | 87 | 86 | 81 | 80 | 76 | 71 | 71 | 63
148 | Satkhira 132/33kV Grid Sub-Station | 60 | 52 | 46 | 45 | 45 | 46 | 50 | 70 | 88 | 72 | 61 | 60 | 63 | 76 | 64 | 56 | 51 | 60 | 86 | 88 | 86 | 84 | 84 | 79 | 73 | 64
149 | Satmasjid 132/33kV Grid Sub-Station | 56 | 50 | 44 | 40 | 40 | 38 | 42 | 46 | 52 | 60 | 66 | 72 | 78 | 84 | 82 | 75 | 71 | 71 | 76 | 75 | 74 | 74 | 73 | 71 | 69 | 63
150 | Savar 132/33kV Grid Sub-Station | 122 | 122 | 114 | 114 | 114 | 114 | 114 | 114 | 142 | 170 | 166 | 134 | 146 | 116 | 154 | 178 | 178 | 176 | 158 | 158 | 158 | 162 | 155 | 150 | 136 | 130
151 | SevenRings 132/11kV Sub-Station | 12.06 | 10.95 | 10.23 | 10.33 | 10.54 | 11.19 | 9.69 | 9.24 | 15 | 14.2 | 14.01 | 13.79 | 14.13 | 14.18 | 13.55 | 14.68 | 15.63 | 15.33 | 14.5 | 14.63 | 15 | 14.88 | 14.71 | 14.48 | 16.68 | 17.82
152 | ShahCement 132/33kV Grid Sub-Station | 20 | 20 | 19 | 19 | 19 | 20 | 25 | 19 | 10 | 15 | 14 | 14 | 15 | 15 | 14 | 15 | 15 | 7 | 7 | 7 | 7 | 7 | 8 | 20 | 20 | 20
153 | Shahjadpur 132/33kV Grid Sub-Station | 28 | 26 | 26 | 26 | 24 | 30 | 36 | 43 | 43 | 43 | 42 | 48 | 49 | 44 | 36 | 42 | 44 | 46 | 50 | 53 | 53 | 54 | 53 | 48 | 39 | 32
154 | Shahjibazar 132/33kV Grid Sub-Station | 59 | 56 | 52 | 50 | 50 | 48 | 48 | 50 | 53 | 52 | 52 | 52 | 53 | 56 | 47 | 54 | 49 | 49 | 67 | 76 | 76 | 76 | 76 | 73 | 73 | 61
155 | Shahmirpur 132/33kV Grid Sub-Station | 30 | 30 | 28 | 28 | 28 | 28 | 28 | 28 | 32 | 20 | 20 | 14 | 14 | 19 | 19 | 21 | 34 | 33 | 32 | 32 | 29 | 29 | 28.5 | 27 | 26 | 26
156 | Shariatpur 132/33kV Grid Sub-Station | 41 | 40 | 38 | 36 | 34 | 33 | 38 | 36 | 38 | 37 | 35 | 35 | 44 | 42 | 38 | 36 | 32 | 36 | 49 | 47 | 49 | 51 | 52 | 52 | 50 | 45
157 | Sherpur 132/33kV Grid Sub-Station | 78 | 78 | 76 | 70 | 70 | 66 | 72 | 88 | 102 | 100 | 80 | 70 | 82 | 82 | 82 | 78 | 78 | 86 | 104 | 106 | 106 | 106 | 104 | 98 | 102 | 94
158 | Shikalbaha 132/33kV Sub-Station | 11 | 10 | 10 | 10 | 9 | 8 | 9 | 10 | 10 | 11 | 12 | 12 | 14 | 13 | 12 | 11 | 11 | 12 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
159 | Shikalbaha 230/132kV Grid Sub-Station | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data
160 | Shitalakhya 132/33kV Grid Sub-Station | 37.4 | 34.2 | 32.5 | 30.3 | 29.3 | 29.6 | 30.2 | 35.2 | 35.4 | 50.6 | 57.6 | 59.7 | 66.6 | 58.7 | 56.2 | 55.9 | 53.9 | 54.8 | 54.1 | 52.7 | 52.4 | 49.9 | 49.6 | 46 | 42.3 | 41.4
161 | Sholosohor 132/33kV Grid Sub-Station | 23 | 21 | 20 | 19 | 19 | 18 | 19 | 20 | 23 | 28 | 31 | 32 | 33 | 31 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 27 | 26 | 25 | 24
162 | Shyampur 132/33kV Grid Sub-Station | 128 | 124 | 120 | 126 | 134 | 132 | 122 | 128 | 130 | 132 | 130 | 148 | 152 | 144 | 146 | 138 | 134 | 124 | 112 | 94 | 94 | 86 | 68 | 72 | 78 | 106
163 | Siddhirganj 132/33kV Grid Sub-Station | 64 | 57 | 55 | 55 | 55 | 54 | 57 | 81 | 86 | 102 | 99 | 106 | 113 | 102 | 97 | 82 | 92 | 88 | 86 | 87 | 83 | 82 | 75 | 80 | 77 | 73
164 | Sirajganj 132/33kV Grid Sub-Station | 44 | 40 | 38 | 34 | 34 | 32 | 36 | 50 | 58 | 58 | 56 | 62 | 62 | 46 | 52 | 58 | 58 | 62 | 68 | 74 | 74 | 74 | 74 | 66 | 58 | 50
165 | Sonargaon 132/33kV Grid Sub-Station | 66 | 64 | 61 | 60 | 63 | 62 | 61 | 61 | 71 | 73 | 69 | 84 | 77 | 81 | 68 | 69 | 78 | 73 | 74 | 73 | 72 | 77 | 70 | 52 | 56 | 60
166 | Sreemongol 132/33kV Grid Sub-Station | 42 | 37 | 36 | 36 | 36 | 36 | 36 | 37 | 37 | 38 | 38 | 36 | 38 | 40 | 44 | 38 | 38 | 42 | 51 | 50 | 50 | 50 | 50 | 50 | 45 | 41
167 | Sreepur 230/132/33kV Grid Sub-Station | 48 | 45 | 43 | 43 | 41 | 42 | 46 | 49 | 46 | 52 | 52 | 60 | 61 | 17 | 33 | 55 | 56 | 57 | 58 | 59 | 58 | 57 | 55 | 54 | 51 | 47
168 | Srinagar 132/33kV Grid Sub-Station | 24.8 | 23 | 23 | 21.2 | 21 | 21 | 21.4 | 21.4 | 22 | 22.6 | 21.2 | 23 | 23.8 | 27.2 | 28 | 23 | 22.4 | 21.8 | 26.6 | 27 | 27.6 | 28.2 | 28 | 29.2 | 27.4 | 25
169 | Sunamganj 132/33kV Grid Sub-Station | 28 | 26 | 24 | 24 | 22 | 22 | 24 | 26 | 27 | 29 | 29 | 25 | 24 | 26 | 24 | 22 | 24 | 24 | 35 | 34 | 34 | 34.5 | 36 | 36 | 32 | 28
170 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 24 | 22 | 20 | 18 | 25 | 18 | 18 | 18 | 20 | 20 | 14 | 26 | 24 | 28 | 26 | 22 | 22 | 24 | 28 | 28 | 26 | 26 | 26 | 28 | 28 | 26
171 | Sylhet 132/33kV Grid Sub-Station | 56 | 55 | 53 | 51 | 50 | 50 | 47 | 44 | 49 | 54 | 60 | 61 | 70 | 70 | 68 | 68 | 64 | 63 | 73 | 73 | 69 | 69 | 69 | 71 | 69 | 59
172 | TK chemical 132kV Grid Sub-Station | 16.4 | 16.4 | 16 | 15.4 | 14.4 | 13.4 | 13.4 | 14.4 | 15 | 15.4 | 15.4 | 16.4 | 17 | 19.4 | 18 | 16.2 | 16.2 | 16.2 | 19.2 | 21 | 20 | 20 | 19 | 19.2 | 19 | 17.4
173 | Tangail 132/33kV Grid Sub-Station | 102 | 94 | 88 | 86 | 82 | 88 | 94 | 112 | 118 | 116 | 102 | 108 | 114 | 108 | 102 | 96 | 98 | 110 | 126 | 126 | 128 | 128 | 122 | 122 | 118 | 108
174 | Thakurgaon 132/33kV Grid Sub-Station | 42 | 44 | 40 | 37 | 37 | 36 | 39 | 46 | 61 | 65 | 61 | 58 | 55 | 58 | 56 | 50 | 48 | 46 | 73 | 75 | 73 | 67 | 68 | 63 | 58 | 53
175 | Tongi 230/132/33kV Grid Sub-Station | 64 | 61 | 59 | 57 | 54 | 57 | 60 | 62 | 76 | 84 | 80 | 92 | 80 | 80 | 77 | 104 | 104 | 97 | 96 | 96 | 96 | 89 | 89 | 86 | 86 | 73
176 | Ullahpara 132/33kV Grid Sub-Station | 24 | 20 | 20 | 18 | 18 | 18 | 17 | 22 | 25 | 20 | 18 | 15 | 15 | 14 | 14 | 13 | 14 | 18 | 18 | 23 | 23 | 21 | 22 | 18 | 20 | 18
177 | Ullon 132/33kV Grid Sub-Station | 27 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 25 | 27 | 27 | 30 | 32 | 33 | 34 | 29 | 28 | 30 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 29
178 | Uttara 132/33kV Grid Sub-Station | 36 | 34 | 31 | 30 | 30 | 28 | 30 | 34 | 40 | 45 | 48 | 48 | 51 | 53 | 53 | 50 | 48 | 49 | 51 | 50 | 49 | 49 | 48 | 47 | 45 | 39
179 | UttaraNew 132/33kV Grid Sub-Station | 22 | 20 | 18 | 18 | 18 | 18 | 20 | 22 | 25 | 27 | 27 | 28 | 32 | 32 | 31 | 27 | 25 | 28 | 30 | 29 | 29 | 29 | 28 | 29 | 27 | 25
180 | Zigatola 132/33kV Grid Sub-Station | 51 | 44 | 40 | 36 | 35 | 34 | 35 | 38 | 44 | 52 | 56 | 60 | 64 | 58 | 66 | 62 | 58 | 60 | 62 | 62 | 62 | 62 | 60 | 60 | 58 | 54

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-01-2025 | [28 empty] | Date: | 08-01-2025 | [28 empty] | Date: | 08-01-2025 | [28 empty] | Date: | 08-01-2025 | [28 empty] | Date: | 08-01-2025 | [18 empty] | Date: | 08-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [18 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 150.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 0.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 50.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 450 | 0 | 0 | 0 | 0 | 28 | 280 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 24 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 203 | 36 | 0 | 50 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 270 | 340 | 382 | 15 | 0 | 30 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 18 | 19 | 11 | 0 | 0 | 0 | 4341 | 913 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 415.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 220 | 0 | 1120 | 0 | 4357.14 | 8698.14 | 93.62
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 24 | 502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 182 | 36 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 280 | 316 | 379 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 8 | 9 | 16 | 0 | 0 | 0 | 4077 | 913 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 2.5 | 174 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 220 | 0 | 1000 | 0 | 4151.5 | 8228.5 | 93.61
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 0 | 7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 24 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 183 | 36 | 0 | 70 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 280 | 316 | 379 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 3965 | 726 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 2.5 | 174 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 220 | 0 | 900 | 0 | 3867.5 | 7832.5 | 93.61
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 18 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 182 | 33 | 0 | 50 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 275 | 316 | 379 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 3854 | 727 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 2.5 | 174 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 700 | 0 | 3672.5 | 7526.5 | 93.61
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 24 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 51 | 0 | 130 | 0 | 0 | 0 | 29 | 191 | 33 | 0 | 50 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 0 | 290 | 316 | 380 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 3831 | 633 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 2.5 | 175 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 220 | 0 | 600 | 0 | 3436.5 | 7267.5 | 93.61
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 24 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 51 | 0 | 130 | 0 | 0 | 0 | 29 | 183 | 33 | 0 | 50 | 0 | 0 | 11 | 0 | 40 | 0 | 0 | 0 | 280 | 316 | 380 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 3804 | 632 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 2.5 | 175 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 220 | 0 | 600 | 0 | 3434.5 | 7238.5 | 93.6
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 0 | 6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 22 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 182 | 33 | 0 | 50 | 0 | 0 | 15 | 0 | 44 | 0 | 0 | 0 | 280 | 316 | 379 | 15 | 0 | 30 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 3921 | 632 | 319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 2.5 | 175 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 140 | 220 | 0 | 650 | 0 | 3651.5 | 7572.5 | 93.6
07:00 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 3 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 16.5 | 335 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 23 | 463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 1 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 221 | 33 | 0 | 50 | 0 | 0 | 10 | 0 | 42 | 0 | 2 | 0 | 285 | 360 | 379 | 15 | 0 | 30 | 0 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 10 | 18 | 18 | 0 | 0 | 0 | 4150.5 | 726 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 137 | 0 | 130 | 0 | 170 | 0 | 0 | 0 | 0 | 2.5 | 175 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 140 | 220 | 0 | 830 | 0 | 4029.5 | 8180 | 93.6
08:00 | 0 | 90 | 34 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 26 | 48 | 0 | 0 | 17 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 2 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 26 | 0 | 2 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 5 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 207 | 33 | 0 | 50 | 0 | 0 | 11 | 0 | 42 | 0 | 7 | 0 | 285 | 351 | 381 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 0 | 46 | 18 | 10 | 0 | 0.78 | 0 | 4528.78 | 914 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 373 | 0 | 610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1.45 | 189 | 0 | 180 | 0 | 188 | 0 | 0 | 0 | 0.16 | 2.5 | 205 | 67 | 0 | 0 | 0 | 0 | 0 | 0.4 | 2 | 0 | 0 | 254 | 4 | 140 | 180 | 0 | 1000 | 0 | 4599.51 | 9128.29 | 93.6
09:00 | 0 | 90 | 34 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 32 | 48 | 0 | 0 | 17 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 4 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 2 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 11 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 193 | 36 | 0 | 50 | 0 | 0 | 11 | 0 | 52 | 0 | 14 | 0 | 285 | 351 | 380 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 46 | 18 | 6 | 1 | 2.9 | 8 | 4649.9 | 914 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.98 | 374 | 0 | 701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 7.97 | 202 | 0 | 182 | 0 | 192 | 0 | 0 | 0 | 0.63 | 2.5 | 210 | 68 | 0 | 2 | 0 | 0 | 0 | 0.7 | 8 | 0 | 0 | 272 | 4 | 140 | 220 | 0 | 1210 | 0 | 5069.78 | 9719.68 | 93.59
10:00 | 0 | 90 | 34 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 0 | 32 | 48 | 0 | 0 | 35 | 0 | 22 | 0 | 380 | 0 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 2 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 15 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 198 | 43 | 0 | 50 | 0 | 0 | 15 | 0 | 52 | 0 | 16 | 0 | 290 | 346 | 333 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 0 | 0 | 0 | 215 | 0 | 47 | 18 | 5 | 1 | 4.07 | 22 | 4574.07 | 914 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.46 | 372 | 0 | 702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 9.82 | 198 | 0 | 183 | 0 | 192 | 0 | 0 | 0 | 1.1 | 5.5 | 210 | 69 | 0 | 2 | 0 | 0 | 0 | 2.2 | 34 | 0 | 0 | 250 | 4 | 80 | 220 | 0 | 1120 | 0 | 4901.08 | 9475.15 | 93.59
11:00 | 0 | 90 | 34 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 10 | 0 | 32 | 64 | 0 | 0 | 35 | 0 | 22 | 0 | 340 | 0 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 3 | 46 | 0 | 2 | 575 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 18 | 51 | 7 | 185 | 0 | 0 | 0 | 29 | 183 | 41 | 0 | 50 | 0 | 5 | 15 | 0 | 56 | 0 | 12 | 0 | 280 | 316 | 334 | 15 | 0 | 30 | 2 | 120 | 13 | 0 | 50 | 0 | 0 | 0 | 214 | 0 | 58 | 18 | 5 | 1 | 3.8 | 22 | 4527.8 | 915 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.08 | 368 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 36.2 | 193 | 0 | 193 | 0 | 205 | 0 | 0 | 0 | 1.98 | 5.5 | 210 | 68 | 0 | 4 | 0 | 0 | 0 | 3.4 | 34 | 0 | 0 | 250 | 4 | 80 | 220 | 0 | 1090 | 8 | 4973.16 | 9500.96 | 93.59
12:00 | 0 | 90 | 34 | 0 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 17 | 0 | 32 | 64 | 0 | 0 | 35 | 0 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 17 | 15 | 0 | 0 | 4 | 0 | 0 | 17 | 0 | 0 | 3 | 46 | 0 | 2 | 575 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 18 | 51 | 20 | 185 | 0 | 0 | 0 | 29 | 182 | 34 | 0 | 50 | 0 | 16 | 15 | 0 | 60 | 0 | 12 | 0 | 275 | 372 | 317 | 15 | 0 | 30 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 68 | 18 | 5 | 1 | 20.08 | 22 | 4799.08 | 914 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.82 | 371 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 25.13 | 186 | 0 | 209 | 0 | 210 | 0 | 0 | 0 | 1.55 | 5.5 | 210 | 71 | 0 | 3 | 0 | 0 | 0 | 1.6 | 24 | 0 | 0 | 307 | 4 | 140 | 220 | 0 | 1090 | 17 | 5183.6 | 9982.68 | 93.59
13:00 | 0 | 90 | 34 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 0 | 17 | 0 | 32 | 64 | 15 | 0 | 35 | 0 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 30 | 310 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 5 | 0 | 0 | 17 | 0 | 0 | 3 | 46 | 0 | 6 | 575 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 18 | 51 | 10 | 157 | 0 | 0 | 0 | 29 | 183 | 36 | 0 | 50 | 0 | 16 | 17 | 0 | 63 | 0 | 13 | 0 | 275 | 400 | 316 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 214 | 0 | 78 | 18 | 5 | 2 | 18.01 | 22 | 4844.01 | 914 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.87 | 374 | 0 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 34.45 | 186 | 0 | 179 | 0 | 197 | 0 | 0 | 0 | 1.43 | 5.5 | 210 | 71 | 0 | 2 | 0 | 0 | 0 | 2 | 71 | 0 | 0 | 291 | 4 | 140 | 220 | 0 | 1100 | 0 | 5200.25 | 10044.26 | 93.58
14:00 | 0 | 90 | 34 | 0 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 0 | 17 | 0 | 34 | 48 | 15 | 0 | 35 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 17 | 0 | 0 | 2 | 26 | 0 | 8 | 503 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 12 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 182 | 36 | 0 | 50 | 0 | 16 | 0 | 0 | 64 | 0 | 16 | 0 | 270 | 350 | 333 | 15 | 0 | 30 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 2 | 68 | 18 | 5 | 1 | 30.86 | 22 | 4681.86 | 915 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.77 | 372 | 0 | 714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 46.7 | 160 | 0 | 183 | 0 | 185 | 0 | 0 | 0 | 3.79 | 5.5 | 210 | 70 | 0 | 6 | 0 | 0 | 0 | 0.7 | 38 | 0 | 0 | 250 | 4 | 80 | 180 | 0 | 990 | 0 | 4774.46 | 9456.32 | 93.58
15:00 | 0 | 90 | 34 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 17 | 0 | 34 | 48 | 15 | 0 | 35 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 17 | 0 | 0 | 1 | 26 | 0 | 4 | 502 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 535 | 9 | 51 | 0 | 127 | 0 | 0 | 0 | 29 | 183 | 39 | 0 | 50 | 0 | 16 | 15 | 0 | 58 | 0 | 10 | 0 | 270 | 350 | 328 | 15 | 0 | 30 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 17 | 68 | 19 | 5 | 1 | 24.58 | 22 | 4679.58 | 913 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.39 | 373 | 0 | 711.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 16.31 | 160 | 0 | 204 | 0 | 185 | 0 | 0 | 0 | 2.69 | 5.5 | 210 | 73 | 0 | 1 | 0 | 0 | 0 | 0.3 | 22 | 0 | 0 | 242 | 4 | 80 | 180 | 0 | 920 | 0 | 4678.61 | 9358.19 | 93.58
16:00 | 0 | 90 | 34 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 17 | 0 | 34 | 48 | 15 | 0 | 35 | 0 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 17 | 0 | 0 | 1 | 26 | 0 | 6 | 503 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 5 | 51 | 0 | 127 | 0 | 0 | 0 | 29 | 182 | 38 | 0 | 50 | 0 | 16 | 15 | 0 | 57 | 0 | 3 | 0 | 285 | 350 | 347 | 15 | 0 | 30 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 216 | 17 | 68 | 19 | 5 | 0 | 10.15 | 22 | 4671.15 | 913 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.56 | 373 | 0 | 607.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 7.68 | 160 | 0 | 205 | 0 | 185 | 0 | 0 | 0 | 0.54 | 5.5 | 210 | 72 | 0 | 1 | 0 | 0 | 0 | 0.4 | 22 | 0.1 | 0 | 200 | 4 | 80 | 180 | 0 | 900 | 0 | 4451.11 | 9122.26 | 93.58
17:00 | 0 | 96 | 34 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 17 | 0 | 34 | 48 | 15 | 0 | 35 | 0 | 22 | 0 | 450 | 40 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 2 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 17 | 0 | 0 | 0 | 26 | 0 | 12 | 502 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 1 | 51 | 21 | 127 | 0 | 0 | 0 | 29 | 183 | 38 | 0 | 50 | 0 | 16 | 15 | 0 | 57 | 0 | 1 | 0 | 295 | 386 | 347 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 17 | 68 | 19 | 5 | 0 | 1.35 | 22 | 4802.35 | 913 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.47 | 394 | 0 | 683.73 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 | 0 | 0 | 4 | 0 | 1.77 | 160 | 0 | 205 | 0 | 185 | 0 | 0 | 0 | 0.12 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.02 | 0 | 200 | 4 | 80 | 180 | 0 | 960 | 0 | 4560.11 | 9362.46 | 93.57
18:00 | 0 | 101 | 34 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 17 | 34 | 0 | 34 | 48 | 0 | 0 | 35 | 35 | 22 | 0 | 450 | 42 | 0 | 0 | 17 | 30 | 335 | 0 | 0 | 0 | 34 | 20 | 22 | 0 | 0 | 25 | 80 | 0 | 0 | 12 | 0 | 0 | 54.36 | 0 | 12 | 0 | 26 | 0 | 10 | 575 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 51 | 100 | 185 | 0 | 0 | 0 | 29 | 182 | 40 | 48 | 50 | 0 | 10 | 17 | 0 | 56 | 0 | 0 | 0 | 270 | 386 | 347 | 15 | 0 | 30 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 215 | 17 | 78 | 19 | 5 | 0 | 0 | 0 | 5395.36 | 914 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 531 | 0 | 751.39 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 177 | 0 | 205 | 0 | 0 | 0 | 0 | 8.5 | 210 | 73 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 7 | 140 | 220 | 0 | 1010 | 36 | 5113.89 | 10509.25 | 93.57
19:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 36 | 0 | 32 | 48 | 0 | 0 | 0 | 17 | 22 | 0 | 450 | 95 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 72 | 20 | 22 | 0 | 0 | 35 | 15 | 0 | 0 | 11 | 0 | 0 | 17 | 0 | 0 | 0 | 26 | 0 | 18 | 575 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 10 | 185 | 0 | 0 | 0 | 29 | 183 | 40 | 44 | 50 | 0 | 9 | 17 | 0 | 57 | 0 | 0 | 0 | 270 | 386 | 347 | 40 | 0 | 30 | 0 | 163 | 13 | 0 | 86 | 25 | 0 | 0 | 216 | 0 | 69 | 19 | 8 | 0 | 0 | 0 | 5269 | 915 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614 | 0 | 757.65 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 201 | 0 | 204 | 0 | 0 | 0 | 0 | 8.5 | 210 | 73 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1192 | 17 | 5439.15 | 10708.15 | 93.57
19:30 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 36 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 94 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 72 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 21 | 576 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 183 | 40 | 34 | 50 | 0 | 9 | 17 | 0 | 56 | 0 | 0 | 0 | 290 | 386 | 369 | 42 | 0 | 30 | 0 | 163 | 13 | 0 | 86 | 25 | 0 | 0 | 216 | 0 | 45 | 28 | 9 | 0 | 0 | 0 | 5133 | 914 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616 | 0 | 758.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 204 | 0 | 204 | 0 | 0 | 0 | 0 | 8.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1222 | 0 | 5356.35 | 10489.35
20:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 36 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 92 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 62 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 24 | 575 | 0 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 182 | 44 | 25 | 50 | 0 | 9 | 17 | 0 | 54 | 0 | 0 | 0 | 270 | 350 | 347 | 42 | 0 | 20 | 0 | 163 | 13 | 0 | 86 | 25 | 0 | 0 | 216 | 0 | 45 | 19 | 10 | 0 | 0 | 0 | 5126 | 915 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 594 | 0 | 760.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 202 | 0 | 201 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1222 | 0 | 5328.7 | 10454.7 | 93.57
21:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 36 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 102 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 35 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 26 | 575 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 580 | 0 | 51 | 0 | 189 | 0 | 0 | 0 | 29 | 204 | 45 | 16 | 50 | 0 | 9 | 17 | 0 | 54 | 0 | 0 | 0 | 285 | 316 | 375 | 42 | 30 | 0 | 2 | 163 | 8 | 0 | 86 | 25 | 0 | 0 | 217 | 0 | 45 | 19 | 10 | 0 | 0 | 0 | 4952 | 914 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 0 | 690.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 197 | 0 | 197 | 0 | 0 | 0 | 0 | 8.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 7 | 140 | 220 | 0 | 1244 | 0 | 5215.84 | 10167.84 | 93.56
22:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 36 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 330 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 35 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 30 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 189 | 0 | 0 | 0 | 29 | 183 | 45 | 16 | 50 | 0 | 9 | 17 | 0 | 54 | 0 | 0 | 0 | 290 | 316 | 347 | 15 | 30 | 0 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 217 | 0 | 45 | 19 | 9 | 0 | 0 | 0 | 4946 | 913 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 611.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 196 | 0 | 197 | 0 | 0 | 0 | 0 | 8.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 7 | 140 | 220 | 0 | 1140 | 0 | 4950.27 | 9896.27 | 93.56
23:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 336 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 8 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 32 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 0 | 43 | 0 | 189 | 0 | 0 | 0 | 29 | 183 | 45 | 0 | 50 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 275 | 316 | 346 | 15 | 30 | 0 | 2 | 120 | 13 | 0 | 50 | 25 | 0 | 0 | 216 | 0 | 24 | 19 | 7 | 0 | 0 | 0 | 4695 | 914 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 567.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 0 | 5.5 | 163 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 180 | 0 | 1080 | 0 | 4487.95 | 9182.95 | 93.56
Total KWH | 0 | 1275840 | 496800 | 0 | 0 | 0 | 0 | 0 | 6501600 | 0 | 0 | 26280 | 357480 | 0 | 469872 | 757440 | 90327 | 0 | 351373 | 56160 | 525240 | 0 | 10100300 | 1007651 | 0 | 0 | 34633 | 692700 | 7820840 | 0 | 0 | 9203 | 243600 | 381000 | 500400 | 0 | 0 | 111655 | 160582 | 0 | 0 | 115680 | 0 | 0 | 217517 | 0 | 11520 | 18238 | 715080 | 0 | 367200 | 12392727.27 | 0 | 0 | 202560 | 0 | 0 | 77203 | 0 | 0 | 0 | 10739999 | 110565 | 1210375 | 247563 | 4114909 | 0 | 0 | 0 | 692160 | 4614000 | 900216 | 177600 | 1231220 | 0 | 169680 | 347150 | 0 | 1235520 | 0 | 103082 | 0 | 6875500 | 8202900 | 8942000 | 486360 | 95000 | 602040 | 48336 | 3801272.72 | 328464 | 0 | 1319040 | 568896 | 0 | 0 | 4367040 | 81000 | 988800 | 336000 | 213120 | 7400 | 132440 | 207120 | 109585468.99 | 17477090 | 7282944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275040 | 10523640 | 0 | 14698295 | 0 | 0 | 0 | 0 | 0 | 0 | 90224 | 0 | 0 | 0 | 379870 | 0 | 208500 | 4087727 | 0 | 4363282 | 0 | 4453309 | 0 | 0 | 0 | 16620 | 115848 | 4789000 | 1666036 | 106781 | 25578 | 0 | 0 | 0 | 10236.84 | 254160 | 305 | 0 | 5520000 | 139421 | 2833000 | 5214130 | 0 | 24453818.18 | 116400 | 109101255.02 | 218686724.01

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2025-01-08 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
Aminbazar | 411 | 05:00 | 383 | 14:00 | Kaliakoir | 376 | 04:00 | 353 | 10:00
Ashuganj | 406 | 4:00 | 391 | 10:00 | Madunaghat | 406 | 04:00 | 383 | 13:00
Bhulta | 405 | 03:00 | 381 | 13:00 | Meghnaghat | 399 | 01:00 | 375 | 12:00
Bibiana | 396 | 22:00 | 386 | 16:00 | Payra | 419 | 04:00 | 408 | 09:00
BIPTC | 409 | 03:00 | 386 | 10:00 | Rahanpur | 414 | 04:00 | 399 | 13:00
Bogura | 410 | 03:00 | 392 | 09:00 | Rampal | 415 | 03:00 | 391 | 13:00
Gopalganj | 415 | 05:00 | 394 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Agargaon | 233 | 03:00 | 216 | 13:00 | Haripur | 237 | 05:00 | 220 | 12:00
AKSML | 233 | 02:00 | 216 | 13:00 | Hasnabad | 232 | 01:00 | 218 | 12:00
Aminbazar | 234 | 04:00 | 216 | 12:00 | Hathazari | 233 | 04:00 | 221 | 10:00
Ashuganj | 238 | 04:00 | 227 | 10:00 | Ishurdi | 243 | 03:00 | 229 | 13:00
Ashuganj-400 | 236 | 6:00 | 220 | 12:00 | Jhenaidah | 241 | 03:00 | 225 | 12:00
Baghabari | 240 | 04:00 | 231 | 11:00 | Kaliakoir | 235 | 02:00 | 222 | 12:00
Barapukuria | 226 | 01:00 | 218 | 09:00 | Keranigonj | 233 | 03:00 | 216 | 13:00
Barapukuria-230 | 225 | 6:00 | 215 | 11:00 | Khulna(S) | 241 | 03:00 | 226 | 13:00
Barishal | 246 | 04:00 | 237 | 09:00 | Madunaghat | 233 | 03:00 | 220 | 12:00
Bheramara | 241 | 03:00 | 227 | 13:00 | Madunaghat-400 | 233 | 05:00 | 220 | 13:00
Bhulta | 236 | 02:00 | 222 | 12:00 | Maniknagar | 236 | 04:00 | 220 | 13:00
Bibiana | 229 | 22:00 | 221 | 11:00 | Meghnaghat | 238 | 00:00 | 227 | 13:00
BIPTC | 242 | 03:00 | 227 | 13:00 | Meghnaghat-400 | 237 | 05:00 | 220 | 12:00
Bogura | 240 | 03:00 | 229 | 09:00 | Mirsorai | 232 | 05:00 | 216 | 13:00
Bogura-400 | 238 | 03:00 | 228 | 09:00 | Rajshahi | 242 | 04:00 | 226 | 13:00
Borhanuddin | 248 | 02:00 | 242 | 13:00 | Rampal | 240 | 03:00 | 223 | 13:00
BSRM | 232 | 03:00 | 215 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Cumilla(N) | 233 | 03:00 | 219 | 12:00 | Rampura | 237 | 05:00 | 223 | 11:00
Faridpur | 246 | 03:00 | 233 | 12:00 | Shikalbaha | 233 | 05:00 | 218 | 14:00
Fenchuganj | 233 | 02:00 | 225 | 12:00 | Shyampur | 234 | 03:00 | 219 | 12:00
Ghorashal | 240 | 23:00 | 230 | 13:00 | Siddhirganj | 235 | 01:00 | 222 | 12:00
Ghorashal-230 | 236 | 05:00 | 222 | 12:00 | Sirajgonj | 246 | 06:00 | 238 | 12:00
Gopalganj | 246 | 05:00 | 233 | 12:00 | Sreepur | 240 | 03:00 | 129 | 06:00
GPH | 233 | 03:00 | 215 | 13:00 | Tongi | 231 | 23:00 | 216 | 15:00
132 KV | KV |  | KV |  | 132 KV | KV |  | KV
Aftabnagar | 136 | 03:00 | 126 | 12:00 | Kurigram | 132 | 03:00 | 120 | 09:00
Agargaon | 139 | 05:00 | 128 | 13:00 | Kushtia | 140 | 02:00 | 132 | 13:00
Agrabad | 133 | 01:00 | 125 | 13:00 | Lalbag | 136 | 02:00 | 125 | 12:00
AKS | 132 | 03:00 | 123 | 10:00 | Lalmonirhat | 132 | 01:00 | 122 | 08:00
Aminbazar | 142 | 04:00 | 139 | 07:00 | Madanganj | 133 | 05:00 | 123 | 12:00
Amnura | 139 | 19:00 | 132 | 08:00 | Madaripur | 134 | 00:00 | 131 | 10:00
Ashuganj | 141 | 02:00 | 136 | 10:00 | Madartek | 136 | 04:00 | 126 | 10:00
Bagerhat | 138 | 01:00 | 127 | 13:00 | Madunaghat | 134 | 03:00 | 123 | 21:00
Bajitpur | 136 | 04:00 | 132 | 09:00 | Magura | 140 | 03:00 | 130 | 08:00
Bakulia | 133 | 02:00 | 124 | 13:00 | Mahasthangarh | 136 | 02:00 | 128 | 09:00
Banani | 135 | 03:00 | 126 | 13:00 | Manikganj | 131 | 02:00 | 120 | 10:00
Bangabhaban | 134 | 01:00 | 125 | 12:00 | Maniknagar | 134 | 01:00 | 129 | 19:30
Barapukuria | 136 | 01:00 | 129 | 09:00 | Matarbari | 131 | 07:00 | 117 | 13:00
Barguna | 138 | 03:00 | 134 | 09:00 | Matuail | 133 | 01:00 | 126 | 16:00
Barishal | 135 | 01:00 | 129 | 12:00 | Millgate | 134 | 04:00 | 122 | 17:00
Barishal-230 | 138 | 05:00 | 130 | 13:00 | Mirpur | 140 | 03:00 | 130 | 10:00
Baroaulia | 132 | 03:00 | 125 | 13:00 | Mirzapur | 131 | 03:00 | 126 | 19:30
Baroirhat | 131 | 04:00 | 120 | 12:00 | Mithapukur | 135 | 03:00 | 124 | 09:00
Bashundhara | 137 | 05:00 | 123 | 10:00 | MI_Cement | 135 | 03:00 | 124 | 13:00
BashundharaCement | 133 | 05:00 | 123 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Beanibazar | 134 | 02:00 | 131 | 13:00 | Mogbazar | 136 | 04:00 | 126 | 13:00
Benapole | 138 | 02:00 | 123 | 13:00 | Mongla | 137 | 05:00 | 128 | 12:00
Bhaluka | 130 | 03:00 | 120 | 13:00 | Motijheel | 134 | 01:00 | 125 | 12:00
Bhandaria | 134 | 06:00 | 128 | 13:00 | Munshiganj | 133 | 01:00 | 124 | 13:00
Bhangura | 140 | 04:00 | 133 | 10:00 | Mymensingh | 132 | 12:00 | 118 | 08:00
Bheramara | 140 | 03:00 | 133 | 13:00 | Naogaon | 137 | 05:00 | 128 | 08:00
Bheramara(GK) | 139 | 02:00 | 133 | 13:00 | Narail | 140 | 04:00 | 129 | 13:00
Bhulta | 124 | 22:00 | 113 | 11:00 | Narinda | 134 | 4:00 | 129 | 12:00
Bog-Sherpur | 137 | 02:00 | 130 | 08:00 | Narshingdi | 134 | 23:00 | 117 | 12:00
Bogura | 138 | 04:00 | 131 | 09:00 | Natore | 138 | 01:00 | 131 | 13:00
Bogura-230 | 138 | 03:00 | 131 | 09:00 | Nawabganj | 136 | 23:00 | 126 | 13:00
Brahmanbaria | 134 | 01:00 | 128 | 11:00 | Netrakona | 130 | 07:00 | 118 | 10:00
Cantonment | 139 | 03:00 | 128 | 13:00 | New | 133 | 03:00 | 125 | 09:00
Chandpur | 126 | 23:00 | 116 | 13:00 | Niamatpur | 140 | 06:00 | 134 | 08:00
Chandraghona | 135 | 03:00 | 127 | 12:00 | Noapara | 140 | 03:00 | 127 | 13:00
Chapai | 139 | 01:00 | 132 | 12:00 | Pabna | 140 | 02:00 | 132 | 13:00
Charsaidpur | 134 | 03:00 | 124 | 12:00 | Palashbari | 134 | 04:00 | 125 | 08:00
Chauddagram | 131 | 02:00 | 121 | 13:00 | Panchagarh | 135 | 03:00 | 120 | 09:00
Chhatak | 134 | 23:00 | 131 | 15:00 | Patuakhali | 137 | 18:00 | 133 | 08:00
Chowmuhani | 124 | 00:00 | 117 | 14:00 | Payra | 138 | 02:00 | 134 | 13:00
Chuadanga | 139 | 01:00 | 129 | 13:00 | PHP | 130 | 03:00 | 118 | 13:00
Coxsbazar | 126 | 03:00 | 119 | 18:30 | Postogola | 138 | 05:00 | 127 | 13:00
Cumilla(N) | 135 | 02:00 | 126 | 13:00 | Purbachal | 136 | 03:00 | 126 | 13:00
Cumilla(S) | 134 | 05:00 | 124 | 10:00 | Purbasadipur | 132 | 04:00 | 118 | 08:00
Daudkandi | 131 | 22:00 | 121 | 13:00 | Rahanpur | 140 | 03:00 | 135 | 08:00
Dhaka | 135 | 01:00 | 126 | 13:00 | Rahanpur-400 | 141 | 04:00 | 135 | 13:00
Dhamrai | 137 | 05:00 | 129 | 10:00 | Rahim | 132 | 04:00 | 122 | 13:00
Dhanmondi | 137 | 04:00 | 127 | 12:00 | Rajbari | 137 | 05:00 | 128 | 13:00
Dohazari | 130 | 05:00 | 123 | 12:00 | Rajendrapur | 136 | 05:00 | 128 | 11:00
Faridpur | 136 | 03:00 | 130 | 11:00 | Rajshahi | 139 | 06:00 | 132 | 13:00
Fatullah | 136 | 04:00 | 126 | 12:00 | Rajshahi-230 | 140 | 03:00 | 129 | 13:00
Fenchuganj | 138 | 01:00 | 135 | 10:00 | Ramganj | 125 | 00:00 | 113 | 13:00
Feni | 130 | 06:00 | 121 | 10:00 | Rampur | 135 | 05:00 | 125 | 11:00
Ghatail | 131 | 09:00 | 123 | 08:00 | Rampura | 136 | 03:00 | 127 | 10:00
Ghorashal | 140 | 23:00 | 135 | 13:00 | Rangamati | 135 | 05:00 | 124 | 12:00
Goalpara | 139 | 03:00 | 129 | 10:00 | Rangpur | 133 | 05:00 | 122 | 20:00
Gollamari | 140 | 04:00 | 130 | 13:00 | Ruppur | 141 | 05:00 | 134 | 12:00
Gopalganj | 138 | 03:00 | 130 | 12:00 | Saidpur | 132 | 02:00 | 122 | 08:00
Gopalganj-400 | 138 | 04:00 | 130 | 13:00 | Satkhira | 138 | 06:00 | 127 | 13:00
Gulshan | 135 | 04:00 | 126 | 10:00 | Satmasjid | 139 | 04:00 | 128 | 12:00
Halishahar | 132 | 05:00 | 124 | 09:00 | Savar | 139 | 02:00 | 130 | 09:00
Haripur | 133 | 05:00 | 122 | 12:00 | SevenRings | 141 | 03:00 | 135 | 10:00
HaripurSBU | 133 | 05:00 | 122 | 12:00 | ShahCement | 134 | 03:00 | 124 | 12:00
Hasnabad | 137 | 23:00 | 128 | 12:00 | Shahjadpur | 143 | 04:00 | 135 | 13:00
Hathazari | 136 | 04:00 | 127 | 10:00 | Shahjibazar | 135 | 18:30 | 129 | 13:00
Ishurdi | 142 | 03:00 | 135 | 12:00 | Shahmirpur | 134 | 02:00 | 126 | 11:00
Jaldhaka | 131 | 05:00 | 119 | 09:00 | Shariatpur | 138 | 05:00 | 129 | 13:00
Jamalpur | 133 | 15:00 | 120 | 07:00 | Sherpur | 132 | 15:00 | 116 | 07:00
Jashore | 137 | 04:00 | 125 | 13:00 | Shikalbaha | 123 | 03:00 | 114 | 13:00
Jhenaidah | 140 | 01:00 | 130 | 13:00 | Shikalbaha-230 | 135 | 05:00 | 126 | 13:00
Jhenaidah-230 | 141 | 03:00 | 131 | 12:00 | Shitalakhya | 135 | 03:00 | 124 | 13:00
Joydebpur | 139 | 23:00 | 131 | 09:00 | Sholosohor | 134 | 03:00 | 124 | 13:00
Joypurhat | 136 | 05:00 | 128 | 09:00 | Shyampur | 135 | 04:00 | 125 | 13:00
Juldah | 132 | 01:00 | 125 | 11:00 | Shyampur-230 | 136 | 03:00 | 126 | 12:00
Kabirpur | 133 | 17:00 | 122 | 10:00 | Siddhirganj | 133 | 02:00 | 127 | 16:00
Kachua | 129 | 02:00 | 117 | 13:00 | Sirajganj | 140 | 04:00 | 131 | 13:00
Kaliakoir | 138 | 05:00 | 129 | 10:00 | Sonargaon | 132 | 04:00 | 121 | 12:00
Kallyanpur | 135 | 03:00 | 126 | 10:00 | Sreemongol | 135 | 01:00 | 130 | 12:00
Kalurghat | 134 | 02:00 | 125 | 13:00 | Sreepur | 131 | 03:00 | 125 | 07:00
Kamrangirchar | 136 | 02:00 | 125 | 10:00 | Srinagar | 137 | 04:00 | 126 | 12:00
Kaptai | N/A | N/A | N/A | N/A | SSM | 138 | 22:00 | 129 | 13:00
Kazla | 135 | 04:00 | 124 | 13:00 | Sunamganj | 133 | 04:00 | 130 | 13:00
Keranigonj | 137 | 05:00 | 125 | 13:00 | Sylhet | 135 | 01:00 | 132 | 12:00
Khagrachori | 134 | 05:00 | 122 | 13:00 | Sylhet-132 | 134 | 20:00 | 132 | 12:00
Khulna | 138 | 02:00 | 128 | 13:00 | Tangail | 129 | 12:00 | 123 | 20:00
Khulna(S) | 141 | 04:00 | 130 | 13:00 | Thakurgaon | 133 | 03:00 | 119 | 09:00
Khulshi | 133 | 04:00 | 123 | 10:00 | TK | 133 | 03:00 | 125 | 13:00
Kishoreganj | 133 | 02:00 | 127 | 09:00 | Tongi | 134 | 04:00 | 125 | 11:00
Kodda | 137 | 07:00 | 126 | 00:00 | Ullahpara | 139 | 03:00 | 132 | 12:00
KSRM | 134 | 01:00 | 124 | 13:00 | Ullon | 135 | 04:00 | 125 | 12:00
Kulaura | 137 | 23:00 | 134 | 10:00 | Uttara | 141 | 03:00 | 130 | 10:00
Zigatola | 135 | 04:00 | 126 | 12:00
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7