## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-01-2025 | during | 11-01-2025 | during | 11-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 234.58 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 316 | 327 | 400.37 | 400.37 | 320 | 330 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 259 | 300 | 335 | 335 | 300 | 320 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 12 | 13 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 12 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 17 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 32 | 33 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 0 | 8 | 52.19 | 52.19 | 34 | 34 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 77 | 51 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 63 | 50 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 17 | 17 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 0 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | Machine problem
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 7401.63 | 5842.27 | 1283 | 1264 | 4022.99 | 4001.99 | 2985.35 | 2994.35
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0.01 | 0.01 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 14 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 26 | 30 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 91 | 151 | 225 | 225 | 151 | 151 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 33 | 0 | 36 | 37 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 55 | 55 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.42 | 0 | 3.42 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 12 | 0 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1320 | 1224 | 492 | 585 | 1224 | 1224 | 612 | 612 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 66 | 60 | 0 | 4 | 0 | 0 | 0 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1200 | 1200 | 785 | 865 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 5102.36 | 4873.22 | 1479 | 1672 | 4045.14 | 4023.72 | 3299.15 | 3277.73
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 182 | 189 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | schedule outage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 44 | 42 | 46.94 | 46.94 | 45 | 45 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 55 | 55 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 189 | 182 | 195 | 195 | 185 | 185 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 145 | 145 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 46 | 46 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 58 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 17 | 20.83 | 20.83 | 18 | 18 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 10 | 0 | 9 | 9 | 113 | 113 | Fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 4 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 62 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 676 | 618 | 1578.97 | 1528.97 | 1510.2 | 1460.2
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 7 | 23 | 210 | 210 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 19 | 200 | 200 | 19 | 19 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 56 | 55 | 115 | 115 | 65 | 65 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.42 | 0 | 20.08 | 0 | 20.08 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654.5 | 654.21 | 127.42 | 97 | 623.48 | 601.5 | 202.48 | 180.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 44 | 44 | 0 | 0 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 0 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 50 | 86 | 86 | 50 | 50 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 135 | 133 | 135 | 135 | 135 | 135 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 13 | 13 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 341 | 341 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 337 | 332 | 400 | 400 | 372 | 372 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 346 | 350 | 383 | 383 | 353 | 353 | FGMO
Sylhet Area Total |  |  |  |  | 2411 | 2370.57 | 1068 | 1030 | 1587.5 | 1587.5 | 1088.01 | 1088.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 905 | 906 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 288 | 318 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 77.83 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 617 | 617 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3743 | 3686.2 | 1270.83 | 1224 | 3239 | 3169 | 2177.01 | 2107.01
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 135 | 135 | 135 | 135 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 640 | 1100 | 1244 | 1244 | 1244 | 1244 | -
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.47 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1328.47 | 1774 | 2176.12 | 2176.12 | 2173 | 2173
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 162 | 188 | 214 | 214 | 190 | 190 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 196 | 220 | 220 | 220 | 200 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 205 | 221 | 220 | 220 | 200 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 8.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 0 | 0 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 3.11 | 0 | 3.9 | 0 | 3.9 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 604 | 755 | 1347.54 | 1347.54 | 800 | 800 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 55.7 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 100 | 100 | 90 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3575.55 | 3393.2 | 1321.31 | 1392.5 | 2671.64 | 2522.74 | 2007.9 | 1899
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 71 | 70 | 70 | 75 | 75 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 210 | 210 | 210 | 210 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.4 | 0 | 4 | 0 | 4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 12 | 0 | 12 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 151 | 0 | 135.39 | 0 | 135.39 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 466.4 | 281 | 679.39 | 528 | 664.4 | 513.01
System Total |  |  |  |  | 29109.24 | 26932.25 | 9020.43 | 9352.5 | 20624.23 | 20139.54 | 16107.5 | 15692.81
Forecast Scenario (11-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8200 |  | 0 |  | 8200
|  |  |  | 1:00 | 7740 |  | 0 |  | 7740
|  |  |  | 2:00 | 7440 |  | 0 |  | 7440
|  |  |  | 3:00 | 7010 |  | 0 |  | 7010
|  |  |  | 4:00 | 6530 |  | 0 |  | 6530
|  |  |  | 5:00 | 6600 |  | 0 |  | 6600
|  |  |  | 6:00 | 7135 |  | 0 |  | 7135
|  |  |  | 7:00 | 7654 |  | 0 |  | 7654
|  |  |  | 8:00 | 8500 |  | 0 |  | 8500
|  |  |  | 9:00 | 8970 |  | 0 |  | 8970
|  |  |  | 10:00 | 8960 |  | 0 |  | 8960
|  |  |  | 11:00 | 9175 |  | 0 |  | 9175
|  |  |  | 12:00 | 9265 |  | 0 |  | 9265
|  |  |  | 13:00 | 9680 |  | 0 |  | 9680
|  |  |  | 14:00 | 9440 |  | 0 |  | 9440
|  |  |  | 15:00 | 8765 |  | 0 |  | 8765
|  |  |  | 16:00 | 8480 |  | 0 |  | 8480
|  |  |  | 17:00 | 9000 |  | 0 |  | 9000
|  |  |  | 18:00 | 10550 |  | 0 |  | 10550
|  |  |  | 18:30 | 10575 |  | 0 |  | 10575
|  |  |  | 19:00 | 10600 |  | 0 |  | 10600
|  |  |  | 19:30 | 10560 |  | 0 |  | 10560
|  |  |  | 20:00 | 10280 |  | 0 |  | 10280
|  |  |  | 21:00 | 10080 |  | 0 |  | 10080
|  |  |  | 22:00 | 9500 |  | 0 |  | 9500
|  |  |  | 23:00 | 9000 |  | 0 |  | 9000
Probable Maximum Temperature: |  |  | 26.00°C
Probable Maximum Demand at Day Peak: |  |  | 9265.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 10600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 208.554 MKWHr.
Yesterday (10-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 24.30°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 715.67
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 17.6698 | Peak Hour Flow: |  | 906.00 MW at 19:30 hrs.
Energy Flow from West to East |  | 6142728000 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 12.6343 | Peak Hour Flow: |  | 755.00 MW at 19:30 hrs.
Power Flow during Peak Demand |  | 750 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.2336 | Peak Hour Flow: |  | 58.00 MW at 19:30 hrs.
Maximum Power Flow |  | 881 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 31.5377 | Peak Hour Flow: |  | 1719.00 MW at 19:30 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-01-2025 | [28 empty] | Date: | 10-01-2025 | [28 empty] | Date: | 10-01-2025 | [28 empty] | Date: | 10-01-2025 | [28 empty] | Date: | 10-01-2025 | [18 empty] | Date: | 10-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 150.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 0.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 50.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 270 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 750 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 484 | 0 | 51 | 0 | 189 | 0 | 0 | 0 | 29 | 182 | 45 | 0 | 50 | 0 | 0 | 16 | 0 | 56 | 0 | 0 | 0 | 290 | 320 | 333 | 15 | 30 | 0 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 135 | 0 | 17 | 19 | 6 | 0 | 0 | 0 | 4944 | 905 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 140 | 0 | 187 | 0 | 0 | 0 | 0 | 5.5 | 160 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 940 | 0 | 3936.5 | 8880.5 | 93.5
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 273 | 0 | 0 | 0 | 26 | 335 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 679 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 403 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 181 | 45 | 0 | 50 | 0 | 0 | 16 | 0 | 50 | 0 | 0 | 0 | 285 | 320 | 333 | 15 | 30 | 0 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 135 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 4615 | 717 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 140 | 0 | 187 | 0 | 0 | 0 | 0 | 5.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 890 | 0 | 3688.5 | 8303.5 | 93.49
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 265 | 0 | 0 | 0 | 26 | 335 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 707 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 330 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 181 | 45 | 0 | 50 | 0 | 0 | 16 | 0 | 50 | 0 | 0 | 0 | 265 | 320 | 333 | 15 | 30 | 0 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 135 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 4528 | 718 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 140 | 0 | 185 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 220 | 0 | 750 | 0 | 3460.5 | 7988.5 | 93.49
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 271 | 0 | 0 | 0 | 29 | 335 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 576 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 295 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 181 | 45 | 0 | 50 | 0 | 0 | 16 | 0 | 46 | 0 | 0 | 0 | 280 | 320 | 333 | 15 | 30 | 0 | 2 | 163 | 13 | 0 | 5 | 25 | 0 | 0 | 135 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 4330 | 718 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 140 | 0 | 182 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 540 | 0 | 3245.5 | 7575.5 | 93.49
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 301 | 0 | 0 | 0 | 29 | 335 | 0 | 0 | 0 | 0 | 10 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 577 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 11 | 189 | 5 | 0 | 50 | 0 | 0 | 16 | 0 | 44 | 0 | 0 | 0 | 295 | 280 | 333 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 25 | 0 | 0 | 135 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 4136 | 530 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 140 | 0 | 180 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 540 | 0 | 3054.5 | 7190.5 | 93.49
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 266 | 0 | 0 | 0 | 30 | 335 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 580 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 295 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 5 | 181 | 5 | 0 | 50 | 0 | 0 | 16 | 0 | 48 | 0 | 0 | 0 | 305 | 240 | 333 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 25 | 0 | 0 | 135 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 4065 | 531 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 140 | 0 | 179 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 540 | 0 | 3054.5 | 7119.5 | 93.48
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 304 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 642 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 296 | 0 | 5 | 0 | 112 | 0 | 0 | 0 | 5 | 197 | 20 | 0 | 50 | 0 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 305 | 222 | 365 | 5 | 30 | 0 | 2 | 163 | 13 | 0 | 5 | 25 | 0 | 0 | 135 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 4288 | 530 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 180 | 0 | 182 | 0 | 0 | 0 | 0 | 5.5 | 170 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 560 | 0 | 3078.5 | 7366.5 | 93.48
07:00 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 313 | 0 | 0 | 0 | 33 | 335 | 0 | 0 | 1 | 0 | 13 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 646 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 298 | 1 | 5 | 0 | 145 | 0 | 0 | 0 | 18 | 212 | 38 | 0 | 50 | 0 | 0 | 16 | 0 | 46 | 0 | 2 | 0 | 290 | 210 | 380 | 8 | 30 | 0 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 135 | 0 | 0 | 0 | 19 | 0 | 0.76 | 0 | 4418.76 | 530 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.59 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.59 | 150 | 0 | 181 | 0 | 190 | 0 | 0 | 0 | 0.06 | 5.5 | 163 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.02 | 0 | 150 | 6 | 100 | 180 | 0 | 600 | 0 | 3006.76 | 7425.52 | 93.49
08:00 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 305 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 7 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 40 | 703 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 292 | 3 | 29 | 0 | 182 | 0 | 0 | 0 | 29 | 188 | 41 | 0 | 50 | 0 | 0 | 16 | 0 | 44 | 0 | 16 | 0 | 295 | 210 | 379 | 15 | 30 | 0 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 135 | 0 | 0 | 3 | 10 | 0 | 9.14 | 0 | 4270.14 | 810 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.25 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 9.14 | 150 | 0 | 182 | 0 | 193 | 0 | 0 | 0 | 0.54 | 5.5 | 163 | 72 | 0 | 5 | 0 | 0 | 0 | 0.8 | 24 | 0.14 | 0 | 200 | 5 | 100 | 180 | 0 | 690 | 0 | 3529.37 | 7799.51 | 93.48
09:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 275 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 16 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 35 | 790 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 398 | 13 | 43 | 0 | 184 | 0 | 0 | 0 | 27 | 181 | 45 | 0 | 50 | 0 | 0 | 16 | 0 | 42 | 0 | 36 | 0 | 285 | 200 | 347 | 15 | 30 | 0 | 2 | 163 | 13 | 0 | 50 | 25 | 0 | 0 | 135 | 0 | 35 | 19 | 10 | 1 | 9.14 | 0 | 4502.14 | 811 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.35 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 26.32 | 162 | 0 | 192 | 0 | 193 | 0 | 0 | 0 | 1.48 | 5.5 | 200 | 73 | 0 | 14 | 0 | 0 | 0 | 1.4 | 62 | 0.26 | 0 | 200 | 3 | 140 | 220 | 0 | 780 | 0 | 3880.31 | 8382.45 | 93.48
10:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 300 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 23 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 0 | 36 | 776 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 401 | 16 | 43 | 0 | 185 | 0 | 0 | 0 | 29 | 182 | 45 | 0 | 50 | 0 | 0 | 5 | 0 | 44 | 0 | 53 | 0 | 275 | 216 | 346 | 15 | 30 | 0 | 2 | 120 | 13 | 0 | 10 | 25 | 0 | 0 | 135 | 0 | 35 | 19 | 10 | 2 | 13.66 | 0 | 4490.66 | 811 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.26 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 41.27 | 184 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 3.32 | 5.5 | 210 | 72 | 0 | 21 | 0 | 0 | 0 | 4 | 101 | 0.4 | 0 | 150 | 3 | 140 | 180 | 0 | 700 | 0 | 3723.75 | 8214.41 | 93.47
11:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 324 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 27 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 26 | 0 | 29 | 785 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 420 | 19 | 43 | 0 | 189 | 0 | 0 | 0 | 29 | 212 | 41 | 0 | 50 | 0 | 0 | 5 | 0 | 52 | 0 | 64 | 0 | 280 | 230 | 393 | 15 | 30 | 0 | 2 | 120 | 13 | 0 | 10 | 0 | 0 | 0 | 135 | 0 | 38 | 19 | 7 | 2 | 40.59 | 0 | 4649.59 | 905 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.1 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 50.89 | 140 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 2.88 | 5.5 | 210 | 72 | 0 | 28 | 0 | 0 | 0 | 4.9 | 135 | 0.46 | 0 | 165 | 3 | 140 | 180 | 0 | 640 | 0 | 3804.73 | 8454.32 | 93.47
12:00 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 450 | 259 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 28 | 0 | 12 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 26 | 0 | 36 | 785 | 0 | 0 | 14 | 0 | 0 | 91 | 0 | 0 | 0 | 492 | 19 | 43 | 0 | 189 | 0 | 0 | 0 | 29 | 182 | 44 | 4 | 50 | 0 | 10 | 5 | 0 | 58 | 0 | 62 | 0 | 0 | 346 | 337 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 135 | 0 | 56 | 19 | 7 | 2 | 43.42 | 0 | 4633.42 | 905 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.83 | 0 | 0 | 604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 55.7 | 162 | 0 | 196 | 0 | 205 | 0 | 0 | 0 | 3.11 | 5.5 | 210 | 70 | 0 | 30 | 0 | 0 | 0 | 5.4 | 151 | 0.47 | 0 | 307 | 4 | 140 | 220 | 0 | 640 | 17 | 4387.01 | 9020.43 | 93.47
13:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 72 | 17 | 0 | 450 | 266 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 29 | 0 | 12 | 12 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 26 | 0 | 36 | 845 | 0 | 0 | 14 | 0 | 0 | 151 | 0 | 0 | 0 | 590 | 18 | 43 | 0 | 189 | 0 | 0 | 0 | 29 | 183 | 44 | 18 | 50 | 0 | 27 | 16 | 0 | 66 | 0 | 59 | 0 | 0 | 346 | 289 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 132 | 2 | 65 | 19 | 7 | 2 | 40.09 | 0 | 4959.09 | 905 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.38 | 0 | 0 | 662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 54.7 | 183 | 0 | 197 | 0 | 204 | 0 | 0 | 0 | 3.12 | 5.5 | 210 | 70 | 0 | 29 | 0 | 0 | 0 | 5.2 | 149 | 0.49 | 0 | 307 | 4 | 140 | 220 | 0 | 920 | 54 | 4728.39 | 9687.48 | 93.46
14:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 269 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 25 | 0 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 26 | 0 | 36 | 850 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 582 | 15 | 10 | 0 | 78 | 0 | 0 | 0 | 21 | 182 | 41 | 0 | 50 | 0 | 0 | 16 | 0 | 60 | 0 | 51 | 0 | 0 | 316 | 290 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 10 | 0 | 0 | 0 | 132 | 0 | 18 | 19 | 10 | 2 | 33.84 | 0 | 4216.84 | 905 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.64 | 0 | 0 | 578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 45.92 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 2.73 | 5.5 | 210 | 70 | 0 | 23 | 0 | 0 | 0 | 4.6 | 122 | 0.41 | 0 | 170 | 4 | 100 | 180 | 0 | 820 | 0 | 4039.8 | 8256.64 | 93.46
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 277 | 0 | 0 | 0 | 33 | 38 | 0 | 0 | 19 | 0 | 12 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 0 | 36 | 851 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 451 | 12 | 10 | 0 | 78 | 0 | 0 | 0 | 5 | 183 | 41 | 0 | 50 | 0 | 0 | 16 | 0 | 56 | 0 | 34 | 0 | 0 | 316 | 300 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 11 | 0 | 0 | 0 | 132 | 0 | 18 | 19 | 15 | 1 | 23.18 | 0 | 4031.18 | 717 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.22 | 0 | 0 | 461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 31.19 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 2.45 | 5.5 | 210 | 70 | 0 | 17 | 0 | 0 | 0 | 3.3 | 90 | 0.27 | 0 | 150 | 4 | 100 | 180 | 0 | 700 | 0 | 3498.93 | 7530.11 | 93.46
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 285 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 10 | 0 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 26 | 0 | 32 | 850 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 400 | 7 | 10 | 0 | 78 | 0 | 0 | 0 | 5 | 185 | 41 | 0 | 50 | 0 | 0 | 16 | 0 | 54 | 0 | 15 | 0 | 0 | 316 | 300 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 10 | 0 | 0 | 0 | 131 | 0 | 18 | 19 | 16 | 0 | 8.7 | 0 | 3909.7 | 717 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.77 | 0 | 0 | 461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 11.72 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0.91 | 0 | 175 | 70 | 0 | 8 | 0 | 0 | 0 | 1.5 | 43 | 0.14 | 0 | 196 | 4 | 100 | 180 | 0 | 700 | 0 | 3377.04 | 7286.74 | 93.46
17:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 256 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 2 | 0 | 14 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 38 | 892 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 500 | 1 | 10 | 0 | 78 | 0 | 0 | 0 | 5 | 182 | 41 | 0 | 50 | 0 | 0 | 16 | 0 | 54 | 0 | 2 | 0 | 0 | 316 | 302 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 10 | 0 | 0 | 0 | 131 | 0 | 18 | 19 | 19 | 0 | 1.39 | 0 | 4005.39 | 884 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.12 | 0 | 0 | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.13 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0.2 | 5.5 | 210 | 71 | 0 | 1 | 0 | 0 | 0 | 0.2 | 7 | 0.03 | 0 | 307 | 5 | 100 | 180 | 0 | 690 | 0 | 3693.18 | 7698.57 | 93.45
18:00 | 0 | 26 | 8 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 5 | 0 | 40 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 450 | 317 | 0 | 0 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 0 | 0 | 6 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 38 | 930 | 0 | 0 | 4 | 0 | 3 | 151 | 0 | 0 | 0 | 567 | 0 | 28 | 0 | 182 | 0 | 0 | 0 | 13 | 190 | 41 | 27 | 50 | 7 | 2 | 16 | 0 | 54 | 0 | 0 | 0 | 0 | 353 | 373 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 133 | 0 | 55 | 19 | 20 | 0 | 0 | 0 | 4740 | 904 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 186 | 0 | 177 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 140 | 220 | 0 | 750 | 0 | 4174.5 | 8914.5 | 93.45
19:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 292 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 37 | 868 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 585 | 0 | 51 | 0 | 182 | 0 | 0 | 0 | 29 | 183 | 42 | 0 | 70 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 0 | 320 | 298 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 133 | 0 | 55 | 19 | 23 | 0 | 0 | 0 | 4620 | 905 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 215 | 0 | 203 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1030 | 0 | 4565.5 | 9185.5 | 93.45
19:30 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 300 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 37 | 865 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 585 | 0 | 51 | 0 | 182 | 0 | 0 | 0 | 29 | 189 | 42 | 0 | 50 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 0 | 350 | 332 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 133 | 0 | 55 | 19 | 23 | 0 | 0 | 0 | 4681 | 906 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 220 | 0 | 221 | 0 | 0 | 0 | 0 | 8.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1100 | 0 | 4671.5 | 9352.5
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 316 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 37 | 868 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 205 | 42 | 0 | 50 | 0 | 0 | 17 | 0 | 60 | 0 | 0 | 0 | 0 | 350 | 378 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 133 | 0 | 55 | 19 | 23 | 0 | 0 | 0 | 4645 | 905 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 220 | 0 | 220 | 0 | 0 | 0 | 0 | 8.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1090 | 0 | 4660.5 | 9305.5 | 93.45
21:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 302 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 37 | 867 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 190 | 45 | 0 | 50 | 0 | 0 | 17 | 0 | 60 | 0 | 0 | 0 | 0 | 320 | 345 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 135 | 0 | 55 | 19 | 23 | 0 | 0 | 0 | 4538 | 905 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 220 | 0 | 218 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1090 | 0 | 4666.93 | 9204.93 | 93.44
22:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 288 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 37 | 867 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 524 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 182 | 45 | 0 | 50 | 0 | 0 | 17 | 0 | 60 | 0 | 0 | 0 | 0 | 320 | 347 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 135 | 0 | 35 | 19 | 23 | 0 | 0 | 0 | 4421 | 905 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 669.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 130 | 0 | 220 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1090 | 0 | 4491.89 | 8912.89 | 93.44
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 450 | 300 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 37 | 871 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 451 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 182 | 45 | 0 | 50 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 0 | 300 | 345 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 135 | 0 | 0 | 19 | 23 | 0 | 0 | 0 | 4244 | 905 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1090 | 0 | 4300.11 | 8544.11 | 93.44
Total KWH | 0 | 546240 | 33120 | 0 | 0 | 0 | 0 | 0 | 7725600 | 0 | 0 | 0 | 11520 | 0 | 640080 | 0 | 0 | 0 | 9800 | 136800 | 396000 | 0 | 9804000 | 6965236 | 0 | 0 | 29131 | 762800 | 2706683 | 0 | 0 | 184784 | 6000 | 297600 | 336600 | 0 | 0 | 76527 | 0 | 0 | 0 | 219840 | 0 | 0 | 0 | 0 | 0 | 21598 | 751140 | 0 | 899040 | 18639999.9 | 0 | 0 | 40800 | 0 | 18400 | 2535993 | 0 | 0 | 0 | 10461817 | 125280 | 854734 | 1672 | 3445818 | 0 | 0 | 0 | 522240 | 4585000 | 942336 | 83520 | 1209610 | 18720 | 59640 | 360040 | 0 | 1233600 | 0 | 399364 | 0 | 3246930 | 7030400 | 8532000 | 164376 | 337000 | 0 | 58320 | 3729764 | 165600 | 0 | 855360 | 260448 | 0 | 0 | 3216580 | 9000 | 582000 | 290400 | 341760 | 11400 | 221280 | 0 | 107151340.9 | 17669818 | 6836256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 484560 | 0 | 0 | 12634311 | 0 | 0 | 0 | 0 | 0 | 0 | 14336 | 0 | 0 | 0 | 560660 | 0 | 328496 | 4238273 | 0 | 3934300 | 0 | 4665318 | 0 | 0 | 0 | 20580 | 134982 | 4876000 | 1696145 | 36521 | 176093 | 0 | 0 | 0 | 31520.04 | 887040 | 3018 | 0 | 5389000 | 136883 | 3119000 | 5206150 | 0 | 20072727.27 | 64800 | 93216787.31 | 200368128.21

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 10-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 9020.43 | MW | 12:00 Hr. | Energy Generated |  |  | 200368.1282 |  | MWHr
Day Peak Demand |  |  | 9020.43 | MW | 12:00 Hr. | Energy Unserverd |  |  | 38 |  | MWHr
Evening Peak Generation |  |  | 9352.5 | MW | 19:30 Hr. | Energy Demand |  |  | 200406.1282 |  | MWHr
Evening Peak Demand |  |  | 9352.5 | MW | 19:30 Hr.
Minimum Generation of the Day |  |  | 7119.5 | MW | 05:00 Hr.
Maximum Generation of the Day |  |  | 9687.48 | MW | 13:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 28994.519 | 0 | 1412.691 | 0 | 0 | 184.784 | 0 | 0 | 30591.994 | Gas | 100559.03 | Gas | 359587607.34
Chattogram Zone |  |  | 3435.033 | 29101.8169 | 135.727 | 0 | 751.14 | 146.878 | 0 | 219.84 | 33790.4349 | Coal | 61135.6892 | Coal | 434133718.3191
Cumilla Zone |  |  | 11919.778 | 0 | 163.552 | 0 | 0 | 399.364 | 1233.6 | 0 | 13716.294 | HFO | 2709.027 | HFO | 51758474.12
Mymensingh Zone |  |  | 341.76 | 0 | 881.4 | 0 | 0 | 232.68 | 0 | 0 | 1455.84 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 27596.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27596.778 | Hydro | 751.14 | Hydro | 75114
Khulna Zone |  |  | 6836.256 | 0 | 0 | 0 | 0 | 484.56 | 17669.818 | 0 | 24990.634 | Solar | 3455.673 | Solar | 53814779.104
Barishal Zone |  |  | 8462.033 | 25461.7273 | 64.8 | 0 | 0 | 3.018 | 0 | 0 | 33991.5783 | Import | 31537.729 | Import | 160075745.21
Rajshahi Zone |  |  | 12972.873 | 0 | 14.336 | 0 | 0 | 909.736 | 12634.311 | 0 | 26531.256 | Wind | 219.84 | Wind | 3429504
Rangpur Zone |  |  | 0 | 6572.145 | 36.521 | 0 | 0 | 1094.653 | 0 | 0 | 7703.319
Total |  |  | 100559.03 | 61135.6892 | 2709.027 | 0 | 751.14 | 3455.673 | 31537.729 | 219.84 | 200368.1282
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 359587607.34 |  | Hydro | 75114
|  |  | Coal | 434133718.3191 |  | Solar | 53814779.104
|  |  | HFO | 51758474.12 |  | Import | 160075745.21
|  |  | HSD | 0 |  | Wind | 3429504
|  |  |  | Total: | 1062874942.0931 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Barapukuria TPP Unit-2 |  |  | 85
| 3 | Khulna 330 MW CCPP GT |  |  | 220
| 4 | Khulna 330 MW CCPP ST |  |  | 110
| 5 | Siddhirgonj 210 MW TPP |  |  | 115
| 6 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 7 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1044 |  |  |  | Total | 35.09
|  |  | Total Unavailable Capacity |  |  |  | 1079.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3016
|  |  | Chattogram |  | 0 |  | 1012
|  |  | Cumilla |  | 0 |  | 805
|  |  | Mymensingh |  | 0 |  | 833
|  |  | Sylhet |  | 0 |  | 338
|  |  | Khulna |  | 0 |  | 1105
|  |  | Barishal |  | 0 |  | 283
|  |  | Rajshahi |  | 0 |  | 899
|  |  | Rangpur |  | 0 |  | 598
|  |  | Total |  | 0 |  | 8889
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:06 | 17:17 | Shahjadpur 132/33kV S/S Main Bus Scheduled S/D Due to Bus Maintenance | [7 empty] | 15.0MW load interrup.
08:07 | 17:48 | Pabna- Shahjadpur 132kV Ckt-1 Scheduled S/D from Pabna 132/33kV end.
08:16 | 10:39 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Project Work S/D | [7 empty] | 12.0MW load interrup.
08:20 |  | Dohazari 132/33kV S/S Power Transformer -T-1 HT Project Work S/D | [7 empty] | 11.0MW load interrup.
08:20 | 16:15 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Scheduled S/D from Faridpur 132/33kV end Due to Project Work
08:20 | 16:17 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Scheduled S/D from Faridpur 132/33kV end Due to Project Work
08:31 | 16:15 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Project Work S/D from Gopalganj 400/132kV end Due to Project work
08:31 | 16:00 | Bogura-Sirajganj 230 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to Annual
Maintenance and from Sirajgonj 230 end Due to Annual Maintenance work
08:32 | 16:16 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Project Work S/D from Gopalganj 400/132kV end Due to Project work
08:45 |  | Hathazari 230/132/33kV S/S AKSML-02 Scheduled S/D
09:52 | 14:33 | Siddhirganj 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance Work Done By DPDC. | [7 empty] | 15.0MW load interrup.
09:52 |  | BB-BB50mw p/p 132kv ckt S/D.
09:52 | 14:33 | Siddhirganj 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance Work Done By DPDC. | [7 empty] | 15.0MW load interrup.
09:54 | 16:57 | Gopalganj 400/132kV S/S 400kV Bus-02 Project Work S/D
10:12 | 16:32 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to SAS integration
by Project
| 11:12 | Shahmirpur 132/33kV S/S Bus-1 is restored.
11:21 |  | Anlima Energy Ltd. Synchronized
11:22 |  | BB-BB50mw p/p 132kv ckt Syn.
11:47 |  | Summit Bibiana-2 341 MW CCPP was shutdown due to gas shortage. | [7 empty] | 320MW generation interrup.
12:00 |  | Day Peak Generation: 9017 MW.
12:09 | 12:56 | Rahanpur 132/33kV S/S TR-1 404T HT Project Work S/D Due to Transformer makes abnormal sound.
12:09 | 12:54 | Rahanpur 132/33kV S/S TR-1 404T LT Project Work S/D Due to Transformer has abnormal sound.
| 12:50 | Munshiganj 132/33kV S/S Transformer-2 LT is restored.
| 12:50 | Munshiganj 132/33kV S/S Transformer-2 HT is restored.
12:51 | 12:57 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT Scheduled S/D Due to Shift 132kV
B-Bus(Ash-Srrepur Side) to A- Bus(Kaliakore side) Due to avoid over load of 132kV
Bhaluka- Srrepur Line.
| 12:55 | Ramganj 132/33kV S/S Transformer -02 LT is restored.
| 12:55 | Ramganj 132/33kV S/S Transformer -02 HT is restored.
12:56 | 12:56 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D Due to Shift 132kV
B-Bus(Ash-Srrepur Side) to A- Bus(Kaliakore side) Due to avoid over load of 132kV
Bhaluka- Srrepur Line permission with NLDC
13:24 |  | Ashuganj 51 MW PP (Midland) Running with remarks:- All Engines are running
13:25 |  | Anlima Energy Ltd. Shutdown
14:03 |  | Ashuganj 51 MW PP (Midland) Partially Running with remarks:- NLDC demand 10 MW
| 16:52 | Meghnaghat-Shyampur 230kV Ckt-2 is restored.
| 17:17 | Shahjadpur 132/33kV S/S Main Bus is restored.
17:29 |  | Anlima Energy Ltd. Synchronized
17:48 |  | Ashuganj 150MW PP (Midland) Synchronized
17:58 |  | Ashuganj 150MW PP (Midland) Shutdown
18:14 |  | Anlima Energy Ltd. Shutdown
18:30 |  | Ashuganj 51 MW PP (Midland) Running with remarks:- All engines are running.
| 19:16 | Kabirpur -Kodda 132kV Ckt-1 is restored.
19:17 |  | Ishurdi-Ghorasal GIS 230KV Ckt-2 was switched on
| 19:22 | Ghorasal- Ishwardi 230 kV Ckt-2 is restored.
19:30 |  | Evening Peak Gen. 9352 MW
22:10 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
22:10 |  | Sirajgonj 225MW CCPP Unit-2 ST Shutdown with remarks:- None
22:20 |  | Sirajgonj 225MW CCPP Unit-2 GT Shutdown with remarks:- None
22:20 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
22:20 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- GT
02:24 |  | Gopalganj(N)-Rampal Ckt-1 Forced S/D from Rampal 400/230kV end Due to Due to high Voltage
( Bus voltage -419KV )
02:28 | 07:52 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Forced S/D
02:46 |  | Ashuganj 51 MW PP (Midland) Partially Running with remarks:- NLDC demand is 05 MW at 02:23
05:00 |  | Minimum Generation = 6,594MW
06:01 |  | Ashuganj 51 MW PP (Midland) Partially Running with remarks:- One (01) Nos Engine stop
for maintenance.
06:25 |  | Kabirpur -Kodda 132kV Ckt-1 Project Work S/D from Kabirpur 132/33kV end Due to
Re-Conductoring work safety purpose.
06:38 |  | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to 33 KV BUS chainging work purpose. | [7 empty] | 40.0MW load interrup
06:39 |  | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to 33 KV BUS chainging work purpose. | [7 empty] | 70.0MW load interrup
06:40 |  | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33 KV BUS chainging work purpose. | [7 empty] | 70.0MW load interrup
06:40 |  | Bhandaria 132/33kV S/S Main Bus Bar Project Work S/D Due to G2G project work. | [7 empty] | 24.0MW load interrup
06:40 |  | Bhandaria 132/33kV S/S Transformer-1 HT Project Work S/D Due to G2G project work | [7 empty] | 24.0MW load interrup
06:40 |  | Bhandaria 132/33kV S/S Transformer-1 LT Project Work S/D Due to G2G project work. | [7 empty] | 24.0MW load interrup
06:40 |  | Bhandaria 132/33kV S/S Transformer-1 LT Project Work S/D Due to G2G project work. | [7 empty] | 24.0MW load interrup
06:40 |  | Barishal-Bhandaria 132 kV Ckt-1 Project Work S/D from Bhandaria 132/33kV end Due to G2G | [7 empty] | 24.0MW load
|  | project work. and from Barishal 132/33kV end Due to Due to Bhandaria End Main Bus | [7 empty] | interrup. Bhandaria
|  | Maintenance | [7 empty] | 132/33kV end and
27.0MW load
interrup. Barishal
132/33kV end
06:42 |  | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to Ordered
by ALDC khulna. Bhandaria grid 132kV main bus bar maintenance work.
07:11 |  | Bogura 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Red hot maintenance work.
07:11 |  | Bogura 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Red hot maintenance work.
07:17 |  | Khulshi 132/33kV S/S 405T (T1) LT Scheduled S/D Due to Annual Maintenance
07:18 |  | Khulshi 132/33kV S/S 405T (T1) HT Scheduled S/D Due to Annual Maintenance
07:40 |  | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Patuakhali 132/33kV end Due to Annual
Maintenance-2025 and from Payra 400/132/33kV end Due to Annual maintenance
07:51 |  | Agargaon 230/132kV S/S Auxiliary Tr-2 LT Scheduled S/D Due to Annual Maintenance
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 327 | 7725600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9804000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 6965236 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 2706683 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 9800 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 29131 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13 | 297600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 336600 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 396000 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 33 | 762800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 8 | 33120 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 51 | 640080 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 546240 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 136800 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 184784 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 0 | 11520 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 6000 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 1264 | 30591994
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125280 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 40800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 751140 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 151 | 2535993 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 18400 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 0 | 37 | 899040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 21598 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 76527 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 585 | 10461817 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 4 | 219840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 865 | 18639999.9 | -
Chattogram Area Total |  |  |  |  | 4873.22 | 1672 | 33790434.9
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 189 | 4585000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 42 | 942336 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 522240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 182 | 3445818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 854734 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 1672 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1209610 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 18720 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 58 | 1233600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 360040 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 59640 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 83520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 399364 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 618 | 13716294
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 23 | 341760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 290400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 55 | 582000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 221280 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 9000 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 97 | 1455840
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 0 | 337000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3729764 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 164376 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 58320 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 0 | 260448 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 50 | 855360 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 133 | 3216580 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 165600 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 3246930 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 332 | 8532000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 350 | 7030400 | FGMO
Sylhet Area Total |  |  |  |  | 2370.57 | 1030 | 27596778
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 906 | 17669818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 318 | 6836256 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 484560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1224 | 24990634
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 136883 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 3119000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 20072727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5206150 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 64800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5389000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3018 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1774 | 33991578.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 188 | 4238273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 220 | 3934300 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 221 | 4665318 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 8.5 | 134982 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 14336 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 755 | 12634311 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 328496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 560660 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1392.5 | 26531256
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 71 | 1696145 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4876000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31520.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 36521 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 176093 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 887040 | -
Rangpur Area Total |  |  |  |  | 950 | 281 | 7703319.04
Eastern Grid Total |  |  |  |  | 16637.75 | 4681 | 107151340.9
Western Grid Total |  |  |  |  | 10294.5 | 4671.5 | 93216787.31
National Grid Total |  |  |  |  | 26932.25 | 9352.5 | 200368128.21
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-01-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6003.81 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 2885.2 | MW
i) Dhaka area |  |  | 3015.51 |  | MW | i) Khulna area |  |  |  | 1105 | MW
ii) Chattogram area |  |  | 1012.3 |  | MW | ii) Barishal area |  |  |  | 283.4 | MW
iii) Cumilla area |  |  | 805 |  | MW | iii) Rajshahi area |  |  |  | 898.8 | MW
iv) Mymensingh area |  |  | 833 |  | MW | iv) Rangpur area |  |  |  | 598 | MW
v) Sylhet area |  |  | 338 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 8889.01 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 5 | 11:00 | 67 | Jaldhaka | 54 | 18:00 | 133 | Purbasadipur | 105 | 12:00
2 | AKSML | 49.3 | 23:00 | 68 | Jamalpur | 91 | 18:30 | 134 | Rahanpur | 0 | 00:00
3 | Aftabnagar | 24 | 12:00 | 69 | Jashore | 94 | 13:00 | 135 | Rahim | 20 | 11:00
4 | Agargaon | 73 | 13:00 | 70 | Jhenaidah | 92 | 13:00 | 136 | Rajbari | 50 | 18:00
5 | Agrabad | 50 | 18:00 | 71 | Joydebpur | 95 | 12:00 | 137 | Rajendrapur | 88 | 13:00
6 | Amnura | 49 | 12:00 | 72 | Joypurhat | 40 | 09:00 | 138 | Rajshahi | 92 | 13:00
7 | Ashuganj | 49 | 00:00 | 73 | Juldah | 8 | 00:00 | 139 | Rajshahi-230 | 54 | 13:00
8 | BSRM | 203 | 01:00 | 74 | KSRM | 38 | 18:30 | 140 | Ramganj | 76 | 13:00
9 | Bagerhat | 68 | 20:00 | 75 | Kabirpur | 169 | 00:00 | 141 | Rampur | 25 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 42 | 13:00 | 142 | Rangamati | 14 | 18:00
11 | Bakulia | 55 | 12:00 | 77 | Kallyanpur | 75 | 13:00 | 143 | Rangpur | 112 | 13:00
12 | Banani | 32 | 12:00 | 78 | Kalurghat | 18 | 00:00 | 144 | Ruppur | 4 | 10:00
13 | Bangabhaban | 3 | 10:00 | 79 | Kamrangirchar | 41.3 | 00:00 | 145 | SSM | 15 | 01:00
14 | Barapukuria | 41 | 09:00 | 80 | Kaptai | N/A | N/A | 146 | Saidpur | 74 | 09:00
15 | Barguna | 14 | 22:00 | 81 | Kazla | 76 | 13:00 | 147 | Satkhira | 88 | 08:00
16 | Barishal | 82 | 13:00 | 82 | Keranigonj | 46 | 13:00 | 148 | Satmasjid | 72 | 13:00
17 | Barishal-230 | 58 | 20:00 | 83 | Khagrachori | 24 | 13:00 | 149 | Savar | 108 | 00:00
18 | Baroaulia | 48 | 11:00 | 84 | Khulna | 69 | 13:00 | 150 | SevenRings | 6.68 | 00:00
19 | Baroirhat | 49 | 13:00 | 85 | Khulshi | 137 | 12:00 | 151 | ShahCement | 32 | 00:00
20 | Bashundhara | 129 | 13:00 | 86 | Kishoreganj | 116 | 13:00 | 152 | Shahjadpur | 57 | 19:00
21 | BashundharaCement | 8 | 00:00 | 87 | Kodda | 192 | 00:00 | 153 | Shahjibazar | 68 | 00:00
22 | Beanibazar | 44 | 13:00 | 88 | Kulaura | 27 | 13:00 | 154 | Shahmirpur | 39 | 00:00
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 46 | 18:00 | 155 | Shariatpur | 52 | 21:00
24 | Bhaluka | 96 | 12:00 | 90 | Kushtia | 102 | 13:00 | 156 | Sherpur | 110 | 18:00
25 | Bhandaria | 35 | 21:00 | 91 | Lalbag | 57 | 00:00 | 157 | Shikalbaha | 15 | 10:00
26 | Bhangura | 22 | 13:00 | 92 | Lalmonirhat | 40 | 18:00 | 158 | Shitalakhya | 44.1 | 13:00
27 | Bheramara(GK) | 43.03 | 10:00 | 93 | MI_Cement | 17.5 | 11:00 | 159 | Sholosohor | 25 | 12:00
28 | Bhulta | 226 | 00:00 | 94 | Madanganj | 26 | 00:00 | 160 | Shyampur | 136 | 15:00
29 | Bog-Sherpur | 50 | 09:00 | 95 | Madaripur | 65 | 21:00 | 161 | Siddhirganj | 73 | 00:00
30 | Bogura | 87 | 13:00 | 96 | Madartek | 64 | 13:00 | 162 | Sirajganj | 54 | 18:30
31 | Borhanuddin | 51 | 21:00 | 97 | Madunaghat | 36 | 13:00 | 163 | Sonargaon | 70 | 00:00
32 | Brahmanbaria | 107 | 13:00 | 98 | Magura | 42 | 18:00 | 164 | Sreemongol | 49 | 13:00
33 | Cantonment | 78 | 13:00 | 99 | Mahasthangarh | 46 | 18:30 | 165 | Sreepur | 46 | 00:00
34 | Chandpur | 52 | 13:00 | 100 | Manikganj | 94 | 18:30 | 166 | Srinagar | 34.54 | 13:00
35 | Chandraghona | 23 | 18:00 | 101 | Maniknagar | 42 | 13:00 | 167 | Sunamganj | 34 | 18:00
36 | Chapai | 46 | 10:00 | 102 | Matarbari | 31 | 19:00 | 168 | Sylhet | 26 | 13:00
37 | Charsaidpur | 44 | 01:00 | 103 | Matuail | 38 | 00:00 | 169 | Sylhet-132 | 74 | 13:00
38 | Chauddagram | 43 | 12:00 | 104 | Millgate | 63 | 00:00 | 170 | TK | 20.4 | 18:00
39 | Chhatak | 20 | 18:00 | 105 | Mirpur | 94 | 13:00 | 171 | Tangail | 130 | 18:00
40 | Chowmuhani | 148 | 13:00 | 106 | Mirsorai | 7 | 00:00 | 172 | Thakurgaon | 72 | 18:30
41 | Chuadanga | 66 | 13:00 | 107 | Mirzapur | 28 | 21:00 | 173 | Tongi | 70 | 13:00
42 | Coxsbazar | 92 | 18:30 | 108 | Mithapukur | 40 | 18:00 | 174 | Ullahpara | 23 | 16:00
43 | Cumilla(N) | 101 | 20:00 | 109 | Modern | 0 | 00:00 | 175 | Ullon | 43 | 13:00
44 | Cumilla(S) | 117 | 13:00 | 110 | Mogbazar | 68.5 | 12:00 | 176 | Uttara | 48 | 12:00
45 | Daudkandi | 80 | 00:00 | 111 | Mongla | 28 | 00:00 | 177 | UttaraNew | 37 | 13:00
46 | Dhaka | 18 | 12:00 | 112 | Motijheel | 23 | 13:00 | 178 | Zigatola | 71 | 13:00
47 | Dhamrai | 76 | 00:00 | 113 | Munshiganj | 72 | 13:00
48 | Dhanmondi | 76.6 | 13:00 | 114 | Mymensingh | 172 | 18:00
49 | Dohazari | 58 | 18:30 | 115 | Naogaon | 78 | 09:00
50 | Faridpur | 95 | 20:00 | 116 | Narail | 41 | 18:30
51 | Fatullah | 58 | 00:00 | 117 | Narinda | 35 | 12:00
52 | Fenchuganj | 30 | 12:00 | 118 | Narshingdi | 137 | 20:00
53 | Feni | 68 | 13:00 | 119 | Natore | 100 | 18:30
54 | GPH | 83 | 05:00 | 120 | Nawabganj | 41.8 | 13:00
55 | Ghatail | 26 | 08:00 | 121 | Netrakona | 120 | 08:00
56 | Ghorashal | 6 | 00:00 | 122 | New | 46.7 | 00:00
57 | Ghorashal-230 | 46 | 18:30 | 123 | Niamatpur | 60 | 09:00
58 | Goalpara | 28 | 13:00 | 124 | Noapara | 27 | 19:00
59 | Gollamari | 54 | 13:00 | 125 | PHP | 7 | 06:00
60 | Gopalganj | 73 | 18:30 | 126 | Pabna | 77 | 18:30
61 | Gulshan | 48 | 13:00 | 127 | Palashbari | 70 | 18:30
62 | Halishahar | 39 | 12:00 | 128 | Panchagarh | 43 | 18:30
63 | HaripurSBU | 132 | 03:00 | 129 | Patuakhali | 53.3 | 21:00
64 | Hasnabad | 63 | 12:00 | 130 | Payra | 14 | 12:00
65 | Hathazari | 50 | 12:00 | 131 | Postogola | 34 | 13:00
66 | Ishurdi | 47 | 13:00 | 132 | Purbachal | 16 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8880.5 | 0 |  | 8880.5
1:00 | 8303.5 | 0 |  | 8303.5
2:00 | 7988.5 | 0 |  | 7988.5
3:00 | 7575.5 | 0 |  | 7575.5
4:00 | 7190.5 | 0 |  | 7190.5
5:00 | 7119.5 | 0 |  | 7119.5
6:00 | 7366.5 | 0 |  | 7366.5
7:00 | 7425.52 | 0 |  | 7425.52
8:00 | 7799.51 | 0 |  | 7799.51
9:00 | 8382.45 | 0 |  | 8382.45
10:00 | 8214.41 | 0 |  | 8214.41
11:00 | 8454.32 | 0 |  | 8454.32
12:00 | 9020.43 | 0 |  | 9020.43
13:00 | 9687.48 | 38 |  | 9727.19
14:00 | 8256.64 | 0 |  | 8256.64
15:00 | 7530.11 | 0 |  | 7530.11
16:00 | 7286.74 | 0 |  | 7286.74
17:00 | 7698.57 | 0 |  | 7698.57
18:00 | 8914.5 | 0 |  | 8914.5
19:00 | 9185.5 | 0 |  | 9185.5
19:30 | 9352.5 | 0 |  | 9352.5
20:00 | 9305.5 | 0 |  | 9305.5
21:00 | 9204.93 | 0 |  | 9204.93
22:00 | 8912.89 | 0 |  | 8912.89
23:00 | 8544.11 | 0 |  | 8544.11
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4944 | 3936.5 | 8880.5 | DAILY LOAD CURVE
00:30 | 4779.5 | 3812.5 | 8592
01:00 | 4615 | 3688.5 | 8303.5 | 10-01-2025
01:30 | 4571.5 | 3574.5 | 8146
02:00 | 4528 | 3460.5 | 7988.5
02:30 | 4429 | 3353 | 7782
03:00 | 4330 | 3245.5 | 7575.5
03:30 | 4233 | 3150 | 7383
04:00 | 4136 | 3054.5 | 7190.5
04:30 | 4100.5 | 3054.5 | 7155
05:00 | 4065 | 3054.5 | 7119.5
05:30 | 4176.5 | 3066.5 | 7243
06:00 | 4288 | 3078.5 | 7366.5
06:30 | 4353.38 | 3042.63 | 7396.01
07:00 | 4418.76 | 3006.76 | 7425.52
07:30 | 4344.45 | 3268.065 | 7612.515
08:00 | 4270.14 | 3529.37 | 7799.51
08:30 | 4386.14 | 3704.84 | 8090.98
09:00 | 4502.14 | 3880.31 | 8382.45
09:30 | 4496.4 | 3802.03 | 8298.43
10:00 | 4490.66 | 3723.75 | 8214.41
10:30 | 4570.125 | 3764.24 | 8334.365
11:00 | 4649.59 | 3804.73 | 8454.32
11:30 | 4641.505 | 4095.87 | 8737.375
12:00 | 4633.42 | 4387.01 | 9020.43
12:30 | 4796.255 | 4557.7 | 9353.955
13:00 | 4959.09 | 4728.39 | 9687.48
13:30 | 4587.965 | 4384.095 | 8972.06
14:00 | 4216.84 | 4039.8 | 8256.64
14:30 | 4124.01 | 3769.365 | 7893.375
15:00 | 4031.18 | 3498.93 | 7530.11
15:30 | 3970.44 | 3437.985 | 7408.425
16:00 | 3909.7 | 3377.04 | 7286.74
16:30 | 3957.545 | 3535.11 | 7492.655
17:00 | 4005.39 | 3693.18 | 7698.57
17:30 | 4372.695 | 3933.84 | 8306.535
18:00 | 4740 | 4174.5 | 8914.5
18:30 | 4680 | 4370 | 9050
19:00 | 4620 | 4565.5 | 9185.5
19:30 | 4681 | 4671.5 | 9352.5
20:00 | 4645 | 4660.5 | 9305.5
20:30 | 4591.5 | 4663.715 | 9255.215 |  | Executive Engineer
21:00 | 4538 | 4666.93 | 9204.93 |  | Network Operation Division
21:30 | 4479.5 | 4579.41 | 9058.91
22:00 | 4421 | 4491.89 | 8912.89
22:30 | 4332.5 | 4396 | 8728.5
23:00 | 4244 | 4300.11 | 8544.11

## En-Curve
QF-LDC-12
Date | 10-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2784 | 1841.5 | 905 | 0 | 56 | 514 | 40 | 2604 | 0 | 0 | 110 | 0 | 0 | 26 | 0 | DAILY ENERGY CURVE
00:30 | 2784 | 1808.5 | 811 | 0 | 53 | 484 | 40 | 2528.5 | 0 | 0 | 55 | 0 | 0 | 28 | 0 | 10-01-2025
01:00 | 2784 | 1775.5 | 717 | 0 | 50 | 454 | 40 | 2453 | 0 | 0 | 0 | 0 | 0 | 30 | 0
01:30 | 2784 | 1759 | 717.5 | 0 | 50 | 436 | 40 | 2335 | 0 | 0 | 0 | 0 | 0 | 24.5 | 0 |  | Total Energy | 200.3681 |  | MKWHr
02:00 | 2784 | 1742.5 | 718 | 0 | 50 | 418 | 40 | 2217 | 0 | 0 | 0 | 0 | 0 | 19 | 0 |  | Energy not Served | 0.038 |  | MKWHr
02:30 | 2770 | 1732.5 | 718 | 0 | 48 | 417.5 | 40 | 2029 | 0 | 0 | 0 | 0 | 0 | 27 | 0 |  | Energy Requirement | 200.4061 |  | MKWHr
03:00 | 2756 | 1722.5 | 718 | 0 | 46 | 417 | 40 | 1841 | 0 | 0 | 0 | 0 | 0 | 35 | 0
03:30 | 2722.5 | 1661.5 | 624 | 0 | 45 | 416.5 | 40 | 1841.5 | 0 | 0 | 0 | 0 | 0 | 32 | 0
04:00 | 2689 | 1600.5 | 530 | 0 | 44 | 416 | 40 | 1842 | 0 | 0 | 0 | 0 | 0 | 29 | 0
04:30 | 2665 | 1586.5 | 530.5 | 0 | 46 | 416 | 40 | 1843.5 | 0 | 0 | 0 | 0 | 0 | 27.5 | 0
05:00 | 2641 | 1572.5 | 531 | 0 | 48 | 416 | 40 | 1845 | 0 | 0 | 0 | 0 | 0 | 26 | 0
05:30 | 2685.5 | 1630 | 530.5 | 0 | 50 | 416.5 | 40 | 1866.5 | 0 | 0 | 0 | 0 | 0 | 24 | 0
06:00 | 2730 | 1687.5 | 530 | 0 | 52 | 417 | 40 | 1888 | 0 | 0 | 0 | 0 | 0 | 22 | 0
06:30 | 2711.5 | 1718.5 | 530 | 0 | 49 | 417 | 40 | 1907.5 | 4.51 | 1 | 0 | 0 | 0 | 17 | 0
07:00 | 2693 | 1749.5 | 530 | 0 | 46 | 417 | 40 | 1927 | 9.02 | 2 | 0 | 0 | 0 | 12 | 0
07:30 | 2524.5 | 1791 | 670 | 0 | 45 | 418 | 40 | 2023.5 | 60.015 | 11 | 20.5 | 0 | 0 | 9 | 0
08:00 | 2356 | 1832.5 | 810 | 0 | 44 | 419 | 40 | 2120 | 111.01 | 20 | 41 | 0 | 0 | 6 | 0
08:30 | 2370 | 1851 | 810.5 | 0 | 43 | 419 | 20 | 2280.5 | 189.98 | 27 | 73.5 | 0 | 0 | 6.5 | 0
09:00 | 2384 | 1869.5 | 811 | 0 | 42 | 419 | 0 | 2441 | 268.95 | 34 | 106 | 0 | 0 | 7 | 0
09:30 | 2341 | 1812 | 811 | 0 | 43 | 419.5 | 13 | 2375 | 339.43 | 34 | 106 | 0 | 0 | 4.5 | 0
10:00 | 2298 | 1754.5 | 811 | 0 | 44 | 420 | 26 | 2309 | 409.91 | 34 | 106 | 0 | 0 | 2 | 0
10:30 | 2305.5 | 1762.5 | 858 | 0 | 48 | 419.5 | 26 | 2300.5 | 471.865 | 34 | 107.5 | 0 | 0 | 1 | 0
11:00 | 2313 | 1770.5 | 905 | 0 | 52 | 419 | 26 | 2292 | 533.82 | 34 | 109 | 0 | 0 | 0 | 0
11:30 | 2406 | 1667 | 905 | 0 | 55 | 511.5 | 26 | 2398 | 552.875 | 48.5 | 167.5 | 0 | 0 | 0 | 0
12:00 | 2499 | 1563.5 | 905 | 0 | 58 | 604 | 26 | 2504 | 571.93 | 63 | 226 | 0 | 0 | 0 | 0
12:30 | 2490.5 | 1573 | 905 | 0 | 62 | 633 | 26 | 2723 | 565.455 | 66.5 | 309.5 | 0 | 0 | 0 | 19
13:00 | 2482 | 1582.5 | 905 | 0 | 66 | 662 | 26 | 2942 | 558.98 | 70 | 393 | 0 | 0 | 0 | 38
13:30 | 2365 | 1361.5 | 905 | 0 | 63 | 620 | 26 | 2822 | 513.06 | 52 | 244.5 | 0 | 0 | 0 | 19
14:00 | 2248 | 1140.5 | 905 | 0 | 60 | 578 | 26 | 2702 | 467.14 | 34 | 96 | 0 | 0 | 0 | 0
14:30 | 2275 | 1137 | 811 | 0 | 58 | 519.5 | 26 | 2567 | 399.875 | 25.5 | 74.5 | 0 | 0 | 0 | 0
15:00 | 2302 | 1133.5 | 717 | 0 | 56 | 461 | 26 | 2432 | 332.61 | 17 | 53 | 0 | 0 | 0 | 0
15:30 | 2291 | 1132.75 | 717 | 0 | 55 | 461 | 26 | 2411.5 | 244.175 | 17 | 53 | 0 | 0 | 0 | 0
16:00 | 2280 | 1132 | 717 | 0 | 54 | 461 | 26 | 2391 | 155.74 | 17 | 53 | 0 | 0 | 0 | 0
16:30 | 2284.5 | 1124.25 | 800.5 | 0 | 54 | 511 | 26 | 2530.5 | 90.905 | 17 | 53 | 0 | 0 | 1 | 0
17:00 | 2289 | 1116.5 | 884 | 0 | 54 | 561 | 26 | 2670 | 26.07 | 17 | 53 | 0 | 0 | 2 | 0
17:30 | 2435 | 1310.5 | 894 | 0 | 54 | 614.5 | 28 | 2752 | 13.035 | 45.5 | 156.5 | 0 | 0 | 3.5 | 0
18:00 | 2581 | 1504.5 | 904 | 0 | 54 | 668 | 30 | 2834 | 0 | 74 | 260 | 0 | 0 | 5 | 0
18:30 | 2593.5 | 1545.5 | 904.5 | 0 | 53 | 709 | 30 | 2952 | 0 | 66 | 192.5 | 0 | 0 | 4 | 0
19:00 | 2606 | 1586.5 | 905 | 0 | 52 | 750 | 30 | 3070 | 0 | 58 | 125 | 0 | 0 | 3 | 0
19:30 | 2684 | 1594.5 | 906 | 0 | 58 | 755 | 30 | 3138 | 0 | 58 | 125 | 0 | 0 | 4 | 0
20:00 | 2746 | 1611.5 | 905 | 0 | 60 | 756 | 30 | 3096 | 0 | 25 | 74 | 0 | 0 | 2 | 0
20:30 | 2713 | 1597 | 905 | 0 | 60 | 756.215 | 29 | 3095 | 0 | 25 | 74 | 0 | 0 | 1 | 0
21:00 | 2680 | 1582.5 | 905 | 0 | 60 | 756.43 | 28 | 3094 | 0 | 25 | 74 | 0 | 0 | 0 | 0
21:30 | 2632.5 | 1554.5 | 905 | 0 | 60 | 712.91 | 28 | 3081 | 0 | 21 | 64 | 0 | 0 | 0 | 0
22:00 | 2585 | 1526.5 | 905 | 0 | 60 | 669.39 | 28 | 3068 | 0 | 17 | 54 | 0 | 0 | 0 | 0
22:30 | 2508 | 1511 | 905 | 0 | 59 | 639.5 | 27 | 3033.5 | 0 | 8.5 | 36.5 | 0 | 0 | 0.5 | 0
23:00 | 2431 | 1495.5 | 905 | 0 | 58 | 609.61 | 26 | 2999 | 0 | 0 | 19 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-10 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 419 | 03:00 | 402 | 13:00 | Kaliakoir | 381 | 06:00 | 372 | 02:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 410 | 6:00 | 384 | 12:00 | Madunaghat | 410 | 05:00 | 399 | 14:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 412 | 03:00 | 398 | 13:00 | Meghnaghat | 415 | 05:00 | 399 | 13:00
| Bibiana | 398 | 06:00 | 389 | 12:00 | Payra | 421 | 04:00 | 410 | 18:30
| BIPTC | 408 | 02:00 | 389 | 13:00 | Rahanpur | 414 | 02:00 | 404 | 18:30
| Bogura | 412 | 03:00 | 396 | 13:00 | Rampal | 418 | 04:00 | 399 | 13:00
| Gopalganj | 421 | 05:00 | 400 | 13:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 238 | 03:00 | 229 | 13:00 | Haripur | 236 | 05:00 | 225 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 235 | 07:00 | 226 | 12:00 | Hasnabad | 235 | 00:00 | 221 | 12:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 237 | 04:00 | 229 | 13:00 | Hathazari | 234 | 00:00 | 220 | 12:00
| Ashuganj | 241 | 03:00 | 235 | 13:00 | Ishurdi | 242 | 01:00 | 231 | 12:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 6:00 | 225 | 12:00 | Jhenaidah | 240 | 02:00 | 226 | 12:00
| Baghabari | 243 | 05:00 | 236 | 18:00 | Kaliakoir | 237 | 03:00 | 224 | 12:00 | 230 kV MAX | 250 |  | 250 | 215
| Barapukuria | 227 | 04:00 | 220 | 18:30 | Keranigonj | 236 | 05:00 | 220 | 12:00 | 230 kV MIN | 215 |  | 242 | 217 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 226 | 1:00 | 215 | 18:00 | Khulna(S) | 241 | 04:00 | 228 | 12:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 248 | 04:00 | 234 | 14:00 | Madunaghat | 234 | 02:00 | 220 | 12:00 | 132 kV MAX | 145 |  | 144 | 113 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 244 | 03:00 | 234 | 13:00 | Madunaghat-400 | 234 | 05:00 | 220 | 13:00 | 132 kV MIN | 110 |  | 145 | 110 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 240 | 03:00 | 233 | 11:00 | Maniknagar | 237 | 04:00 | 223 | 12:00 | [35 empty] | 6:00
| Bibiana | 231 | 09:00 | 224 | 13:00 | Meghnaghat | 242 | 00:00 | 228 | 14:00 | [35 empty] | 392
| BIPTC | 245 | 03:00 | 233 | 13:00 | Meghnaghat-400 | 240 | 06:00 | 225 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 240 | 03:00 | 231 | 13:00 | Mirsorai | 233 | 02:00 | 217 | 13:00 | ` | [34 empty] | 21:00
| Bogura-400 | 239 | 03:00 | 230 | 13:00 | Rajshahi | 242 | 04:00 | 228 | 13:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 250 | 05:00 | 243 | 00:00 | Rampal | 238 | 00:00 | 226 | 12:00 |  |  |  |  | Ash 400-299274
| BSRM | 233 | 08:00 | 225 | 20:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 235 | 03:00 | 229 | 13:00 | Rampura | 239 | 05:00 | 224 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 249 | 05:00 | 237 | 13:00 | Shikalbaha | 233 | 03:00 | 218 | 13:00 |  | kaptai by call 399528
| Fenchuganj | 235 | 02:00 | 229 | 14:00 | Shyampur | 237 | 04:00 | 222 | 12:00
| Ghorashal | 242 | 02:00 | 235 | 00:00 | Siddhirganj | 238 | 02:00 | 226 | 12:00
| Ghorashal-230 | 238 | 03:00 | 230 | 13:00 | Sirajgonj | 246 | 03:00 | 239 | 12:00
| Gopalganj | 249 | 03:00 | 239 | 18:30 | Sreepur | 238 | 23:00 | 228 | 12:00
| GPH | 233 | 03:00 | 226 | 20:00 | Tongi | 237 | 04:00 | 221 | 12:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 137 | 03:00 | 133 | 12:00 | Kurigram | 133 | 05:00 | 122 | 13:00 |  | Gopalganj-230 | 599470
| Agargaon | 141 | 02:00 | 133 | 13:00 | Kushtia | 141 | 00:00 | 136 | 13:00
| Agrabad | 135 | 03:00 | 130 | 08:00 | Lalbag | 139 | 03:00 | 134 | 11:00
| AKS | 133 | 05:00 | 128 | 13:00 | Lalmonirhat | 132 | 02:00 | 122 | 18:00
| Aminbazar | 144 | 04:00 | 133 | 13:00 | Madanganj | 135 | 04:00 | 132 | 11:00
| Amnura | 142 | 05:00 | 132 | 13:00 | Madaripur | 136 | 15:00 | 133 | 00:00
| Ashuganj | 142 | 08:00 | 140 | 00:00 | Madartek | 138 | 03:00 | 132 | 13:00
| Bagerhat | 140 | 04:00 | 130 | 13:00 | Madunaghat | 135 | 08:00 | 131 | 11:00
| Bajitpur | 136 | 08:00 | 134 | 00:00 | Magura | 142 | 04:00 | 133 | 12:00
| Bakulia | 134 | 01:00 | 130 | 13:00 | Mahasthangarh | 137 | 03:00 | 131 | 09:00
| Banani | 138 | 04:00 | 130 | 12:00 | Manikganj | 132 | 01:00 | 128 | 11:00
| Bangabhaban | 137 | 06:00 | 132 | 12:00 | Maniknagar | 138 | 06:00 | 131 | 13:00
| Barapukuria | 137 | 04:00 | 131 | 13:00 | Matarbari | 127 | 06:00 | 120 | 18:00
| Barguna | 138 | 03:00 | 134 | 18:30 | Matuail | 136 | 06:00 | 133 | 00:00
| Barishal | 138 | 01:00 | 131 | 13:00 | Millgate | 134 | 01:00 | 131 | 00:00
| Barishal-230 | 138 | 02:00 | 132 | 12:00 | Mirpur | 145 | 06:00 | 133 | 19:30
| Baroaulia | 137 | 05:00 | 130 | 19:00 | Mirzapur | 133 | 09:00 | 129 | 18:00
| Baroirhat | 133 | 06:00 | 125 | 13:00 | Mithapukur | 135 | 03:00 | 128 | 18:00
| Bashundhara | 138 | 03:00 | 129 | 13:00 | MI_Cement | 137 | 03:00 | 132 | 13:00
| BashundharaCement | 135 | 04:00 | 132 | 11:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 136 | 03:00 | 133 | 13:00 | Mogbazar | 140 | 04:00 | 134 | 12:00
| Benapole | 141 | 04:00 | 128 | 13:00 | Mongla | 140 | 06:00 | 131 | 13:00
| Bhaluka | 131 | 03:00 | 124 | 12:00 | Motijheel | 137 | 06:00 | 132 | 12:00
| Bhandaria | 135 | 17:00 | 128 | 13:00 | Munshiganj | 134 | 03:00 | 131 | 21:00
| Bhangura | 139 | 01:00 | 136 | 13:00 | Mymensingh | 131 | 10:00 | 115 | 08:00
| Bheramara | 142 | 03:00 | 137 | 13:00 | Naogaon | 137 | 06:00 | 130 | 09:00
| Bheramara(GK) | 142 | 05:00 | 138 | 11:00 | Narail | 141 | 04:00 | 132 | 13:00
| Bhulta | 126 | 14:00 | 123 | 00:00 | Narinda | 138 | 6:00 | 131 | 13:00
| Bog-Sherpur | 138 | 03:00 | 132 | 18:30 | Narshingdi | 136 | 02:00 | 127 | 20:00
| Bogura | 138 | 03:00 | 133 | 11:00 | Natore | 140 | 01:00 | 135 | 18:30
| Bogura-230 | 140 | 03:00 | 132 | 13:00 | Nawabganj | 140 | 03:00 | 132 | 13:00
| Brahmanbaria | 137 | 07:00 | 133 | 14:00 | Netrakona | 130 | 04:00 | 121 | 18:00
| Cantonment | 141 | 01:00 | 132 | 13:00 | New | 134 | 03:00 | 132 | 11:00
| Chandpur | 129 | 06:00 | 124 | 14:00 | Niamatpur | 140 | 03:00 | 135 | 12:00
| Chandraghona | 136 | 01:00 | 131 | 13:00 | Noapara | 140 | 01:00 | 132 | 13:00
| Chapai | 139 | 03:00 | 133 | 13:00 | Pabna | 142 | 03:00 | 136 | 13:00
| Charsaidpur | 137 | 07:00 | 132 | 00:00 | Palashbari | 134 | 06:00 | 126 | 13:00
| Chauddagram | 134 | 03:00 | 128 | 14:00 | Panchagarh | 137 | 03:00 | 125 | 09:00
| Chhatak | 135 | 00:00 | 132 | 12:00 | Patuakhali | 138 | 01:00 | 133 | 18:30
| Chowmuhani | 128 | 05:00 | 121 | 13:00 | Payra | 139 | 02:00 | 135 | 18:30
| Chuadanga | 141 | 01:00 | 130 | 13:00 | PHP | 132 | 03:00 | 124 | 13:00
| Coxsbazar | 128 | 08:00 | 121 | 18:00 | Postogola | 140 | 03:00 | 135 | 13:00
| Cumilla(N) | 137 | 03:00 | 132 | 13:00 | Purbachal | 138 | 01:00 | 132 | 12:00
| Cumilla(S) | 137 | 03:00 | 129 | 09:00 | Purbasadipur | 132 | 04:00 | 123 | 09:00
| Daudkandi | 135 | 05:00 | 130 | 11:00 | Rahanpur | 140 | 03:00 | 136 | 13:00
| Dhaka | 137 | 01:00 | 133 | 11:00 | Rahanpur-400 | 140 | 00:00 | 137 | 09:00
| Dhamrai | 138 | 03:00 | 134 | 12:00 | Rahim | 134 | 03:00 | 130 | 14:00
| Dhanmondi | 138 | 05:00 | 130 | 04:00 | Rajbari | 138 | 03:00 | 130 | 13:00
| Dohazari | 133 | 08:00 | 126 | 19:00 | Rajendrapur | 137 | 19:30 | 131 | 00:00
| Faridpur | 138 | 06:00 | 131 | 13:00 | Rajshahi | 141 | 06:00 | 135 | 13:00
| Fatullah | 138 | 04:00 | 133 | 13:00 | Rajshahi-230 | 141 | 01:00 | 129 | 13:00
| Fenchuganj | 140 | 00:00 | 136 | 12:00 | Ramganj | 129 | 05:00 | 120 | 13:00
| Feni | 131 | 05:00 | 125 | 13:00 | Rampur | 135 | 04:00 | 130 | 13:00
| Ghatail | 132 | 12:00 | 122 | 08:00 | Rampura | 138 | 03:00 | 132 | 13:00
| Ghorashal | 142 | 02:00 | 138 | 15:00 | Rangamati | 135 | 04:00 | 130 | 13:00
| Goalpara | 143 | 03:00 | 133 | 13:00 | Rangpur | 133 | 04:00 | 125 | 13:00
| Gollamari | 142 | 06:00 | 133 | 13:00 | Ruppur | 142 | 09:00 | 138 | 12:00
| Gopalganj | 140 | 03:00 | 133 | 13:00 | Saidpur | 134 | 06:00 | 124 | 09:00
| Gopalganj-400 | 140 | 03:00 | 134 | 18:30 | Satkhira | 140 | 02:00 | 131 | 13:00
| Gulshan | 136 | 06:00 | 132 | 11:00 | Satmasjid | 140 | 01:00 | 132 | 13:00
| Halishahar | 133 | 17:00 | 126 | 12:00 | Savar | 141 | 03:00 | 132 | 19:30
| Haripur | 135 | 05:00 | 132 | 00:00 | SevenRings | 142 | 03:00 | 139 | 13:00
| HaripurSBU | 135 | 05:00 | 132 | 00:00 | ShahCement | 137 | 07:00 | 132 | 00:00
| Hasnabad | 139 | 01:00 | 136 | 11:00 | Shahjadpur | 144 | 04:00 | 140 | 18:00
| Hathazari | 137 | 03:00 | 133 | 19:00 | Shahjibazar | 138 | 07:00 | 134 | 15:00
| Ishurdi | 144 | 03:00 | 138 | 18:30 | Shahmirpur | 133 | 00:00 | 130 | 12:00
| Jaldhaka | 132 | 04:00 | 122 | 09:00 | Shariatpur | 138 | 02:00 | 132 | 13:00
| Jamalpur | 132 | 09:00 | 113 | 08:00 | Sherpur | 130 | 12:00 | 110 | 08:00
| Jashore | 141 | 05:00 | 132 | 13:00 | Shikalbaha | 125 | 03:00 | 119 | 13:00
| Jhenaidah | 142 | 04:00 | 133 | 13:00 | Shikalbaha-230 | 135 | 00:00 | 131 | 13:00
| Jhenaidah-230 | 143 | 05:00 | 133 | 13:00 | Shitalakhya | 137 | 03:00 | 132 | 13:00
| Joydebpur | 143 | 09:00 | 134 | 15:00 | Sholosohor | 138 | 19:00 | 130 | 13:00
| Joypurhat | 137 | 02:00 | 130 | 11:00 | Shyampur | 137 | 01:00 | 133 | 11:00
| Juldah | 134 | 05:00 | 130 | 11:00 | Shyampur-230 | 138 | 03:00 | 133 | 00:00
| Kabirpur | 136 | 15:00 | 129 | 11:00 | Siddhirganj | 138 | 00:00 | 132 | 13:00
| Kachua | 131 | 00:00 | 127 | 13:00 | Sirajganj | 139 | 06:00 | 134 | 18:00
| Kaliakoir | 140 | 06:00 | 132 | 12:00 | Sonargaon | 135 | 04:00 | 130 | 11:00
| Kallyanpur | 136 | 00:00 | 131 | 13:00 | Sreemongol | 138 | 04:00 | 134 | 13:00
| Kalurghat | 135 | 04:00 | 130 | 11:00 | Sreepur | 132 | 02:00 | 127 | 13:00
| Kamrangirchar | 138 | 03:00 | 131 | 13:00 | Srinagar | 140 | 05:00 | 133 | 12:00
| Kaptai | N/A | N/A | N/A | N/A | SSM | 140 | 03:00 | 132 | 12:00
| Kazla | 137 | 05:00 | 131 | 13:00 | Sunamganj | 134 | 04:00 | 130 | 12:00
| Keranigonj | 139 | 03:00 | 132 | 13:00 | Sylhet | 136 | 02:00 | 132 | 13:00
| Khagrachori | 135 | 04:00 | 129 | 13:00 | Sylhet-132 | 136 | 01:00 | 133 | 14:00
| Khulna | 139 | 01:00 | 132 | 12:00 | Tangail | 130 | 10:00 | 123 | 08:00
| Khulna(S) | 142 | 05:00 | 133 | 13:00 | Thakurgaon | 134 | 03:00 | 122 | 09:00
| Khulshi | 134 | 03:00 | 128 | 13:00 | TK | 134 | 06:00 | 131 | 11:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 134 | 08:00 | 130 | 13:00 | Tongi | 136 | 04:00 | 133 | 13:00 |  |  | Nos | Nos | Nos
| Kodda | 138 | 08:00 | 129 | 01:00 | Ullahpara | 141 | 05:00 | 136 | 12:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 137 | 04:00 | 130 | 20:00 | Ullon | 138 | 03:00 | 131 | 13:00
| Kulaura | 139 | 05:00 | 136 | 13:00 | Uttara | 144 | 04:00 | 133 | 18:30
| Zigatola | 135 | 04:00 | 126 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.