## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-01-2025 | during | 12-01-2025 | during | 12-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 234.58 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 301 | 327 | 400.37 | 400.37 | 315 | 315 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 307 | 264 | 335 | 335 | 300 | 300 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 29 | 22 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 28 | 34 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 95 | 111 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 36 | 17 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0.01 | 0.01 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 7401.63 | 5842.27 | 1493 | 1769 | 4022.99 | 4001.99 | 2398.55 | 2377.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 26 | 35 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 53 | 226 | 225 | 225 | 151 | 151 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 44 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 24 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 17 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 33 | 0 | 11 | 21 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4 | 0 | 4 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 20 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 36 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1320 | 1224 | 500 | 614 | 1224 | 1224 | 612 | 612 | Coal shortage
56 | Cox's Bazar Wind | Wind | PDB |  | 66 | 60 | 0 | 0 | 0 | 16 | 0 | 16 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1200 | 1200 | 929 | 935 | 1150 | 1150 | 935 | 935 | -
Chattogram Area Total |  |  |  |  | 5102.36 | 4873.22 | 1543 | 2026 | 3931.72 | 3924.72 | 3030.72 | 3023.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 194 | 181 | 221 | 221 | 190 | 190 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | schedule outage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 40 | 41 | 46.94 | 46.94 | 45 | 45 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 55 | 55 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 182 | 180 | 195 | 195 | 190 | 190 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 90 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 40 | 163 | 163 | 50 | 50 | Gas shortage
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 120 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 46 | 58 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 17 | 20.83 | 20.83 | 18 | 18 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 9 | 9 | 9 | 9 | Fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 72 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 669 | 899 | 1589.97 | 1529.97 | 1411.2 | 1351.2
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 31 | 31 | 210 | 210 | 25 | 25 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 45 | 47 | 200 | 200 | 45 | 45 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 47 | 115 | 115 | 55 | 55 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.94 | 0 | 44.25 | 0 | 44.25 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 22 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654.5 | 654.21 | 151.94 | 147 | 647.75 | 601.5 | 247.75 | 201.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 44 | 44 | 0 | 0 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 0 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 131 | 133 | 135 | 135 | 135 | 135 | Gas shortage
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 341 | 341 | 0 | 0 | Plant shutdown as per NLDC requirement.
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 339 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 360 | 340 | 383 | 383 | 353 | 353 | FGMO
Sylhet Area Total |  |  |  |  | 2411 | 2370.57 | 1072 | 1062 | 1554.5 | 1554.5 | 1091.01 | 1091.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 910 | 894 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 30 | 30 | 30 | 30 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 352 | 353 | 410 | 410 | 360 | 360 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 71.28 | 0 | 73.5 | 0 | 73.5 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3743 | 3686.2 | 1333.28 | 1247 | 3232.5 | 3159 | 1738.5 | 1665
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 135 | 135 | 140 | 140 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 950 | 1244 | 1244 | 1244 | 1244 | 1244 | -
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 100 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.54 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1564.54 | 2018 | 2176.12 | 2176.12 | 2178 | 2178
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | availability is 47MW but unable to submit to web
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 214 | 173 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 220 | 172 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 11.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52 | 52.2 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 43 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.92 | 0 | 4.15 | 0 | 4.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 518.21 | 756 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.64 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 100 | 100 | 87 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3575.55 | 3393.2 | 1108.27 | 1207.5 | 2706.89 | 2552.74 | 2391.29 | 2237.14
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 70 | 70 | 70 | 75 | 75 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 210 | 210 | 210 | 210 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.7 | 0 | 5.4 | 0 | 5.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 163 | 0 | 120.42 | 0 | 120.42 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 473.7 | 350 | 683.82 | 528 | 688.82 | 533
System Total |  |  |  |  | 29109.24 | 26932.25 | 9408.73 | 10725.5 | 20546.26 | 20028.54 | 15175.84 | 14658.12
Forecast Scenario (12-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8740 |  | 0 |  | No Data
|  |  |  | 1:00 | 8020 |  | 0 |  | No Data
|  |  |  | 2:00 | 7580 |  | 0 |  | 7580
|  |  |  | 3:00 | 7360 |  | 0 |  | 7360
|  |  |  | 4:00 | 7260 |  | 0 |  | 7260
|  |  |  | 5:00 | 7150 |  | 0 |  | 7150
|  |  |  | 6:00 | 7670 |  | 0 |  | 7670
|  |  |  | 7:00 | 8350 |  | 0 |  | 8350
|  |  |  | 8:00 | 9400 |  | 0 |  | 9400
|  |  |  | 9:00 | 9610 |  | 0 |  | 9610
|  |  |  | 10:00 | 9360 |  | 0 |  | 9360
|  |  |  | 11:00 | 9580 |  | 0 |  | 9580
|  |  |  | 12:00 | 10170 |  | 0 |  | 10170
|  |  |  | 13:00 | 10430 |  | 0 |  | 10430
|  |  |  | 14:00 | 9950 |  | 0 |  | 9950
|  |  |  | 15:00 | 9440 |  | 0 |  | 9440
|  |  |  | 16:00 | 9070 |  | 0 |  | 9070
|  |  |  | 17:00 | 9280 |  | 0 |  | 9280
|  |  |  | 18:00 | 10510 |  | 0 |  | 10510
|  |  |  | 18:30 | 10600 |  | 0 |  | 10600
|  |  |  | 19:00 | 10690 |  | 0 |  | 10690
|  |  |  | 19:30 | 10480 |  | 0 |  | 10480
|  |  |  | 20:00 | 10420 |  | 0 |  | 10420
|  |  |  | 21:00 | 10240 |  | 0 |  | 10240
|  |  |  | 22:00 | 9950 |  | 0 |  | 9950
|  |  |  | 23:00 | 9320 |  | 0 |  | 9320
Probable Maximum Temperature: |  |  | 24.30°C
Probable Maximum Demand at Day Peak: |  |  | 10170.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 10690.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10690.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 219.55 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (11-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 27.90°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 716.15
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 19.6305 | Peak Hour Flow: |  | 894.00 MW at 19:00 hrs.
Energy Flow from West to East |  | 13987200 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 13.1176 | Peak Hour Flow: |  | 756.00 MW at 19:00 hrs.
Power Flow during Peak Demand |  | 706 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.1904 | Peak Hour Flow: |  | 58.00 MW at 19:00 hrs.
Maximum Power Flow |  | 881 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 33.9386 | Peak Hour Flow: |  | 1708.00 MW at 19:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-01-2025 | [28 empty] | Date: | 11-01-2025 | [28 empty] | Date: | 11-01-2025 | [28 empty] | Date: | 11-01-2025 | [28 empty] | Date: | 11-01-2025 | [18 empty] | Date: | 11-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [18 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 150.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 0.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 50.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 281 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 33 | 867 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 450 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 183 | 45 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 0 | 300 | 347 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4132 | 764 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 7 | 140 | 180 | 0 | 1000 | 0 | 3868.1 | 8000.1 | 93.44
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 302 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 36 | 867 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 310 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 193 | 44 | 0 | 50 | 0 | 0 | 15 | 0 | 46 | 0 | 0 | 0 | 0 | 285 | 351 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4008 | 717 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 180 | 0 | 860 | 0 | 3536.92 | 7544.92 | 93.43
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 400 | 265 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 36 | 760 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 300 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 183 | 41 | 0 | 50 | 0 | 0 | 15 | 0 | 50 | 0 | 0 | 0 | 0 | 280 | 347 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 3849 | 716 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 5.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 180 | 0 | 700 | 0 | 3334.73 | 7183.73 | 93.43
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 400 | 285 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 38 | 666 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 88 | 0 | 0 | 0 | 19 | 184 | 41 | 0 | 50 | 0 | 0 | 11 | 0 | 48 | 0 | 0 | 0 | 0 | 280 | 346 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 5 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 3640 | 717 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 180 | 0 | 700 | 0 | 3335.1 | 6975.1 | 93.43
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 400 | 276 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 40 | 665 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 88 | 0 | 0 | 0 | 5 | 183 | 41 | 0 | 50 | 0 | 0 | 11 | 0 | 48 | 0 | 0 | 0 | 0 | 280 | 342 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 5 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 3602 | 528 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 5.5 | 210 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 180 | 0 | 700 | 0 | 3147.46 | 6749.46 | 93.43
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 400 | 310 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 40 | 664 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 5 | 200 | 41 | 0 | 50 | 0 | 0 | 11 | 0 | 42 | 0 | 0 | 0 | 0 | 250 | 325 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 5 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 3506 | 528 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 210 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 180 | 0 | 710 | 0 | 3088.92 | 6594.92 | 93.42
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 400 | 300 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 40 | 868 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 320 | 0 | 15 | 0 | 8 | 0 | 0 | 0 | 7 | 206 | 41 | 0 | 50 | 0 | 0 | 11 | 0 | 42 | 0 | 0 | 0 | 0 | 240 | 330 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 22 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 3666 | 528 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 210 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 6 | 140 | 220 | 0 | 840 | 0 | 3304.59 | 6970.59 | 93.42
07:00 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 350 | 318 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 1 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 33 | 873 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 390 | 1 | 43 | 0 | 60 | 0 | 0 | 0 | 21 | 212 | 41 | 0 | 50 | 0 | 0 | 11 | 0 | 42 | 0 | 2 | 0 | 0 | 240 | 350 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 35 | 0 | 0.79 | 0 | 3929.79 | 716 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 150 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0.05 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.02 | 0 | 250 | 0 | 100 | 220 | 0 | 1000 | 0 | 3603.5 | 7533.29 | 93.42
08:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 420 | 314 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 4 | 0 | 29 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 26 | 0 | 14 | 872 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 460 | 7 | 43 | 0 | 185 | 0 | 0 | 0 | 29 | 207 | 44 | 0 | 50 | 0 | 0 | 11 | 0 | 42 | 0 | 18 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 136 | 0 | 9 | 10 | 35 | 0 | 5.52 | 0 | 4480.52 | 811 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.22 | 0 | 0 | 606.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 6.98 | 143 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0.85 | 5.5 | 180 | 73 | 0 | 6 | 0 | 0 | 0 | 0.4 | 32 | 0.13 | 0 | 307 | 0 | 140 | 220 | 0 | 1090 | 0 | 4099.71 | 8580.23 | 93.42
09:00 | 0 | 44 | 20 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 0 | 0 | 54 | 48 | 0 | 0 | 17 | 0 | 16 | 0 | 420 | 267 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 0 | 29 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 0 | 5 | 871 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 550 | 13 | 43 | 0 | 185 | 0 | 0 | 0 | 29 | 183 | 41 | 0 | 50 | 0 | 0 | 16 | 0 | 42 | 0 | 42 | 0 | 0 | 340 | 380 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 136 | 0 | 18 | 28 | 36 | 1 | 24.05 | 0 | 4553.05 | 814 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.13 | 0 | 0 | 609.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 27.54 | 136 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 2.29 | 0 | 175 | 73 | 0 | 15 | 0 | 0 | 0 | 2.9 | 81 | 0.22 | 0 | 250 | 0 | 140 | 220 | 0 | 1140 | 0 | 4305.26 | 8858.31 | 93.41
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 16 | 0 | 81 | 48 | 0 | 0 | 35 | 0 | 16 | 0 | 350 | 300 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 22 | 0 | 29 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 26 | 0 | 12 | 859 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 460 | 17 | 43 | 0 | 185 | 0 | 0 | 0 | 29 | 183 | 38 | 0 | 50 | 0 | 0 | 16 | 0 | 36 | 0 | 58 | 0 | 0 | 340 | 345 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 134 | 0 | 35 | 56 | 33 | 2 | 36.31 | 1 | 4523.31 | 909 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.47 | 0 | 0 | 463.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 44.6 | 193 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 3.49 | 5.5 | 178 | 72 | 0 | 22 | 0 | 0 | 0 | 4.2 | 119 | 0.38 | 0 | 200 | 5 | 100 | 180 | 0 | 1000 | 0 | 4131.32 | 8654.63 | 93.41
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 36 | 0 | 95 | 32 | 0 | 0 | 35 | 0 | 25 | 0 | 350 | 313 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 28 | 0 | 29 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 26 | 0 | 12 | 860 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 450 | 19 | 43 | 0 | 192 | 0 | 0 | 0 | 29 | 201 | 40 | 0 | 50 | 0 | 0 | 16 | 0 | 42 | 0 | 66 | 0 | 0 | 370 | 345 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 131 | 0 | 16 | 56 | 31 | 2 | 43.08 | 11 | 4639.08 | 909 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.1 | 0 | 0 | 461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 55.21 | 214 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 4.45 | 5.5 | 210 | 70 | 0 | 25 | 0 | 0 | 0 | 5.1 | 151 | 0.49 | 0 | 200 | 4 | 100 | 180 | 0 | 920 | 0 | 4162.85 | 8801.93 | 93.41
12:00 | 0 | 70 | 28 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 36 | 0 | 95 | 32 | 0 | 0 | 35 | 0 | 25 | 0 | 450 | 307 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 30 | 0 | 29 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 26 | 0 | 11 | 929 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 500 | 20 | 43 | 0 | 182 | 0 | 0 | 0 | 29 | 194 | 40 | 0 | 50 | 0 | 0 | 16 | 0 | 46 | 0 | 69 | 0 | 0 | 360 | 368 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 131 | 0 | 16 | 45 | 31 | 2 | 45.94 | 12 | 4928.94 | 910 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.28 | 0 | 0 | 518.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 58.64 | 214 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 4.92 | 5.5 | 210 | 70 | 0 | 25 | 0 | 0 | 0 | 5.7 | 163 | 0.54 | 0 | 250 | 4 | 140 | 220 | 0 | 950 | 0 | 4479.79 | 9408.73 | 93.41
13:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 36 | 0 | 95 | 32 | 0 | 0 | 35 | 0 | 25 | 0 | 450 | 300 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 29 | 0 | 29 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 26 | 0 | 18 | 935 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 550 | 19 | 43 | 0 | 182 | 0 | 0 | 0 | 29 | 193 | 40 | 0 | 50 | 0 | 0 | 16 | 0 | 60 | 0 | 64 | 0 | 0 | 345 | 336 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 129 | 0 | 16 | 45 | 28 | 2 | 45.1 | 12 | 4978.1 | 910 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.93 | 0 | 0 | 608.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 50.41 | 214 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 4.22 | 5.5 | 210 | 70 | 0 | 25 | 0 | 0 | 0 | 5.5 | 163 | 0.52 | 0 | 307 | 4 | 140 | 220 | 0 | 1140 | 0 | 4807.43 | 9785.53 | 93.4
14:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 36 | 0 | 95 | 32 | 0 | 0 | 35 | 0 | 25 | 0 | 450 | 274 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 26 | 0 | 29 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 26 | 0 | 15 | 937 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 550 | 17 | 43 | 0 | 158 | 0 | 0 | 0 | 29 | 183 | 42 | 0 | 50 | 0 | 0 | 17 | 0 | 64 | 0 | 57 | 0 | 0 | 346 | 312 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 130 | 0 | 35 | 55 | 28 | 2 | 34.93 | 12 | 4912.93 | 909 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.04 | 0 | 0 | 606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 42.37 | 186 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 3.71 | 5.5 | 210 | 70 | 0 | 24 | 0 | 0 | 0 | 4.6 | 137 | 0.41 | 0 | 307 | 4 | 100 | 180 | 0 | 1244 | 0 | 4697.63 | 9610.56 | 93.4
15:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 36 | 0 | 95 | 16 | 0 | 0 | 35 | 0 | 25 | 0 | 380 | 267 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 19 | 0 | 26 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 0 | 2 | 861 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 500 | 13 | 43 | 0 | 108 | 0 | 0 | 0 | 29 | 184 | 41 | 0 | 50 | 0 | 0 | 17 | 0 | 54 | 0 | 45 | 0 | 0 | 320 | 288 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 130 | 0 | 16 | 55 | 29 | 1 | 28.56 | 12 | 4621.56 | 908 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.04 | 0 | 0 | 511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 30.74 | 162 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 2.78 | 5.5 | 207 | 69 | 0 | 17 | 0 | 0 | 0 | 3.4 | 96 | 0.3 | 0 | 250 | 4 | 138 | 220 | 0 | 1120 | 0 | 4347.76 | 8969.32 | 93.4
16:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 36 | 0 | 95 | 16 | 0 | 4 | 0 | 0 | 25 | 0 | 380 | 291 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 25.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 26 | 0 | 2 | 865 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 500 | 8 | 43 | 0 | 108 | 0 | 0 | 0 | 29 | 204 | 40 | 0 | 50 | 0 | 0 | 17 | 0 | 54 | 0 | 25 | 0 | 0 | 350 | 307 | 0 | 0 | 0 | 2 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 129 | 0 | 16 | 35 | 30 | 0 | 14.22 | 12 | 4606.72 | 909 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.29 | 0 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 12.45 | 162 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 1.33 | 5.5 | 175 | 70 | 0 | 9 | 0 | 0 | 0 | 1.3 | 46 | 0.14 | 0 | 200 | 4 | 138 | 220 | 0 | 1100 | 0 | 4139.01 | 8745.73 | 93.4
17:00 | 0 | 80 | 34 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 36 | 0 | 95 | 32 | 0 | 20 | 35 | 46 | 25 | 0 | 380 | 244 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 2 | 0 | 25.5 | 22 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 26 | 1 | 13 | 935 | 17 | 0 | 1 | 0 | 1 | 227 | 0 | 0 | 0 | 530 | 1 | 43 | 8 | 102 | 0 | 0 | 0 | 29 | 183 | 41 | 2 | 50 | 4 | 3 | 17 | 0 | 54 | 0 | 2 | 0 | 0 | 330 | 290 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 50 | 0 | 0 | 0 | 129 | 3 | 29 | 47 | 30 | 0 | 2.44 | 14 | 4835.94 | 909 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.19 | 0 | 0 | 533 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 8 | 5 | 0 | 2.11 | 180 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0.2 | 5.5 | 175 | 70 | 13 | 1 | 0 | 0 | 0 | 0.3 | 8 | 0.03 | 0 | 259 | 5 | 100 | 180 | 0 | 1110 | 6 | 4103.33 | 8939.27 | 93.39
18:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 35 | 36 | 0 | 111 | 32 | 0 | 55 | 35 | 162 | 25 | 0 | 450 | 302 | 0 | 0 | 35 | 33 | 0 | 0 | 0 | 0 | 47 | 22 | 22 | 0 | 0 | 35 | 45 | 0 | 0 | 0 | 17 | 24 | 0 | 12 | 12 | 0 | 26 | 17 | 21 | 935 | 17 | 0 | 18 | 0 | 30 | 223 | 0 | 0 | 0 | 590 | 0 | 43 | 80 | 172 | 0 | 0 | 0 | 29 | 194 | 41 | 45 | 50 | 95 | 26 | 17 | 0 | 64 | 0 | 0 | 0 | 0 | 360 | 351 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 132 | 17 | 47 | 47 | 30 | 0 | 0 | 22 | 5998 | 893 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 50 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 11.5 | 175 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1150 | 100 | 4602.5 | 10600.5 | 93.39
19:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 54 | 17 | 0 | 111 | 16 | 0 | 55 | 17 | 162 | 25 | 0 | 450 | 264 | 0 | 0 | 55 | 33 | 0 | 0 | 0 | 0 | 35 | 22 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 24 | 0 | 0 | 36 | 0 | 35 | 20 | 21 | 935 | 0 | 0 | 19 | 0 | 44 | 226 | 0 | 0 | 0 | 614 | 0 | 43 | 90 | 180 | 0 | 0 | 0 | 29 | 181 | 41 | 72 | 40 | 120 | 28 | 17 | 0 | 58 | 0 | 0 | 0 | 0 | 340 | 339 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 133 | 0 | 47 | 47 | 31 | 0 | 0 | 22 | 5903 | 894 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 11.5 | 210 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1244 | 100 | 4822.5 | 10725.5 | 93.39
19:30 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 54 | 17 | 0 | 111 | 0 | 0 | 0 | 0 | 162 | 25 | 0 | 450 | 310 | 0 | 0 | 55 | 33 | 0 | 0 | 0 | 0 | 35 | 22 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 24 | 935 | 0 | 0 | 19 | 0 | 51 | 227 | 0 | 0 | 0 | 614 | 0 | 51 | 0 | 180 | 0 | 0 | 0 | 29 | 191 | 42 | 115 | 40 | 100 | 28 | 17 | 0 | 56 | 0 | 0 | 0 | 0 | 350 | 343 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 132 | 0 | 47 | 47 | 31 | 0 | 0 | 22 | 5739 | 893 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 765 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 11.5 | 210 | 71 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 140 | 220 | 0 | 1244 | 100 | 4733.5 | 10472.5
20:00 | 0 | 50 | 34 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 54 | 17 | 0 | 110 | 0 | 0 | 0 | 0 | 162 | 25 | 0 | 450 | 307 | 0 | 0 | 55 | 33 | 0 | 0 | 0 | 0 | 35 | 22 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 935 | 0 | 0 | 19 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 189 | 42 | 108 | 40 | 100 | 27 | 14 | 0 | 56 | 0 | 0 | 0 | 0 | 340 | 341 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 132 | 0 | 47 | 47 | 31 | 0 | 0 | 22 | 5697 | 894 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 11.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1244 | 100 | 4713.5 | 10410.5 | 93.39
21:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 54 | 17 | 0 | 111 | 0 | 0 | 0 | 0 | 162 | 25 | 0 | 450 | 301 | 0 | 0 | 55 | 33 | 0 | 0 | 0 | 0 | 17 | 22 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 935 | 0 | 0 | 19 | 0 | 51 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 183 | 42 | 115 | 40 | 51 | 29 | 14 | 0 | 56 | 0 | 0 | 0 | 0 | 340 | 333 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 135 | 0 | 47 | 47 | 32 | 0 | 0 | 22 | 5616 | 893 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 11.5 | 165 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1244 | 100 | 4664.5 | 10280.5 | 93.38
22:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 17 | 0 | 0 | 111 | 0 | 0 | 0 | 0 | 35 | 22 | 0 | 450 | 283 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 936 | 0 | 0 | 19 | 0 | 0 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 182 | 42 | 51 | 35 | 0 | 29 | 14 | 0 | 54 | 0 | 0 | 0 | 0 | 330 | 336 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 135 | 0 | 16 | 24 | 30 | 0 | 0 | 22 | 5085 | 884 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 8.5 | 165 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 140 | 220 | 0 | 1244 | 100 | 4596.5 | 9681.5 | 93.38
23:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 450 | 274 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 936 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 560 | 0 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 182 | 42 | 25 | 30 | 0 | 0 | 14 | 0 | 52 | 0 | 0 | 0 | 0 | 330 | 336 | 0 | 0 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 135 | 0 | 16 | 24 | 29 | 0 | 0 | 22 | 4815 | 884 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 8.5 | 196 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 8 | 140 | 220 | 0 | 1244 | 0 | 4483.5 | 9298.5 | 93.38
Total KWH | 0 | 1077120 | 508320 | 0 | 0 | 0 | 0 | 0 | 7387200 | 0 | 0 | 227160 | 378720 | 0 | 1597968 | 369600 | 0 | 136182 | 294787 | 701280 | 515880 | 0 | 9925000 | 7045527 | 0 | 0 | 204879 | 764900 | 0 | 0 | 0 | 183731 | 144000 | 483600 | 455760 | 0 | 0 | 185673 | 82800 | 0 | 0 | 112800 | 31123 | 36096 | 0 | 26880 | 48960 | 23879 | 685500 | 57708 | 589920 | 20901818.18 | 30109 | 0 | 107520 | 0 | 206581 | 3417741 | 0 | 0 | 0 | 11389090 | 133515 | 976269 | 232509 | 3328727 | 0 | 0 | 0 | 605280 | 4657000 | 1007352 | 517440 | 1125200 | 429600 | 148680 | 358950 | 0 | 1190400 | 0 | 454564 | 0 | 0 | 7732800 | 8539000 | 0 | 0 | 0 | 42960 | 3658255 | 0 | 0 | 1225920 | 0 | 0 | 0 | 3205590 | 41760 | 438000 | 684000 | 731520 | 12000 | 291840 | 247680 | 112352623.18 | 19630545 | 8384544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462960 | 0 | 0 | 13117634 | 0 | 0 | 0 | 0 | 0 | 0 | 185776 | 0 | 0 | 83098 | 540700 | 0 | 331504 | 4294727 | 0 | 0 | 0 | 4535936 | 0 | 0 | 0 | 27960 | 145944 | 4771000 | 1615854 | 107728 | 166953 | 0 | 0 | 0 | 34138.92 | 990720 | 3192 | 0 | 5804000 | 124640 | 3142000 | 5179040 | 0 | 25213090.91 | 540000 | 99433684.83 | 211786308.01

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 11-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 9408.73 | MW | 12:00 Hr. | Energy Generated |  |  | 211786.308 |  | MWHr
Day Peak Demand |  |  | 9408.73 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MWHr
Evening Peak Generation |  |  | 10725.5 | MW | 19:00 Hr. | Energy Demand |  |  | 211786.308 |  | MWHr
Evening Peak Demand |  |  | 10725.5 | MW | 19:00 Hr.
Minimum Generation of the Day |  |  | 6594.92 | MW | 05:00 Hr.
Maximum Generation of the Day |  |  | 10725.5 | MW | 19:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 26577.867 | 0 | 5640.016 | 0 | 0 | 183.731 | 0 | 0 | 32401.614 | Gas | 93587.182 | Gas | 331518602.76
Chattogram Zone |  |  | 4007.661 | 32290.9082 | 813.45 | 0 | 685.5 | 157.394 | 0 | 112.8 | 38067.7132 | Coal | 69694.8531 | Coal | 491070770.6667
Cumilla Zone |  |  | 12058.778 | 0 | 1328.229 | 0 | 0 | 454.564 | 1190.4 | 0 | 15031.971 | HFO | 10109.737 | HFO | 185767931.38
Mymensingh Zone |  |  | 731.52 | 0 | 1411.44 | 0 | 0 | 303.84 | 0 | 0 | 2446.8 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 24404.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24404.525 | Hydro | 685.5 | Hydro | 68550
Khulna Zone |  |  | 8384.544 | 0 | 0 | 0 | 0 | 462.96 | 19630.545 | 0 | 28478.049 | Solar | 3657.6569 | Solar | 57273353.962
Barishal Zone |  |  | 8445.68 | 31017.0909 | 540 | 0 | 0 | 3.192 | 0 | 0 | 40005.9629 | Import | 33938.579 | Import | 168765418.72
Rajshahi Zone |  |  | 8976.607 | 0 | 268.874 | 0 | 0 | 900.164 | 13117.634 | 0 | 23263.279 | Wind | 112.8 | Wind | 1759680
Rangpur Zone |  |  | 0 | 6386.854 | 107.728 | 0 | 0 | 1191.8119 | 0 | 0 | 7686.3939
Total |  |  | 93587.182 | 69694.8531 | 10109.737 | 0 | 685.5 | 3657.6569 | 33938.579 | 112.8 | 211786.308
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 331518602.76 |  | Hydro | 68550
|  |  | Coal | 491070770.6667 |  | Solar | 57273353.962
|  |  | HFO | 185767931.38 |  | Import | 168765418.72
|  |  | HSD | 0 |  | Wind | 1759680
|  |  |  | Total: | 1236224307.4887 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Barapukuria TPP Unit-2 |  |  | 85
| 3 | Khulna 330 MW CCPP GT |  |  | 220
| 4 | Khulna 330 MW CCPP ST |  |  | 110
| 5 | Siddhirgonj 210 MW TPP |  |  | 115
| 6 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 7 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1044 |  |  |  | Total | 35.09
|  |  | Total Unavailable Capacity |  |  |  | 1079.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3722
|  |  | Chattogram |  | 0 |  | 1136
|  |  | Cumilla |  | 0 |  | 917
|  |  | Mymensingh |  | 0 |  | 920
|  |  | Sylhet |  | 0 |  | 375
|  |  | Khulna |  | 0 |  | 1198
|  |  | Barishal |  | 0 |  | 299
|  |  | Rajshahi |  | 0 |  | 999
|  |  | Rangpur |  | 0 |  | 685
|  |  | Total |  | 0 |  | 10251
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:01 |  | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) LT Scheduled S/D Due to Annual
Maintenance
08:02 | 17:46 | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) HT Scheduled S/D Due to Annual
Maintenance
08:02 | 16:49 | Agargaon 230/132kV S/S Auxiliary Tr-2 HT Scheduled S/D Due to Annual Maintenance
08:08 | 17:22 | Sunamganj 132/33kV S/S Tr-2 LT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
08:09 | 17:21 | Sunamganj 132/33kV S/S Tr-2 HT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
08:12 | 10:23 | Sunamganj 132/33kV S/S Tr-1 LT Scheduled S/D | [7 empty] | 7.0MW load
interrup.
08:13 | 10:22 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D | [7 empty] | 7.0MW load
interrup.
08:13 | 16:17 | Ullahpara 132/33kV S/S Power Transformer -1 LT Scheduled S/D Due to Annual Maintenance
08:15 | 16:15 | Ullahpara 132/33kV S/S Power Transformer -1 HT Scheduled S/D Due to Annual Maintenance
08:17 | 16:55 | Lalmonirhat-Rangpur 132 kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end. and from | [7 empty] | and 30.0MW load
|  | Lalmonirhat 132/33kV end Due to Annual maintenance | [7 empty] | interrup.
Lalmonirhat
132/33kV end
08:22 | 17:15 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Scheduled S/D from Faridpur 132/33kV end Due to Annual
maintenance and from Gopalganj 400/132kVend.
08:22 | 17:15 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Scheduled S/D from Faridpur 132/33kV end Due to Annual
maintenance and from Gopalganj 400/132kVend.
08:22 | 16:11 | Bogura-Mahasthangar (New)) 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to
Shut down taken by mahasthangarh 132KV S/S. and from Mahasthangarh 132/33kV end Due to
Annual Maintenance work.
08:27 | 13:42 | Cumilla(N)-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Maintenance work in 132 KV Shahjibazar grid SS
08:28 | 13:00 | Noapara 132/33kV S/S BUS-B Scheduled S/D Due to Annual Maintenance
08:28 | 13:40 | Bibiyana-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to Am
08:33 | 11:57 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Scheduled S/D
08:34 | 10:59 | Aminbazar 400/230/132kV S/S Gopalganj-1 Scheduled S/D
08:44 | 16:09 | Baroirhat-Feni 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end.
08:50 | 18:16 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Scheduled S/D
08:52 | 18:15 | Madanganj-Shitalakhya 132kV ckt-1 Forced S/D from Shitalakhya 132/33kV end.
08:55 | 16:10 | Baroirhat-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to Due to annual | [7 empty] | 40.0MW load
|  | dead line maintenance | [7 empty] | interrup. Feni
132/33kV end
08:58 | 15:40 | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
09:00 | 16:16 | Cumilla(N)-Kachua 132 kV Ckt-2 Scheduled S/D from Kachua 132/33kV end Due to Annual
Maintenance
09:01 |  | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual maintenance work
09:05 | 13:40 | Bheramara(GK) 132/33kV S/S TR-1 LT Scheduled S/D Due to Annual Maintenance
09:06 | 13:38 | Bheramara(GK) 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual Maintenance
09:08 |  | Thakurgaon 132/33kV S/S T-3(432T) LT Project Work S/D Due to Thakurgaon-Panchagarh
Circuit-2 comissioning work
09:08 |  | Thakurgaon 132/33kV S/S T-3(432T) HT Project Work S/D Due to Thakurgaon-Panchagarh
Circuit-2 comissioning work
09:11 | 16:48 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual maintenance
09:12 | 16:45 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual maintenance
09:13 | 16:16 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D Due to Annual maintenance work
09:13 | 16:18 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Scheduled S/D
09:19 | 13:47 | Cumilla(N)-Shahjibazar 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Maintenance work in 132 KV Shahjibazar GSS
09:20 |  | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Scheduled S/D Due to Testing work by RTS
09:20 |  | Hasnabad 132/33kV S/S 132/33kV 424 T-5 HT Scheduled S/D Due to Testing work by RTS
09:29 | 17:21 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Annual
Maintenance
09:34 | 18:09 | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown for
annual maintenance.
09:38 | 15:40 | Bhulta 132/33kV S/S GT2 HT Scheduled S/D Due to Annual maintainece
09:38 | 15:45 | Bhulta 132/33kV S/S GT2 LT Scheduled S/D Due to Annual maintainece
09:38 | 14:43 | Jhenaidah 132/33kV S/S Transformer T-1 LT Scheduled S/D Due to Annualn Maintenance.
| 09:40 | Bogura 132/33kV S/S Transformer-2 LT is restored.
| 09:40 | Bogura 132/33kV S/S Transformer-2 HT is restored.
09:42 | 12:37 | Kushtia 132/33kV S/S T-3 LT Forced S/D Due to Hooking Up a 33 kV Lahini (PBS) Feeder to a | [7 empty] | 29.0MW load
|  | 33 kV Busbar (Section 3 Side) | [7 empty] | interrup.
09:43 | 12:35 | Kushtia 132/33kV S/S T-3 HT Forced S/D Due to Hooking Up a 33 kV Lahini (PBS) Feeder to a | [7 empty] | 29.0MW load
|  | 33 kV Busbar (Section 3 Side) | [7 empty] | interrup.
09:43 |  | Gopalganj 400/132kV S/S 400kV Rampal Ckt-2 Scheduled S/D
09:51 | 15:01 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to Annual maintenance
and main BUS-II DS replacement.
09:59 | 14:43 | Jhenaidah 132/33kV S/S Transformer T-1 HT Scheduled S/D Due to Annual Maintenance.
10:00 | 16:52 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D Due to Annual Maintenance
10:00 | 16:11 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end.
10:05 | 17:40 | Fenchuganj 230/132/33kV S/S 132 KV Bus-1 Scheduled S/D Due to Annual Maintenance Work
10:13 |  | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Scheduled S/D Due to For Transfer Oil
Centrifuge.
10:14 |  | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Scheduled S/D Due to For Transfer Oil
Centrifuge.
10:43 |  | Aminbazar-Meghnaghat 400kV Ckt-2 Forced S/D from Meghnaghat 400/230kV end Due to
Instructed by NLDC and from Aminbazar 400/230/132kV end Due to Disce cleaning
10:45 | 11:22 | Bheramara P/S-Ishurdi 132 kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end Due to Dc
earth fault locator installation and from Bheramara 230/132kV end Due to DC FAULT
10:45 | 11:22 | Bheramara P/S-Ishurdi 132 kV Ckt-2 Scheduled S/D from Ishurdi 132/33kV end Due to Dc
earth fault locator installation and from Bheramara 230/132kV end Due to DC FAULT
10:45 |  | Sylhet 132/33kV S/S T1 HT Scheduled S/D Due to T1A 33 KV Cable Y-Phase Burn
10:45 |  | Sylhet 132/33kV S/S T1 LT Scheduled S/D Due to T1A 33 KV Y-Phase Cable Burn
10:47 | 11:35 | BIPTC S/S 10CF16 Forced S/D Due to shutdown is taken by Md. sadequl islam for emergency
maintenance.
10:49 | 16:42 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT Scheduled S/D Due to Annual Maintence
10:49 | 16:42 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 HT Scheduled S/D Due to Annual Maintenance
11:28 | 12:49 | Ishwardi-Natore 132kV Ckt-1 Scheduled S/D from Natore 132/33kV end Due to Shutdown
taken ishurdi Grid Sub-station and from Ishurdi 132/33kV end Due to for DC eart fault
locator installation
11:28 | 12:48 | Ishwardi-Natore 132kV Ckt-2 Scheduled S/D from Natore 132/33kV end Due to Shutdown
taken ishurdi Grid Sub-station and from Ishurdi 132/33kV end Due to for DC eart fault
locator installation
11:31 |  | Shikalbaha 225MW CCPP STG synch
11:34 | 11:55 | Hasnabad-Sitalakhya 132kV Ckt-1 Tripped from Hasnabad 132/33kV end showing Main | [7 empty] | 70.0MW load
|  | protection relay, Back up protection relay. relays Due to Unknown | [7 empty] | interrup. Hasnabad
132/33kV end
| 11:48 | Dohazari 132/33kV S/S Power Transformer -T-1 HT is restored.
12:00 |  | Day peak Generation is 9404 MW
12:27 | 13:31 | Fenchuganj-Kulaura 132 kV Ckt-1 Scheduled S/D from Kulaura 132/33kV end Due to Fenchuganj
sub station take this shutdown
| 12:43 | Khulshi 132/33kV S/S 405T (T1) HT is restored.
| 12:44 | Khulshi 132/33kV S/S 405T (T1) LT is restored.
13:19 |  | Sirajgonj 225MW CCPP Unit-1, FGMO is ON with remarks:-
14:20 | 15:34 | Tangail 132/33kV S/S Tr-4 HT Forced S/D Due to oil leakage maintenance
14:20 | 15:34 | Tangail 132/33kV S/S Tr-4 LT Forced S/D Due to oil leakage maintenance
| 14:52 | Kabirpur 132/33kV S/S XFR, T-I HT is restored.
15:16 | 16:17 | Fenchuganj-Kulaura 132 kV Ckt-2 Project Work S/D from Kulaura 132/33kV end Due to From
NLDC. and from Fenchuganj 230/132/33kV end Due to Annual maintenance
15:17 | 15:47 | Ishurdi 230/132kV S/S 230/132 kV T-03 HT Scheduled S/D Due to For DC fearth fault locator
connection
15:17 | 15:47 | Ishurdi 230/132kV S/S 230/132 kV T-03 LT Scheduled S/D Due to For DC fearth fault locator
connection
15:23 |  | Rampal 400/230kV S/S Generator Transformer-2 (GT-2) HT Project Work S/D Due to Permit has
taken Against PTW No:14961
| 16:05 | Bhandaria 132/33kV S/S Main Bus Bar is restored.
| 16:06 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
| 16:07 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
| 16:08 | Barishal-Bhandaria 132 kV Ckt-1 is restored.
| 16:09 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
| 16:18 | Kabirpur 132/33kV S/S XFR, T-2 HT is restored.
| 16:23 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
16:44 | 17:34 | Fenchuganj-Fenchuganj 132 kV Ckt-4 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual maintenance
17:00 | 18:21 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Forced S/D Due to Ct change by pdb
| 17:16 | Patuakhali-Payra 132kV Ckt-1 is restored.
19:00 |  | Evening Peak Generation: 10725 MW.
19:23 |  | Ashuganj 450 MW CCPP(South) record a general event:- Interbus Transformer 02 BREAKER (Q0)
CLOSED at 19.21
| 20:19 | Kabirpur -Kodda 132kV Ckt-1 is restored.
| 01:19 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor is restored.
04:00 |  | Min. Gen. 7177 MW
07:21 |  | Aminbazar-Airport(Old) 230kV Ckt-1 Scheduled S/D from Agargaon 230/132kV end Due to 230
kV Agargaon-Aminbazar S/D due to Disc Cleaning.
07:26 |  | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Patuakhali 132/33kV end Due to Annual
Maintenance 2025 and from Payra 400/132/33kV end Due to Annual maintenance
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 327 | 7387200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9925000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 264 | 7045527 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 136182 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 227160 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 369600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 294787 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 204879 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 483600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 455760 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 515880 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 33 | 764900 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 34 | 508320 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 111 | 1597968 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1077120 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 701280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 183731 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 17 | 378720 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Machine problem
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 35 | 144000 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 1769 | 32401614
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133515 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 107520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 685500 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 3417741 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 44 | 206581 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 24 | 36096 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 17 | 31123 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 26880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 0 | 21 | 589920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23879 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 82800 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 20 | 57708 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 36 | 48960 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 185673 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 30109 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 614 | 11389090 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 0 | 112800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 935 | 20901818.18 | -
Chattogram Area Total |  |  |  |  | 4873.22 | 2026 | 38067713.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4657000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | schedule outage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 41 | 1007352 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 605280 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 180 | 3328727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 976269 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 90 | 232509 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 1125200 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 429600 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 58 | 1190400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 358950 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 148680 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 517440 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 454564 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 899 | 15031971
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 31 | 731520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 47 | 684000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 438000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 291840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 247680 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 41760 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 147 | 2446800
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3658255 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 42960 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1225920 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 133 | 3205590 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 339 | 8539000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 340 | 7732800 | FGMO
Sylhet Area Total |  |  |  |  | 2370.57 | 1062 | 24404525
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 894 | 19630545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 353 | 8384544 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 462960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1247 | 28478049
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 124640 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 3142000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 25213090.91 | -
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5179040 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 540000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5804000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3192 | -
Barishal Area Total |  |  |  |  | 2265.1 | 2018 | 40005962.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 173 | 4294727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 172 | 4535936 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 11.5 | 145944 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52 | 83098 | Liquid fuel shortage
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 43 | 185776 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 27960 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 756 | 13117634 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 331504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 540700 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1207.5 | 23263279
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 70 | 1615854 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4771000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34138.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 107728 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 166953 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 990720 | -
Rangpur Area Total |  |  |  |  | 950 | 350 | 7686393.92
Eastern Grid Total |  |  |  |  | 16637.75 | 5903 | 112352623.18
Western Grid Total |  |  |  |  | 10294.5 | 4822.5 | 99433684.83
National Grid Total |  |  |  |  | 26932.25 | 10725.5 | 211786308.01
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7070.49 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3180.6 | MW
i) Dhaka area |  |  | 3722.29 |  | MW | i) Khulna area |  |  |  | 1198 | MW
ii) Chattogram area |  |  | 1136.2 |  | MW | ii) Barishal area |  |  |  | 299 | MW
iii) Cumilla area |  |  | 917 |  | MW | iii) Rajshahi area |  |  |  | 998.6 | MW
iv) Mymensingh area |  |  | 920 |  | MW | iv) Rangpur area |  |  |  | 685 | MW
v) Sylhet area |  |  | 375 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10251.09 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 16 | 20:00 | 67 | Jaldhaka | 56 | 18:00 | 133 | Purbasadipur | 99 | 18:30
2 | AKSML | 100.6 | 23:00 | 68 | Jamalpur | 94 | 18:30 | 134 | Rahanpur | 0 | 00:00
3 | Aftabnagar | 24 | 13:00 | 69 | Jashore | 97 | 18:30 | 135 | Rahim | 30 | 22:00
4 | Agargaon | 68 | 13:00 | 70 | Jhenaidah | 95 | 18:00 | 136 | Rajbari | 56 | 18:30
5 | Agrabad | 60 | 18:30 | 71 | Joydebpur | 125 | 18:00 | 137 | Rajendrapur | 100 | 13:00
6 | Amnura | 45 | 12:00 | 72 | Joypurhat | 46 | 13:00 | 138 | Rajshahi | 82 | 18:30
7 | Ashuganj | 52 | 14:00 | 73 | Juldah | 10 | 11:00 | 139 | Rajshahi-230 | 51 | 13:00
8 | BSRM | 192 | 05:00 | 74 | KSRM | 31 | 19:30 | 140 | Ramganj | 98 | 18:00
9 | Bagerhat | 70 | 18:30 | 75 | Kabirpur | 160 | 18:00 | 141 | Rampur | 26 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 52 | 19:00 | 142 | Rangamati | 11 | 18:00
11 | Bakulia | 81 | 18:00 | 77 | Kallyanpur | 78 | 12:00 | 143 | Rangpur | 106 | 18:30
12 | Banani | 35 | 13:00 | 78 | Kalurghat | 26 | 12:00 | 144 | Ruppur | 3 | 00:00
13 | Bangabhaban | 4 | 10:00 | 79 | Kamrangirchar | 51.39 | 13:00 | 145 | SSM | 15 | 00:00
14 | Barapukuria | 45 | 18:00 | 80 | Kaptai | N/A | N/A | 146 | Saidpur | 87 | 18:30
15 | Barguna | 14 | 18:30 | 81 | Kazla | 88 | 13:00 | 147 | Satkhira | 88 | 18:30
16 | Barishal | 73 | 20:00 | 82 | Keranigonj | 56 | 17:00 | 148 | Satmasjid | 75 | 13:00
17 | Barishal-230 | 64 | 20:00 | 83 | Khagrachori | 22 | 18:00 | 149 | Savar | 154 | 11:00
18 | Baroaulia | 51 | 12:00 | 84 | Khulna | 65 | 13:00 | 150 | SevenRings | 19.26 | 19:30
19 | Baroirhat | 37 | 18:00 | 85 | Khulshi | 153 | 13:00 | 151 | ShahCement | 29 | 22:00
20 | Bashundhara | 121 | 13:00 | 86 | Kishoreganj | 123 | 18:00 | 152 | Shahjadpur | 50 | 18:30
21 | BashundharaCement | 6 | 15:00 | 87 | Kodda | 272 | 18:00 | 153 | Shahjibazar | 82 | 18:00
22 | Beanibazar | 42 | 18:00 | 88 | Kulaura | 26 | 18:00 | 154 | Shahmirpur | 39 | 16:00
23 | Benapole | 50 | 09:00 | 89 | Kurigram | 46 | 18:30 | 155 | Shariatpur | 52 | 19:30
24 | Bhaluka | 114 | 12:00 | 90 | Kushtia | 108 | 18:30 | 156 | Sherpur | 114 | 18:00
25 | Bhandaria | 40 | 18:00 | 91 | Lalbag | 64 | 13:00 | 157 | Shikalbaha | 20 | 18:00
26 | Bhangura | 22 | 18:00 | 92 | Lalmonirhat | 47 | 18:30 | 158 | Shitalakhya | 58.8 | 14:00
27 | Bheramara(GK) | 50 | 13:00 | 93 | MI_Cement | 15.8 | 17:00 | 159 | Sholosohor | 30 | 15:00
28 | Bhulta | 227 | 17:00 | 94 | Madanganj | 28 | 12:00 | 160 | Shyampur | 140 | 11:00
29 | Bog-Sherpur | 56 | 19:00 | 95 | Madaripur | 71 | 19:00 | 161 | Siddhirganj | 102 | 12:00
30 | Bogura | 111 | 19:00 | 96 | Madartek | 62.75 | 13:00 | 162 | Sirajganj | 64 | 18:30
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 39 | 18:00 | 163 | Sonargaon | 68 | 09:00
32 | Brahmanbaria | 109 | 19:30 | 98 | Magura | 46 | 18:30 | 164 | Sreemongol | 52 | 18:30
33 | Cantonment | 74 | 13:00 | 99 | Mahasthangarh | 50 | 19:00 | 165 | Sreepur | 62 | 18:30
34 | Chandpur | 48 | 20:00 | 100 | Manikganj | 108 | 18:30 | 166 | Srinagar | 30 | 21:00
35 | Chandraghona | 25 | 18:00 | 101 | Maniknagar | 36 | 13:00 | 167 | Sunamganj | 46 | 18:30
36 | Chapai | 47 | 13:00 | 102 | Matarbari | 35 | 18:30 | 168 | Sylhet | 28 | 19:00
37 | Charsaidpur | 37 | 23:00 | 103 | Matuail | 44 | 10:00 | 169 | Sylhet-132 | 76 | 18:00
38 | Chauddagram | 41 | 18:00 | 104 | Millgate | 66 | 12:00 | 170 | TK | 21 | 18:00
39 | Chhatak | 20 | 18:00 | 105 | Mirpur | 91 | 14:00 | 171 | Tangail | 134 | 18:00
40 | Chowmuhani | 139 | 18:00 | 106 | Mirsorai | 8 | 18:00 | 172 | Thakurgaon | 76 | 18:30
41 | Chuadanga | 78 | 13:00 | 107 | Mirzapur | 50 | 08:00 | 173 | Tongi | 92 | 11:00
42 | Coxsbazar | 96 | 19:30 | 108 | Mithapukur | 40 | 18:00 | 174 | Ullahpara | 21 | 13:00
43 | Cumilla(N) | 110 | 19:00 | 109 | Modern | 0 | 00:00 | 175 | Ullon | 33 | 14:00
44 | Cumilla(S) | 125 | 18:00 | 110 | Mogbazar | 71.9 | 16:00 | 176 | Uttara | 56 | 17:00
45 | Daudkandi | 102 | 18:30 | 111 | Mongla | 25 | 12:00 | 177 | UttaraNew | 33 | 12:00
46 | Dhaka | 28 | 13:00 | 112 | Motijheel | 24 | 13:00 | 178 | Zigatola | 68 | 13:00
47 | Dhamrai | 92 | 18:00 | 113 | Munshiganj | 64 | 19:30
48 | Dhanmondi | 84 | 13:00 | 114 | Mymensingh | 185 | 18:00
49 | Dohazari | 66 | 18:30 | 115 | Naogaon | 93 | 19:00
50 | Faridpur | 108 | 19:00 | 116 | Narail | 40 | 18:00
51 | Fatullah | 74 | 12:00 | 117 | Narinda | 46 | 13:00
52 | Fenchuganj | 27 | 17:00 | 118 | Narshingdi | 149 | 20:00
53 | Feni | 85 | 18:00 | 119 | Natore | 108 | 18:30
54 | GPH | 82 | 18:00 | 120 | Nawabganj | 34.8 | 14:00
55 | Ghatail | 28 | 08:00 | 121 | Netrakona | 127 | 18:30
56 | Ghorashal | 8 | 20:00 | 122 | New | 62.3 | 12:00
57 | Ghorashal-230 | 57 | 18:00 | 123 | Niamatpur | 63 | 13:00
58 | Goalpara | 26 | 13:00 | 124 | Noapara | 34 | 18:30
59 | Gollamari | 54 | 13:00 | 125 | PHP | 9 | 15:00
60 | Gopalganj | 73.2 | 18:30 | 126 | Pabna | 76 | 18:30
61 | Gulshan | 54 | 13:00 | 127 | Palashbari | 74 | 18:30
62 | Halishahar | 33 | 09:00 | 128 | Panchagarh | 43 | 18:00
63 | HaripurSBU | 158 | 17:00 | 129 | Patuakhali | 56 | 21:00
64 | Hasnabad | 73 | 12:00 | 130 | Payra | 14 | 18:00
65 | Hathazari | 55 | 13:00 | 131 | Postogola | 40 | 13:00
66 | Ishurdi | 55 | 18:30 | 132 | Purbachal | 15 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8000.1 | 0 |  | 8000.1
1:00 | 7544.92 | 0 |  | 7544.92
2:00 | 7183.73 | 0 |  | 7183.73
3:00 | 6975.1 | 0 |  | 6975.1
4:00 | 6749.46 | 0 |  | 6749.46
5:00 | 6594.92 | 0 |  | 6594.92
6:00 | 6970.59 | 0 |  | 6970.59
7:00 | 7533.29 | 0 |  | 7533.29
8:00 | 8580.23 | 0 |  | 8580.23
9:00 | 8858.31 | 0 |  | 8858.31
10:00 | 8654.63 | 0 |  | 8654.63
11:00 | 8801.93 | 0 |  | 8801.93
12:00 | 9408.73 | 0 |  | 9408.73
13:00 | 9785.53 | 0 |  | 9785.53
14:00 | 9610.56 | 0 |  | 9610.56
15:00 | 8969.32 | 0 |  | 8969.32
16:00 | 8745.73 | 0 |  | 8745.73
17:00 | 8939.27 | 0 |  | 8939.27
18:00 | 10600.5 | 0 |  | 10600.5
19:00 | 10725.5 | 0 |  | 10725.5
19:30 | 10472.5 | 0 |  | 10472.5
20:00 | 10410.5 | 0 |  | 10410.5
21:00 | 10280.5 | 0 |  | 10280.5
22:00 | 9681.5 | 0 |  | 9681.5
23:00 | 9298.5 | 0 |  | 9298.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4132 | 3868.1 | 8000.1 | DAILY LOAD CURVE
00:30 | 4070 | 3702.51 | 7772.51
01:00 | 4008 | 3536.92 | 7544.92 | 11-01-2025
01:30 | 3928.5 | 3435.825 | 7364.325
02:00 | 3849 | 3334.73 | 7183.73
02:30 | 3744.5 | 3334.915 | 7079.415
03:00 | 3640 | 3335.1 | 6975.1
03:30 | 3621 | 3241.28 | 6862.28
04:00 | 3602 | 3147.46 | 6749.46
04:30 | 3554 | 3118.19 | 6672.19
05:00 | 3506 | 3088.92 | 6594.92
05:30 | 3586 | 3196.755 | 6782.755
06:00 | 3666 | 3304.59 | 6970.59
06:30 | 3797.895 | 3454.045 | 7251.94
07:00 | 3929.79 | 3603.5 | 7533.29
07:30 | 4205.155 | 3851.605 | 8056.76
08:00 | 4480.52 | 4099.71 | 8580.23
08:30 | 4516.785 | 4202.485 | 8719.27
09:00 | 4553.05 | 4305.26 | 8858.31
09:30 | 4538.18 | 4218.29 | 8756.47
10:00 | 4523.31 | 4131.32 | 8654.63
10:30 | 4581.195 | 4147.085 | 8728.28
11:00 | 4639.08 | 4162.85 | 8801.93
11:30 | 4784.01 | 4321.32 | 9105.33
12:00 | 4928.94 | 4479.79 | 9408.73
12:30 | 4953.52 | 4643.61 | 9597.13
13:00 | 4978.1 | 4807.43 | 9785.53
13:30 | 4945.515 | 4752.53 | 9698.045
14:00 | 4912.93 | 4697.63 | 9610.56
14:30 | 4767.245 | 4522.695 | 9289.94
15:00 | 4621.56 | 4347.76 | 8969.32
15:30 | 4614.14 | 4243.385 | 8857.525
16:00 | 4606.72 | 4139.01 | 8745.73
16:30 | 4721.33 | 4121.17 | 8842.5
17:00 | 4835.94 | 4103.33 | 8939.27
17:30 | 5416.97 | 4352.915 | 9769.885
18:00 | 5998 | 4602.5 | 10600.5
18:30 | 5950.5 | 4712.5 | 10663
19:00 | 5903 | 4822.5 | 10725.5
19:30 | 5739 | 4733.5 | 10472.5
20:00 | 5697 | 4713.5 | 10410.5
20:30 | 5656.5 | 4689 | 10345.5 |  | Executive Engineer
21:00 | 5616 | 4664.5 | 10280.5 |  | Network Operation Division
21:30 | 5350.5 | 4630.5 | 9981
22:00 | 5085 | 4596.5 | 9681.5
22:30 | 4950 | 4540 | 9490
23:00 | 4815 | 4483.5 | 9298.5

## En-Curve
QF-LDC-12
Date | 11-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2420 | 1379.5 | 764 | 0 | 48 | 507.6 | 26 | 2850 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | DAILY ENERGY CURVE
00:30 | 2419.5 | 1390.5 | 740.5 | 0 | 47 | 459.51 | 26 | 2683.5 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 11-01-2025
01:00 | 2419 | 1401.5 | 717 | 0 | 46 | 411.42 | 26 | 2517 | 0 | 0 | 0 | 0 | 0 | 7 | 0
01:30 | 2409 | 1382 | 716.5 | 0 | 48 | 416.325 | 26 | 2354 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0 |  | Total Energy | 211.7863 |  | MKWHr
02:00 | 2399 | 1362.5 | 716 | 0 | 50 | 421.23 | 26 | 2191 | 0 | 0 | 0 | 0 | 0 | 18 | 0 |  | Energy not Served | 0 |  | MKWHr
02:30 | 2399.5 | 1301 | 716.5 | 0 | 49 | 419.415 | 26 | 2144.5 | 0 | 0 | 0 | 0 | 0 | 23.5 | 0 |  | Energy Requirement | 211.7863 |  | MKWHr
03:00 | 2400 | 1239.5 | 717 | 0 | 48 | 417.6 | 26 | 2098 | 0 | 0 | 0 | 0 | 0 | 29 | 0
03:30 | 2394.5 | 1228.5 | 622.5 | 0 | 48 | 419.28 | 26 | 2096 | 0 | 0 | 0 | 0 | 0 | 27.5 | 0
04:00 | 2389 | 1217.5 | 528 | 0 | 48 | 420.96 | 26 | 2094 | 0 | 0 | 0 | 0 | 0 | 26 | 0
04:30 | 2341.5 | 1194.5 | 528 | 0 | 45 | 419.19 | 26 | 2098.5 | 0 | 0 | 0 | 0 | 0 | 19.5 | 0
05:00 | 2294 | 1171.5 | 528 | 0 | 42 | 417.42 | 26 | 2103 | 0 | 0 | 0 | 0 | 0 | 13 | 0
05:30 | 2225 | 1223.5 | 528 | 0 | 42 | 417.755 | 26 | 2312 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0
06:00 | 2156 | 1275.5 | 528 | 0 | 42 | 418.09 | 26 | 2521 | 0 | 0 | 0 | 0 | 0 | 4 | 0
06:30 | 2126 | 1308 | 622 | 0 | 42 | 417.045 | 26 | 2657 | 4.395 | 28.5 | 16.5 | 0 | 0 | 4.5 | 0
07:00 | 2096 | 1340.5 | 716 | 0 | 42 | 416 | 26 | 2793 | 8.79 | 57 | 33 | 0 | 0 | 5 | 0
07:30 | 2205 | 1445 | 763.5 | 0 | 42 | 511.315 | 26 | 2887.5 | 59.945 | 61.5 | 51.5 | 0 | 0 | 3.5 | 0
08:00 | 2314 | 1549.5 | 811 | 0 | 42 | 606.63 | 26 | 2982 | 111.1 | 66 | 70 | 0 | 0 | 2 | 0
08:30 | 2304.5 | 1512.25 | 812.5 | 0 | 42 | 607.905 | 26 | 3020.5 | 208.615 | 89 | 93.5 | 0 | 0 | 2.5 | 0
09:00 | 2295 | 1475 | 814 | 0 | 42 | 609.18 | 26 | 3059 | 306.13 | 112 | 117 | 0 | 0 | 3 | 0
09:30 | 2274.5 | 1423.75 | 861.5 | 0 | 39 | 536.43 | 26 | 2914 | 381.79 | 127.5 | 170.5 | 0 | 0 | 1.5 | 0
10:00 | 2254 | 1372.5 | 909 | 0 | 36 | 463.68 | 26 | 2769 | 457.45 | 143 | 224 | 0 | 0 | 0 | 0
10:30 | 2284.5 | 1390 | 909 | 0 | 39 | 462.34 | 26 | 2739.5 | 506.44 | 135 | 236.5 | 0 | 0 | 0 | 0
11:00 | 2315 | 1407.5 | 909 | 0 | 42 | 461 | 26 | 2710 | 555.43 | 127 | 249 | 0 | 0 | 0 | 0
11:30 | 2384.5 | 1498.5 | 909.5 | 0 | 44 | 489.605 | 26 | 2809.5 | 571.225 | 128.5 | 244 | 0 | 0 | 0 | 0
12:00 | 2454 | 1589.5 | 910 | 0 | 46 | 518.21 | 26 | 2909 | 587.02 | 130 | 239 | 0 | 0 | 0 | 0
12:30 | 2444.5 | 1589.5 | 910 | 0 | 53 | 563.28 | 26 | 3060.5 | 578.35 | 133 | 239 | 0 | 0 | 0 | 0
13:00 | 2435 | 1589.5 | 910 | 0 | 60 | 608.35 | 26 | 3212 | 569.68 | 136 | 239 | 0 | 0 | 0 | 0
13:30 | 2389.5 | 1523 | 909.5 | 0 | 62 | 607.175 | 26 | 3265 | 524.87 | 136 | 253.5 | 0 | 0 | 1.5 | 0
14:00 | 2344 | 1456.5 | 909 | 0 | 64 | 606 | 26 | 3318 | 480.06 | 136 | 268 | 0 | 0 | 3 | 0
14:30 | 2362.5 | 1405 | 908.5 | 0 | 59 | 558.5 | 26 | 3162.5 | 418.94 | 128 | 258.5 | 0 | 0 | 2.5 | 0
15:00 | 2381 | 1353.5 | 908 | 0 | 54 | 511 | 26 | 3007 | 357.82 | 120 | 249 | 0 | 0 | 2 | 0
15:30 | 2424.5 | 1357.25 | 908.5 | 0 | 54 | 515.5 | 26 | 2958.5 | 268.775 | 120 | 223.5 | 0 | 0 | 1 | 0
16:00 | 2468 | 1361 | 909 | 0 | 54 | 520 | 26 | 2910 | 179.73 | 120 | 198 | 0 | 0 | 0 | 0
16:30 | 2423.5 | 1350 | 909 | 0 | 54 | 526.5 | 26 | 2994.5 | 104.5 | 149 | 305.5 | 0 | 0 | 0 | 0
17:00 | 2379 | 1339 | 909 | 0 | 54 | 533 | 26 | 3079 | 29.27 | 178 | 413 | 0 | 0 | 0 | 0
17:30 | 2457 | 1481.75 | 901 | 0 | 59 | 621.5 | 26 | 3153 | 14.635 | 240 | 816 | 0 | 0 | 0 | 0
18:00 | 2535 | 1624.5 | 893 | 0 | 64 | 710 | 26 | 3227 | 0 | 302 | 1219 | 0 | 0 | 0 | 0
18:30 | 2515.5 | 1609.5 | 893.5 | 0 | 61 | 733 | 30.5 | 3303.5 | 0 | 270.5 | 1246 | 0 | 0 | 0 | 0
19:00 | 2496 | 1594.5 | 894 | 0 | 58 | 756 | 35 | 3380 | 0 | 239 | 1273 | 0 | 0 | 0 | 0
19:30 | 2528 | 1650.5 | 893 | 0 | 56 | 765 | 40 | 3381 | 0 | 162 | 997 | 0 | 0 | 0 | 0
20:00 | 2519 | 1651.5 | 894 | 0 | 56 | 755 | 40 | 3379 | 0 | 162 | 954 | 0 | 0 | 0 | 0
20:30 | 2514 | 1650.5 | 893.5 | 0 | 56 | 755.5 | 40 | 3356.5 | 0 | 145 | 934.5 | 0 | 0 | 0 | 0
21:00 | 2509 | 1649.5 | 893 | 0 | 56 | 756 | 40 | 3334 | 0 | 128 | 915 | 0 | 0 | 0 | 0
21:30 | 2491.5 | 1641 | 888.5 | 0 | 55 | 755 | 40 | 3334 | 0 | 106.5 | 669.5 | 0 | 0 | 0 | 0
22:00 | 2474 | 1632.5 | 884 | 0 | 54 | 754 | 40 | 3334 | 0 | 85 | 424 | 0 | 0 | 0 | 0
22:30 | 2460 | 1625.5 | 884 | 0 | 53 | 756 | 40 | 3302 | 0 | 68 | 301.5 | 0 | 0 | 0 | 0
23:00 | 2446 | 1618.5 | 884 | 0 | 52 | 758 | 40 | 3270 | 0 | 51 | 179 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 420 | 04:00 | 388 | 12:00 | Kaliakoir | 383 | 02:00 | 272 | 22:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 414 | 2:00 | 381 | 13:00 | Madunaghat | 409 | 03:00 | 394 | 13:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 413 | 02:00 | 386 | 13:00 | Meghnaghat | 415 | 02:00 | 385 | 13:00
| Bibiana | 397 | 04:00 | 383 | 13:00 | Payra | 420 | 04:00 | 404 | 13:00
| BIPTC | 407 | 02:00 | 387 | 10:00 | Rahanpur | 416 | 04:00 | 400 | 13:00
| Bogura | 412 | 02:00 | 395 | 13:00 | Rampal | 418 | 02:00 | 390 | 13:00
| Gopalganj | 419 | 02:00 | 391 | 13:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 240 | 04:00 | 221 | 13:00 | Haripur | 242 | 04:00 | 222 | 13:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 236 | 02:00 | 220 | 12:00 | Hasnabad | 235 | 00:00 | 221 | 13:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 237 | 01:00 | 221 | 12:00 | Hathazari | 232 | 00:00 | 224 | 16:00
| Ashuganj | 243 | 03:00 | 228 | 13:00 | Ishurdi | 246 | 02:00 | 230 | 13:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 243 | 03:00 | 228 | 13:00 | Jhenaidah | 244 | 02:00 | 225 | 14:00
| Baghabari | 241 | 00:00 | 232 | 12:00 | Kaliakoir | 240 | 02:00 | 226 | 13:00 | 230 kV MAX | 250 |  | 250 | 219
| Barapukuria | 226 | 01:00 | 219 | 18:00 | Keranigonj | 239 | 04:00 | 221 | 13:00 | 230 kV MIN | 219 |  | 246 | 221 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 226 | 01:00 | 219 | 18:00 | Khulna(S) | 244 | 02:00 | 223 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 248 | 04:00 | 236 | 13:00 | Madunaghat | 234 | 06:00 | 224 | 13:00 | 132 kV MAX | 143 |  | 143 | 112 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 244 | 02:00 | 227 | 13:00 | Madunaghat-400 | 235 | 04:00 | 225 | 13:00 | 132 kV MIN | 109 |  | 143 | 109 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 241 | 02:00 | 225 | 12:00 | Maniknagar | 239 | 03:00 | 224 | 13:00 | [35 empty] | 6:00
| Bibiana | 230 | 01:00 | 220 | 13:00 | Meghnaghat | 245 | 06:00 | 230 | 12:00 | [35 empty] | 392
| BIPTC | 245 | 02:00 | 228 | 13:00 | Meghnaghat-400 | 241 | 02:00 | 223 | 13:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 240 | 02:00 | 230 | 13:00 | Mirsorai | 234 | 02:00 | 221 | 14:00 | ` | [34 empty] | 21:00
| Bogura-400 | 240 | 04:00 | 229 | 12:00 | Rajshahi | 243 | 03:00 | 227 | 13:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 250 | 04:00 | 242 | 13:00 | Rampal | 241 | 02:00 | 223 | 13:00 |  |  |  |  | Ash 400-299274
| BSRM | 233 | 03:00 | 222 | 12:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 234 | 00:00 | 222 | 13:00 | Rampura | 241 | 04:00 | 224 | 13:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 248 | 02:00 | 235 | 12:00 | Shikalbaha | 234 | 03:00 | 221 | 12:00 |  | kaptai by call 399528
| Fenchuganj | 233 | 00:00 | 223 | 11:00 | Shyampur | 239 | 02:00 | 224 | 13:00
| Ghorashal | 240 | 00:00 | 230 | 13:00 | Siddhirganj | 241 | 01:00 | 226 | 12:00
| Ghorashal-230 | 241 | 04:00 | 223 | 13:00 | Sirajgonj | 247 | 04:00 | 237 | 12:00
| Gopalganj | 248 | 02:00 | 232 | 13:00 | Sreepur | 242 | 04:00 | 228 | 13:00
| GPH | 234 | 04:00 | 222 | 13:00 | Tongi | 236 | 01:00 | 223 | 16:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 139 | 02:00 | 128 | 13:00 | Kurigram | 132 | 04:00 | 120 | 18:30 |  | Gopalganj-230 | 599470
| Agargaon | 140 | 04:00 | 127 | 13:00 | Kushtia | 140 | 00:00 | 133 | 13:00
| Agrabad | 135 | 03:00 | 127 | 13:00 | Lalbag | 140 | 04:00 | 129 | 13:00
| AKS | 132 | 00:00 | 126 | 13:00 | Lalmonirhat | 131 | 17:00 | 120 | 08:00
| Aminbazar | 137 | 01:00 | 127 | 12:00 | Madanganj | 135 | 06:00 | 126 | 14:00
| Amnura | 140 | 00:00 | 131 | 12:00 | Madaripur | 137 | 05:00 | 132 | 18:30
| Ashuganj | 142 | 07:00 | 136 | 13:00 | Madartek | 137 | 02:00 | 127 | 12:00
| Bagerhat | 140 | 04:00 | 125 | 13:00 | Madunaghat | 135 | 07:00 | 129 | 12:00
| Bajitpur | 137 | 02:00 | 132 | 16:00 | Magura | 141 | 02:00 | 128 | 13:00
| Bakulia | 135 | 04:00 | 127 | 13:00 | Mahasthangarh | 137 | 02:00 | 129 | 12:00
| Banani | 139 | 04:00 | 128 | 13:00 | Manikganj | 131 | 03:00 | 123 | 17:00
| Bangabhaban | 138 | 02:00 | 125 | 13:00 | Maniknagar | 137 | 05:00 | 127 | 13:00
| Barapukuria | 136 | 01:00 | 130 | 18:00 | Matarbari | 126 | 03:00 | 120 | 21:00
| Barguna | 140 | 17:00 | 132 | 13:00 | Matuail | 137 | 02:00 | 127 | 13:00
| Barishal | 136 | 01:00 | 130 | 13:00 | Millgate | 137 | 03:00 | 126 | 13:00
| Barishal-230 | 139 | 04:00 | 131 | 13:00 | Mirpur | 137 | 02:00 | 128 | 12:00
| Baroaulia | 135 | 05:00 | 128 | 13:00 | Mirzapur | 134 | 07:00 | 125 | 13:00
| Baroirhat | 130 | 00:00 | 124 | 12:00 | Mithapukur | 135 | 01:00 | 126 | 12:00
| Bashundhara | 138 | 01:00 | 125 | 13:00 | MI_Cement | 139 | 04:00 | 129 | 13:00
| BashundharaCement | 135 | 06:00 | 126 | 15:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 135 | 00:00 | 130 | 13:00 | Mogbazar | 141 | 02:00 | 128 | 13:00
| Benapole | 140 | 02:00 | 124 | 13:00 | Mongla | 140 | 02:00 | 128 | 18:30
| Bhaluka | 129 | 00:00 | 120 | 14:00 | Motijheel | 138 | 02:00 | 125 | 13:00
| Bhandaria | 135 | 06:00 | 126 | 18:00 | Munshiganj | 136 | 06:00 | 127 | 14:00
| Bhangura | 139 | 00:00 | 134 | 16:00 | Mymensingh | 133 | 10:00 | 116 | 07:00
| Bheramara | 141 | 01:00 | 134 | 13:00 | Naogaon | 136 | 01:00 | 128 | 13:00
| Bheramara(GK) | 141 | 01:00 | 134 | 13:00 | Narail | 142 | 04:00 | 128 | 13:00
| Bhulta | 126 | 03:00 | 120 | 12:00 | Narinda | 137 | 7:00 | 127 | 13:00
| Bog-Sherpur | 138 | 02:00 | 130 | 13:00 | Narshingdi | 135 | 00:00 | 124 | 12:00
| Bogura | 138 | 05:00 | 131 | 13:00 | Natore | 140 | 03:00 | 131 | 13:00
| Bogura-230 | 138 | 02:00 | 131 | 13:00 | Nawabganj | 139 | 01:00 | 129 | 13:00
| Brahmanbaria | 137 | 00:00 | 130 | 12:00 | Netrakona | 129 | 00:00 | 116 | 14:00
| Cantonment | 140 | 04:00 | 127 | 13:00 | New | 135 | 04:00 | 126 | 12:00
| Chandpur | 135 | 18:30 | 119 | 13:00 | Niamatpur | 140 | 03:00 | 134 | 12:00
| Chandraghona | 136 | 03:00 | 129 | 13:00 | Noapara | 140 | 03:00 | 127 | 13:00
| Chapai | 139 | 02:00 | 132 | 13:00 | Pabna | 142 | 02:00 | 133 | 13:00
| Charsaidpur | 138 | 03:00 | 128 | 12:00 | Palashbari | 132 | 03:00 | 124 | 18:30
| Chauddagram | 134 | 03:00 | 122 | 13:00 | Panchagarh | 139 | 04:00 | 123 | 13:00
| Chhatak | 136 | 05:00 | 129 | 18:00 | Patuakhali | 139 | 17:00 | 132 | 12:00
| Chowmuhani | 128 | 02:00 | 118 | 12:00 | Payra | 138 | 01:00 | 133 | 13:00
| Chuadanga | 140 | 04:00 | 126 | 13:00 | PHP | 133 | 05:00 | 121 | 13:00
| Coxsbazar | 125 | 17:00 | 120 | 19:30 | Postogola | 141 | 03:00 | 131 | 13:00
| Cumilla(N) | 137 | 04:00 | 128 | 13:00 | Purbachal | 139 | 02:00 | 127 | 12:00
| Cumilla(S) | 137 | 04:00 | 125 | 13:00 | Purbasadipur | 132 | 04:00 | 122 | 13:00
| Daudkandi | 134 | 02:00 | 125 | 13:00 | Rahanpur | 140 | 00:00 | 135 | 12:00
| Dhaka | 137 | 00:00 | 128 | 13:00 | Rahanpur-400 | 141 | 02:00 | 135 | 13:00
| Dhamrai | 139 | 02:00 | 128 | 13:00 | Rahim | 134 | 07:00 | 127 | 13:00
| Dhanmondi | 138.5 | 03:00 | 128 | 13:00 | Rajbari | 138 | 02:00 | 128 | 13:00
| Dohazari | 129 | 00:00 | 126 | 16:00 | Rajendrapur | 137 | 02:00 | 131 | 13:00
| Faridpur | 138 | 04:00 | 128 | 13:00 | Rajshahi | 139 | 01:00 | 130 | 12:00
| Fatullah | 139 | 02:00 | 130 | 13:00 | Rajshahi-230 | 141 | 03:00 | 128 | 13:00
| Fenchuganj | 140 | 01:00 | 134 | 12:00 | Ramganj | 130 | 18:30 | 117 | 13:00
| Feni | 131 | 04:00 | 123 | 13:00 | Rampur | 136 | 04:00 | 128 | 13:00
| Ghatail | 132 | 04:00 | 122 | 08:00 | Rampura | 139 | 04:00 | 127 | 13:00
| Ghorashal | 142 | 04:00 | 136 | 11:00 | Rangamati | 135 | 03:00 | 128 | 12:00
| Goalpara | 142 | 02:00 | 128 | 13:00 | Rangpur | 132 | 02:00 | 124 | 18:00
| Gollamari | 142 | 04:00 | 129 | 13:00 | Ruppur | 142 | 01:00 | 136 | 12:00
| Gopalganj | 140 | 02:00 | 128 | 13:00 | Saidpur | 135 | 05:00 | 124 | 13:00
| Gopalganj-400 | 140 | 04:00 | 131 | 13:00 | Satkhira | 139 | 01:00 | 125 | 13:00
| Gulshan | 138 | 04:00 | 128 | 12:00 | Satmasjid | 140 | 04:00 | 127 | 13:00
| Halishahar | 133 | 03:00 | 126 | 11:00 | Savar | 137 | 03:00 | 128 | 11:00
| Haripur | 136 | 02:00 | 126 | 13:00 | SevenRings | 143 | 02:00 | 135 | 13:00
| HaripurSBU | 136 | 02:00 | 126 | 13:00 | ShahCement | 138 | 03:00 | 128 | 12:00
| Hasnabad | 139 | 01:00 | 133 | 12:00 | Shahjadpur | 140 | 00:00 | 138 | 14:00
| Hathazari | 135 | 10:00 | 131 | 16:00 | Shahjibazar | 139 | 03:00 | 131 | 13:00
| Ishurdi | 143 | 01:00 | 135 | 13:00 | Shahmirpur | 133 | 05:00 | 128 | 16:00
| Jaldhaka | 133 | 03:00 | 122 | 09:00 | Shariatpur | 139 | 02:00 | 130 | 13:00
| Jamalpur | 134 | 10:00 | 112 | 07:00 | Sherpur | 131 | 10:00 | 109 | 07:00
| Jashore | 138 | 00:00 | 126 | 13:00 | Shikalbaha | 128 | 13:00 | 116 | 17:00
| Jhenaidah | 140 | 00:00 | 130 | 13:00 | Shikalbaha-230 | 136 | 03:00 | 128 | 12:00
| Jhenaidah-230 | 143 | 02:00 | 130 | 13:00 | Shitalakhya | 139 | 04:00 | 129 | 13:00
| Joydebpur | 140 | 07:00 | 134 | 03:00 | Sholosohor | 134 | 01:00 | 128 | 12:00
| Joypurhat | 136 | 03:00 | 126 | 13:00 | Shyampur | 137 | 04:00 | 130 | 15:00
| Juldah | 133 | 03:00 | 128 | 12:00 | Shyampur-230 | 139 | 02:00 | 126 | 16:00
| Kabirpur | 136 | 03:00 | 125 | 17:00 | Siddhirganj | 136 | 01:00 | 128 | 12:00
| Kachua | 135 | 19:00 | 120 | 13:00 | Sirajganj | 140 | 04:00 | 132 | 13:00
| Kaliakoir | 141 | 04:00 | 129 | 13:00 | Sonargaon | 135 | 04:00 | 125 | 12:00
| Kallyanpur | 136 | 03:00 | 128 | 12:00 | Sreemongol | 138 | 00:00 | 130 | 13:00
| Kalurghat | 135 | 03:00 | 128 | 12:00 | Sreepur | 132 | 04:00 | 123 | 14:00
| Kamrangirchar | 139 | 05:00 | 126 | 12:00 | Srinagar | 139 | 04:00 | 128 | 13:00
| Kaptai | 138 | 3:00 | 131 | 13:00 | SSM | 140 | 04:00 | 131 | 16:00
| Kazla | 138 | 03:00 | 126 | 13:00 | Sunamganj | 134 | 01:00 | 128 | 18:00
| Keranigonj | 140 | 02:00 | 128 | 13:00 | Sylhet | 136 | 02:00 | 130 | 13:00
| Khagrachori | 135 | 03:00 | 127 | 13:00 | Sylhet-132 | 136 | 01:00 | 131 | 13:00
| Khulna | 137 | 00:00 | 127 | 13:00 | Tangail | 132 | 10:00 | 122 | 18:00
| Khulna(S) | 142 | 02:00 | 130 | 13:00 | Thakurgaon | 136 | 04:00 | 122 | 13:00
| Khulshi | 132 | 03:00 | 125 | 13:00 | TK | 134 | 03:00 | 128 | 13:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 135 | 00:00 | 128 | 14:00 | Tongi | 138 | 01:00 | 128 | 12:00 |  |  | Nos | Nos | Nos
| Kodda | 138 | 07:00 | 131 | 00:00 | Ullahpara | 140 | 00:00 | 134 | 13:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 135 | 03:00 | 128 | 12:00 | Ullon | 137 | 06:00 | 127 | 12:00
| Kulaura | 138 | 01:00 | 131 | 13:00 | Uttara | 137 | 02:00 | 128 | 12:00
| Zigatola | 140 | 02:00 | 130 | 13:00 | UttaraNew | 138 | 02:00 | 127 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.