## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-01-2025 | [28 empty] | Date: | 13-01-2025 | [28 empty] | Date: | 13-01-2025 | [28 empty] | Date: | 13-01-2025 | [28 empty] | Date: | 13-01-2025 | [18 empty] | Date: | 13-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [18 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 150.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 0.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 50.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 400 | 302 | 0 | 0 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 1150 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 572 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 190 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 62 | 0 | 0 | 0 | 0 | 316 | 308 | 30 | 30 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 5 | 0 | 0 | 20 | 4689.5 | 904 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 203 | 0 | 193 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 7 | 80 | 180 | 0 | 1120 | 0 | 4316.5 | 9006 | 93.32
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 400 | 244 | 0 | 0 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 1050 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 510 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 56 | 0 | 0 | 0 | 0 | 316 | 303 | 39 | 30 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 12 | 4404.5 | 890 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 182 | 0 | 182 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 80 | 180 | 0 | 1000 | 0 | 4087.5 | 8492 | 93.31
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 400 | 262 | 0 | 0 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 1050 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 430 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 50 | 0 | 0 | 0 | 0 | 316 | 303 | 43 | 30 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 4267.5 | 718 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 178 | 0 | 177 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 80 | 180 | 0 | 980 | 0 | 3741.5 | 8009 | 93.31
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 400 | 288 | 0 | 0 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 1050 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 380 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 48 | 0 | 0 | 0 | 0 | 316 | 301 | 39 | 29 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 4218.5 | 718 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 177 | 0 | 176 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 900 | 0 | 3558.5 | 7777 | 93.31
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 400 | 286 | 0 | 0 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 1005 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 350 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 184 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 44 | 0 | 0 | 0 | 0 | 326 | 303 | 39 | 29 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 4141.5 | 624 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 177 | 0 | 175 | 0 | 0 | 0 | 0 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 800 | 0 | 3364.5 | 7506 | 93.31
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 400 | 288 | 0 | 0 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 1008 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 350 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 42 | 0 | 0 | 0 | 0 | 316 | 300 | 43 | 29 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 4132.5 | 624 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 177 | 0 | 174 | 0 | 0 | 0 | 0 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 800 | 0 | 3363.5 | 7496 | 93.3
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 350 | 301 | 0 | 0 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 14.6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 1007 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 375 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 199 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 52 | 0 | 0 | 0 | 0 | 316 | 322 | 39 | 29 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 11 | 0 | 0 | 0 | 4174.1 | 718 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 177 | 0 | 174 | 0 | 0 | 0 | 0 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 7 | 80 | 220 | 0 | 820 | 0 | 3611.5 | 7785.6 | 93.3
07:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 332 | 0 | 0 | 0 | 18.5 | 0 | 0 | 0 | 0 | 0 | 18.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 1008 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 450 | 1 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 221 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 54 | 0 | 2 | 0 | 0 | 400 | 368 | 43 | 29 | 0 | 2 | 163 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 5 | 0 | 0.7 | 0 | 4626.7 | 906 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.37 | 0 | 0 | 511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52 | 169 | 0 | 177 | 0 | 175 | 0 | 0 | 0 | 0.06 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 209 | 6 | 140 | 220 | 0 | 990 | 0 | 4044.46 | 8671.16 | 93.3
08:00 | 0 | 40 | 25 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 2 | 0 | 29 | 16 | 0 | 0 | 0 | 35 | 22 | 0 | 380 | 320 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 5 | 0 | 18 | 22 | 0 | 0 | 1 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 10 | 1150 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 565 | 7 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 43 | 1 | 0 | 0 | 0 | 14 | 0 | 46 | 0 | 22 | 0 | 0 | 340 | 377 | 43 | 30 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 19 | 55 | 5 | 0 | 9 | 6 | 4899 | 906 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 609.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8.38 | 166 | 0 | 177 | 0 | 176 | 0 | 0 | 0 | 0.78 | 5.5 | 210 | 72 | 0 | 4 | 0 | 0 | 0 | 0.9 | 16 | 0.1 | 0 | 307 | 6 | 140 | 220 | 0 | 1160 | 6 | 4488.43 | 9387.43 | 93.3
09:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 15 | 27 | 0 | 51 | 16 | 0 | 0 | 0 | 35 | 0 | 0 | 380 | 282 | 0 | 0 | 17 | 18 | 0 | 0 | 0 | 13 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 6 | 1150 | 0 | 0 | 19 | 0 | 0 | 230 | 0 | 0 | 0 | 575 | 13 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 34 | 50 | 0 | 0 | 5 | 14 | 0 | 44 | 0 | 44 | 0 | 0 | 340 | 379 | 43 | 30 | 0 | 2 | 130 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 19 | 55 | 4 | 1 | 20.75 | 22 | 5039.75 | 907 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 21.46 | 166 | 0 | 178 | 0 | 177 | 0 | 0 | 0 | 1.77 | 5.5 | 210 | 72 | 0 | 10 | 0 | 0 | 0 | 2.4 | 84 | 0.24 | 0 | 262 | 5 | 100 | 220 | 0 | 1220 | 24 | 4741.37 | 9781.12 | 93.29
10:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 35 | 36 | 0 | 51 | 16 | 0 | 0 | 0 | 35 | 17 | 0 | 330 | 295 | 0 | 0 | 17 | 12 | 0 | 0 | 0 | 19 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 6 | 1150 | 0 | 0 | 20 | 0 | 0 | 227 | 0 | 0 | 0 | 500 | 17 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 186 | 36 | 50 | 0 | 0 | 9 | 14 | 0 | 56 | 0 | 60 | 0 | 0 | 340 | 381 | 39 | 30 | 0 | 2 | 130 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 19 | 55 | 0 | 1 | 29.06 | 22 | 5053.06 | 906 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 690.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 33.92 | 168 | 0 | 178 | 0 | 177 | 0 | 0 | 0 | 2.68 | 5.5 | 210 | 71 | 0 | 18 | 0 | 0 | 0 | 3.9 | 113 | 0.38 | 0 | 250 | 4 | 100 | 180 | 0 | 1100 | 17 | 4584.93 | 9637.99 | 93.29
11:00 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 35 | 36 | 0 | 51 | 16 | 0 | 0 | 0 | 35 | 25 | 0 | 330 | 312 | 0 | 0 | 17 | 12 | 0 | 0 | 0 | 22 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 5 | 1150 | 0 | 0 | 19 | 0 | 0 | 226 | 0 | 0 | 0 | 550 | 19 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 188 | 37 | 50 | 0 | 0 | 9 | 14 | 0 | 58 | 0 | 69 | 0 | 0 | 340 | 383 | 43 | 30 | 0 | 2 | 130 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 19 | 55 | 0 | 1 | 34.08 | 22 | 5181.08 | 906 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 661.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 43.47 | 170 | 0 | 174 | 0 | 172 | 0 | 0 | 0 | 3.31 | 5.5 | 210 | 70 | 0 | 26 | 0 | 0 | 0 | 4.9 | 126 | 0.48 | 0 | 250 | 4 | 100 | 180 | 0 | 1070 | 17 | 4564.69 | 9745.77 | 93.29
12:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 35 | 34 | 0 | 59 | 32 | 0 | 0 | 0 | 72 | 22 | 0 | 380 | 304 | 0 | 0 | 17 | 12 | 0 | 0 | 0 | 25 | 0 | 17 | 20 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 6 | 1150 | 0 | 0 | 22 | 0 | 0 | 222 | 0 | 0 | 0 | 595 | 20 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 195 | 42 | 62 | 0 | 13 | 9 | 14 | 0 | 62 | 0 | 68 | 0 | 0 | 340 | 384 | 43 | 30 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 1 | 24.38 | 22 | 5406.38 | 907 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 704.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 43.14 | 171 | 0 | 171 | 0 | 188 | 0 | 0 | 0 | 3.51 | 5.5 | 210 | 70 | 0 | 28 | 0 | 0 | 0 | 5.3 | 123 | 0.47 | 0 | 307 | 4 | 140 | 220 | 0 | 1080 | 17 | 4778.25 | 10184.63 | 93.29
13:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 37 | 36 | 0 | 85 | 48 | 0 | 0 | 0 | 108 | 22 | 0 | 420 | 300 | 0 | 0 | 35 | 7 | 0 | 0 | 0 | 24 | 0 | 17 | 20 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 6 | 1153 | 0 | 0 | 32 | 0 | 0 | 220 | 0 | 0 | 0 | 608 | 19 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 187 | 41 | 88 | 0 | 42 | 0 | 14 | 0 | 64 | 0 | 66 | 0 | 0 | 340 | 361 | 42 | 30 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 2 | 32.43 | 22 | 5562.43 | 907 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 750.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 39.16 | 171 | 0 | 164 | 0 | 169 | 0 | 0 | 0 | 3.18 | 5.5 | 170 | 69 | 0 | 27 | 0 | 0 | 0 | 5 | 122 | 0.47 | 0 | 307 | 4 | 140 | 220 | 0 | 1180 | 54 | 4857.44 | 10419.87 | 93.28
14:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 54 | 36 | 0 | 100 | 48 | 0 | 0 | 0 | 108 | 22 | 0 | 420 | 317 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 18 | 0 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 10 | 1108 | 0 | 0 | 33 | 0 | 0 | 222 | 0 | 0 | 0 | 605 | 17 | 51 | 0 | 199 | 0 | 0 | 0 | 28 | 199 | 41 | 88 | 0 | 51 | 0 | 14 | 0 | 66 | 0 | 55 | 0 | 0 | 320 | 335 | 42 | 30 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 1 | 26.11 | 22 | 5500.11 | 907 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 32.34 | 172 | 0 | 162 | 0 | 164 | 0 | 0 | 0 | 2.78 | 5.5 | 160 | 67 | 0 | 22 | 0 | 0 | 0 | 4.3 | 118 | 0.37 | 0 | 250 | 4 | 140 | 220 | 0 | 1100 | 17 | 4632.29 | 10132.4 | 93.28
15:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 54 | 36 | 0 | 102 | 48 | 0 | 0 | 0 | 108 | 25 | 0 | 420 | 300 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 13 | 0 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 4 | 1008 | 0 | 0 | 33 | 0 | 0 | 223 | 0 | 0 | 0 | 565 | 13 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 182 | 41 | 50 | 0 | 17 | 0 | 14 | 0 | 62 | 0 | 43 | 0 | 0 | 320 | 335 | 39 | 30 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 1 | 19.62 | 22 | 5218.62 | 907 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 23.06 | 177 | 0 | 138 | 0 | 162 | 0 | 0 | 0 | 1.97 | 5.5 | 208 | 67 | 0 | 15 | 0 | 0 | 0 | 2.9 | 84 | 0.25 | 0 | 250 | 4 | 140 | 220 | 0 | 1050 | 17 | 4522.68 | 9741.3 | 93.28
16:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 54 | 36 | 0 | 95 | 48 | 0 | 0 | 0 | 108 | 25 | 0 | 380 | 311 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 6 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 1008 | 0 | 0 | 33 | 0 | 0 | 223 | 0 | 0 | 0 | 555 | 8 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 184 | 41 | 50 | 0 | 17 | 0 | 14 | 0 | 56 | 0 | 24 | 0 | 0 | 320 | 335 | 39 | 30 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 20 | 0 | 19 | 58 | 0 | 0 | 9.12 | 22 | 5125.12 | 907 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 9.94 | 175 | 0 | 144 | 0 | 158 | 0 | 0 | 0 | 0.79 | 5.5 | 210 | 67 | 0 | 8 | 0 | 0 | 0 | 1.4 | 35 | 0.11 | 0 | 250 | 4 | 140 | 220 | 0 | 1040 | 17 | 4404.74 | 9529.86 | 93.28
17:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 54 | 36 | 0 | 95 | 48 | 0 | 0 | 0 | 108 | 25 | 0 | 380 | 253 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 2 | 0 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 1150 | 0 | 0 | 33 | 0 | 0 | 223 | 0 | 0 | 0 | 605 | 1 | 51 | 16 | 197 | 0 | 0 | 0 | 29 | 183 | 41 | 50 | 0 | 21 | 0 | 12 | 0 | 52 | 0 | 3 | 0 | 0 | 320 | 357 | 42 | 30 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 20 | 0 | 19 | 58 | 0 | 0 | 1.73 | 22 | 5317.73 | 906 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.26 | 176 | 0 | 148 | 0 | 157 | 0 | 0 | 0 | 0.19 | 5.5 | 179 | 67 | 0 | 1 | 0 | 0 | 0 | 0.3 | 7 | 0.02 | 0 | 250 | 5 | 140 | 220 | 0 | 1070 | 90 | 4397.27 | 9715 | 93.27
18:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 54 | 36 | 0 | 95 | 48 | 0 | 20 | 2 | 162 | 25 | 0 | 380 | 318 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 0 | 17 | 16.5 | 20 | 0 | 0 | 27 | 0 | 0 | 0 | 1 | 0 | 24 | 0 | 10 | 36 | 0 | 40 | 26 | 10 | 1150 | 0 | 0 | 35 | 0 | 60 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 110 | 197 | 0 | 0 | 0 | 29 | 196 | 41 | 83 | 0 | 83 | 23 | 14 | 0 | 58 | 0 | 0 | 31 | 0 | 320 | 383 | 43 | 30 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 43 | 31 | 18 | 86 | 0 | 0 | 0 | 22 | 6032.5 | 906 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 8 | 0 | 0 | 0 | 175 | 0 | 147 | 0 | 155 | 0 | 0 | 0 | 0 | 11 | 210 | 68 | 90 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1100 | 90 | 4735 | 10767.5 | 93.27
19:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 54 | 36 | 0 | 95 | 16 | 0 | 43 | 55 | 162 | 25 | 0 | 380 | 280 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 0 | 17 | 17.5 | 20 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12 | 12 | 0 | 40 | 53 | 24 | 1150 | 34 | 0 | 33 | 0 | 51 | 230 | 0 | 0 | 0 | 612 | 0 | 51 | 100 | 197 | 0 | 0 | 0 | 29 | 182 | 42 | 115 | 0 | 175 | 27 | 14 | 0 | 56 | 0 | 0 | 49 | 0 | 320 | 382 | 43 | 30 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 55 | 48 | 18 | 87 | 0 | 0 | 0 | 22 | 6257.5 | 907 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 8 | 0 | 0 | 0 | 174 | 0 | 152 | 0 | 153 | 0 | 0 | 0 | 0 | 11 | 210 | 68 | 50 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 140 | 220 | 0 | 1210 | 150 | 4898 | 11155.5 | 93.27
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 54 | 36 | 0 | 85 | 16 | 0 | 55 | 35 | 108 | 25 | 0 | 380 | 316 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 0 | 17 | 17 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 18 | 1150 | 0 | 0 | 33 | 0 | 17 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 197 | 0 | 0 | 0 | 29 | 217 | 42 | 115 | 0 | 85 | 27 | 14 | 0 | 56 | 0 | 0 | 0 | 0 | 320 | 383 | 43 | 30 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 55 | 54.5 | 18 | 88 | 0 | 0 | 0 | 22 | 5886.5 | 907 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 8 | 0 | 0 | 0 | 173 | 0 | 155 | 0 | 153 | 0 | 0 | 0 | 0 | 11 | 210 | 68 | 50 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1222 | 150 | 4879 | 10765.5
20:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 54 | 36 | 0 | 85 | 16 | 0 | 55 | 17 | 108 | 25 | 0 | 380 | 312 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 0 | 17 | 17.5 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 22 | 1150 | 0 | 0 | 33 | 0 | 17 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 199 | 0 | 0 | 0 | 29 | 200 | 42 | 115 | 0 | 85 | 29 | 14 | 0 | 54 | 0 | 0 | 0 | 0 | 320 | 372 | 43 | 30 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 55 | 54.5 | 18 | 88 | 0 | 0 | 0 | 22 | 5846 | 907 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 8 | 0 | 0 | 0 | 173 | 0 | 147 | 0 | 152 | 0 | 0 | 0 | 0 | 11 | 210 | 70 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 140 | 220 | 0 | 1222 | 150 | 4870 | 10716 | 93.27
21:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 54 | 36 | 0 | 85 | 16 | 0 | 55 | 17 | 108 | 25 | 0 | 380 | 289 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 0 | 17 | 17 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 23 | 1150 | 0 | 0 | 33 | 0 | 17 | 226 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 199 | 0 | 0 | 0 | 29 | 182 | 39 | 115 | 0 | 85 | 29 | 14 | 0 | 57 | 0 | 0 | 0 | 0 | 320 | 343 | 43 | 30 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 67 | 54.5 | 18 | 78 | 0 | 0 | 0 | 22 | 5774.5 | 908 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.64 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 150 | 0 | 152 | 0 | 0 | 0 | 0 | 11 | 210 | 69 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1222 | 150 | 4866.64 | 10641.14 | 93.26
22:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 54 | 36 | 0 | 65 | 16 | 0 | 15 | 0 | 54 | 25 | 0 | 380 | 255 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 28 | 1150 | 0 | 0 | 33 | 0 | 17 | 228 | 0 | 0 | 0 | 612 | 0 | 51 | 10 | 199 | 0 | 0 | 0 | 29 | 182 | 42 | 50 | 0 | 34 | 29 | 14 | 0 | 56 | 0 | 0 | 0 | 0 | 320 | 343 | 43 | 30 | 0 | 2 | 163 | 0 | 0 | 85 | 0 | 0 | 0 | 84 | 17 | 18 | 58 | 0 | 0 | 0 | 22 | 5345 | 907 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.43 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 156 | 0 | 153 | 0 | 0 | 0 | 0 | 11 | 210 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1244 | 100 | 4720.43 | 10065.43 | 93.26
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 54 | 36 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 380 | 310 | 0 | 0 | 35 | 12 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 1150 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 502 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 42 | 0 | 0 | 0 | 9 | 14 | 0 | 56 | 0 | 0 | 0 | 0 | 320 | 343 | 43 | 30 | 0 | 2 | 120 | 0 | 0 | 85 | 0 | 0 | 0 | 90 | 0 | 18 | 48 | 0 | 0 | 0 | 22 | 4911 | 907 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 157 | 0 | 156 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1244 | 0 | 4570.24 | 9481.24 | 93.26
Total KWH | 0 | 1126080 | 382080 | 0 | 0 | 0 | 0 | 0 | 6753600 | 0 | 0 | 743400 | 590400 | 0 | 1278144 | 439680 | 0 | 214632 | 101751.45 | 1350720 | 560880 | 0 | 9315500 | 7125149 | 0 | 0 | 481434 | 337300 | 0 | 0 | 0 | 145168 | 68400 | 398400 | 460440 | 0 | 0 | 296073 | 0 | 0 | 0 | 25440 | 0 | 56640 | 0 | 43200 | 54720 | 24000 | 965660 | 149708 | 543840 | 26538181.82 | 23418 | 0 | 443520 | 0 | 237527 | 5249084 | 0 | 0 | 0 | 12714544 | 133920 | 1208405 | 411490 | 4767273 | 0 | 0 | 0 | 692640 | 4673000 | 992592 | 1139520 | 0 | 720480 | 196560 | 343370 | 0 | 1322880 | 0 | 461464 | 50208 | 0 | 7917700 | 8727000 | 986976 | 706000 | 0 | 56640 | 3543464 | 11472 | 0 | 2055360 | 0 | 0 | 0 | 1287230 | 233640 | 340800 | 1087200 | 72960 | 9100 | 211250 | 374400 | 123973708.27 | 18868363 | 5810112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403920 | 0 | 0 | 15888364 | 0 | 0 | 0 | 0 | 0 | 0 | 420896 | 0 | 0 | 23179 | 448797 | 0 | 254248 | 4426555 | 0 | 4174745 | 0 | 4266358 | 0 | 0 | 0 | 20580 | 164790 | 5059000 | 1635927 | 290496 | 161342 | 171878 | 0 | 0 | 31101 | 756000 | 2970 | 0 | 6065000 | 140828 | 2829000 | 5189.74 | 0 | 26802909.09 | 946800 | 100069347.83 | 224043056.1

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-01-2025 | during | 14-01-2025 | during | 14-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 234.58 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 301 | 297 | 400.37 | 400.37 | 300 | 300 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 380 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 304 | 280 | 335 | 335 | 335 | 335 | -
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 43 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 335 | 335 | 0 | 0 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 17 | 17.5 | 30 | 30 | 25 | 25 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 20 | 20 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 12 | 12 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 25 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 59 | 95 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 25 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 34 | 36 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0.01 | 0.01 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 7401.63 | 5842.27 | 1425 | 1639.5 | 4022.99 | 4001.99 | 2497.55 | 2476.55
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 22 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 230 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 51 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 40 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 33 | 0 | 6 | 24 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.88 | 0 | 3.88 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 53 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 7 | 35 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 34 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1320 | 1224 | 595 | 612 | 1224 | 1224 | 612 | 612 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 66 | 60 | 0 | 0 | 30 | 30 | 30 | 30 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1200 | 1200 | 1150 | 1150 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 5102.36 | 4873.22 | 2066 | 2326 | 4070.6 | 4046.72 | 3458.6 | 3434.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 195 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 42 | 42 | 46.94 | 46.94 | 45 | 45 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 199 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 49 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 13 | 175 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 62 | 56 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 7.34 | 20.83 | 7.34 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 27 | 9 | 9 | 9 | 9 | Fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 62 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 744 | 1037 | 1556.48 | 1504.97 | 1375.54 | 1324.03
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 30 | 30 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 87 | 200 | 200 | 77 | 77 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 18 | 115 | 115 | 18 | 18 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 24.38 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 48 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654.5 | 654.21 | 124.38 | 175 | 651.5 | 601.5 | 251.5 | 201.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 43 | 44 | 44 | 44 | 44 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 0 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 55 | 212 | 212 | 90 | 90 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 341 | 341 | 0 | 0 | Plant shutdown as per NLDC requirement.
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 384 | 382 | 385 | 385 | 357 | 357 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 340 | 320 | 383 | 383 | 353 | 353 | FGMO
Sylhet Area Total |  |  |  |  | 2411 | 2370.57 | 1047 | 1080 | 1666.5 | 1666.5 | 1095.01 | 1095.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 907 | 907 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 30 | 30 | 30 | 30 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 238 | 206 | 410 | 410 | 290 | 290 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 68 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Under Maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3743 | 3686.2 | 1213 | 1113 | 3231 | 3159 | 1667 | 1595
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 6 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 135 | 135 | 140 | 140 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1080 | 1210 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.47 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1768.47 | 2033 | 2177.12 | 2176.12 | 2142.12 | 2141.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 171 | 174 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 152 | 220 | 220 | 150 | 150 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 188 | 153 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 11 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 3.51 | 0 | 4.15 | 0 | 4.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 704.33 | 756 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 43.14 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 100 | 100 | 74 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3575.55 | 3393.2 | 1360.48 | 1354 | 2770.89 | 2616.74 | 2629.89 | 2475.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 68 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 200 | 200 | 210 | 210 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.3 | 0 | 5.4 | 0 | 5.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 50 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 123 | 0 | 110.21 | 0 | 110.21 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 436.3 | 398 | 677.61 | 532 | 687.61 | 542
System Total |  |  |  |  | 29109.24 | 26932.25 | 10184.63 | 11155.5 | 20824.69 | 20305.54 | 15804.82 | 15285.67
Forecast Scenario (14-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8900 |  | 0 |  | 8900
|  |  |  | 1:00 | 8350 |  | 0 |  | 8350
|  |  |  | 2:00 | 7950 |  | 0 |  | 7950
|  |  |  | 3:00 | 7680 |  | 0 |  | 7680
|  |  |  | 4:00 | 7450 |  | 0 |  | 7450
|  |  |  | 5:00 | 7390 |  | 0 |  | 7390
|  |  |  | 6:00 | 7650 |  | 0 |  | 7650
|  |  |  | 7:00 | 8550 |  | 0 |  | 8550
|  |  |  | 8:00 | 9300 |  | 0 |  | 9300
|  |  |  | 9:00 | 9740 |  | 0 |  | 9740
|  |  |  | 10:00 | 9510 |  | 0 |  | 9510
|  |  |  | 11:00 | 9650 |  | 0 |  | 9650
|  |  |  | 12:00 | 10040 |  | 0 |  | 10040
|  |  |  | 13:00 | 10450 |  | 0 |  | 10450
|  |  |  | 14:00 | 9950 |  | 0 |  | 9950
|  |  |  | 15:00 | 9530 |  | 0 |  | 9530
|  |  |  | 16:00 | 9400 |  | 0 |  | 9400
|  |  |  | 17:00 | 9510 |  | 0 |  | 9510
|  |  |  | 18:00 | 10760 |  | 0 |  | 10760
|  |  |  | 18:30 | 10850 |  | 0 |  | 10850
|  |  |  | 19:00 | 10970 |  | 0 |  | 10970
|  |  |  | 19:30 | 10650 |  | 0 |  | 10650
|  |  |  | 20:00 | 10590 |  | 0 |  | 10590
|  |  |  | 21:00 | 10460 |  | 0 |  | 10460
|  |  |  | 22:00 | 10040 |  | 0 |  | 10040
|  |  |  | 23:00 | 9420 |  | 0 |  | 9420
Probable Maximum Temperature: |  |  | 26.90°C
Probable Maximum Demand at Day Peak: |  |  | 10040.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 10970.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10970.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 223.24 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (13-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 27.20°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 723.25
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 18.8684 | Peak Hour Flow: |  | 907.00 MW at 19:00 hrs.
Energy Flow from West to East |  | 12131218.286 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 15.8884 | Peak Hour Flow: |  | 756.00 MW at 19:00 hrs.
Power Flow during Peak Demand |  | 630 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.3229 | Peak Hour Flow: |  | 56.00 MW at 19:00 hrs.
Maximum Power Flow |  | 912 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 36.0796 | Peak Hour Flow: |  | 1719.00 MW at 19:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 13-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 10184.63 | MW | 12:00 Hr. | Energy Generated |  |  | 224043.0561 |  | MWHr
Day Peak Demand |  |  | 10184.63 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MWHr
Evening Peak Generation |  |  | 11155.5 | MW | 19:00 Hr. | Energy Demand |  |  | 224043.0561 |  | MWHr
Evening Peak Demand |  |  | 11155.5 | MW | 19:00 Hr.
Minimum Generation of the Day |  |  | 7496 | MW | 05:00 Hr.
Maximum Generation of the Day |  |  | 11155.5 | MW | 19:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 24951.269 | 0 | 6776.7215 | 0 | 0 | 145.168 | 0 | 0 | 31873.1584 | Gas | 90603.8527 | Gas | 329966518.5526
Chattogram Zone |  |  | 5792.924 | 39252.7258 | 1304.806 | 0 | 965.66 | 157.92 | 0 | 25.44 | 47499.4758 | Coal | 78815.5619 | Coal | 553223637.5533
Cumilla Zone |  |  | 12677.28 | 0 | 2518.258 | 0 | 0 | 461.464 | 1322.88 | 0 | 16979.882 | HFO | 14489.0745 | HFO | 263835603.8625
Mymensingh Zone |  |  | 72.96 | 0 | 2036.04 | 0 | 0 | 220.35 | 0 | 0 | 2329.35 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 25291.842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25291.842 | Hydro | 965.66 | Hydro | 96566
Khulna Zone |  |  | 5810.112 | 0 | 0 | 0 | 0 | 403.92 | 18868.363 | 0 | 25082.395 | Solar | 3063.86 | Solar | 47407330.14
Barishal Zone |  |  | 2975.0177 | 32867.9091 | 946.8 | 0 | 0 | 2.97 | 0 | 0 | 36792.6968 | Import | 36079.607 | Import | 190234938.1
Rajshahi Zone |  |  | 13032.448 | 0 | 444.075 | 0 | 0 | 723.625 | 15888.364 | 0 | 30088.512 | Wind | 25.44 | Wind | 396864
Rangpur Zone |  |  | 0 | 6694.927 | 462.374 | 0 | 0 | 948.443 | 0 | 0 | 8105.744
Total |  |  | 90603.8527 | 78815.5619 | 14489.0745 | 0 | 965.66 | 3063.86 | 36079.607 | 25.44 | 224043.0561
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 329966518.5526 |  | Hydro | 96566
|  |  | Coal | 553223637.5533 |  | Solar | 47407330.14
|  |  | HFO | 263835603.8625 |  | Import | 190234938.1
|  |  | HSD | 0 |  | Wind | 396864
|  |  |  | Total: | 1385161458.2084 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120
| 3 | Baghabari 100 MW GTPP |  |  | 100
| 4 | Barapukuria TPP Unit-2 |  |  | 85
| 5 | Khulna 330 MW CCPP GT |  |  | 220
| 6 | Khulna 330 MW CCPP ST |  |  | 110
| 7 | Siddhirgonj 210 MW TPP |  |  | 115
| 8 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 9 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1404 |  |  |  | Total | 35.09
|  |  | Total Unavailable Capacity |  |  |  | 1439.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3747
|  |  | Chattogram |  | 0 |  | 753
|  |  | Cumilla |  | 0 |  | 448
|  |  | Mymensingh |  | 0 |  | 907
|  |  | Sylhet |  | 0 |  | 387
|  |  | Khulna |  | 0 |  | 1217
|  |  | Barishal |  | 0 |  | 299
|  |  | Rajshahi |  | 0 |  | 990
|  |  | Rangpur |  | 0 |  | 673
|  |  | Total |  | 0 |  | 9421
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:08 | 13:45 | Juldah-Shahmirpur 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to Dead line
chack and from Shahmirpur 132/33kV end Due to Deadline Checking
08:13 | 16:36 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual maintenance
08:14 | 16:36 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual maintenance
08:19 |  | Bhulta-Haripur 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end Due to Re-arrangement
of 230kV Haripur-Bhulta circuit-01. and from Haripur 230/132kV end Due to Unknown.
08:22 | 15:52 | Daudkandi-Sonargaon 132 kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to Annual
maintenance purpose at Daudkandi end. and from Daudkandi 132/33kV end Due to annual
maintenance
08:23 | 17:20 | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Patuakhali 132/33kV end Due to Annual
Maintenance-2025 and from Payra 400/132/33kV end Due to Annual maintenance
08:30 | 16:19 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Annual
maintenance
08:46 | 14:50 | Ramganj 132/33kV S/S Ramgonj-Desh Energy Ckt-02 Scheduled S/D Due to Annual Maintenance
08:46 |  | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to annual
maintenance
08:48 | 03:19 | Rampal 400/230kV S/S Gopalganj Line-2 Reactor Scheduled S/D Due to Jobs at gopalganj
ends.
08:49 |  | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to By
NLDC
08:49 | 13:46 | Bheramara(GK) 132/33kV S/S TR-3 LT Scheduled S/D Due to Annual Maintenance Work
08:49 |  | Gopalganj(N)-Rampal Ckt-2 Scheduled S/D from Rampal 400/230kV end Due to Jobs at
gopalganj ends.
08:50 | 13:44 | Bheramara(GK) 132/33kV S/S TR-3 HT Scheduled S/D Due to Annual Maintenance Work
08:53 | 15:40 | Madanganj-Munsiganj 132 kV Ckt-1 Scheduled S/D from Munshiganj 132/33kV end Due to Annual
Maintenance and from Madanganj 132/33kVend.
08:58 | 15:17 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Dead line
checking
08:59 | 17:23 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-2 Scheduled S/D Due to Annual maintenance
09:04 | 14:57 | Hathazari 230/132/33kV S/S Shikolbaha-02 Scheduled S/D Due to annual maintenance
09:05 | 14:56 | Madunaghat 400/230kV S/S Madunaghat-Hathazari 230kV Ckt.-2 Scheduled S/D
| 09:06 | Sylhet 132/33kV S/S T1 LT is restored.
| 09:06 | Sylhet 132/33kV S/S T1 HT is restored.
09:07 |  | Kallyanpur 132/33kV S/S Reserve bus Scheduled S/D
09:10 |  | Fenchuganj 230/132/33kV S/S TR-02 LT Scheduled S/D Due to Annual maintenance
09:13 |  | BIPTC S/S Baharampur-3 Scheduled S/D Due to For annual maintenance
09:14 |  | Kodda-Rajendrapur 132kV Ckt-1 Scheduled S/D from Rajendrapur 132/33kV end Due to Yearly
deadline checking of kodda ckt-1 and from Kodda 132/33kVend.
09:15 |  | Fenchuganj 230/132/33kV S/S TR-02 HT Scheduled S/D Due to Annual maintenance
09:15 | 16:39 | Khulna(S) 230/132kV S/S TR-2 LT Scheduled S/D Due to Annual Maintenance Work.
09:16 | 16:38 | Khulna(S) 230/132kV S/S TR-2 HT Scheduled S/D Due to Annual Maintenance Work.
09:31 | 15:41 | Jhenaidah 132/33kV S/S Transformer T-3 HT Scheduled S/D Due to Annual Maintenance.
09:35 | 16:35 | Siddhirganj 132/33kV S/S 132kV Bus B Scheduled S/D Due to Annual maintenance work
09:40 | 16:52 | Sonargaon 132/33kV S/S OPML(IEL-1) Scheduled S/D Due to Annual maintenance bay &dead line
checking
09:47 | 17:53 | Haripur-Siddirganj 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Ananciator
replacing.
09:47 | 17:53 | Haripur-Siddirganj 132kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Ananciator
Replacing.
09:56 |  | Fenchuganj 230/132/33kV S/S 132 KV Bus-2 Scheduled S/D Due to Annual maintenance
09:58 | 17:39 | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
09:59 | 11:47 | Fenchuganj-Kulaura 132 kV Ckt-1 Scheduled S/D from Kulaura 132/33kV end Due to NLDC took
this shutdown for Fenchuganj SS. and from Fenchuganj 230/132/33kV end Due to Annual
maintenance
10:10 | 18:26 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D
10:35 | 17:08 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Scheduled S/D Due to Annual maintenance
10:35 | 17:06 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Scheduled S/D Due to Annul maintenance
10:39 | 11:43 | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D Due to Test
10:39 | 11:43 | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D Due to Test
11:10 | 14:59 | Bagerhat-Labanchura 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end.
11:17 |  | BSRM-Mirsharai 230 kV Ckt-2 Project Work S/D from BSRM 230/33kV end Due to OPGW Work and
from Mirsorai 230/33kV end Due to Project work
11:24 | 18:13 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Dead line maintenance
11:30 | 15:44 | Khulna (C) S/S Tr-3 405T LT Forced S/D Due to 33kv bus PT change
11:32 | 15:42 | Khulna (C) S/S Tr-3 405T HT Forced S/D Due to 33 kv bus PT change
11:45 | 12:58 | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D Due to Test
11:45 | 12:58 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D Due to Test
11:48 | 14:21 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Kulaura 132/33kV end Due to NLDC Took
the shutdown for Fenchuganj SS. and from Fenchuganj 230/132/33kV end Due to Due to 132
kV Bus-2 Annual maintenance.
12:00 |  | Day Peak Generation = 10,184MW
12:03 | 01:12 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to Due to low voltage.
12:04 | 01:02 | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due to low voltage.
12:15 |  | Sylhet 132/33kV S/S T1 LT Forced S/D Due to Request of SDE,Sylhet SS.
12:15 |  | Sylhet 132/33kV S/S T1 HT Forced S/D Due to Request of SDE,Sylhet SS.
12:15 | 12:20 | Sylhet 132/33kV S/S T2 LT Forced S/D Due to Request of SDE,Sylhet SS.
12:15 | 12:20 | Sylhet 132/33kV S/S T2 HT Forced S/D Due to Request of SDE,Sylhet SS.
| 14:59 | Bagerhat-Labanchura 132 kV Ckt-2 is restored.
15:13 | 16:09 | Fenchuganj-Fenchuganj 132 kV Ckt-4 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
15:16 |  | Sylhet CCPP 225 MW GT was sync.
| 16:01 | Thakurgaon 132/33kV S/S T-3(432T) HT is restored.
| 16:03 | Thakurgaon 132/33kV S/S T-3(432T) LT is restored.
| 16:06 | Baghabari-Ullahpara 132 kV Ckt-1 is restored.
16:20 |  | Fenchuganj-Fenchuganj 132 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Annual Maintenance
| 16:24 | Kishoreganj-Mymensingh 132kV Ckt-2 is restored.
| 17:02 | Goalpara-Labanchura 132kV Ckt-2 is restored.
17:05 |  | Ashuganj 450 MW CCPP(North) GT Planned Shutdown with remarks:- Unit was given shutdown on
06 January, 2025 at 06:41 hours due to Major Inspection.
17:08 |  | Ashuganj 450 MW CCPP(North) ST Planned Shutdown with remarks:- ST was given shutdown on
04 January, 2025 at 00:34 hrs due to Major Inspection.
| 17:52 | Aminbazar-Airport(Old) 230kV Ckt-1 is restored.
17:53 |  | Sylhet CCPP 225 MW ST was sync.
| 18:37 | Bashundhara-Rampura 132 kV Ckt-1 is restored.
19:00 |  | Evening peak Generation is 11155 MW
05:00 |  | Minimum generation 7469 MW
06:35 |  | Summit Bibiyana-2 GT was sync.
06:56 |  | Bashundhara-Rampura 132 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual
maintenance 2024-25 (Deadline check)
06:57 |  | Dohazari 132/33kV S/S Power Transformer -T-2 LT Project Work S/D Due to BUS | [7 empty] | 16.0MW load
|  | Re-conductoring by G2G | [7 empty] | interrup.
06:57 |  | Dohazari 132/33kV S/S Power Transformer -T-2 HT Project Work S/D | [7 empty] | 16.0MW load
interrup.
07:24 |  | Ramganj 132/33kV S/S Ramgonj-Desh Energy Ckt-02 Scheduled S/D Due to Annual
Maintenance(Schedule shutdown)
07:36 |  | Ramganj 132/33kV S/S 132 Kv Bus- A Scheduled S/D Due to Due to Annual Maintenance
07:44 |  | Payra-Patuakhali CKT-2 is S/D due Annual maintenance.
07:51 |  | Rampal 400/230kV S/S Gopalganj Line-2 Reactor Scheduled S/D Due to For ALDC work purpose
07:52 |  | Gopalgang- Rampal 400 kv CKT-2 is S/D due to Annual Maintenance.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 297 | 6753600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 9315500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 280 | 7125149 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 43 | 214632 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 743400 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 439680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 101751.45 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 481434 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17.5 | 398400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 460440 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 560880 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 12 | 337300 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 25 | 382080 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 95 | 1278144 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1126080 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1350720 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 145168 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 36 | 590400 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 17 | 68400 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 1639.5 | 31873158.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 133920 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 443520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 965660 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 230 | 5249084 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 237527 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 40 | 56640 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 43200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 0 | 24 | 543840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 24000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 53 | 149708 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 54720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 296073 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 34 | 23418 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 12714544 | Coal shortage
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 0 | 25440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 1150 | 26538181.82 | -
Chattogram Area Total |  |  |  |  | 4873.22 | 2326 | 47499475.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4673000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | schedule outage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 42 | 992592 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 692640 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 4767273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1208405 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 411490 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 49 | 50208 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 175 | 720480 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 56 | 1322880 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 343370 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 196560 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1139520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 461464 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1037 | 16979882
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 72960 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1087200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 18 | 340800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 211250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 374400 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 48 | 233640 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 175 | 2329350
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 706000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3543464 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 43 | 986976 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 56640 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 2055360 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 55 | 1287230 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 11472 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Plant shutdown as per NLDC requirement.
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 382 | 8727000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7917700 | FGMO
Sylhet Area Total |  |  |  |  | 2370.57 | 1080 | 25291842
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 907 | 18868363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 206 | 5810112 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 403920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1113 | 25082395
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 6 | 140828 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2829000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1210 | 26802909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5189.74 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 946800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6065000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2970 | -
Barishal Area Total |  |  |  |  | 2265.1 | 2033 | 36792696.83
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 174 | 4426555 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 152 | 4174745 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 153 | 4266358 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 11 | 164790 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 23179 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 420896 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 756 | 15888364 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 254248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 448797 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1354 | 30088512
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 68 | 1635927 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 5059000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 171878 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31101 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 50 | 290496 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 161342 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 756000 | -
Rangpur Area Total |  |  |  |  | 950 | 398 | 8105744
Eastern Grid Total |  |  |  |  | 16637.75 | 6257.5 | 123973708.27
Western Grid Total |  |  |  |  | 10294.5 | 4898 | 100069347.83
National Grid Total |  |  |  |  | 26932.25 | 11155.5 | 224043056.1
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9006 | 0 |  | 9006
1:00 | 8492 | 0 |  | 8492
2:00 | 8009 | 0 |  | 8009
3:00 | 7777 | 0 |  | 7777
4:00 | 7506 | 0 |  | 7506
5:00 | 7496 | 0 |  | 7496
6:00 | 7785.6 | 0 |  | 7785.6
7:00 | 8671.16 | 0 |  | 8671.16
8:00 | 9387.43 | 0 |  | 9387.43
9:00 | 9781.12 | 0 |  | 9781.12
10:00 | 9637.99 | 0 |  | 9637.99
11:00 | 9745.77 | 0 |  | 9745.77
12:00 | 10184.63 | 0 |  | 10184.63
13:00 | 10419.87 | 0 |  | 10419.87
14:00 | 10132.4 | 0 |  | 10132.4
15:00 | 9741.3 | 0 |  | 9741.3
16:00 | 9529.86 | 0 |  | 9529.86
17:00 | 9715 | 0 |  | 9715
18:00 | 10767.5 | 0 |  | 10767.5
19:00 | 11155.5 | 0 |  | 11155.5
19:30 | 10765.5 | 0 |  | 10765.5
20:00 | 10716 | 0 |  | 10716
21:00 | 10641.14 | 0 |  | 10641.14
22:00 | 10065.43 | 0 |  | 10065.43
23:00 | 9481.24 | 0 |  | 9481.24
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4689.5 | 4316.5 | 9006 | DAILY LOAD CURVE
00:30 | 4547 | 4202 | 8749
01:00 | 4404.5 | 4087.5 | 8492 | 13-01-2025
01:30 | 4336 | 3914.5 | 8250.5
02:00 | 4267.5 | 3741.5 | 8009
02:30 | 4243 | 3650 | 7893
03:00 | 4218.5 | 3558.5 | 7777
03:30 | 4180 | 3461.5 | 7641.5
04:00 | 4141.5 | 3364.5 | 7506
04:30 | 4137 | 3364 | 7501
05:00 | 4132.5 | 3363.5 | 7496
05:30 | 4153.3 | 3487.5 | 7640.8
06:00 | 4174.1 | 3611.5 | 7785.6
06:30 | 4400.4 | 3827.98 | 8228.38
07:00 | 4626.7 | 4044.46 | 8671.16
07:30 | 4762.85 | 4266.445 | 9029.295
08:00 | 4899 | 4488.43 | 9387.43
08:30 | 4969.375 | 4614.9 | 9584.275
09:00 | 5039.75 | 4741.37 | 9781.12
09:30 | 5046.405 | 4663.15 | 9709.555
10:00 | 5053.06 | 4584.93 | 9637.99
10:30 | 5117.07 | 4574.81 | 9691.88
11:00 | 5181.08 | 4564.69 | 9745.77
11:30 | 5293.73 | 4671.47 | 9965.2
12:00 | 5406.38 | 4778.25 | 10184.63
12:30 | 5484.405 | 4817.845 | 10302.25
13:00 | 5562.43 | 4857.44 | 10419.87
13:30 | 5531.27 | 4744.865 | 10276.135
14:00 | 5500.11 | 4632.29 | 10132.4
14:30 | 5359.365 | 4577.485 | 9936.85
15:00 | 5218.62 | 4522.68 | 9741.3
15:30 | 5171.87 | 4463.71 | 9635.58
16:00 | 5125.12 | 4404.74 | 9529.86
16:30 | 5221.425 | 4401.005 | 9622.43
17:00 | 5317.73 | 4397.27 | 9715
17:30 | 5675.115 | 4566.135 | 10241.25
18:00 | 6032.5 | 4735 | 10767.5
18:30 | 6145 | 4816.5 | 10961.5
19:00 | 6257.5 | 4898 | 11155.5
19:30 | 5886.5 | 4879 | 10765.5
20:00 | 5846 | 4870 | 10716
20:30 | 5810.25 | 4868.32 | 10678.57 |  | Executive Engineer
21:00 | 5774.5 | 4866.64 | 10641.14 |  | Network Operation Division
21:30 | 5559.75 | 4793.535 | 10353.285
22:00 | 5345 | 4720.43 | 10065.43
22:30 | 5128 | 4645.335 | 9773.335
23:00 | 4911 | 4570.24 | 9481.24

## En-Curve
QF-LDC-12
Date | 13-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2344 | 1542 | 904 | 0 | 62 | 617 | 40 | 3375 | 0 | 34 | 88 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2320.5 | 1516.5 | 897 | 0 | 59 | 616 | 40 | 3207.5 | 0 | 25.5 | 67 | 0 | 0 | 0 | 0 | 13-01-2025
01:00 | 2297 | 1491 | 890 | 0 | 56 | 615 | 40 | 3040 | 0 | 17 | 46 | 0 | 0 | 0 | 0
01:30 | 2288.5 | 1502 | 804 | 0 | 53 | 566.5 | 40 | 2965 | 0 | 8.5 | 23 | 0 | 0 | 0 | 0 |  | Total Energy | 224.0431 |  | MKWHr
02:00 | 2280 | 1513 | 718 | 0 | 50 | 518 | 40 | 2890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Energy not Served | 0 |  | MKWHr
02:30 | 2267.5 | 1525 | 718 | 0 | 49 | 468.5 | 40 | 2825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Energy Requirement | 224.0431 |  | MKWHr
03:00 | 2255 | 1537 | 718 | 0 | 48 | 419 | 40 | 2760 | 0 | 0 | 0 | 0 | 0 | 0 | 0
03:30 | 2255.5 | 1536 | 671 | 0 | 46 | 419.5 | 40 | 2673.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:00 | 2256 | 1535 | 624 | 0 | 44 | 420 | 40 | 2587 | 0 | 0 | 0 | 0 | 0 | 0 | 0
04:30 | 2247.5 | 1537.5 | 624 | 0 | 43 | 420.5 | 40 | 2588.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:00 | 2239 | 1540 | 624 | 0 | 42 | 421 | 40 | 2590 | 0 | 0 | 0 | 0 | 0 | 0 | 0
05:30 | 2242 | 1540.3 | 671 | 0 | 47 | 463.5 | 40 | 2634 | 0 | 0 | 2 | 0 | 0 | 1 | 0
06:00 | 2245 | 1540.6 | 718 | 0 | 52 | 506 | 40 | 2678 | 0 | 0 | 4 | 0 | 0 | 2 | 0
06:30 | 2344 | 1610.05 | 812 | 0 | 53 | 508.5 | 40 | 2808.5 | 3.83 | 21 | 25 | 0 | 0 | 2.5 | 0
07:00 | 2443 | 1679.5 | 906 | 0 | 54 | 511 | 40 | 2939 | 7.66 | 42 | 46 | 0 | 0 | 3 | 0
07:30 | 2407 | 1643.5 | 906 | 0 | 50 | 560.385 | 40 | 3201.5 | 55.91 | 61.5 | 100 | 0 | 0 | 3.5 | 0
08:00 | 2371 | 1607.5 | 906 | 0 | 46 | 609.77 | 40 | 3464 | 104.16 | 81 | 154 | 0 | 0 | 4 | 0
08:30 | 2348 | 1558.5 | 906.5 | 0 | 45 | 680.385 | 40 | 3476.5 | 193.89 | 86 | 246.5 | 0 | 0 | 3 | 0
09:00 | 2325 | 1509.5 | 907 | 0 | 44 | 751 | 40 | 3489 | 283.62 | 91 | 339 | 0 | 0 | 2 | 0
09:30 | 2344 | 1473.5 | 906.5 | 0 | 50 | 720.775 | 40 | 3385 | 345.28 | 91 | 352.5 | 0 | 0 | 1 | 0
10:00 | 2363 | 1437.5 | 906 | 0 | 56 | 690.55 | 40 | 3281 | 406.94 | 91 | 366 | 0 | 0 | 0 | 0
10:30 | 2364.5 | 1448 | 906 | 0 | 57 | 675.79 | 40 | 3290.5 | 445.59 | 98.5 | 365.5 | 0 | 0 | 0.5 | 0
11:00 | 2366 | 1458.5 | 906 | 0 | 58 | 661.03 | 40 | 3300 | 484.24 | 106 | 365 | 0 | 0 | 1 | 0
11:30 | 2394 | 1517.5 | 906.5 | 0 | 60 | 682.68 | 40 | 3356 | 486.02 | 116.5 | 405.5 | 0 | 0 | 0.5 | 0
12:00 | 2422 | 1576.5 | 907 | 0 | 62 | 704.33 | 40 | 3412 | 487.8 | 127 | 446 | 0 | 0 | 0 | 0
12:30 | 2387 | 1570 | 907 | 0 | 63 | 727.23 | 40 | 3449.5 | 479.02 | 135 | 544.5 | 0 | 0 | 0 | 0
13:00 | 2352 | 1563.5 | 907 | 0 | 64 | 750.13 | 40 | 3487 | 470.24 | 143 | 643 | 0 | 0 | 0 | 0
13:30 | 2331.5 | 1576 | 907 | 0 | 65 | 754.565 | 40 | 3388.5 | 437.57 | 143 | 632 | 0 | 0 | 1 | 0
14:00 | 2311 | 1588.5 | 907 | 0 | 66 | 759 | 40 | 3290 | 404.9 | 143 | 621 | 0 | 0 | 2 | 0
14:30 | 2287.5 | 1576.5 | 907 | 0 | 64 | 758.5 | 40 | 3219 | 350.35 | 143 | 586 | 0 | 0 | 5 | 0
15:00 | 2264 | 1564.5 | 907 | 0 | 62 | 758 | 40 | 3148 | 295.8 | 143 | 551 | 0 | 0 | 8 | 0
15:30 | 2275 | 1543 | 907 | 0 | 59 | 757.5 | 40 | 3139 | 219.58 | 143 | 547.5 | 0 | 0 | 5 | 0
16:00 | 2286 | 1521.5 | 907 | 0 | 56 | 757 | 40 | 3130 | 143.36 | 143 | 544 | 0 | 0 | 2 | 0
16:30 | 2296 | 1523 | 906.5 | 0 | 54 | 756 | 40 | 3225.5 | 84.93 | 143 | 590.5 | 0 | 0 | 3 | 0
17:00 | 2306 | 1524.5 | 906 | 0 | 52 | 755 | 40 | 3321 | 26.5 | 143 | 637 | 0 | 0 | 4 | 0
17:30 | 2334 | 1564 | 906 | 0 | 55 | 755 | 40 | 3384 | 13.25 | 228 | 959.5 | 0 | 0 | 2.5 | 0
18:00 | 2362 | 1603.5 | 906 | 0 | 58 | 755 | 40 | 3447 | 0 | 313 | 1282 | 0 | 0 | 1 | 0
18:30 | 2362.5 | 1591.5 | 906.5 | 0 | 57 | 755.5 | 40 | 3502 | 0 | 315 | 1431 | 0 | 0 | 0.5 | 0
19:00 | 2363 | 1579.5 | 907 | 0 | 56 | 756 | 40 | 3557 | 0 | 317 | 1580 | 0 | 0 | 0 | 0
19:30 | 2390 | 1605 | 907 | 0 | 56 | 758 | 40 | 3569 | 0 | 228 | 1212.5 | 0 | 0 | 0 | 0
20:00 | 2356 | 1606.5 | 907 | 0 | 54 | 758 | 40 | 3571 | 0 | 228 | 1195.5 | 0 | 0 | 0 | 0
20:30 | 2341.5 | 1595.75 | 907.5 | 0 | 55.5 | 757.32 | 40 | 3570.5 | 0 | 224 | 1186.5 | 0 | 0 | 0 | 0
21:00 | 2327 | 1585 | 908 | 0 | 57 | 756.64 | 40 | 3570 | 0 | 220 | 1177.5 | 0 | 0 | 0 | 0
21:30 | 2336.5 | 1572.5 | 907.5 | 0 | 56.5 | 757.035 | 40 | 3580.5 | 0 | 173 | 929.75 | 0 | 0 | 0 | 0
22:00 | 2346 | 1560 | 907 | 0 | 56 | 757.43 | 40 | 3591 | 0 | 126 | 682 | 0 | 0 | 0 | 0
22:30 | 2351 | 1568.25 | 907 | 0 | 56 | 757.085 | 40 | 3537 | 0 | 80 | 477 | 0 | 0 | 0 | 0
23:00 | 2356 | 1576.5 | 907 | 0 | 56 | 756.74 | 40 | 3483 | 0 | 34 | 272 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-13 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 415 | 04:00 | 384 | 12:00 | Kaliakoir | 379 | 05:00 | 353 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 413 | 5:00 | 373 | 12:00 | Madunaghat | 405 | 04:00 | 390 | 12:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 410 | 05:00 | 376 | 12:00 | Meghnaghat | 411 | 04:00 | 382 | 12:00
| Bibiana | 396 | 02:00 | 286 | 20:00 | Payra | 417 | 02:00 | 403 | 12:00
| BIPTC | 408 | 02:00 | 387 | 09:00 | Rahanpur | 414 | 03:00 | 399 | 12:00
| Bogura | 410 | 04:00 | 390 | 13:00 | Rampal | 417 | 03:00 | 390 | 10:00
| Gopalganj | 416 | 03:00 | 387 | 12:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 236 | 04:00 | 216 | 12:00 | Haripur | 234 | 07:00 | 224 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 231 | 05:00 | 219 | 11:00 | Hasnabad | 231 | 03:00 | 219 | 12:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 235 | 05:00 | 217 | 12:00 | Hathazari | 232 | 05:00 | 222 | 12:00
| Ashuganj | 239 | 05:00 | 224 | 13:00 | Ishurdi | 244 | 01:00 | 226 | 12:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 239 | 05:00 | 224 | 13:00 | Jhenaidah | 242 | 01:00 | 220 | 13:00
| Baghabari | 242 | 02:00 | 227 | 12:00 | Kaliakoir | 236 | 03:00 | 219 | 12:00 | 230 kV MAX | 248 |  | 248 | 212
| Barapukuria | 227 | 03:00 | 219 | 12:00 | Keranigonj | 235 | 04:00 | 215 | 12:00 | 230 kV MIN | 212 |  | 244 | 215 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 227 | 03:00 | 219 | 12:00 | Khulna(S) | 243 | 04:00 | 220 | 12:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 246 | 03:00 | 212 | 22:00 | Madunaghat | 232 | 04:00 | 230 | 00:00 | 132 kV MAX | 143 |  | 142 | 115 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 242 | 01:00 | 223 | 12:00 | Madunaghat-400 | 232 | 04:00 | 223 | 12:00 | 132 kV MIN | 112 |  | 143 | 112 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 239 | 05:00 | 229 | 17:00 | Maniknagar | 237 | 05:00 | 216 | 12:00 | [35 empty] | 6:00
| Bibiana | 229 | 01:00 | 218 | 12:00 | Meghnaghat | 242 | 03:00 | 224 | 12:00 | [35 empty] | 392
| BIPTC | 244 | 01:00 | 224 | 12:00 | Meghnaghat-400 | 239 | 04:00 | 221 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 240 | 04:00 | 227 | 12:00 | Mirsorai | 232 | 02:00 | 219 | 11:00 | ` | [34 empty] | 21:00
| Bogura-400 | 238 | 02:00 | 227 | 16:00 | Rajshahi | 242 | 04:00 | 224 | 12:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 248 | 01:00 | 242 | 13:00 | Rampal | 240 | 02:00 | 222 | 12:00 |  |  |  |  | Ash 400-299274
| BSRM | 232 | 02:00 | 217 | 12:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 235 | 05:00 | 218 | 12:00 | Rampura | 239 | 04:00 | 218 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 246 | 01:00 | 231 | 12:00 | Shikalbaha | 231 | 04:00 | 222 | 12:00 |  | kaptai by call 399528
| Fenchuganj | 231 | 06:00 | 224 | 11:00 | Shyampur | 237 | 05:00 | 217 | 12:00
| Ghorashal | 240 | 01:00 | 235 | 00:00 | Siddhirganj | 233 | 00:00 | 220 | 12:00
| Ghorashal-230 | 237 | 04:00 | 218 | 12:00 | Sirajgonj | 247 | 03:00 | 235 | 12:00
| Gopalganj | 247 | 23:00 | 230 | 12:00 | Sreepur | 240 | 02:00 | 230 | 18:30
| GPH | 231 | 01:00 | 217 | 12:00 | Tongi | 234 | 04:00 | 215 | 11:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 137 | 01:00 | 124 | 12:00 | Kurigram | 131 | 03:00 | 119 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 137 | 01:00 | 125 | 12:00 | Kushtia | 141 | 02:00 | 130 | 12:00
| Agrabad | 134 | 04:00 | 125 | 12:00 | Lalbag | 138 | 04:00 | 124 | 12:00
| AKS | 130 | 07:00 | 124 | 11:00 | Lalmonirhat | 130 | 05:00 | 120 | 08:00
| Aminbazar | 137 | 03:00 | 124 | 13:00 | Madanganj | 133 | 21:00 | 123 | 12:00
| Amnura | 141 | 21:00 | 130 | 12:00 | Madaripur | 136 | 00:00 | 130 | 13:00
| Ashuganj | 141 | 05:00 | 134 | 11:00 | Madartek | 137 | 04:00 | 123 | 12:00
| Bagerhat | 140 | 01:00 | 122 | 12:00 | Madunaghat | 133 | 03:00 | 127 | 12:00
| Bajitpur | 133 | 01:00 | 128 | 12:00 | Magura | 141 | 04:00 | 128 | 12:00
| Bakulia | 133 | 05:00 | 127 | 11:00 | Mahasthangarh | 136 | 02:00 | 128 | 12:00
| Banani | 138 | 01:00 | 124 | 12:00 | Manikganj | 130 | 02:00 | 117 | 12:00
| Bangabhaban | 136 | 02:00 | 122 | 12:00 | Maniknagar | 137 | 05:00 | 122 | 12:00
| Barapukuria | 137 | 03:00 | 130 | 08:00 | Matarbari | 124 | 01:00 | 118 | 12:00
| Barguna | 141 | 19:00 | 134 | 12:00 | Matuail | 136 | 05:00 | 127 | 12:00
| Barishal | 136 | 01:00 | 128 | 12:00 | Millgate | 134 | 03:00 | 120 | 12:00
| Barishal-230 | 138 | 04:00 | 129 | 12:00 | Mirpur | 137 | 05:00 | 125 | 11:00
| Baroaulia | 133 | 04:00 | 126 | 12:00 | Mirzapur | 131 | 04:00 | 124 | 12:00
| Baroirhat | 131 | 18:30 | 123 | 11:00 | Mithapukur | 136 | 04:00 | 125 | 13:00
| Bashundhara | 138 | 03:00 | 121 | 12:00 | MI_Cement | 137 | 04:00 | 124 | 12:00
| BashundharaCement | 133 | 21:00 | 123 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 135 | 01:00 | 127 | 12:00 | Mogbazar | 138 | 01:00 | 125 | 12:00
| Benapole | 140 | 01:00 | 122 | 12:00 | Mongla | 138 | 02:00 | 122 | 12:00
| Bhaluka | 130 | 05:00 | 117 | 12:00 | Motijheel | 136 | 02:00 | 122 | 12:00
| Bhandaria | 135 | 06:00 | 126 | 13:00 | Munshiganj | 134 | 04:00 | 123 | 12:00
| Bhangura | 140 | 04:00 | 131 | 12:00 | Mymensingh | 127 | 21:00 | 114 | 12:00
| Bheramara | 141 | 01:00 | 131 | 12:00 | Naogaon | 137 | 05:00 | 127 | 12:00
| Bheramara(GK) | 142 | 05:00 | 131 | 12:00 | Narail | 140 | 01:00 | 127 | 12:00
| Bhulta | 125 | 02:00 | 115 | 12:00 | Narinda | 136 | 2:00 | 122 | 12:00
| Bog-Sherpur | 138 | 03:00 | 129 | 12:00 | Narshingdi | 130 | 22:00 | 115 | 12:00
| Bogura | 137 | 02:00 | 130 | 13:00 | Natore | 139 | 01:00 | 130 | 12:00
| Bogura-230 | 138 | 02:00 | 130 | 12:00 | Nawabganj | 137 | 01:00 | 124.3 | 12:00
| Brahmanbaria | 135 | 04:00 | 123 | 12:00 | Netrakona | 125 | 05:00 | 114 | 12:00
| Cantonment | 138 | 04:00 | 125 | 12:00 | New | 133 | 03:00 | 121 | 12:00
| Chandpur | 138 | 18:00 | 122 | 11:00 | Niamatpur | 140 | 05:00 | 133 | 08:00
| Chandraghona | 134 | 04:00 | 127 | 11:00 | Noapara | 139 | 04:00 | 124 | 13:00
| Chapai | 138 | 04:00 | 132 | 08:00 | Pabna | 141 | 01:00 | 130 | 12:00
| Charsaidpur | 136 | 04:00 | 124 | 12:00 | Palashbari | 133 | 05:00 | 124 | 08:00
| Chauddagram | 134 | 19:00 | 121 | 12:00 | Panchagarh | 137 | 04:00 | 122 | 08:00
| Chhatak | 136 | 05:00 | 125 | 12:00 | Patuakhali | 140 | 17:00 | 133 | 23:00
| Chowmuhani | 127 | 05:00 | 117 | 11:00 | Payra | 137 | 01:00 | 130 | 18:00
| Chuadanga | 141 | 02:00 | 126 | 12:00 | PHP | 130 | 03:00 | 121 | 12:00
| Coxsbazar | 128 | 10:00 | 118 | 11:00 | Postogola | 137 | 05:00 | 127 | 12:00
| Cumilla(N) | 137 | 05:00 | 126 | 12:00 | Purbachal | 138 | 03:00 | 124 | 12:00
| Cumilla(S) | 135 | 04:00 | 125 | 13:00 | Purbasadipur | 131 | 02:00 | 119 | 08:00
| Daudkandi | 133 | 06:00 | 122 | 12:00 | Rahanpur | 140 | 02:00 | 135 | 08:00
| Dhaka | 137 | 03:00 | 124 | 12:00 | Rahanpur-400 | 140 | 01:00 | 135 | 08:00
| Dhamrai | 137 | 04:00 | 125 | 12:00 | Rahim | 134 | 04:00 | 122 | 13:00
| Dhanmondi | 137 | 03:00 | 125 | 12:00 | Rajbari | 137 | 04:00 | 127 | 12:00
| Dohazari | 129 | 05:00 | 124 | 11:00 | Rajendrapur | 135 | 05:00 | 123 | 13:00
| Faridpur | 135 | 01:00 | 129 | 12:00 | Rajshahi | 141 | 05:00 | 130 | 12:00
| Fatullah | 138 | 04:00 | 126 | 12:00 | Rajshahi-230 | 141 | 03:00 | 127 | 13:00
| Fenchuganj | 139 | 05:00 | 133 | 11:00 | Ramganj | 127 | 05:00 | 117 | 11:00
| Feni | 130 | 04:00 | 122 | 12:00 | Rampur | 133 | 04:00 | 126 | 12:00
| Ghatail | 128 | 10:00 | 121 | 07:00 | Rampura | 137 | 01:00 | 124 | 12:00
| Ghorashal | 139 | 01:00 | 136 | 08:00 | Rangamati | 134 | 02:00 | 127 | 11:00
| Goalpara | 142 | 01:00 | 126 | 12:00 | Rangpur | 134 | 06:00 | 125 | 09:00
| Gollamari | 140 | 03:00 | 125 | 13:00 | Ruppur | 141 | 03:00 | 133 | 12:00
| Gopalganj | 139 | 01:00 | 127 | 12:00 | Saidpur | 134 | 18:30 | 121 | 08:00
| Gopalganj-400 | 138 | 01:00 | 129 | 12:00 | Satkhira | 139 | 03:00 | 124 | 13:00
| Gulshan | 137 | 05:00 | 123 | 12:00 | Satmasjid | 137 | 01:00 | 125 | 12:00
| Halishahar | 132 | 05:00 | 128 | 11:00 | Savar | 133 | 03:00 | 122 | 12:00
| Haripur | 132 | 03:00 | 129 | 09:00 | SevenRings | 141 | 03:00 | 131 | 12:00
| HaripurSBU | 132 | 02:00 | 123 | 11:00 | ShahCement | 136 | 04:00 | 124 | 12:00
| Hasnabad | 137 | 21:00 | 126 | 13:00 | Shahjadpur | 143 | 03:00 | 134 | 12:00
| Hathazari | 135 | 05:00 | 130 | 11:00 | Shahjibazar | 137 | 01:00 | 127 | 12:00
| Ishurdi | 142 | 01:00 | 133 | 12:00 | Shahmirpur | 133 | 19:00 | 126 | 11:00
| Jaldhaka | 131 | 05:00 | 125 | 22:00 | Shariatpur | 138 | 03:00 | 128 | 11:00
| Jamalpur | 130 | 21:00 | 116 | 02:00 | Sherpur | 129 | 10:00 | 112 | 02:00
| Jashore | 138 | 04:00 | 123 | 12:00 | Shikalbaha | 123 | 03:00 | 116 | 12:00
| Jhenaidah | 141 | 01:00 | 130 | 20:00 | Shikalbaha-230 | 134 | 04:00 | 127 | 12:00
| Jhenaidah-230 | 142 | 01:00 | 128 | 12:00 | Shitalakhya | 137 | 04:00 | 124 | 12:00
| Joydebpur | 140 | 04:00 | 130 | 12:00 | Sholosohor | 133 | 01:00 | 126 | 12:00
| Joypurhat | 136 | 01:00 | 126 | 12:00 | Shyampur | 135 | 21:00 | 125 | 12:00
| Juldah | 130 | 01:00 | 126 | 11:00 | Shyampur-230 | 138 | 05:00 | 125 | 12:00
| Kabirpur | 134 | 17:00 | 120 | 11:00 | Siddhirganj | 133 | 03:00 | 127 | 12:00
| Kachua | 137 | 18:00 | 124 | 11:00 | Sirajganj | 139 | 01:00 | 130 | 12:00
| Kaliakoir | 138 | 03:00 | 130 | 06:00 | Sonargaon | 128 | 00:00 | 121 | 12:00
| Kallyanpur | 134 | 03:00 | 126 | 12:00 | Sreemongol | 135 | 01:00 | 126 | 12:00
| Kalurghat | 134 | 02:00 | 127 | 12:00 | Sreepur | 131 | 03:00 | 121 | 12:00
| Kamrangirchar | 137 | 04:00 | 124 | 12:00 | Srinagar | 137 | 02:00 | 125 | 12:00
| Kaptai | 136 | 4:00 | 130 | 12:00 | SSM | 139 | 18:30 | 130 | 03:00
| Kazla | 136 | 04:00 | 121 | 13:00 | Sunamganj | 133 | 01:00 | 125 | 12:00
| Keranigonj | 138 | 04:00 | 125 | 12:00 | Sylhet | 137 | 05:00 | 126 | 13:00
| Khagrachori | 133 | 03:00 | 127 | 11:00 | Sylhet-132 | 136 | 01:00 | 127 | 13:00
| Khulna | 140 | 04:00 | 125 | 08:00 | Tangail | 127 | 09:00 | 122 | 18:30
| Khulna(S) | 141 | 01:00 | 126 | 12:00 | Thakurgaon | 135 | 04:00 | 119 | 08:00
| Khulshi | 132 | 04:00 | 124 | 12:00 | TK | 132 | 17:00 | 127 | 12:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 131 | 00:00 | 125 | 12:00 | Tongi | 136 | 04:00 | 124 | 11:00 |  |  | Nos | Nos | Nos
| Kodda | 134 | 21:00 | 124 | 12:00 | Ullahpara | 139 | 02:00 | 133 | 08:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 133 | 01:00 | 128 | 11:00 | Ullon | 136 | 03:00 | 124 | 12:00
| Kulaura | 138 | 03:00 | 131 | 12:00 | Uttara | 137 | 03:00 | 123 | 12:00
| Zigatola | 140 | 02:00 | 130 | 13:00 | UttaraNew | 138 | 02:00 | 127 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.