## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-01-2025 | [28 empty] | Date: | 14-01-2025 | [28 empty] | Date: | 14-01-2025 | [28 empty] | Date: | 14-01-2025 | [28 empty] | Date: | 14-01-2025 | [18 empty] | Date: | 14-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [18 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 150.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 0.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 50.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 17 | 36 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 380 | 292 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 1150 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 405 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 55 | 0 | 0 | 0 | 0 | 300 | 340 | 43 | 30 | 0 | 2 | 120 | 8 | 0 | 85 | 0 | 0 | 0 | 98 | 0 | 19 | 48 | 0 | 0 | 0 | 0 | 4665 | 907 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 715.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 155 | 0 | 156 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 7 | 100 | 180 | 0 | 1244 | 0 | 4428.95 | 9093.95 | 93.26
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 275 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 15 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 1053 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 400 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 54 | 0 | 0 | 0 | 0 | 300 | 343 | 43 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 105 | 0 | 19 | 24 | 0 | 0 | 0 | 0 | 4451 | 908 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 613.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 157 | 0 | 156 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 180 | 0 | 1060 | 0 | 4057.6 | 8508.6 | 93.24
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 291 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 1053 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 330 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 50 | 0 | 0 | 0 | 0 | 300 | 343 | 43 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 106 | 0 | 19 | 16 | 0 | 0 | 0 | 0 | 4357 | 719 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 519.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 157 | 0 | 156 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 1000 | 0 | 3712.76 | 8069.76 | 93.24
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 306 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 1000 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 300 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 186 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 44 | 0 | 0 | 0 | 0 | 300 | 343 | 43 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4239 | 719 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 161 | 0 | 159 | 0 | 0 | 0 | 0 | 5.5 | 166 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 900 | 0 | 3436.41 | 7675.41 | 93.24
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 310 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 1009 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 300 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 197 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 50 | 0 | 0 | 0 | 0 | 300 | 359 | 43 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4280 | 624 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 163 | 0 | 160 | 0 | 0 | 0 | 0 | 5.5 | 160 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 800 | 0 | 3237.6 | 7517.6 | 93.24
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 314 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 1007 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 300 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 197 | 42 | 0 | 0 | 0 | 0 | 14 | 0 | 50 | 0 | 0 | 0 | 0 | 300 | 342 | 43 | 30 | 0 | 2 | 120 | 13 | 0 | 50 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4211 | 624 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 165 | 0 | 164 | 0 | 0 | 0 | 0 | 5.5 | 160 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 800 | 0 | 3258.7 | 7469.7 | 93.24
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 333 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 14.6 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 1020 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 0 | 300 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 222 | 42 | 0 | 0 | 0 | 0 | 12 | 0 | 52 | 0 | 0 | 0 | 0 | 240 | 405 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 50 | 0 | 0 | 0 | 128 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 4320.6 | 720 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 428.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 170 | 0 | 168 | 0 | 0 | 0 | 0 | 5.5 | 160 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 140 | 220 | 0 | 830 | 0 | 3534.93 | 7855.53 | 93.24
07:00 | 0 | 17 | 6 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 380 | 284 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 1060 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 390 | 1 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 185 | 42 | 0 | 0 | 0 | 0 | 12 | 0 | 36 | 0 | 2 | 0 | 10 | 226 | 374 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 0 | 0 | 0 | 215 | 0 | 19 | 56 | 0 | 0 | 0.52 | 8 | 4610.52 | 908 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.23 | 0 | 0 | 558.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 170 | 0 | 173 | 0 | 170 | 0 | 0 | 0 | 0.03 | 5.5 | 159 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.02 | 0 | 229 | 6 | 140 | 220 | 0 | 980 | 0 | 4055.38 | 8665.9 | 93.24
08:00 | 0 | 37 | 25 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 5 | 6 | 0 | 55 | 25 | 0 | 0 | 5 | 17 | 24 | 0 | 380 | 262 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 5 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 1150 | 0 | 0 | 4 | 0 | 0 | 233 | 0 | 0 | 0 | 500 | 6 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 42 | 2 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 14 | 0 | 15 | 212 | 343 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 0 | 0 | 0 | 217 | 0 | 19 | 56 | 0 | 0 | 7.84 | 22 | 4925.84 | 908 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.51 | 0 | 0 | 579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 7.13 | 173 | 0 | 183 | 0 | 181 | 0 | 0 | 0 | 0.55 | 5.5 | 166 | 70 | 0 | 5 | 0 | 0 | 0 | 0.9 | 28 | 0.12 | 0 | 307 | 5 | 140 | 220 | 0 | 1160 | 7 | 4435.71 | 9361.55 | 93.24
09:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 15 | 17 | 0 | 74 | 32 | 0 | 0 | 35 | 17 | 25 | 0 | 380 | 280 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 13 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 1153 | 0 | 0 | 18 | 0 | 0 | 233 | 0 | 0 | 0 | 500 | 12 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 42 | 16 | 0 | 0 | 0 | 14 | 0 | 48 | 0 | 30 | 0 | 25 | 205 | 333 | 43 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 205 | 0 | 19 | 56 | 0 | 1 | 0 | 22 | 5043 | 908 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.08 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 22.11 | 179 | 0 | 183 | 0 | 183 | 0 | 0 | 0 | 1.85 | 5.5 | 200 | 70 | 0 | 13 | 0 | 0 | 0 | 2.2 | 75 | 0.22 | 0 | 307 | 4 | 140 | 220 | 0 | 1200 | 17 | 4812.96 | 9855.96 | 93.23
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 17 | 17 | 0 | 75 | 32 | 0 | 0 | 35 | 17 | 25 | 0 | 380 | 292 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 20 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 1056 | 0 | 0 | 19 | 0 | 0 | 227 | 0 | 0 | 0 | 450 | 16 | 51 | 0 | 155 | 0 | 0 | 0 | 29 | 183 | 37 | 16 | 0 | 0 | 0 | 14 | 0 | 54 | 0 | 44 | 0 | 40 | 205 | 380 | 43 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 208 | 0 | 19 | 58 | 0 | 1 | 0 | 22 | 4952 | 908 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.39 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 35.78 | 187 | 0 | 183 | 0 | 183 | 0 | 0 | 0 | 2.94 | 5.5 | 210 | 70 | 0 | 21 | 0 | 0 | 0 | 3.8 | 115 | 0.36 | 0 | 250 | 3 | 100 | 180 | 0 | 1100 | 17 | 4695.77 | 9647.77 | 93.23
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 237 | 0 | 0 | 32 | 30 | 0 | 75 | 32 | 0 | 8 | 35 | 17 | 25 | 0 | 320 | 318 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 25 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 2 | 1063 | 0 | 0 | 19 | 0 | 0 | 227 | 0 | 0 | 0 | 450 | 19 | 51 | 0 | 108 | 0 | 0 | 0 | 28 | 204 | 37 | 16 | 0 | 0 | 0 | 14 | 0 | 54 | 0 | 53 | 0 | 60 | 275 | 380 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 41 | 0 | 0 | 0 | 208 | 0 | 19 | 58 | 0 | 2 | 0 | 22 | 5047 | 909 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.64 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 44.79 | 140 | 0 | 180 | 0 | 140 | 0 | 0 | 0 | 3.54 | 5.5 | 210 | 70 | 0 | 28 | 0 | 0 | 0 | 4.9 | 124 | 0.48 | 0 | 250 | 3 | 100 | 180 | 0 | 1080 | 17 | 4637.85 | 9684.85 | 93.23
12:00 | 0 | 72 | 25 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 53 | 36 | 0 | 75 | 32 | 0 | 45 | 35 | 17 | 25 | 0 | 400 | 287 | 0 | 0 | 17 | 24 | 0 | 0 | 0 | 25 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 2 | 1150 | 0 | 0 | 19 | 0 | 0 | 227 | 0 | 0 | 0 | 500 | 19 | 51 | 1 | 145 | 0 | 0 | 0 | 28 | 185 | 38 | 16 | 0 | 6 | 0 | 14 | 0 | 60 | 0 | 55 | 0 | 140 | 320 | 380 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 41 | 0 | 0 | 0 | 207 | 0 | 19 | 58 | 0 | 2 | 0 | 22 | 5467 | 910 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.9 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 49.66 | 140 | 0 | 170 | 0 | 162 | 0 | 0 | 0 | 4 | 5.5 | 210 | 70 | 0 | 31 | 0 | 0 | 0 | 5.4 | 125 | 0.5 | 0 | 250 | 3 | 140 | 220 | 0 | 1100 | 17 | 4777.96 | 10244.96 | 93.22
13:00 | 0 | 80 | 25 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 54 | 36 | 0 | 75 | 32 | 0 | 45 | 35 | 17 | 33 | 0 | 400 | 280 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 26 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 2 | 1150 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 550 | 18 | 51 | 15 | 192 | 0 | 0 | 0 | 28 | 189 | 38 | 16 | 0 | 34 | 5 | 14 | 0 | 70 | 0 | 52 | 0 | 260 | 320 | 383 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 206 | 0 | 19 | 58 | 0 | 2 | 0 | 24 | 5749 | 910 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.05 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 50.17 | 173 | 0 | 178 | 0 | 184 | 0 | 0 | 0 | 4.07 | 5.5 | 210 | 70 | 0 | 20 | 0 | 0 | 0 | 5.3 | 123 | 0.49 | 0 | 200 | 3 | 140 | 220 | 0 | 1120 | 0 | 4678.58 | 10427.58 | 93.22
14:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 54 | 36 | 0 | 62 | 32 | 0 | 45 | 35 | 0 | 33 | 0 | 400 | 279 | 0 | 0 | 0 | 24 | 5 | 0 | 0 | 20 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 1153 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 500 | 16 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 182 | 38 | 16 | 0 | 34 | 13 | 15 | 0 | 62 | 0 | 38 | 0 | 280 | 320 | 383 | 43 | 30 | 0 | 2 | 120 | 13 | 0 | 61 | 0 | 0 | 0 | 205 | 0 | 19 | 58 | 0 | 2 | 0 | 24 | 5653 | 911 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.9 | 0 | 0 | 563.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 40.43 | 185 | 0 | 185 | 0 | 189 | 0 | 0 | 0 | 3.16 | 5.5 | 210 | 70 | 0 | 25 | 0 | 0 | 0 | 4.4 | 128 | 0.38 | 0 | 150 | 3 | 140 | 220 | 0 | 1100 | 0 | 4513.31 | 10166.31 | 93.22
15:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 54 | 36 | 0 | 50 | 32 | 0 | 45 | 35 | 0 | 33 | 0 | 340 | 262 | 0 | 0 | 0 | 24 | 1 | 0 | 0 | 18 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 1103 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 455 | 12 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 182 | 38 | 16 | 0 | 34 | 9 | 16 | 0 | 62 | 0 | 25 | 0 | 280 | 320 | 383 | 43 | 30 | 0 | 2 | 120 | 13 | 0 | 61 | 0 | 0 | 0 | 205 | 0 | 19 | 59 | 0 | 1 | 0 | 24 | 5451 | 909 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.69 | 0 | 0 | 561.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 29.4 | 187 | 0 | 165 | 0 | 175 | 0 | 0 | 0 | 2.08 | 5.5 | 210 | 70 | 0 | 18 | 0 | 0 | 0 | 3.1 | 99 | 0.28 | 0 | 150 | 3 | 100 | 220 | 0 | 1000 | 0 | 4250.14 | 9701.14 | 93.21
16:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 54 | 36 | 0 | 50 | 32 | 0 | 47 | 35 | 0 | 33 | 0 | 340 | 269 | 0 | 0 | 0 | 24 | 100 | 0 | 0 | 7 | 0 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 0 | 1101 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 455 | 6 | 51 | 1 | 197 | 0 | 0 | 0 | 29 | 182 | 38 | 16 | 0 | 34 | 9 | 14 | 0 | 54 | 0 | 13 | 0 | 280 | 320 | 383 | 43 | 30 | 0 | 2 | 120 | 13 | 0 | 61 | 0 | 0 | 0 | 205 | 0 | 19 | 58 | 0 | 0 | 10.42 | 24 | 5523.42 | 909 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.03 | 0 | 0 | 560.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 10.5 | 160 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0.9 | 5.5 | 210 | 68 | 0 | 10 | 0 | 0 | 0 | 1.5 | 48 | 0.12 | 0 | 150 | 3 | 100 | 190 | 0 | 990 | 0 | 3993.32 | 9516.74 | 93.21
17:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 54 | 36 | 0 | 50 | 32 | 0 | 47 | 35 | 0 | 33 | 0 | 400 | 282 | 0 | 0 | 5 | 24 | 260 | 0 | 0 | 2 | 0 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 18 | 0 | 0 | 1 | 0 | 40 | 0 | 2 | 1105 | 0 | 0 | 1 | 0 | 0 | 223 | 0 | 0 | 0 | 500 | 1 | 51 | 20 | 157 | 0 | 0 | 0 | 29 | 190 | 38 | 16 | 0 | 34 | 12 | 14 | 0 | 56 | 0 | 3 | 0 | 290 | 320 | 334 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 205 | 0 | 19 | 58 | 0 | 0 | 1.37 | 24 | 5787.37 | 910 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.67 | 0 | 0 | 561.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3.16 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0.26 | 5.5 | 210 | 68 | 0 | 2 | 0 | 0 | 0 | 0.3 | 5 | 0.03 | 0 | 200 | 6 | 100 | 190 | 0 | 1000 | 7 | 3929.59 | 9716.96 | 93.21
18:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 54 | 36 | 0 | 64 | 64 | 0 | 30 | 35 | 54 | 33 | 0 | 400 | 266 | 0 | 0 | 35 | 24 | 335 | 0 | 0 | 0 | 0 | 21 | 22 | 0 | 0 | 12 | 0 | 0 | 0 | 16 | 0 | 33 | 0 | 0 | 12 | 0 | 40 | 0 | 2 | 1150 | 0 | 0 | 15 | 0 | 21 | 227 | 0 | 0 | 0 | 570 | 0 | 51 | 30 | 195 | 0 | 0 | 0 | 29 | 183 | 39 | 44 | 0 | 50 | 28 | 15 | 0 | 62 | 0 | 0 | 0 | 270 | 320 | 379 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 207 | 17 | 19 | 68 | 0 | 0 | 0 | 24 | 6270 | 909 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 642.3 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 16 | 0 | 0 | 0 | 168 | 0 | 179 | 0 | 168 | 0 | 0 | 0 | 0 | 8.5 | 210 | 68 | 34 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 100 | 190 | 0 | 1080 | 54 | 4431.8 | 10701.8 | 93.2
19:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 35 | 17 | 0 | 110 | 48 | 0 | 0 | 0 | 35 | 33 | 0 | 400 | 259 | 0 | 0 | 32 | 24 | 335 | 0 | 0 | 0 | 17 | 16 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 1150 | 0 | 0 | 19 | 0 | 17 | 227 | 0 | 0 | 0 | 612 | 0 | 51 | 10 | 197 | 0 | 0 | 0 | 29 | 183 | 39 | 34 | 30 | 34 | 28 | 5 | 0 | 66 | 0 | 0 | 0 | 265 | 320 | 381 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 207 | 0 | 19 | 68 | 0 | 0 | 0 | 24 | 6148 | 909 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 737.82 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 200 | 0 | 179 | 0 | 0 | 0 | 0 | 11.5 | 210 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1244 | 17 | 4754.32 | 10902.32 | 93.2
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 35 | 0 | 0 | 96 | 48 | 0 | 0 | 0 | 35 | 32 | 0 | 400 | 283 | 0 | 0 | 17 | 24 | 335 | 0 | 0 | 0 | 17 | 16 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 3 | 1152 | 0 | 0 | 19 | 0 | 0 | 227 | 0 | 0 | 0 | 572 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 39 | 34 | 40 | 34 | 28 | 14 | 0 | 63 | 0 | 0 | 0 | 285 | 320 | 381 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 207 | 0 | 19 | 68 | 0 | 0 | 0 | 24 | 6093 | 909 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 206 | 0 | 180 | 0 | 0 | 0 | 0 | 11.5 | 210 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 140 | 220 | 0 | 1244 | 17 | 4680.3 | 10773.3
20:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 35 | 0 | 0 | 96 | 48 | 0 | 0 | 0 | 35 | 32 | 0 | 400 | 260 | 0 | 0 | 17 | 24 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 1151 | 0 | 0 | 19 | 0 | 0 | 228 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 39 | 34 | 50 | 34 | 28 | 14 | 0 | 64 | 0 | 0 | 0 | 280 | 320 | 381 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 206 | 0 | 19 | 68 | 0 | 0 | 0 | 24 | 6043 | 909 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 206 | 0 | 180 | 0 | 0 | 0 | 0 | 11.5 | 210 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 140 | 220 | 0 | 1244 | 17 | 4683.4 | 10726.4 | 93.2
21:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 35 | 0 | 0 | 78 | 32 | 0 | 0 | 0 | 35 | 32 | 0 | 350 | 271 | 0 | 0 | 17 | 24 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 1150 | 0 | 0 | 19 | 0 | 0 | 228 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 42 | 34 | 50 | 34 | 29 | 14 | 0 | 58 | 0 | 0 | 0 | 295 | 320 | 381 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 207 | 0 | 19 | 49 | 0 | 0 | 0 | 24 | 5952 | 909 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 205 | 0 | 180 | 0 | 0 | 0 | 0 | 11.5 | 210 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 140 | 220 | 0 | 1120 | 17 | 4506.5 | 10458.5 | 93.19
22:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 75 | 32 | 0 | 0 | 0 | 0 | 32 | 0 | 350 | 236 | 0 | 0 | 0 | 26 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 1150 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 42 | 0 | 70 | 0 | 30 | 14 | 0 | 56 | 0 | 0 | 0 | 275 | 320 | 381 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 207 | 0 | 19 | 48 | 0 | 0 | 0 | 24 | 5725 | 909 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 204 | 0 | 180 | 0 | 0 | 0 | 0 | 11.5 | 210 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 140 | 220 | 0 | 1090 | 0 | 4400.5 | 10125.5 | 93.19
23:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 350 | 292 | 0 | 0 | 0 | 28 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 1059 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 197 | 42 | 0 | 50 | 0 | 0 | 14 | 0 | 54 | 0 | 0 | 0 | 285 | 320 | 348 | 10 | 30 | 0 | 2 | 130 | 13 | 0 | 61 | 0 | 0 | 0 | 209 | 0 | 19 | 48 | 0 | 0 | 0 | 0 | 5450 | 905 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 206 | 0 | 179 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 900 | 0 | 3977.5 | 9427.5 | 93.18
Total KWH | 0 | 1086720 | 407040 | 0 | 0 | 0 | 0 | 0 | 6501600 | 0 | 0 | 586800 | 444600 | 0 | 1234800 | 542400 | 0 | 359033 | 395089 | 273600 | 619200 | 0 | 9054000 | 6882269 | 0 | 0 | 202439 | 540600 | 2555301 | 0 | 0 | 160409 | 20400 | 439200 | 527040 | 0 | 0 | 85309 | 0 | 0 | 0 | 453600 | 0 | 52512 | 0 | 0 | 13440 | 23281 | 967140 | 0 | 420960 | 26450909.1 | 0 | 0 | 188640 | 0 | 56872 | 5349433 | 0 | 0 | 0 | 10909090 | 127035 | 1218118 | 118763 | 4516363.64 | 0 | 0 | 0 | 693600 | 4574000 | 970056 | 352320 | 230700 | 381120 | 208320 | 334480 | 0 | 1264320 | 0 | 331409 | 0 | 3558580 | 6994200 | 9098000 | 790056 | 717000 | 0 | 58272 | 3637555 | 364848 | 0 | 1617600 | 0 | 0 | 0 | 3788500 | 29160 | 379200 | 1080000 | 0 | 11150 | 20530 | 390240 | 125659221.74 | 21034909 | 6126624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403200 | 0 | 0 | 14563636 | 0 | 0 | 0 | 0 | 0 | 0 | 80080 | 0 | 0 | 21379 | 544124 | 0 | 292500 | 4477936 | 0 | 4489836 | 0 | 4327136 | 0 | 0 | 0 | 23580 | 162198 | 4800000 | 1595782 | 57413 | 185049 | 47357 | 0 | 0 | 31801.56 | 872640 | 3084 | 0 | 5258000 | 133977 | 2889000 | 5146380 | 0 | 25617454.55 | 208800 | 103393876.11 | 229053097.85

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-01-2025 | during | 15-01-2025 | during | 15-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 243 | 294 | 400.37 | 400.37 | 300 | 300 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 287 | 259 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 45 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 53 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 32 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 20 | 16 | 30 | 30 | 25 | 25 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 24 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 25 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 75 | 110 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 72 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 25 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 36 | 17 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6257.05 | 5842.27 | 1453 | 1772 | 4009.99 | 3988.99 | 2702.04 | 2681.04
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 227 | 227 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 0 | 2 | 8 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.83 | 0 | 3.83 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 500 | 612 | 1224 | 1224 | 612 | 612 | network constraint
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 14 | 17 | 18 | 25 | 18 | 25 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 1150 | 1150 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4917.36 | 4873.22 | 1975 | 2107 | 4066.55 | 4049.72 | 3454.55 | 3437.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 185 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 38 | 39 | 46.94 | 46.94 | 45 | 45 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 28 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 145 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 1 | 10 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 30 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 6 | 34 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 60 | 66 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 5 | 20.83 | 20.83 | 20.83 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 28 | 55 | 55 | 55 | 55 | Fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 34 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 55 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 599 | 706 | 1610.97 | 1550.97 | 1430.03 | 1370.03
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 68 | 200 | 200 | 55 | 88 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 115 | 115 | 18 | 18 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 0 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 24 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 101 | 111 | 645.5 | 601.5 | 193.5 | 182.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 10 | 44 | 44 | 44 | 44 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 0 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 41 | 61 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 207 | 207 | 210 | 210 | 205 | 205 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 0 | 0 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 140 | 265 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 381 | 395 | 395 | 367 | 367 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2370.57 | 1339 | 1452 | 1611.5 | 1611.5 | 1537.01 | 1537.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 910 | 909 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 252 | 272 | 410 | 410 | 280 | 280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 66.9 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1228.9 | 1181 | 3194 | 3124 | 1390.01 | 1320.01
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 3 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 135 | 135 | 140 | 140 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1730.5 | 1935 | 2177.12 | 2176.12 | 2182.12 | 2181.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | availability is 47MW but unable to submit to web
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 140 | 190 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 170 | 200 | 220 | 220 | 185 | 185 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 162 | 179 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 11.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 42 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4 | 0 | 4.95 | 0 | 4.95 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 759 | 737.82 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 49.66 | 0 | 45 | 0 | 45 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 87 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1377.16 | 1360.32 | 2702.69 | 2552.74 | 2667.69 | 2517.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 68 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 200 | 200 | 210 | 210 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.4 | 0 | 5.4 | 0 | 5.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 125 | 0 | 124.09 | 0 | 124.09 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 441.4 | 278 | 691.49 | 532 | 667.51 | 508.02
System Total |  |  |  |  | 27734.66 | 27027.25 | 10244.96 | 10902.32 | 20709.81 | 20187.54 | 16224.46 | 15735.19
Forecast Scenario (15-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9000 |  | 0 |  | 9000
|  |  |  | 1:00 | 8490 |  | 0 |  | 8490
|  |  |  | 2:00 | 8000 |  | 0 |  | 8000
|  |  |  | 3:00 | 7770 |  | 0 |  | 7770
|  |  |  | 4:00 | 7500 |  | 0 |  | 7500
|  |  |  | 5:00 | 7490 |  | 0 |  | 7490
|  |  |  | 6:00 | 7780 |  | 0 |  | 7780
|  |  |  | 7:00 | 8670 |  | 0 |  | 8670
|  |  |  | 8:00 | 9380 |  | 0 |  | 9380
|  |  |  | 9:00 | 9780 |  | 0 |  | 9780
|  |  |  | 10:00 | 9630 |  | 0 |  | 9630
|  |  |  | 11:00 | 9740 |  | 0 |  | 9740
|  |  |  | 12:00 | 10180 |  | 0 |  | 10180
|  |  |  | 13:00 | 10420 |  | 0 |  | 10420
|  |  |  | 14:00 | 10130 |  | 0 |  | 10130
|  |  |  | 15:00 | 9740 |  | 0 |  | 9740
|  |  |  | 16:00 | 9530 |  | 0 |  | 9530
|  |  |  | 17:00 | 9710 |  | 0 |  | 9710
|  |  |  | 18:00 | 10760 |  | 0 |  | 10760
|  |  |  | 18:30 | 10900 |  | 0 |  | 10900
|  |  |  | 19:00 | 11150 |  | 0 |  | 11150
|  |  |  | 19:30 | 10760 |  | 0 |  | 10760
|  |  |  | 20:00 | 10710 |  | 0 |  | 10710
|  |  |  | 21:00 | 10640 |  | 0 |  | 10640
|  |  |  | 22:00 | 10060 |  | 0 |  | 10060
|  |  |  | 23:00 | 9480 |  | 0 |  | 9480
Probable Maximum Temperature: |  |  | 27.20°C
Probable Maximum Demand at Day Peak: |  |  | 10280.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 11150.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11150.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 225.74 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (14-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 27.00°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 798.95
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 21.0349 | Peak Hour Flow: |  | 909.00 MW at 19:00 hrs.
Energy Flow from West to East |  | 11387127.377 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 14.5636 | Peak Hour Flow: |  | 737.82 MW at 19:00 hrs.
Power Flow during Peak Demand |  | 594 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.2643 | Peak Hour Flow: |  | 66.00 MW at 19:00 hrs.
Maximum Power Flow |  | 918 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 36.8629 | Peak Hour Flow: |  | 1712.82 MW at 19:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 14-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 10244.96 | MW | 12:00 Hr. | Energy Generated |  |  | 229053.0978 |  | MWHr
Day Peak Demand |  |  | 10244.96 | MW | 12:00 Hr. | Energy Unserverd |  |  | 179 |  | MWHr
Evening Peak Generation |  |  | 10902.32 | MW | 19:00 Hr. | Energy Demand |  |  | 229232.0978 |  | MWHr
Evening Peak Demand |  |  | 10902.32 | MW | 19:00 Hr.
Minimum Generation of the Day |  |  | 7469.7 | MW | 05:00 Hr.
Maximum Generation of the Day |  |  | 10902.32 | MW | 19:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 27119.21 | 0 | 5552.921 | 0 | 0 | 160.409 | 0 | 0 | 32832.54 | Gas | 103804.6186 | Gas | 371818611.386
Chattogram Zone |  |  | 5770.393 | 37359.9991 | 396.773 | 0 | 967.14 | 150.316 | 0 | 453.6 | 45098.2211 | Coal | 74631.2357 | Coal | 523877439.7095
Cumilla Zone |  |  | 12537.3176 | 0 | 1060.523 | 0 | 0 | 331.409 | 1264.32 | 0 | 15193.5696 | HFO | 9303.846 | HFO | 174803159.45
Mymensingh Zone |  |  | 0 | 0 | 1878.6 | 0 | 0 | 31.68 | 0 | 0 | 1910.28 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 30624.611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30624.611 | Hydro | 967.14 | Hydro | 96714
Khulna Zone |  |  | 6126.624 | 0 | 0 | 0 | 0 | 403.2 | 21034.909 | 0 | 27564.733 | Solar | 3029.7926 | Solar | 46627395.726
Barishal Zone |  |  | 8169.357 | 30875.4545 | 208.8 | 0 | 0 | 3.084 | 0 | 0 | 39256.6955 | Import | 36862.865 | Import | 184808749.42
Rajshahi Zone |  |  | 13457.106 | 0 | 101.459 | 0 | 0 | 860.204 | 14563.636 | 0 | 28982.405 | Wind | 453.6 | Wind | 7076160
Rangpur Zone |  |  | 0 | 6395.782 | 104.77 | 0 | 0 | 1089.4906 | 0 | 0 | 7590.0426
Total |  |  | 103804.6186 | 74631.2357 | 9303.846 | 0 | 967.14 | 3029.7926 | 36862.865 | 453.6 | 229053.0978
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 371818611.386 |  | Hydro | 96714
|  |  | Coal | 523877439.7095 |  | Solar | 46627395.726
|  |  | HFO | 174803159.45 |  | Import | 184808749.42
|  |  | HSD | 0 |  | Wind | 7076160
|  |  |  | Total: | 1309108229.6915 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
| 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
| 4 | Barapukuria TPP Unit-2 |  |  | 85
| 5 | Khulna 330 MW CCPP GT |  |  | 220
| 6 | Khulna 330 MW CCPP ST |  |  | 110
| 7 | Siddhirgonj 210 MW TPP |  |  | 115
| 8 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 9 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1404 |  |  |  | Total | 435.09
|  |  | Total Unavailable Capacity |  |  |  | 1839.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 4004
|  |  | Chattogram |  | 0 |  | 1049
|  |  | Cumilla |  | 0 |  | 908
|  |  | Mymensingh |  | 0 |  | 906
|  |  | Sylhet |  | 0 |  | 369
|  |  | Khulna |  | 0 |  | 1183
|  |  | Barishal |  | 0 |  | 294
|  |  | Rajshahi |  | 0 |  | 1005
|  |  | Rangpur |  | 0 |  | 657
|  |  | Total |  | 0 |  | 10375
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:13 | 18:12 | Panchagar-Thakurgaon 132kV Ckt-1 Forced S/D from Panchagarh 132/33kV end Due to
Maintenance Work of Thakurgaon Grid S/S (CB OF Panchagarh Line -01) and from Thakurgaon
132/33kV end Due to PGNS G2G প্রকল্পের আওতায় ঠাকুরগাঁও-পঞ্চগড় সার্কিট-২ এর সাথে
ঠাকুরগাঁও-পঞ্চগড় সার্কিট-১ কমিশনিং।
08:16 | 16:55 | Pabna 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance.
08:16 | 16:55 | Pabna 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance.
08:16 | 14:42 | Juldah-Shahmirpur 132kV Ckt-2 Scheduled S/D from Juldah 132/33kV end Due to Annual dead
line checking work. and from Shahmirpur 132/33kV end Due to Annual Maintenance(Deadline
checking)
08:17 | 17:17 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Annual maintenance
08:17 | 17:17 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual maintenance
08:22 | 15:43 | Goalpara-Labanchura 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to Annual
maintenance.
08:23 | 15:47 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Annual maintenance
work
08:24 | 15:30 | Daudkandi-Sonargaon 132 kV Ckt-1 Forced S/D from Sonargaon 132/33kV end Due to
Instructions by NLDC and from Daudkandi 132/33kV end Due to Annual Maintenance
08:26 |  | BSRM-Mirsharai 230 kV Ckt-1 Project Work S/D from BSRM 230/33kV end Due to ESPNER Project
08:28 |  | Summit Bibiyana -2 CCPP ST was synch
08:32 | 16:19 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to
Annual Maintenance and disc cleaning.
08:49 | 16:34 | Madanganj-Munsiganj 132 kV Ckt-2 Scheduled S/D from Madanganj 132/33kV end Due to annual
maintenance and from Munshiganj 132/33kV end Due to annual maintenance.
08:51 | 13:44 | Sunamganj 132/33kV S/S Tr-2 LT Scheduled S/D
08:52 | 13:43 | Sunamganj 132/33kV S/S Tr-2 HT Scheduled S/D
08:53 | 17:05 | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to Annual
Maintenance
08:58 | 17:02 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D from Dhamrai 132/33kV end Due to Annual
maintenance
09:03 | 14:55 | Bheramara(GK) 132/33kV S/S TR-4 LT Scheduled S/D Due to Annual maintenance
09:04 | 16:15 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D Due to Annual maintenance
09:05 | 14:52 | Bheramara(GK) 132/33kV S/S TR-4 HT Scheduled S/D Due to Annual maintenance.
09:16 | 15:21 | Bhaluka-Mymensingh 132 kV Ckt-2 Scheduled S/D from Bhaluka 132/33kV end Due to Annual
maintenance
09:16 | 15:21 | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Bhaluka 132/33kV end Due to Annual
maintenance
09:23 | 13:00 | Bagerhat-Labanchura 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Orion
power station own maintenance work purpose.
09:28 | 13:12 | Agargaon-Bhasantek 132kV Ckt-1 Scheduled S/D from Cantonment 132/33kV end Due to Annual
maintenance
09:38 | 16:08 | Siddhirganj 132/33kV S/S 132kV Bus A Scheduled S/D Due to Annual maintenance
09:50 | 16:48 | Sonargaon 132/33kV S/S OPML(IEL-1) Scheduled S/D Due to Deadline chaking work for annual
maintenance
10:15 | 13:59 | Bhaluka 132/33kV S/S Bus B Scheduled S/D Due to Annual maintenance
| 10:20 | Tongi 230/132/33kV S/S Tongi-Uttara Ckt is restored.
10:34 | 13:59 | Juldah-Sikalbaha 132kV Ckt-1 Scheduled S/D from Juldah 132/33kV end Due to Sikalbaha
Grid S/S shut down taken due to annual maintenance work. and from Shikalbaha 230/132kV
end Due to Annual Maintenance
10:41 |  | Cumilla(N) 230/132/33kV S/S 132KV T-05 HT Scheduled S/D
10:41 | 12:58 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Scheduled S/D Due to 33 kv bus section -2
PT-2 connection work
10:41 |  | Cumilla(N) 230/132/33kV S/S 132KV T-05 LT Scheduled S/D Due to Development Work
10:42 | 12:55 | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT Scheduled S/D Due to 33 kv bus section -2
PT-2 connection work
10:47 |  | Bogura (W) - Parbatipur 230 -2 charge Bogura (W) S/S.
10:48 | 16:39 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Scheduled S/D from Srinagar
132/33kV end Due to ১৩২ কেভি কেরানিগঞ্জ লাইন-০২ এর ডেড লাইন চেকিং এর জন্য সাটডাউন গ্রহণ
করা হয়। and from Keranigonj 230/132/33kV end Due to Dead Line check.
11:06 | 23:28 | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due to Bus low voltage
11:52 | 12:45 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Fenchuganj
230/132/33kV end Due to Annual maintenance
12:00 |  | Day Peak Gen. 10244 MW
12:04 | 16:14 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Project Work S/D from Thakurgaon 132/33kV end
Due to For project work
13:02 |  | Siddirganj 335 MW CCPP GT was synch.
13:13 |  | Mongla 132/33kV S/S T-1 LT Forced S/D Due to Load test of new transformer T-2 (50/75MVA)
as per request of Xen, GMD, Khulna (S).
13:14 |  | Mongla 132/33kV S/S T-1 HT Forced S/D Due to Load test of new transformer T-2 (50/75MVA)
as per request of Xen, GMD, Khulna (S).
13:24 | 16:15 | Cantonment 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D Due to Annual maintenance
13:49 | 18:37 | Sunamganj 132/33kV S/S Tr-1 LT Scheduled S/D
13:50 | 18:36 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D
| 14:29 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT is restored.
| 14:56 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT is restored.
| 15:30 | Daudkandi-Sonargaon 132 kV Ckt-1 is restored.
| 15:30 | Daudkandi-Sonargaon 132 kV Ckt-1 is restored.
| 15:50 | Bhulta-Haripur 230 kV Ckt-2 is restored.
| 16:28 | Gopalganj(N)-Rampal Ckt-2 is restored.
| 16:36 | Rangpur 132/33kV S/S Rangpur-Teesta Solar-1 is restored.
| 16:42 | Keranigonj 230/132/33kV S/S 132 kV Hasnabad Ckt. 1 is restored.
| 16:43 | Aggreko-keraniganj 132kV Ckt-1 is restored.
| 16:55 | Kallyanpur 132/33kV S/S Reserve bus is restored.
| 17:02 | Dhamrai-Kaliakoir 132 kV Ckt-2 is restored.
| 17:37 | Patuakhali-Payra 132kV Ckt-2 is restored.
| 18:39 | Bashundhara-Rampura 132 kV Ckt-2 is restored.
| 18:43 | BIPTC S/S Baharampur-3 is restored.
19:00 |  | Evening Peak generation = 10,902MW
| 01:00 | Rampal 400/230kV S/S Gopalganj Line-2 Reactor is restored.
01:35 |  | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-2 Tripped from Sirajganj 132/33kV end showing 21
Distance Relay Z2 at A-phase relays Due to PT Blast at Sherpur 132/33KV SS End and from
Bog-Sherpur 132/33kV end showing Distance Protection (P443) Lockout 1 & 2 relays Due to
PT blast of R-phase
05:00 |  | Minimum Generation is 7365 MW
07:06 |  | Haripur 412MW CCPP was shutdown due to air filter change.
07:06 |  | Haripur 412 MW CCPP Shutdown with remarks:- GT
07:12 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
07:13 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
07:21 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Project Work S/D Due to Old T1 shifting work by
project
07:22 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Project Work S/D Due to Old T1 shifting work by
project
07:40 |  | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT Scheduled S/D Due to Annual
Maintenance.
07:40 |  | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) LT Scheduled S/D Due to Annual
Maintenance.
07:41 |  | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to Annual maintenance purpose. | [7 empty] | 20.0MW load
interrup.
07:41 |  | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to Annual maintenance purpose. | [7 empty] | 20.0MW load
interrup.
07:50 |  | Patuakhali-Payra 132kV Ckt-2 Scheduled S/D from Patuakhali 132/33kV end Due to Annual
Maintenance and from Payra 400/132/33kV end Due to Annual maintenance
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 294 | 6501600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9054000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 259 | 6882269 | -
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 359033 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 2555301 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 586800 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 542400 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 395089 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 32 | 202439 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 439200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 527040 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 33 | 619200 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 24 | 540600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 25 | 407040 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 110 | 1234800 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1086720 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 273600 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 160409 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 17 | 444600 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 17 | 20400 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 1772 | 32832540
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 127035 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 188640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 967140 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 5349433 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 56872 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 52512 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 0 | 8 | 420960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23281 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 13440 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 85309 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 10909090 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 17 | 453600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 1150 | 26450909.1 | -
Chattogram Area Total |  |  |  |  | 4873.22 | 2107 | 45098221.1
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4574000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 39 | 970056 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 693600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 4516363.64 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1218118 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 10 | 118763 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 30 | 230700 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 381120 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 66 | 1264320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 5 | 334480 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 208320 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 352320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 331409 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 706 | 15193569.64
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 68 | 1080000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 379200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 20530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 390240 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 29160 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 111 | 1910280
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 717000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3637555 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 790056 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 58272 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 61 | 1617600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 207 | 3788500 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 364848 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 265 | 3558580 | Plant shutdown as per NLDC requirement.
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 381 | 9098000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 6994200 | FGMO
Sylhet Area Total |  |  |  |  | 2370.57 | 1452 | 30624611
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 909 | 21034909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 272 | 6126624 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 403200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Under Maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1181 | 27564733
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 133977 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2889000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 25617454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5146380 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 208800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5258000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3084 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1935 | 39256695.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 190 | 4477936 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 200 | 4489836 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 179 | 4327136 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 11.5 | 162198 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 21379 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 80080 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 23580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 737.82 | 14563636 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 292500 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 544124 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1360.32 | 28982405
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 68 | 1595782 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4800000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 47357 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31801.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 57413 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 185049 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 872640 | -
Rangpur Area Total |  |  |  |  | 950 | 278 | 7590042.56
Eastern Grid Total |  |  |  |  | 16732.75 | 6148 | 125659221.74
Western Grid Total |  |  |  |  | 10294.5 | 4754.32 | 103393876.11
National Grid Total |  |  |  |  | 27027.25 | 10902.32 | 229053097.85
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7236.27 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3139.5 | MW
i) Dhaka area |  |  | 4004.27 |  | MW | i) Khulna area |  |  |  | 1183 | MW
ii) Chattogram area |  |  | 1049 |  | MW | ii) Barishal area |  |  |  | 294.5 | MW
iii) Cumilla area |  |  | 908 |  | MW | iii) Rajshahi area |  |  |  | 1005 | MW
iv) Mymensingh area |  |  | 906 |  | MW | iv) Rangpur area |  |  |  | 657 | MW
v) Sylhet area |  |  | 369 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10375.77 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 12:00 | 67 | Jaldhaka | 55 | 18:30 | 133 | Purbasadipur | 101 | 18:30
2 | AKSML | 107 | 01:00 | 68 | Jamalpur | 99 | 18:30 | 134 | Rahanpur | 0 | 04:00
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 112 | 13:00 | 135 | Rahim | 38 | 08:00
4 | Agargaon | 72 | 13:00 | 70 | Jhenaidah | 94 | 18:00 | 136 | Rajbari | 56 | 18:30
5 | Agrabad | 64 | 18:00 | 71 | Joydebpur | 122 | 18:30 | 137 | Rajendrapur | 100 | 13:00
6 | Amnura | 46 | 12:00 | 72 | Joypurhat | 41 | 18:30 | 138 | Rajshahi | 105 | 13:00
7 | Ashuganj | 60 | 13:00 | 73 | Juldah | 10 | 11:00 | 139 | Rajshahi-230 | 42.5 | 08:00
8 | BSRM | 189 | 06:00 | 74 | KSRM | 26 | 09:00 | 140 | Ramganj | 82 | 18:00
9 | Bagerhat | 62 | 18:30 | 75 | Kabirpur | 220 | 12:00 | 141 | Rampur | 25 | 18:30
10 | Bajitpur | 0 | 14:00 | 76 | Kachua | 50 | 18:30 | 142 | Rangamati | 12 | 18:00
11 | Bakulia | 82 | 18:00 | 77 | Kallyanpur | 66 | 13:00 | 143 | Rangpur | 113 | 18:30
12 | Banani | 39 | 13:00 | 78 | Kalurghat | 12 | 18:00 | 144 | Ruppur | 4.8 | 15:00
13 | Bangabhaban | 8 | 10:00 | 79 | Kamrangirchar | 58 | 13:00 | 145 | SSM | 15 | 03:00
14 | Barapukuria | 47 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | Saidpur | 91 | 18:30
15 | Barguna | 14 | 18:30 | 81 | Kazla | 96 | 12:00 | 147 | Satkhira | 89 | 18:30
16 | Barishal | 83 | 13:00 | 82 | Keranigonj | 59 | 13:00 | 148 | Satmasjid | 81 | 13:00
17 | Barishal-230 | 60 | 18:00 | 83 | Khagrachori | 24 | 18:30 | 149 | Savar | 156 | 11:00
18 | Baroaulia | 51 | 11:00 | 84 | Khulna | 71 | 13:00 | 150 | SevenRings | 17.25 | 15:00
19 | Baroirhat | 41 | 18:00 | 85 | Khulshi | 158 | 13:00 | 151 | ShahCement | 23 | 12:00
20 | Bashundhara | 120 | 13:00 | 86 | Kishoreganj | 124 | 18:30 | 152 | Shahjadpur | 54 | 18:00
21 | BashundharaCement | 12 | 01:00 | 87 | Kodda | 274 | 18:30 | 153 | Shahjibazar | 84 | 18:30
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 26 | 18:00 | 154 | Shahmirpur | 47 | 15:00
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 46 | 08:00 | 155 | Shariatpur | 52 | 20:00
24 | Bhaluka | 136 | 12:00 | 90 | Kushtia | 108 | 13:00 | 156 | Sherpur | 106 | 08:00
25 | Bhandaria | 35 | 21:00 | 91 | Lalbag | 57 | 13:00 | 157 | Shikalbaha | 22 | 12:00
26 | Bhangura | 22 | 18:00 | 92 | Lalmonirhat | 44 | 18:00 | 158 | Shitalakhya | 59 | 13:00
27 | Bheramara(GK) | 41 | 18:30 | 93 | MI_Cement | 15.3 | 00:00 | 159 | Sholosohor | 32 | 15:00
28 | Bhulta | 262 | 12:00 | 94 | Madanganj | 32 | 12:00 | 160 | Shyampur | 156 | 11:00
29 | Bog-Sherpur | 50 | 18:30 | 95 | Madaripur | 67 | 20:00 | 161 | Siddhirganj | 108 | 12:00
30 | Bogura | 109 | 13:00 | 96 | Madartek | 46.69 | 13:00 | 162 | Sirajganj | 74 | 18:30
31 | Borhanuddin | 53 | 22:00 | 97 | Madunaghat | 38 | 18:00 | 163 | Sonargaon | 81 | 07:00
32 | Brahmanbaria | 100 | 19:30 | 98 | Magura | 46 | 18:30 | 164 | Sreemongol | 49 | 19:00
33 | Cantonment | 80 | 13:00 | 99 | Mahasthangarh | 50 | 18:30 | 165 | Sreepur | 65 | 09:00
34 | Chandpur | 43 | 21:00 | 100 | Manikganj | 108 | 18:00 | 166 | Srinagar | 29 | 20:00
35 | Chandraghona | 24 | 18:00 | 101 | Maniknagar | 48 | 13:00 | 167 | Sunamganj | 36 | 19:00
36 | Chapai | 55 | 11:00 | 102 | Matarbari | 35 | 19:00 | 168 | Sylhet | 34 | 11:00
37 | Charsaidpur | 39 | 23:00 | 103 | Matuail | 48 | 12:00 | 169 | Sylhet-132 | 66 | 13:00
38 | Chauddagram | 45 | 13:00 | 104 | Millgate | 70 | 10:00 | 170 | TK | 20 | 18:00
39 | Chhatak | 21 | 18:00 | 105 | Mirpur | 97.5 | 18:00 | 171 | Tangail | 136 | 18:00
40 | Chowmuhani | 149 | 19:00 | 106 | Mirsorai | 8 | 17:00 | 172 | Thakurgaon | 73 | 18:30
41 | Chuadanga | 71 | 18:00 | 107 | Mirzapur | 36 | 18:00 | 173 | Tongi | 115 | 12:00
42 | Coxsbazar | 102 | 18:00 | 108 | Mithapukur | 42 | 18:00 | 174 | Ullahpara | 24 | 08:00
43 | Cumilla(N) | 116 | 19:00 | 109 | Modern | 0 | 05:00 | 175 | Ullon | 35 | 13:00
44 | Cumilla(S) | 129 | 13:00 | 110 | Mogbazar | 92.3 | 13:00 | 176 | Uttara | 59 | 14:00
45 | Daudkandi | 108 | 21:00 | 111 | Mongla | 33 | 07:00 | 177 | UttaraNew | 33 | 14:00
46 | Dhaka | 34 | 13:00 | 112 | Motijheel | 27 | 13:00 | 178 | Zigatola | 52 | 13:00
47 | Dhamrai | 94 | 20:00 | 113 | Munshiganj | 66 | 13:00
48 | Dhanmondi | 81 | 13:00 | 114 | Mymensingh | 182 | 08:00
49 | Dohazari | 50 | 00:00 | 115 | Naogaon | 87 | 12:00
50 | Faridpur | 110 | 18:30 | 116 | Narail | 42 | 18:30
51 | Fatullah | 80 | 12:00 | 117 | Narinda | 58 | 13:00
52 | Fenchuganj | 24 | 18:00 | 118 | Narshingdi | 148 | 18:30
53 | Feni | 73 | 18:00 | 119 | Natore | 106 | 18:30
54 | GPH | 95 | 16:00 | 120 | Nawabganj | 35.4 | 13:00
55 | Ghatail | 28 | 07:00 | 121 | Netrakona | 131 | 18:00
56 | Ghorashal | 8 | 11:00 | 122 | New | 70.3 | 12:00
57 | Ghorashal-230 | 56 | 20:00 | 123 | Niamatpur | 68 | 13:00
58 | Goalpara | 28 | 13:00 | 124 | Noapara | 34 | 18:30
59 | Gollamari | 46 | 13:00 | 125 | PHP | 4 | 11:00
60 | Gopalganj | 81 | 18:30 | 126 | Pabna | 81 | 18:00
61 | Gulshan | 68 | 13:00 | 127 | Palashbari | 73 | 18:30
62 | Halishahar | 50 | 16:00 | 128 | Panchagarh | 41 | 18:00
63 | HaripurSBU | 167 | 19:00 | 129 | Patuakhali | 55 | 21:00
64 | Hasnabad | 66 | 13:00 | 130 | Payra | 12 | 18:00
65 | Hathazari | 52 | 14:00 | 131 | Postogola | 46 | 12:00
66 | Ishurdi | 56 | 18:30 | 132 | Purbachal | 14 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9093.95 | 0 |  | 9093.95
1:00 | 8508.6 | 0 |  | 8508.6
2:00 | 8069.76 | 0 |  | 8069.76
3:00 | 7675.41 | 0 |  | 7675.41
4:00 | 7517.6 | 0 |  | 7517.6
5:00 | 7469.7 | 0 |  | 7469.7
6:00 | 7855.53 | 0 |  | 7855.53
7:00 | 8665.9 | 0 |  | 8665.9
8:00 | 9361.55 | 0 |  | 9361.55
9:00 | 9855.96 | 0 |  | 9855.96
10:00 | 9647.77 | 30 |  | 9679.12
11:00 | 9684.85 | 28 |  | 9713.85
12:00 | 10244.96 | 0 |  | 10244.96
13:00 | 10427.58 | 37 |  | 10466.58
14:00 | 10166.31 | 45 |  | 10213.31
15:00 | 9701.14 | 39 |  | 9742.14
16:00 | 9516.74 | 0 |  | 9516.74
17:00 | 9716.96 | 0 |  | 9716.96
18:00 | 10701.8 | 0 |  | 10701.8
19:00 | 10902.32 | 0 |  | 10902.32
19:30 | 10773.3 | 0 |  | 10773.3
20:00 | 10726.4 | 0 |  | 10726.4
21:00 | 10458.5 | 0 |  | 10458.5
22:00 | 10125.5 | 0 |  | 10125.5
23:00 | 9427.5 | 0 |  | 9427.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 14-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2297 | 1534.5 | 907 | 0 | 55 | 715.45 | 40 | 3368 | 0 | 17 | 160 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2303.5 | 1523 | 907.5 | 0 | 54.5 | 664.275 | 40 | 3180.5 | 0 | 8.5 | 119.5 | 0 | 0 | 0 | 0 | 14-01-2025
01:00 | 2310 | 1511.5 | 908 | 0 | 54 | 613.1 | 40 | 2993 | 0 | 0 | 79 | 0 | 0 | 0 | 0
01:30 | 2306.5 | 1515 | 813.5 | 0 | 52 | 566.18 | 40 | 2928 | 0 | 0 | 65.5 | 0 | 0 | 2.5 | 0 |  | Total Energy | 229.0531 |  | MKWHr
02:00 | 2303 | 1518.5 | 719 | 0 | 50 | 519.26 | 40 | 2863 | 0 | 0 | 52 | 0 | 0 | 5 | 0 |  | Energy not Served | 0.179 |  | MKWHr
02:30 | 2305.5 | 1531 | 719 | 0 | 47 | 471.085 | 40 | 2724.5 | 0 | 0 | 26 | 0 | 0 | 8.5 | 0 |  | Energy Requirement | 229.2321 |  | MKWHr
03:00 | 2308 | 1543.5 | 719 | 0 | 44 | 422.91 | 40 | 2586 | 0 | 0 | 0 | 0 | 0 | 12 | 0
03:30 | 2322.5 | 1546 | 671.5 | 0 | 47 | 421.505 | 40 | 2537.5 | 0 | 0 | 0 | 0 | 0 | 10.5 | 0
04:00 | 2337 | 1548.5 | 624 | 0 | 50 | 420.1 | 40 | 2489 | 0 | 0 | 0 | 0 | 0 | 9 | 0
04:30 | 2326.5 | 1533 | 624 | 0 | 50 | 420.65 | 40 | 2488.5 | 0 | 0 | 0 | 0 | 0 | 11 | 0
05:00 | 2316 | 1517.5 | 624 | 0 | 50 | 421.2 | 40 | 2488 | 0 | 0 | 0 | 0 | 0 | 13 | 0
05:30 | 2353.5 | 1567.3 | 672 | 0 | 51 | 424.815 | 40 | 2535 | 0 | 0 | 6.5 | 0 | 0 | 12.5 | 0
06:00 | 2391 | 1617.1 | 720 | 0 | 52 | 428.43 | 40 | 2582 | 0 | 0 | 13 | 0 | 0 | 12 | 0
06:30 | 2420.5 | 1616.8 | 814 | 0 | 44 | 493.275 | 40 | 2736.5 | 3.64 | 11.5 | 61 | 0 | 0 | 19.5 | 0
07:00 | 2450 | 1616.5 | 908 | 0 | 36 | 558.12 | 40 | 2891 | 7.28 | 23 | 109 | 0 | 0 | 27 | 0
07:30 | 2440.5 | 1596.5 | 908 | 0 | 38 | 568.56 | 40 | 3122 | 55.665 | 55 | 162 | 0 | 0 | 27.5 | 0
08:00 | 2431 | 1576.5 | 908 | 0 | 40 | 579 | 40 | 3353 | 104.05 | 87 | 215 | 0 | 0 | 28 | 0
08:30 | 2415.5 | 1570 | 908 | 0 | 44 | 668 | 40 | 3391.5 | 175.255 | 107 | 269 | 0 | 0 | 20.5 | 0
09:00 | 2400 | 1563.5 | 908 | 0 | 48 | 757 | 40 | 3430 | 246.46 | 127 | 323 | 0 | 0 | 13 | 0
09:30 | 2403.5 | 1534.5 | 908 | 0 | 51 | 756 | 40 | 3283 | 311.865 | 127 | 326 | 0 | 0 | 11 | 15
10:00 | 2407 | 1505.5 | 908 | 0 | 54 | 755 | 40 | 3136 | 377.27 | 127 | 329 | 0 | 0 | 9 | 30
10:30 | 2406.5 | 1474 | 908.5 | 0 | 54 | 756 | 40 | 3129.5 | 414.31 | 127 | 347 | 0 | 0 | 9.5 | 29
11:00 | 2406 | 1442.5 | 909 | 0 | 54 | 757 | 40 | 3123 | 451.35 | 127 | 365 | 0 | 0 | 10 | 28
11:30 | 2450 | 1545.5 | 909.5 | 0 | 57 | 758 | 40 | 3201.5 | 462.905 | 128 | 400.5 | 0 | 0 | 12 | 14
12:00 | 2494 | 1648.5 | 910 | 0 | 60 | 759 | 40 | 3280 | 474.46 | 129 | 436 | 0 | 0 | 14 | 0
12:30 | 2533.5 | 1741.5 | 910 | 0 | 65 | 709.5 | 40 | 3290 | 464.77 | 133 | 434.5 | 0 | 0 | 14.5 | 18.5
13:00 | 2573 | 1834.5 | 910 | 0 | 70 | 660 | 40 | 3300 | 455.08 | 137 | 433 | 0 | 0 | 15 | 37
13:30 | 2594.5 | 1827 | 910.5 | 0 | 66 | 611.77 | 40 | 3241.5 | 431.175 | 132 | 414.5 | 0 | 0 | 28 | 41
14:00 | 2616 | 1819.5 | 911 | 0 | 62 | 563.54 | 40 | 3183 | 407.27 | 127 | 396 | 0 | 0 | 41 | 45
14:30 | 2582.5 | 1782 | 910 | 0 | 62 | 562.315 | 40 | 3085.5 | 353.41 | 127 | 388.5 | 0 | 0 | 40.5 | 42
15:00 | 2549 | 1744.5 | 909 | 0 | 62 | 561.09 | 40 | 2988 | 299.55 | 127 | 381 | 0 | 0 | 40 | 39
15:30 | 2559.5 | 1731 | 909 | 0 | 58 | 560.93 | 40 | 2981 | 226.01 | 127 | 382 | 0 | 0 | 34.5 | 19.5
16:00 | 2570 | 1717.5 | 909 | 0 | 54 | 560.77 | 40 | 2974 | 152.47 | 127 | 383 | 0 | 0 | 29 | 0
16:30 | 2607.5 | 1764 | 909.5 | 0 | 55 | 561.22 | 40 | 3028.5 | 90.63 | 136 | 401 | 0 | 0 | 23.5 | 0
17:00 | 2645 | 1810.5 | 910 | 0 | 56 | 561.67 | 40 | 3083 | 28.79 | 145 | 419 | 0 | 0 | 18 | 0
17:30 | 2773.5 | 1796.5 | 909.5 | 0 | 59 | 601.985 | 40 | 3205.5 | 14.395 | 189.5 | 602.5 | 0 | 0 | 17 | 0
18:00 | 2902 | 1782.5 | 909 | 0 | 62 | 642.3 | 40 | 3328 | 0 | 234 | 786 | 0 | 0 | 16 | 0
18:30 | 2964.5 | 1789.5 | 909 | 0 | 64 | 690.06 | 40 | 3459.5 | 0 | 218 | 651 | 0 | 0 | 16.5 | 0
19:00 | 3027 | 1796.5 | 909 | 0 | 66 | 737.82 | 40 | 3591 | 0 | 202 | 516 | 0 | 0 | 17 | 0
19:30 | 3044 | 1843.5 | 909 | 0 | 63 | 755.8 | 40 | 3496 | 0 | 160 | 443 | 0 | 0 | 19 | 0
20:00 | 3057 | 1828.5 | 909 | 0 | 64 | 754.9 | 40 | 3473 | 0 | 143 | 443 | 0 | 0 | 14 | 0
20:30 | 3059 | 1817 | 909 | 0 | 61 | 727.95 | 40 | 3411 | 0 | 125.5 | 425 | 0 | 0 | 17 | 0
21:00 | 3061 | 1805.5 | 909 | 0 | 58 | 701 | 40 | 3349 | 0 | 108 | 407 | 0 | 0 | 20 | 0
21:30 | 3071 | 1782 | 909 | 0 | 57 | 672.5 | 40 | 3334 | 0 | 100 | 301.5 | 0 | 0 | 25 | 0
22:00 | 3081 | 1758.5 | 909 | 0 | 56 | 644 | 40 | 3319 | 0 | 92 | 196 | 0 | 0 | 30 | 0
22:30 | 3063 | 1779.5 | 907 | 0 | 55 | 554.5 | 40 | 3129 | 0 | 54.5 | 159.5 | 0 | 0 | 34.5 | 0
23:00 | 3045 | 1800.5 | 905 | 0 | 54 | 465 | 40 | 2939 | 0 | 17 | 123 | 0 | 0 | 39 | 0
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4665 | 4428.95 | 9093.95 | DAILY LOAD CURVE
00:30 | 4558 | 4243.275 | 8801.275
01:00 | 4451 | 4057.6 | 8508.6 | 14-01-2025
01:30 | 4404 | 3885.18 | 8289.18
02:00 | 4357 | 3712.76 | 8069.76
02:30 | 4298 | 3574.585 | 7872.585
03:00 | 4239 | 3436.41 | 7675.41
03:30 | 4259.5 | 3337.005 | 7596.505
04:00 | 4280 | 3237.6 | 7517.6
04:30 | 4245.5 | 3248.15 | 7493.65
05:00 | 4211 | 3258.7 | 7469.7
05:30 | 4265.8 | 3396.815 | 7662.615
06:00 | 4320.6 | 3534.93 | 7855.53
06:30 | 4465.56 | 3795.155 | 8260.715
07:00 | 4610.52 | 4055.38 | 8665.9
07:30 | 4768.18 | 4245.545 | 9013.725
08:00 | 4925.84 | 4435.71 | 9361.55
08:30 | 4984.42 | 4624.335 | 9608.755
09:00 | 5043 | 4812.96 | 9855.96
09:30 | 4997.5 | 4754.365 | 9751.865
10:00 | 4952 | 4695.77 | 9647.77
10:30 | 4999.5 | 4666.81 | 9666.31
11:00 | 5047 | 4637.85 | 9684.85
11:30 | 5257 | 4707.905 | 9964.905
12:00 | 5467 | 4777.96 | 10244.96
12:30 | 5608 | 4728.27 | 10336.27
13:00 | 5749 | 4678.58 | 10427.58
13:30 | 5701 | 4595.945 | 10296.945
14:00 | 5653 | 4513.31 | 10166.31
14:30 | 5552 | 4381.725 | 9933.725
15:00 | 5451 | 4250.14 | 9701.14
15:30 | 5487.21 | 4121.73 | 9608.94
16:00 | 5523.42 | 3993.32 | 9516.74
16:30 | 5655.395 | 3961.455 | 9616.85
17:00 | 5787.37 | 3929.59 | 9716.96
17:30 | 6028.685 | 4180.695 | 10209.38
18:00 | 6270 | 4431.8 | 10701.8
18:30 | 6209 | 4593.06 | 10802.06
19:00 | 6148 | 4754.32 | 10902.32
19:30 | 6093 | 4680.3 | 10773.3
20:00 | 6043 | 4683.4 | 10726.4
20:30 | 5997.5 | 4594.95 | 10592.45 |  | Executive Engineer
21:00 | 5952 | 4506.5 | 10458.5 |  | Network Operation Division
21:30 | 5838.5 | 4453.5 | 10292
22:00 | 5725 | 4400.5 | 10125.5
22:30 | 5587.5 | 4189 | 9776.5
23:00 | 5450 | 3977.5 | 9427.5

## Volt
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2021-01-13 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
Aminbazar | 411 | 00:00 | 387 | 13:00 | Kaliakoir | 375 | 05:00 | 344 | 12:00
Ashuganj | 410 | 5:00 | 380 | 12:00 | Madunaghat | 406 | 07:00 | 393 | 13:00
Bhulta | 411 | 05:00 | 374 | 12:00 | Meghnaghat | 412 | 04:00 | 394 | 10:00
Bibiana | 394 | 07:00 | 383 | 01:00 | Payra | 418 | 05:00 | 405 | 13:00
BIPTC | 407 | 04:00 | 388 | 10:00 | Rahanpur | 413 | 02:00 | 400 | 08:00
Bogura | 409 | 02:00 | 392 | 13:00 | Rampal | 415 | 05:00 | 385 | 13:00
Gopalganj | 417 | 01:00 | 390 | 13:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Agargaon | 235 | 02:00 | 217 | 13:00 | Haripur | 231 | 22:00 | 217 | 13:00
AKSML | 233 | 02:00 | 221 | 11:00 | Hasnabad | 232 | 23:00 | 218 | 12:00
Aminbazar | 234 | 06:00 | 220 | 11:00 | Hathazari | 236 | 07:00 | 225 | 12:00
Ashuganj | 239 | 05:00 | 220 | 13:00 | Ishurdi | 243 | 04:00 | 226 | 13:00
Ashuganj-400 | 242 | 5:00 | 224 | 12:00 | Jhenaidah | 242 | 04:00 | 219 | 13:00
Baghabari | 242 | 02:00 | 229 | 12:00 | Kaliakoir | 236 | 05:00 | 215 | 12:00
Barapukuria | 226 | 04:00 | 218 | 19:00 | Keranigonj | 234 | 03:00 | 216 | 13:00
Barapukuria-230 | 226 | 04:00 | 218 | 19:00 | Khulna(S) | 243 | 03:00 | 223 | 13:00
Barishal | 247 | 05:00 | 235 | 13:00 | Madunaghat | 231 | 04:00 | 223 | 13:00
Bheramara | 242 | 03:00 | 222 | 13:00 | Madunaghat-400 | 234 | 09:00 | 223 | 13:00
Bhulta | 239 | 05:00 | 217 | 12:00 | Maniknagar | 236 | 05:00 | 215 | 13:00
Bibiana | 230 | 02:00 | 220 | 12:00 | Meghnaghat | 240 | 04:00 | 225 | 12:00
BIPTC | 243 | 04:00 | 223 | 13:00 | Meghnaghat-400 | 240 | 04:00 | 219 | 13:00
Bogura | 238 | 02:00 | 228 | 13:00 | Mirsorai | 234 | 04:00 | 218 | 13:00
Bogura-400 | 238 | 05:00 | 227 | 13:00 | Rajshahi | 243 | 03:00 | 223 | 13:00
Borhanuddin | 249 | 01:00 | 242 | 11:00 | Rampal | 240 | 04:00 | 220 | 13:00
BSRM | 233 | 04:00 | 217 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Cumilla(N) | 234 | 04:00 | 214 | 13:00 | Rampura | 238 | 05:00 | 216 | 13:00
Faridpur | 246 | 00:00 | 233 | 13:00 | Shikalbaha | 232 | 04:00 | 220 | 13:00
Fenchuganj | 232 | 05:00 | 225 | 16:00 | Shyampur | 230 | 22:00 | 218 | 12:00
Ghorashal | 236 | 06:00 | 220 | 13:00 | Siddhirganj | 233 | 22:00 | 218 | 12:00
Ghorashal-230 | 236 | 03:00 | 213 | 13:00 | Sirajgonj | 246 | 03:00 | 237 | 11:00
Gopalganj | 247 | 01:00 | 231 | 13:00 | Sreepur | 240 | 03:00 | 225 | 11:00
GPH | 233 | 04:00 | 219 | 13:00 | Tongi | 234 | 05:00 | 208 | 12:00
132 KV | KV |  | KV |  | 132 KV | KV |  | KV
Aftabnagar | 137 | 02:00 | 122 | 13:00 | Kurigram | 132 | 04:00 | 120 | 08:00
Agargaon | 137 | 01:00 | 125 | 13:00 | Kushtia | 140 | 00:00 | 129 | 13:00
Agrabad | 133 | 01:00 | 125 | 13:00 | Lalbag | 138 | 03:00 | 125 | 13:00
AKS | 131 | 05:00 | 126 | 11:00 | Lalmonirhat | 132 | 04:00 | 122 | 08:00
Aminbazar | 135 | 06:00 | 126 | 11:00 | Madanganj | 135 | 03:00 | 123 | 13:00
Amnura | 140 | 04:00 | 131 | 08:00 | Madaripur | 137 | 05:00 | 129 | 13:00
Ashuganj | 140 | 03:00 | 131 | 12:00 | Madartek | 136 | 02:00 | 123 | 13:00
Bagerhat | 138 | 02:00 | 123 | 13:00 | Madunaghat | 133 | 05:00 | 128 | 12:00
Bajitpur | 135 | 23:00 | 126 | 12:00 | Magura | 141 | 01:00 | 127 | 13:00
Bakulia | 134 | 04:00 | 126 | 13:00 | Mahasthangarh | 136 | 02:00 | 129 | 08:00
Banani | 137 | 02:00 | 123 | 13:00 | Manikganj | 132 | 22:00 | 115 | 13:00
Bangabhaban | 135 | 05:00 | 121 | 13:00 | Maniknagar | 134 | 01:00 | 122 | 12:00
Barapukuria | 136 | 04:00 | 129 | 19:00 | Matarbari | 127 | 03:00 | 119 | 19:00
Barguna | 137 | 04:00 | 132 | 13:00 | Matuail | 134 | 01:00 | 123 | 12:00
Barishal | 137 | 01:00 | 127 | 13:00 | Millgate | 134 | 23:00 | 118 | 13:00
Barishal-230 | 138 | 03:00 | 129 | 13:00 | Mirpur | 136 | 04:00 | 124 | 12:00
Baroaulia | 134 | 04:00 | 126 | 13:00 | Mirzapur | 130 | 07:00 | 121 | 14:00
Baroirhat | 129 | 03:00 | 119 | 13:00 | Mithapukur | 134 | 02:00 | 125 | 08:00
Bashundhara | 137 | 02:00 | 119 | 12:00 | MI_Cement | 136 | 03:00 | 126 | 12:00
BashundharaCement | 135 | 03:00 | 123 | 13:00 | Modern | 134 | 01:00 | 122 | 12:00
Beanibazar | 136 | 04:00 | 129 | 12:00 | Mogbazar | 138 | 04:00 | 123 | 13:00
Benapole | 140 | 02:00 | 122 | 13:00 | Mongla | 138 | 02:00 | 125 | 13:00
Bhaluka | 131 | 04:00 | 119 | 09:00 | Motijheel | 135 | 05:00 | 121 | 13:00
Bhandaria | 135 | 03:00 | 127 | 13:00 | Munshiganj | 134 | 03:00 | 124 | 12:00
Bhangura | 141 | 03:00 | 132 | 12:00 | Mymensingh | 129 | 03:00 | 112 | 13:00
Bheramara | 141 | 02:00 | 131 | 13:00 | Naogaon | 136 | 03:00 | 128 | 08:00
Bheramara(GK) | 140 | 05:00 | 132 | 13:00 | Narail | 141 | 02:00 | 125 | 13:00
Bhulta | 136 | 04:00 | 115 | 12:00 | Narinda | 134 | 01:00 | 122 | 12:00
Bog-Sherpur | 137 | 02:00 | 129 | 13:00 | Narshingdi | 130 | 00:00 | 115 | 19:00
Bogura | 137 | 02:00 | 130 | 09:00 | Natore | 139 | 04:00 | 129 | 12:00
Bogura-230 | 137 | 02:00 | 130 | 13:00 | Nawabganj | 137 | 01:00 | 125 | 13:00
Brahmanbaria | 133 | 06:00 | 121 | 11:00 | Netrakona | 127 | 00:00 | 112 | 12:00
Cantonment | 137 | 01:00 | 125 | 13:00 | New | 135 | 22:00 | 120 | 12:00
Chandpur | 130 | 18:30 | 118 | 11:00 | Niamatpur | 139 | 04:00 | 132 | 08:00
Chandraghona | 134 | 04:00 | 127 | 13:00 | Noapara | 139 | 01:00 | 125 | 13:00
Chapai | 137 | 05:00 | 132 | 11:00 | Pabna | 141 | 02:00 | 131 | 13:00
Charsaidpur | 136 | 03:00 | 123 | 13:00 | Palashbari | 134 | 02:00 | 124 | 13:00
Chauddagram | 132 | 02:00 | 119 | 13:00 | Panchagarh | 136 | 05:00 | 122 | 13:00
Chhatak | 134 | 01:00 | 130 | 21:00 | Patuakhali | 137 | 18:00 | 133 | 13:00
Chowmuhani | 127 | 18:30 | 114 | 12:00 | Payra | 138 | 05:00 | 13 | 19:30
Chuadanga | 141 | 02:00 | 126 | 13:00 | PHP | 131 | 04:00 | 117 | 13:00
Coxsbazar | 125 | 23:00 | 118 | 18:30 | Postogola | 138 | 01:00 | 130 | 12:00
Cumilla(N) | 136 | 04:00 | 123 | 12:00 | Purbachal | 138 | 03:00 | 122 | 13:00
Cumilla(S) | 132 | 00:00 | 121 | 13:00 | Purbasadipur | 131 | 02:00 | 119 | 08:00
Daudkandi | 133 | 02:00 | 120 | 13:00 | Rahanpur | 140 | 00:00 | 135 | 12:00
Dhaka | 137 | 03:00 | 124 | 13:00 | Rahanpur-400 | 140 | 01:00 | 136 | 09:00
Dhamrai | 136 | 04:00 | 124 | 12:00 | Rahim | 133 | 02:00 | 121 | 13:00
Dhanmondi | 137 | 03:00 | 123 | 13:00 | Rajbari | 137 | 01:00 | 128 | 13:00
Dohazari | 130 | 02:00 | 124 | 13:00 | Rajendrapur | 134 | 05:00 | 122 | 13:00
Faridpur | 136 | 03:00 | 130 | 11:00 | Rajshahi | 139 | 01:00 | 129 | 13:00
Fatullah | 138 | 04:00 | 127 | 12:00 | Rajshahi-230 | 140 | 04:00 | 127 | 08:00
Fenchuganj | 138 | 01:00 | 133 | 15:00 | Ramganj | 128 | 01:00 | 114 | 13:00
Feni | 129 | 04:00 | 121 | 13:00 | Rampur | 134 | 04:00 | 126 | 13:00
Ghatail | 127 | 06:00 | 117 | 13:00 | Rampura | 137 | 05:00 | 123 | 13:00
Ghorashal | 138 | 06:00 | 124 | 15:00 | Rangamati | 134 | 02:00 | 126 | 13:00
Goalpara | 141 | 02:00 | 14 | 05:00 | Rangpur | 133 | 04:00 | 122 | 08:00
Gollamari | 140 | 01:00 | 129 | 13:00 | Ruppur | 141 | 02:00 | 133 | 12:00
Gopalganj | 139 | 01:00 | 128 | 13:00 | Saidpur | 133 | 04:00 | 122 | 08:00
Gopalganj-400 | 138 | 00:00 | 129 | 13:00 | Satkhira | 139 | 01:00 | 125 | 13:00
Gulshan | 135 | 04:00 | 123 | 12:00 | Satmasjid | 137 | 01:00 | 124 | 13:00
Halishahar | 132 | 07:00 | 124 | 14:00 | Savar | 134 | 01:00 | 123 | 12:00
Haripur | 130 | 07:00 | 123 | 12:00 | SevenRings | 141 | 04:00 | 128 | 13:00
HaripurSBU | 134 | 04:00 | 123 | 12:00 | ShahCement | 136 | 03:00 | 123 | 13:00
Hasnabad | 138 | 01:00 | 129 | 12:00 | Shahjadpur | 142 | 00:00 | 135 | 12:00
Hathazari | 136 | 04:00 | 25 | 07:00 | Shahjibazar | 136 | 01:00 | 124 | 15:00
Ishurdi | 142 | 01:00 | 132 | 13:00 | Shahmirpur | 133 | 02:00 | 127 | 13:00
Jaldhaka | 132 | 03:00 | 120 | 08:00 | Shariatpur | 138 | 02:00 | 128 | 13:00
Jamalpur | 129 | 16:00 | 114 | 04:00 | Sherpur | 126 | 16:00 | 110 | 03:00
Jashore | 138 | 04:00 | 124 | 13:00 | Shikalbaha | 122 | 05:00 | 115 | 13:00
Jhenaidah | 140 | 00:00 | 24 | 06:00 | Shikalbaha-230 | 135 | 04:00 | 127 | 13:00
Jhenaidah-230 | 142 | 02:00 | 128 | 13:00 | Shitalakhya | 136 | 05:00 | 126 | 12:00
Joydebpur | 136 | 03:00 | 125 | 12:00 | Sholosohor | 134 | 01:00 | 128 | 12:00
Joypurhat | 136 | 02:00 | 126 | 13:00 | Shyampur | 137 | 05:00 | 128 | 11:00
Juldah | 133 | 04:00 | 125 | 13:00 | Shyampur-230 | 133 | 08:00 | 127 | 12:00
Kabirpur | 135 | 22:00 | 116 | 13:00 | Siddhirganj | 134 | 01:00 | 123 | 12:00
Kachua | 132 | 03:00 | 120 | 11:00 | Sirajganj | 138 | 00:00 | 130 | 13:00
Kaliakoir | 137 | 05:00 | 125 | 12:00 | Sonargaon | 128 | 00:00 | 122 | 07:00
Kallyanpur | 137 | 03:00 | 124 | 13:00 | Sreemongol | 136 | 04:00 | 127 | 13:00
Kalurghat | 134 | 02:00 | 127 | 13:00 | Sreepur | 130 | 02:00 | 121 | 12:00
Kamrangirchar | 137 | 01:00 | 123 | 13:00 | Srinagar | 138 | 02:00 | 126 | 12:00
Kaptai | N/A | N/A | N/A | N/A | SSM | 139 | 03:00 | 132 | 09:00
Kazla | 135 | 03:00 | 121 | 13:00 | Sunamganj | 132 | 01:00 | 129 | 12:00
Keranigonj | 137 | 03:00 | 126 | 12:00 | Sylhet | 135 | 03:00 | 131 | 13:00
Khagrachori | 134 | 03:00 | 125 | 13:00 | Sylhet-132 | 135 | 02:00 | 131 | 12:00
Khulna | 139 | 04:00 | 126 | 08:00 | Tangail | 127 | 06:00 | 118 | 13:00
Khulna(S) | 141 | 02:00 | 128 | 13:00 | Thakurgaon | 133 | 03:00 | 119 | 13:00
Khulshi | 131 | 03:00 | 124 | 13:00 | TK | 134 | 05:00 | 128 | 12:00
Kishoreganj | 132 | 00:00 | 119 | 13:00 | Tongi | 138 | 10:00 | 121 | 12:00
Kodda | 134 | 22:00 | 121 | 14:00 | Ullahpara | 140 | 01:00 | 132 | 10:00
KSRM | 134 | 04:00 | 128 | 11:00 | Ullon | 136 | 01:00 | 122 | 13:00
Kulaura | 138 | 04:00 | 132 | 13:00 | Uttara | 136 | 03:00 | 125 | 11:00
Zigatola | 140 | 02:00 | 130 | 13:00 | UttaraNew | 138 | 02:00 | 127 | 13:00
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7