## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: November 2024
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2024-11-01 |  | 2024-10-01 |  | 2023-11-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13253 | 2024-11-04 | 14677 | 2024-10-01 | 12608 | 2023-11-02 | 16477 | 2024-04-30
|  |  | 19:30 |  | 20:00 |  | 18:00 |  | 21:00
2 | Minimum Generation (MW) | 6915 | 2024-11-23 | 8574 | 2024-10-25 | 5719 | 2023-11-18 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13253 | 2024-11-04 | 15717 | 2024-09-19 | 12608 | 2023-11-02 | 16477 | 2024-04-30
|  |  | 19:30 |  | 21:00 |  | 18:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11963 | 2024-11-05 | 12738 | 2024-10-01 | 11209 | 2023-11-02 | 14488 | 2024-05-16
|  |  | 12:00 |  | 11:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 13253 | 2024-11-03 | 15200 | 2024-10-01 | 12650 | 2023-11-30 | 17200 | 2024-04-29
|  |  | 19:00 |  | 20:00 |  | 18:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11495.5667 |  | 13360.3226 |  | 11024.2667 |  | - | -
7 | Average Generation (MW) at Day Peak | 10157.8333 |  | 11846.0323 |  | 9678.8333 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 955 | 2024-11-15 | 931 | 2024-10-30 | 928 | 2023-11-12 | 970 | 2024-07-06
|  |  | 13:00 |  | 0:30 |  | 5:00 |  | 14:30
9 | Maximum Power Import from Tripura, India (MW) | 92 | 2024-10-19 | 92 | 2024-10-19 | 158 | 2023-11-02 | 194 | 12/06/19
|  |  | 13:00 |  | 13:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 343 | 2024-11-03 | 1301 | 2024-10-31 | 44 | 2023-11-01 | 4395 | 04/10/2022
|  |  | 19:00 |  | 21:00 |  | 19:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 13041 | 2024-11-03 | 12638 | 2024-10-31 | 12524 | 45231 | 14965 | 2024-05-16
|  |  | 19:00 |  | 21:00 | - | 0.79167 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2024-11-01 | 0 | 2024-10-04 | 0 | 45235 | - | -
|  |  | 19:00 |  | 21:00 |  | 19:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12302 | 2024-11-01 | 12218 | 2024-10-04 | 12197 | 2023-11-05 | - | -
|  |  | 19:00 |  | 21:00 |  | 19:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 647 | 2024-11-03 | 760 | 2024-10-02 | 324 | 45238 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 11422 | 2024-11-03 | 12704 | 2024-10-02 | 9911 | 45238 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2024-11-01 | 0 | 2024-10-04 | 0 | 45235 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 11199 | 2024-11-01 | 10526 | 2024-10-04 | 10908 | 45235 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 5 |  | 23 |  | 5 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 4 |  | 22 |  | 6 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1293.3147 |  | 1472.1777 |  | 1832.996 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 41.8445 |  | 58.8403 |  | 22.2246 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1251.4702 |  | 1413.3374 |  | 1810.7714 |  | - | -
23 | Net Generation of IPP (MKWH) | 2454.9734 |  | 2911.4144 |  | 2240.28 |  | - | -
23b | Net Generation by Generation Companies | 2098.615 |  | 2897.3002 |  | 1885.5707
24 | Net Generation of REB (MKWH) | 89.5936 |  | 93.2436 |  | 102.6847 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 78.2023 |  | 131.2355 |  | 101.6965 |  | - | -
25 | Total Net Generation (MKHWh) (Excluding Import) | 5972.8546 |  | 7446.531 |  | 6141.0033 |  | - | -
26 | Energy Generation by Gas (MKWH) | 3635.3513 |  | 3827.7099 |  | 3301.4949 |  | - | -
27 | Energy Generation by Diesel (MKWH) | 15.5319 |  | 21.0254 |  | 7.0767 |  | - | -
28 | Energy Generation by Furnace Oil (MKWH) | 693.3667 |  | 1145.4273 |  | 472.52 |  | - | -
29 | Energy Generation by Hydro (MKWH) | 83.5571 |  | 143.6604 |  | 81.581 |  | - | -
30 | Energy Generation by Solar (MKWH) | 108.5987 |  | 94.1464 |  | 70.8296 |  | - | -
30b | Energy Generation by Wind (MKWH) | 2.9731 |  | 4.2288 |  | 2.1667 |  | - | -
31 | Energy Generation by Coal (MKWH) | 1475.3202 |  | 2269.173 |  | 2227.5458 |  | - | -
32 | Enegry Import from India (MKWH) | 1144.5135 |  | 1444.8078 |  | 620.64 |  | - | -
33 | Monthly Load Factor (%) | 75.0272 |  | 81.9637 |  | 70.0491 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: November 2024
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13253 | 2024-11-04 | 19:30
Generation Period
| Dhaka | MW | 4932.54
| Chattogram | MW | 1216.5
| Cumilla | MW | 1266
| Mymensingh | MW | 983
| Sylhet | MW | 555
a) | Total supply in East zone | MW | 8953.04
| Khulna | MW | 1481.6
| Barisal | MW | 420.2
| Rajshahi | MW | 1173.8
| Rangpur | MW | 680
b) | Total supply in West zone | MW | 3755.6
c) | Total supply in both zone ( a+b) | MW | 12708.64
Ref: | 27.21.0000.603.16.087.20.885 | Date: 17/12/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:November 2024
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | -73 | 2024-11-16 | 8:00
| b) Ishurdi end | MW | 446 | 17/11/2024 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1138 | 2024-11-17 | 10:00
| b) Ishurdi end | MW | -130 | 2024-11-29 | 8:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0
| b) Ishurdi end | MKWH | 216.7118
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 213.4004
| b) Ishurdi end | MKWH | 0
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 300 | 2024-11-17 | 8:00
| b)Serajganj end | MW | 800 | 2024-11-14 | 14:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 480 | 2024-10-25 | 10:00
| b)Sirajganj end | MW | -254 | 2024-11-08 | 18:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0
| b)Sirajganj end | MKWH | 376.7022
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 389.158
| b)Sirajganj end | MKWH | 0
30 | Transmission loss of EWI /NO-2 | % | 3.20'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2418 | 2024-11-03 | 0:00
|  | MW | 1528
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2410 | 2024-11-03 | 0:00
|  | MW | 1527
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 31778 | 2024-11-03 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 31688 | 2024-11-03
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MKWH | 639.988
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MKWH | 637.569
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.378
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: November 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | ATR-01 LT | 2024-11-03 12:01 | 2024-11-03 18:07 | 6:06 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Bus A | 2024-11-07 09:11 | 2024-11-07 16:01 | 6:50 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Tongi 230/132kV Grid Sub-Station | T-1 HT | 2024-11-08 20:02 | 2024-11-08 22:04 | 2:02 | E/O | Due to Temperature high | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Bus Section- 01 & 3 | 2024-11-18 08:00 | 2024-11-18 10:12 | 2:12 | E/O | Due to Red hot in bus section of shakhipur feeder | 0 | 0 | No interruption
Mirzapur 132/33kV Grid Sub-Station | Transformer-01(E05) LT | 2024-11-18 15:13 | 2024-11-18 15:28 | 0:15 | T | Tripped showing Incommer-01 CB relays Due to PBS | 15 | 3.75 | Power interruption
Mirzapur 132/33kV Grid Sub-Station | Transformer-02(E07) LT | 2024-11-18 15:13 | 2024-11-18 15:28 | 0:15 | T | Tripped showing Incommer-01 CB relays Due to PBS | 16 | 4 | Power interruption
Mirzapur 132/33kV Grid Sub-Station | Transformer-02(E07) LT | 2024-11-18 16:26 | 2024-11-18 17:23 | 0:57 | E/O | Due to emergency maint.work at PBS | 17 | 16.15 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-01 HT | 2024-11-30 14:30 | 2024-11-30 16:25 | 1:55 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 20:32 |  | Unserved Energy: |  | 23.9
Dhaka (South) Grid Circle :
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-11-04 11:33 | 2024-11-04 12:07 | 0:34 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-11-06 00:11 | 2024-11-06 01:20 | 1:09 | T | Tripped showing Master Trip relay operated relays | 0 | 0 | No interruption
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2024-11-06 03:32 | 2024-11-06 03:46 | 0:14 | T | Tripped showing VAJ relays | 0 | 0 | No interruption
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2024-11-06 06:42 | 2024-11-06 07:08 | 0:26 | T | Tripped showing VAJ relays | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-11-07 06:43 | 2024-11-07 06:43 | 0:00 | T | Tripped showing 1. LBB protection operated( RED670) relays | 0 | 0 | No interruption
Keranigonj 230/132kV Grid Sub-Station | TR-2 LT | 2024-11-09 06:01 | 2024-11-09 06:13 | 0:12 | T | Due to 33kV feeder fault. | 14 | 2.8 | Power interruption
Hasnabad 132/33kV Grid Sub-Station | 424 T-5 LT | 2024-11-10 17:32 | 2024-11-10 18:54 | 1:22 | E/O | Due to 132kv CT sparking | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulsan-2 | 2024-11-13 15:56 | 2024-11-13 16:19 | 0:23 | T | Tripped showing (REL3168*4): 1). BFP Receive 2). DEF signal Receive3). | 0 | 0 | No interruption
Narsingdi 132/33kV Grid Sub-Station | T-1 LT | 2024-11-13 16:16 | 2024-11-13 17:12 | 0:56 | E/O | Due to 33 kv female finger change maintenance. | 50 | 46.6667 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-11-17 06:28 | 2024-11-17 06:52 | 0:24 | T | Tripped showing LBB initiation relays | 0 | 0 | No interruption
Keranigonj 230/132kV Grid Sub-Station | ATR-3 HT | 2024-11-19 00:31 | 2024-11-19 00:58 | 0:27 | T | Tripped showing PRV relay | 0 | 0 | No interruption
Keranigonj 230/132kV Grid Sub-Station | ATR-3 HT | 2024-11-19 10:27 | 2024-11-19 13:55 | 3:28 | T | Tripped showing PRV relay | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-11-19 11:32 | 2024-11-19 12:30 | 0:58 | E/O | Due to emergency maint.work at PBS | 40 | 38.6667 | Power interruption
Shyampur 132/33kV Grid Sub-Station | GT-3 HT | 2024-11-22 16:39 | 2024-11-22 18:05 | 1:26 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | GT-2 HT | 2024-11-24 10:11 | 2024-11-24 10:11 | 0:00 | T | Tripped showing Backup protection Realy at 33 kV | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | 33kv Main Bus | 2024-11-25 13:03 | 2024-11-25 13:03 | 0:00 | E/O | Due to T5 Main Bus Y phase temperature high. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-11-28 11:15 | 2024-11-28 13:26 | 2:11 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | GT-2 LT | 2024-11-30 13:35 | 2024-11-30 23:37 | 10:02 | E/O | Due to emergency maint.work at 33 | 0 | 0 | No interruption
|  |  | Total : | 24:12 |  | Unserved Energy: |  | 88.1333
Chattogram Grid Circle :
TK chemical 132/33kV Grid Sub-Station | 48/64MVA T-2(415T) HT | 2024-11-13 10:50 | 2024-11-13 13:22 | 2:32 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
BSRM 230/132kV Grid Sub-Station | Transformer-2 (125/140 MVA) HT | 2024-11-16 11:38 | 2024-11-16 14:00 | 2:22 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 4:54 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-02 06:24 | 2024-11-02 14:26 | 8:02 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-03 14:52 | 2024-11-03 15:05 | 0:13 | T | Tripped showing Ret 650 relays Due to Tr-2 trip by Tr-1 over over load | 20 | 4.3333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-03 14:52 | 2024-11-03 15:09 | 0:17 | T | Tripped showing RET-650 relays Due to PRD trip | 20 | 5.6667 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3 | 2024-11-11 14:53 | 2024-11-11 16:10 | 1:17 | E/O | Due to 132 kv side loop (Y) injured . | 0 | 0 | No interruption
Sreemongal 132/33kV Grid Sub-Station | T-3 LT | 2024-11-16 19:31 | 2024-11-17 09:12 | 13:41 | E/O | Due to Emergency maintenance work. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T HT | 2024-11-18 07:07 | 2024-11-18 10:31 | 3:24 | E/O | Due to Emergency maintenance work. | 35 | 119 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-2 LT | 2024-11-18 22:30 | 2024-11-18 23:32 | 1:02 | E/O | Due to Red Hot maintenance | 7 | 7.2333 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-2 HT | 2024-11-18 22:31 | 2024-11-18 23:32 | 1:01 | E/O | Due to Red Hot maintenance | 7 | 7.1167 | Power interruption
Sreemongal 132/33kV Grid Sub-Station | T-3 LT | 2024-11-19 14:42 | 2024-11-19 15:36 | 0:54 | E/O | Due to 33 KV CB sf6 gas refile works. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2024-11-29 03:20 | 2024-11-29 04:08 | 0:48 | T | Tripped showing Siemens relay Due to 33KV feeder Earth fault . | 0 | 0 | No interruption
|  |  | Total : | 30:39 |  | Unserved Energy: |  | 143.35
Khulna Grid Circle :
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 08:51 | 1:18 | E/O | Due to emergency maint.work | 40 | 52 | Power interruption
Madaripur 230/132kV Grid Sub-Station | Aux Tr-01 HT | 2024-11-07 09:27 | 2024-11-07 09:27 | 0:00 | E/O | Due to DFDR & Commissioning work. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 HT | 2024-11-09 00:22 | 2024-11-09 21:52 | 21:30 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Barguna132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-09 08:01 | 2024-11-09 19:21 | 11:20 | T | Due to 33 kV feeder fault | 10 | 25.83 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2024-11-14 13:13 | 2024-11-14 13:41 | 0:28 | T | Tripped showing PRD signal relays Due to PRD signal | 59 | 27.5333 | Power interruption
Khulna(C) 230/ 132/33kV Grid Sub-Station | Tr-3 405T LT | 2024-11-17 10:54 | 2024-11-17 12:35 | 1:41 | E/O | Due to emergency maint.work at PBS | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2024-11-22 11:55 | 2024-11-22 14:47 | 2:52 | E/O | Due to emergency maint.work at PBS | 6 | 17.2 | Power interruption
Khulna(C) 230/ 132/33kV Grid Sub-Station | Tr-2 415 T LT | 2024-11-26 11:38 | 2024-11-26 14:11 | 2:33 | E/O | Due to Due to WZDCL Bus DS Maintenance. | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2024-11-30 00:38 | 2024-11-30 01:18 | 0:40 | T | Tripped showing 50/51 OC/EF relays | 5 | 3.3333 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-2 (415T) LT | 2024-11-30 08:51 | 2024-11-30 09:02 | 0:11 | T | Tripped showing Inst.E/F, inst. O/C relays Due to WZPDCL | 27 | 4.95 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) HT | 2024-11-30 12:30 | 2024-11-30 12:51 | 0:21 | E/O | Due to emergency maint.work | 20 | 7 | Power interruption
|  |  | Total : | 42:54 |  | Unserved Energy: |  | 137.8467
HVDC Grid Circle :
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-11-02 10:44 | 2024-11-02 11:46 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 230/132 Grid Sub-Station | T-2 LT | 2024-11-03 19:56 | 2024-11-03 20:25 | 0:29 | T | Tripped showing SIEMENS SIPROTEC 7UT86 relays Due to Green city fault | 30 | 14.5 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2024-11-05 18:10 | 2024-11-05 18:10 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) LT | 2024-11-19 11:59 | 2024-11-19 13:01 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
BIPTC | 10CF14 | 2024-11-19 14:40 | 2024-11-19 14:40 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
BIPTC | 10CF25 | 2024-11-22 08:21 | 2024-11-22 08:42 | 0:21 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | T-2 HT | 2024-11-28 21:23 | 2024-11-28 22:25 | 1:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 3:56 |  | Unserved Energy: |  | 14.5
Bogura Grid Circle:
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-13 15:45 | 2024-11-13 15:45 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Niamatpur132/33kV Grid Sub-Station | Transformer-2 (417T) LT | 2024-11-17 05:06 | 2024-11-17 05:26 | 0:20 | T | Tripped showing Over current /earth fault. Lockout Optd. | 20 | 6.6667 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2024-11-19 14:58 | 2024-11-19 15:16 | 0:18 | T | Due to 33kv feeder fault | 15 | 4.5 | Power interruption
Naogaon 132/11kV Grid Sub-Station | T-3 LT | 2024-11-28 11:08 | 2024-11-28 12:40 | 1:32 | E/O | Due to Oil leakage maintenance. | 0 | 0 | No interruption
|  |  | Total : | 3:57 |  | Unserved Energy: |  | 11.1667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 131:04 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: November 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirpur 132/33kV Grid Sub-Station | Uttara 3PH 132kV Ckt-1 | 2024-11-03 12:14 | 2024-11-03 12:17 | 0:03 | T | Tripped showing Differential, & Main Protection relay | 66 | 3.3 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-2 | 2024-11-06 02:00 | 2024-11-06 02:00 | 0:00 | T | Tripped showing Distance relay. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-1 | 2024-11-09 11:37 | 2024-11-09 12:31 | 0:54 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Dhamrai- 132/33kV Grid Sub-Station | Kaliakoir 132 kV Ckt-1 | 2024-11-16 08:33 | 2024-11-16 14:50 | 6:17 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Joydevpur 132/33kV Grid Sub-Station | Kodda B 132 kV Ckt-1 | 2024-11-22 09:22 | 2024-11-22 10:17 | 0:55 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Joydevpur 132/33kV Grid Sub-Station | Kodda B 132 kV Ckt-2 | 2024-11-22 09:24 | 2024-11-22 09:24 | 0:00 | T | Tripped showing Distance relay. | 0 | 0 | No interruption
Joydevpur 132/33kV Grid Sub-Station | Kodda B 132 kV Ckt-1 | 2024-11-22 10:28 | 2024-11-22 10:28 | 0:00 | T | Tripped showing Distance relay. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh 132 kV Ckt-2 | 2024-11-24 11:41 | 2024-11-24 11:51 | 0:10 | T | Tripped showing 67 DIR relays. | 68 | 11.3333 | Power interruption
|  |  | Total : | 8:19 |  | Unserved Energy: |  | 14.6333
Dhaka (South) Grid Circle :
Haripur 230/132kV Grid Sub-Station | Narsingdi 132kV Ckt-1 | 2024-11-01 13:05 | 2024-11-01 13:14 | 0:09 | T | Tripped showing 1.Generale Trip, 2.Zone 1 Trip,3.relay | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | Rampur 132kV Ckt-2 | 2024-11-02 19:56 | 2024-11-02 20:26 | 0:30 | T | Tripped showing REC 316*4 ,REL 316*4 relays | 52 | 26 | Power interruption
Gulshan 132/33kV Grid Sub-Station | Rampur 132kV Ckt-2 | 2024-11-02 22:13 | 2024-11-02 22:21 | 0:08 | T | Tripped showing REC 316*4 ,REL 316*4 relays | 44 | 5.8667 | Power interruption
keraniganj 230/132kV Grid Sub-Station | Hasnabad Ckt. 1 | 2024-11-03 10:57 | 2024-11-03 12:45 | 1:48 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Ullon-2 | 2024-11-04 07:56 | 2024-11-04 09:07 | 1:11 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Ullon-1 | 2024-11-04 07:56 | 2024-11-04 09:22 | 1:26 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Ullon-2 | 2024-11-04 09:08 | 2024-11-04 15:19 | 6:11 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Haripur 230/132/33kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-11-06 00:10 | 2024-11-06 01:00 | 0:50 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Ullon (T at Maniknagar) 132kV Ckt-1 | 2024-11-06 00:11 | 2024-11-06 00:11 | 0:00 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Summit 55 MW 132 kv Ckt | 2024-11-06 01:39 | 2024-11-06 03:04 | 1:25 | T | Tripped showing DIR O/C & E/F | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Fatulla (Pre-Brahmongaon) | 2024-11-06 01:41 | 2024-11-06 01:41 | 0:00 | T | Tripped showing Main protection relay | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Sub-Station | Sitalakhya 132kV Ckt-1 | 2024-11-06 01:41 | 2024-11-06 01:56 | 0:15 | T | Tripped showing Main protection relay | 64 | 16 | Power interruption
Hasnabad 132/33kV Grid Sub-Station | Hasnabad -APR P/S | 2024-11-06 07:30 | 2024-11-06 07:30 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Matuail-1 | 2024-11-08 06:43 | 2024-11-08 07:03 | 0:20 | E/O | Due to Y-phase isolator's loop got snapped | 54 | 18 | Power interruption
Hasnabad 132/33kV Grid Sub-Station | Sitalakhya 132kV Ckt-1 | 2024-11-09 07:41 | 2024-11-09 08:32 | 0:51 | T | Tripped showing Main protection relay | 55 | 46.75 | Power interruption
Madanganj 132/33kV Grid Sub-Station | Shitalakhya 132 kv Ckt | 2024-11-09 09:55 | 2024-11-09 09:55 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Haripur 230/132/33kV Grid Sub-Station | Sonargaon 132kV Ckt-1 | 2024-11-10 06:58 | 2024-11-10 06:58 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Haripur 230/132/33kV Grid Sub-Station | Sonargaon 132kV Ckt-2 | 2024-11-10 06:59 | 2024-11-10 06:59 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Matuail 132/33kV Grid Sub-Station | Siddhirganj 132kV Ckt-1 | 2024-11-17 06:28 | 2024-11-17 09:17 | 2:49 | T | Tripped showing Zone-2, Y-phase,6.1 km relays | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Bashundhara 132 kv Ckt | 2024-11-18 10:08 | 2024-11-18 16:28 | 6:20 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Siddhirganj- 132/33kV Grid Sub-Station | Ullon (T at Maniknagar) 132kV Ckt-1 | 2024-11-19 10:16 | 2024-11-19 20:12 | 9:56 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Shitalakhya 132 kv Ckt | 2024-11-22 12:10 | 2024-11-22 12:10 | 0:00 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | Shyampur(New) 132 kV Ckt-1 | 2024-11-23 12:01 | 2024-11-23 13:48 | 1:47 | T | Tripped showing Distance relay | 0 | 0 | No interruption
|  |  | Total : | 35:56 |  | Unserved Energy: |  | 112.6167
Chattogram Grid Circle :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj 230/132kV Grid Sub-Station | Cumilla(N) 230 kV Ckt-2 | 2024-11-13 06:02 | 2024-11-13 06:02 | 0:00 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18 | 0:12 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Kishoreganj 132kV Ckt-2 | 2024-11-24 11:41 | 2024-11-24 11:59 | 0:18 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sreemangal 132kV Ckt-1 | 2024-11-29 13:18 | 2024-11-29 18:13 | 4:55 | T | Tripped showing Distance relay | 0 | 0 | No interruption
|  |  | Total : | 5:25 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Gopalganj 400/230/132 kV Grid Sub-Station | Faridpur-2 | 2024-11-12 12:48 | 2024-11-12 18:00 | 5:12 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Gopalganj 400/230/132 kV Grid Sub-Station | Faridpur-2 | 2024-11-12 13:48 | 2024-11-12 18:01 | 4:13 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | (Barguna T at Bakergonj) 132 kV Ckt | 2024-11-17 06:18 | 2024-11-17 06:18 | 0:00 | T | Tripped showing dist-3phase,Dist 1.5 km.o/c relays | 0 | 0 | No interruption
Rampal 400/230/132 kV Grid Sub-Station | Gopalganj Line-1 | 2024-11-20 10:27 | 2024-11-20 22:21 | 11:54 | E/O | Due to low voltage & high reactive power | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kv Summit power | 2024-11-21 10:46 | 2024-11-21 15:52 | 5:06 | E/O | Due to PT blust | 0 | 0 | No interruption
Rampal 132/33kV Grid Sub-Station | Gopalganj Line-2 | 2024-11-21 15:52 | 2024-11-21 22:22 | 6:30 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
|  |  | Total : | 32:55 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Baghabari 230/132kV Grid Sub-Station | Sirajganj 230 kV Ckt-2 | 2024-11-18 10:59 | 2024-11-18 16:33 | 5:34 | E/O | Tripped showing Distance relay. | 0 | 0 | No interruption
|  |  | Total : | 5:34 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Natore 132/33kV Grid Sub-Station | Rajshahi 132kV Ckt-2 | 2024-11-02 03:04 | 2024-11-02 03:40 | 0:36 | T | Tripped showing Distance relay. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 2024-11-03 10:25 | 2024-11-03 14:47 | 4:22 | E/O | Due to emergency maintenance work | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | Bogura 230 kV Ckt-1 | 2024-11-14 12:54 | 2024-11-14 13:29 | 0:35 | T | Tripped showing AR Blocked,Permit Close relays. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | Bogura 230 kV Ckt-2 | 2024-11-14 12:58 | 2024-11-14 13:28 | 0:30 | T | Tripped showing AR Blocked,Permit Close relays. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | Bogura 230 kV Ckt-1 | 2024-11-14 13:45 | 2024-11-14 16:32 | 2:47 | T | Tripped showing AR Bloked,VT circuit failed relays. | 0 | 0 | No interruption
|  |  | Total : | 8:50 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 96:59 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: November 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2024-11-01 09:04 | 2024-11-01 10:20 | 1:16 | S/O | Maintenance work | 25 | 31.6667 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2024-11-02 07:38 | 2024-11-02 10:59 | 3:21 | S/O | Maintenance work | 20 | 67 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2024-11-02 07:40 | 2024-11-02 10:58 | 3:18 | S/O | Maintenance work | 42 | 138.6 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2024-11-03 08:08 | 2024-11-03 09:44 | 1:36 | S/O | Due to Red-hot Maintenance of 33kV feeder | 10 | 16 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-11-03 09:15 | 2024-11-03 12:40 | 3:25 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Bus A | 2024-11-03 09:17 | 2024-11-03 16:10 | 6:53 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2024-11-03 09:46 | 2024-11-03 10:47 | 1:01 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2024-11-03 09:47 | 2024-11-03 10:47 | 1:00 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Bus-A | 2024-11-03 09:53 | 2024-11-03 14:46 | 4:53 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Tansformer- 02 HT | 2024-11-03 12:42 | 2024-11-03 16:16 | 3:34 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Bus A | 2024-11-04 09:19 | 2024-11-04 16:05 | 6:46 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 HT | 2024-11-04 09:21 | 2024-11-04 12:10 | 2:49 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2024-11-04 09:22 | 2024-11-04 17:16 | 7:54 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Bus A | 2024-11-04 09:52 | 2024-11-04 15:59 | 6:07 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2024-11-04 12:18 | 2024-11-04 16:02 | 3:44 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 LT | 2024-11-04 15:17 | 2024-11-04 18:04 | 2:47 | S/O | Due to Annual Maintenance | 75 | 208.75 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-11-04 15:18 | 2024-11-04 15:40 | 0:22 | S/O | Due to Annual Maintenance | 35 | 12.8333 | Power interruption
Jamalpur United | Sherpur 132kV Ckt-1 | 2024-11-05 08:41 | 2024-11-05 11:56 | 3:15 | S/O | Due to C.T Tan-Delta Test | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Bus A | 2024-11-05 09:04 | 2024-11-05 16:32 | 7:28 | S/O | Due to Annual Maintenance | 35 | 261.3333 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Capacitor Bank- 02 | 2024-11-06 07:20 | 2024-11-06 09:13 | 1:53 | S/O | Due to Red-hot Maintenance of 33kV feeder | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-11-06 07:26 | 2024-11-06 08:51 | 1:25 | S/O | Due to Red-hot Maintenance of 33kV feeder | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Bus Section- 02 | 2024-11-06 07:37 | 2024-11-06 08:45 | 1:08 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2024-11-06 08:45 | 2024-11-06 16:52 | 8:07 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Bus-A | 2024-11-06 10:55 | 2024-11-07 17:40 | 30:45 | S/O | Due to 132kv bus coupler C.T tan Delta test purpose. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2024-11-06 16:54 | 2024-11-06 17:40 | 0:46 | S/O | Due to CT Tan delta Test work by RTS | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-11-07 08:49 | 2024-11-07 15:41 | 6:52 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2024-11-07 10:10 | 2024-11-07 17:48 | 7:38 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-11-07 10:20 | 2024-11-07 16:00 | 5:40 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Bus B | 2024-11-07 10:20 | 2024-11-07 10:56 | 0:36 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Bus A | 2024-11-07 11:10 | 2024-11-07 17:02 | 5:52 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-1 LT | 2024-11-08 15:27 | 2024-11-08 15:57 | 0:30 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 1 | 2024-11-10 08:08 | 2024-11-10 17:22 | 9:14 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Joydebpur132/33kV Grid Sub-Station | GT-3 LT | 2024-11-10 09:11 | 2024-11-10 16:28 | 7:17 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-1 HT | 2024-11-10 09:14 | 2024-11-10 15:24 | 6:10 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Netrakona 132/33kV Grid Sub-Station | Transformer-1 (415T) HT | 2024-11-10 09:44 | 2024-11-10 16:04 | 6:20 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 1 | 2024-11-11 08:10 | 2024-11-11 08:10 | 0:00 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2024-11-11 09:10 | 2024-11-11 12:18 | 3:08 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Bus B | 2024-11-11 09:17 | 2024-11-11 16:45 | 7:28 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Netrakona 132/33kV Grid Sub-Station | Transformer-1 (415T) HT | 2024-11-11 09:20 | 2024-11-11 17:05 | 7:45 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Tr-02 LT | 2024-11-11 10:37 | 2024-11-11 16:37 | 6:00 | S/O | Maintenance work by Pbs | 25 | 150 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 2 | 2024-11-12 08:11 | 2024-11-12 16:46 | 8:35 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 LT | 2024-11-12 08:25 | 2024-11-12 10:19 | 1:54 | S/O | Due to Tan-delta test by RTS. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2024-11-12 08:34 | 2024-11-12 15:30 | 6:56 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Tr-02 LT | 2024-11-12 08:39 | 2024-11-12 16:04 | 7:25 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2024-11-12 08:41 | 2024-11-12 08:41 | 0:00 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-11-12 08:59 | 2024-11-12 16:36 | 7:37 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Tr-02 HT | 2024-11-12 08:59 | 2024-11-12 16:02 | 7:03 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-11-12 09:12 | 2024-11-12 16:28 | 7:16 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-4 HT | 2024-11-12 10:26 | 2024-11-12 15:51 | 5:25 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Tongi (new) 230/132/33kV Grid Sub-Station | T2(413T) LT | 2024-11-12 16:06 | 2024-11-12 16:06 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 HT | 2024-11-13 08:31 | 2024-11-13 15:06 | 6:35 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 2 | 2024-11-13 08:33 | 2024-11-13 08:33 | 0:00 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-11-13 08:52 | 2024-11-13 17:11 | 8:19 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Bus A | 2024-11-13 09:38 | 2024-11-13 17:29 | 7:51 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Kallyanpur132/33kV Grid Sub-Station | GT-2 (132kV) LT | 2024-11-13 10:04 | 2024-11-13 17:12 | 7:08 | S/O | Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Tr-03 LT | 2024-11-13 10:05 | 2024-11-13 16:28 | 6:23 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Tr-03 HT | 2024-11-14 08:19 | 2024-11-14 15:21 | 7:02 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-2 LT | 2024-11-14 08:23 | 2024-11-14 13:36 | 5:13 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-11-14 08:30 | 2024-11-14 15:31 | 7:01 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-11-14 09:07 | 2024-11-14 15:57 | 6:50 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kallyanpur132/33kV Grid Sub-Station | GT-1 (132kV) LT | 2024-11-14 09:33 | 2024-11-14 16:57 | 7:24 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kallyanpur132/33kV Grid Sub-Station | GT-3 (132kV) LT | 2024-11-14 09:33 | 2024-11-14 16:55 | 7:22 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-3 HT | 2024-11-14 13:39 | 2024-11-14 17:54 | 4:15 | S/O | Due to MTR-03 Tan-Delta test by RTS. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-11-16 08:35 | 2024-11-16 14:45 | 6:10 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Tr-03 LT | 2024-11-16 10:33 | 2024-11-16 14:04 | 3:31 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-11-16 10:47 | 2024-11-16 14:02 | 3:15 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-11-16 10:58 | 2024-11-16 16:20 | 5:22 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Lalbagh 132/33kV Grid Sub-Station | Tr-Load HT | 2024-11-16 15:53 | 2024-11-16 15:53 | 0:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-11-17 09:15 | 2024-11-17 16:44 | 7:29 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 LT | 2024-11-17 09:19 | 2024-11-17 15:02 | 5:43 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Gatail 132/33kV Grid Sub-Station | T-1 HT | 2024-11-18 08:31 | 2024-11-18 13:08 | 4:37 | S/O | Due to Mainteance work by 33 kV feeder | 25 | 115.4167 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-11-18 09:19 | 2024-11-18 09:19 | 0:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 230kV Bus 1 | 2024-11-19 08:13 | 2024-11-19 16:13 | 8:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 2024-11-19 08:35 | 2024-11-19 15:25 | 6:50 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | Auxiliary Tr-1 HT | 2024-11-19 09:21 | 2024-11-19 16:05 | 6:44 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Transfer Bus | 2024-11-20 08:45 | 2024-11-20 17:05 | 8:20 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 LT | 2024-11-20 09:21 | 2024-11-20 15:50 | 6:29 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 LT | 2024-11-20 09:35 | 2024-11-20 15:39 | 6:04 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Bus-1 | 2024-11-22 08:40 | 2024-11-22 21:30 | 12:50 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) HT | 2024-11-22 08:49 | 2024-11-22 09:57 | 1:08 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) HT | 2024-11-22 15:17 | 2024-11-22 15:55 | 0:38 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2024-11-22 15:59 | 2024-11-22 16:44 | 0:45 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-3 (50/75 MVA) LT | 2024-11-23 08:14 | 2024-11-23 17:14 | 9:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-3 LT | 2024-11-23 08:35 | 2024-11-23 20:55 | 12:20 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Capacitor Bank-2 | 2024-11-23 09:07 | 2024-11-23 13:35 | 4:28 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2024-11-23 09:22 | 2024-11-23 16:18 | 6:56 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2024-11-23 09:37 | 2024-11-23 16:23 | 6:46 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 HT | 2024-11-23 11:13 | 2024-11-23 14:03 | 2:50 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-11-23 11:30 | 2024-11-23 14:07 | 2:37 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-3 (50/75 MVA) HT | 2024-11-24 08:14 | 2024-11-24 16:28 | 8:14 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-11-24 08:47 | 2024-11-24 13:22 | 4:35 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Capacitor Bank-2 | 2024-11-24 08:56 | 2024-11-24 14:38 | 5:42 | S/O | Due to Capacitor Bank-1 Cell Change Work. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Capacitor Bank-3 | 2024-11-24 08:57 | 2024-11-24 14:38 | 5:41 | S/O | Due to Capacitor Bank-1 Cell Change Work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2024-11-24 09:27 | 2024-11-24 16:14 | 6:47 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2024-11-24 09:30 | 2024-11-24 15:49 | 6:19 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-11-24 13:24 | 2024-11-24 16:14 | 2:50 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-3 (50/75 MVA) LT | 2024-11-24 08:14 | 2024-11-24 16:28 | 8:14 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-11-24 08:47 | 2024-11-24 13:23 | 4:36 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2024-11-24 09:27 | 2024-11-24 16:14 | 6:47 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-4 (50/75 MVA) LT | 2024-11-25 08:42 | 2024-11-25 17:00 | 8:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 LT | 2024-11-25 09:06 | 2024-11-25 16:13 | 7:07 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2024-11-25 09:55 | 2024-11-25 13:08 | 3:13 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 LT | 2024-11-25 10:25 | 2024-11-25 16:53 | 6:28 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 LT | 2024-11-26 08:14 | 2024-11-26 09:52 | 1:38 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-4 (50/75 MVA) LT | 2024-11-26 08:25 | 2024-11-26 17:00 | 8:35 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Bus2 | 2024-11-26 08:55 | 2024-11-26 15:23 | 6:28 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2024-11-26 09:04 | 2024-11-26 15:16 | 6:12 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 LT | 2024-11-26 09:11 | 2024-11-26 16:52 | 7:41 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Capacitor Bank-3 | 2024-11-26 09:14 | 2024-11-26 13:21 | 4:07 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-01 LT | 2024-11-26 11:05 | 2024-11-26 17:02 | 5:57 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | 230 kV Bus-1 | 2024-11-27 08:29 | 2024-11-27 16:24 | 7:55 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) LT | 2024-11-27 08:40 | 2024-11-27 17:47 | 9:07 | S/O | Due to For DPDC | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-4 (50/75 MVA) HT | 2024-11-27 08:45 | 2024-11-27 16:30 | 7:45 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2024-11-27 08:59 | 2024-11-27 14:20 | 5:21 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Capacitor Bank-3 | 2024-11-27 09:10 | 2024-11-27 15:22 | 6:12 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Capacitor Bank-1 & 2 | 2024-11-27 09:10 | 2024-11-27 15:22 | 6:12 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2024-11-27 09:48 | 2024-11-27 09:48 | 0:00 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-01 HT | 2024-11-27 10:55 | 2024-11-27 15:50 | 4:55 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-11-27 11:20 | 2024-11-27 13:39 | 2:19 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-11-27 13:56 | 2024-11-27 15:16 | 1:20 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-4 (50/75 MVA) HT | 2024-11-28 08:34 | 2024-11-28 16:54 | 8:20 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Sreepur 132/33kV Grid Sub-Station | 230 kV Bus-1 | 2024-11-28 08:59 | 2024-11-28 14:05 | 5:06 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-01 HT | 2024-11-28 09:00 | 2024-11-28 13:21 | 4:21 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Capacitor Bank-1 | 2024-11-28 09:09 | 2024-11-28 12:25 | 3:16 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Capacitor Bank-3 | 2024-11-28 09:09 | 2024-11-28 12:25 | 3:16 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2024-11-28 09:43 | 2024-11-28 16:46 | 7:03 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Tongi (new) 230/132/33kV Grid Sub-Station | T-1 LT | 2024-11-28 10:56 | 2024-11-28 21:45 | 10:49 | S/O | Due to Relay testing work by SPMD-2 | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Bus-2 | 2024-11-29 07:13 | 2024-11-29 07:13 | 0:00 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) HT | 2024-11-29 11:32 | 2024-11-29 11:32 | 0:00 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Transformer GT-3 (50/75 MVA) LT | 2024-11-30 09:06 | 2024-11-30 15:14 | 6:08 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2024-11-30 09:29 | 2024-11-30 16:31 | 7:02 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | 230 kV BUS-2 | 2024-11-30 10:17 | 2024-11-30 16:08 | 5:51 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2024-11-30 10:48 | 2024-11-30 13:32 | 2:44 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) HT | 2024-11-30 11:07 | 2024-11-30 14:36 | 3:29 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
|  |  | Total : | 712:29 |  | Unserved Energy: |  | 1001.6
Dhaka (South) Grid Circle :
Hasnadad 132/33kV Grid Sub-Station | 424 T-5 HT | 2024-11-03 06:40 | 2024-11-03 17:11 | 10:31 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Hasnadad 132/33kV Grid Sub-Station | 424 T-5 LT | 2024-11-04 08:02 | 2024-11-04 18:56 | 10:54 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | GT-1 HT | 2024-11-04 09:15 | 2024-11-04 17:09 | 7:54 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-1 LT | 2024-11-05 08:48 | 2024-11-05 16:35 | 7:47 | S/O | Due to Oil Centrifuse | 0 | 0 | No interruption
Shyampur 132/33kV Grid Sub-Station | GT-2 HT | 2024-11-05 09:13 | 2024-11-05 17:28 | 8:15 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Hasnadad 132/33kV Grid Sub-Station | 424 T-5 HT | 2024-11-05 10:02 | 2024-11-05 13:10 | 3:08 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Nawabgnaj 132/33kV Grid Sub-Station | TR-1 HT | 2024-11-06 07:34 | 2024-11-06 16:22 | 8:48 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Nawabgnaj 132/33kV Grid Sub-Station | TR-1 HT | 2024-11-07 07:08 | 2024-11-07 07:08 | 0:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 LT | 2024-11-07 08:08 | 2024-11-07 17:30 | 9:22 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 LT | 2024-11-08 07:52 | 2024-11-08 18:32 | 10:40 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2024-11-09 03:21 | 2024-11-09 08:21 | 5:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 2024-11-09 03:22 | 2024-11-09 08:21 | 4:59 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Hasnadad 132/33kV Grid Sub-Station | 404 T-1 HT | 2024-11-09 07:29 | 2024-11-09 15:41 | 8:12 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | LV AC-1 | 2024-11-09 07:35 | 2024-11-09 17:18 | 9:43 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Aux TR-1 HT | 2024-11-09 07:36 | 2024-11-09 07:36 | 0:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 HT | 2024-11-09 07:37 | 2024-11-09 17:15 | 9:38 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-1 | 2024-11-09 09:00 | 2024-11-09 12:25 | 3:25 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Hasnadad 132/33kV Grid Sub-Station | 404 T-1 LT | 2024-11-10 07:24 | 2024-11-10 17:15 | 9:51 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Tr-02 LT | 2024-11-11 07:47 | 2024-11-11 18:05 | 10:18 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 2024-11-11 15:52 | 2024-11-11 17:16 | 1:24 | S/O | Project Work | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Tr-02 HT | 2024-11-12 08:01 | 2024-11-12 17:00 | 8:59 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Hasnadad 132/33kV Grid Sub-Station | AUTO TR-2 LT | 2024-11-12 08:25 | 2024-11-12 17:24 | 8:59 | S/O | Due to oil filling work. | 0 | 0 | No interruption
Shyampur 132/33kV Grid Sub-Station | GT-4 HT | 2024-11-12 09:13 | 2024-11-12 17:50 | 8:37 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Hasnadad 132/33kV Grid Sub-Station | 414 T-2 LT | 2024-11-13 07:41 | 2024-11-13 17:28 | 9:47 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Hasnadad 132/33kV Grid Sub-Station | 424 T-5 LT | 2024-11-14 08:20 | 2024-11-14 08:20 | 0:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 2024-11-14 10:31 | 2024-11-14 13:06 | 2:35 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Aux TR-2 LT | 2024-11-15 07:44 | 2024-11-15 16:59 | 9:15 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Hasnadad 132/33kV Grid Sub-Station | 414 T-2 HT | 2024-11-15 08:15 | 2024-11-15 12:44 | 4:29 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-2 LT | 2024-11-15 08:16 | 2024-11-15 10:51 | 2:35 | S/O | Due to T-2 33 KV CT Oil leakage maintenance | 40 | 103.3333 | Power interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2024-11-15 08:23 | 2024-11-15 08:23 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 LT | 2024-11-16 00:39 | 2024-11-16 14:37 | 13:58 | S/O | Due to DS Mainteance | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-2 HT | 2024-11-16 07:15 | 2024-11-16 13:06 | 5:51 | S/O | Due to T-2, Incomer CT oil leakage. | 25 | 146.25 | Power interruption
Nawabgnaj 132/33kV Grid Sub-Station | TR-2 LT | 2024-11-16 08:05 | 2024-11-16 17:08 | 9:03 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Nawabgnaj 132/33kV Grid Sub-Station | TR-2 LT | 2024-11-17 07:30 | 2024-11-17 15:47 | 8:17 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS A | 2024-11-18 08:59 | 2024-11-18 16:28 | 7:29 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | ATR-01 HT | 2024-11-18 09:38 | 2024-11-18 16:55 | 7:17 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | ATR-01 HT | 2024-11-19 09:12 | 2024-11-19 17:48 | 8:36 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS B | 2024-11-19 09:40 | 2024-11-19 14:45 | 5:05 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-11-19 15:30 | 2024-11-19 16:41 | 1:11 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Nawabgnaj 132/33kV Grid Sub-Station | Main Bus-2 | 2024-11-20 12:41 | 2024-11-20 15:08 | 2:27 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 230kV BUS A | 2024-11-20 09:16 | 2024-11-20 14:18 | 5:02 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | ATR-02 HT | 2024-11-21 08:48 | 2024-11-21 16:13 | 7:25 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2024-11-22 09:04 | 2024-11-22 12:11 | 3:07 | S/O | Due to Mainteance work | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | ATR-02 HT | 2024-11-23 09:42 | 2024-11-23 16:14 | 6:32 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Keranigonj 230/132kV Grid Sub-Station | ATR-1 LT | 2024-11-25 07:44 | 2024-11-25 15:46 | 8:02 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | ATR-02 LT | 2024-11-25 08:23 | 2024-11-25 16:16 | 7:53 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Capacitor Bank- 1 | 2024-11-26 09:30 | 2024-11-26 09:30 | 0:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-11-26 08:50 | 2024-11-26 16:36 | 7:46 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | ATR-02 (714T) LT | 2024-11-27 08:25 | 2024-11-27 17:16 | 8:51 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Bus1 | 2024-11-27 08:46 | 2024-11-27 15:13 | 6:27 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | 230kV Bus-01 | 2024-11-27 09:02 | 2024-11-27 16:27 | 7:25 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Keranigonj 230/132kV Grid Sub-Station | Earthing Trafo-2 LT | 2024-11-28 07:30 | 2024-11-28 14:33 | 7:03 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Keranigonj 230/132kV Grid Sub-Station | ATR-2 LT | 2024-11-28 07:31 | 2024-11-28 14:35 | 7:04 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) HT | 2024-11-29 07:33 | 2024-11-29 11:47 | 4:14 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auxiliary Transformer-02 LT | 2024-11-29 07:33 | 2024-11-29 11:49 | 4:16 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Keranigonj 230/132kV Grid Sub-Station | ATR-2 LT | 2024-11-29 08:38 | 2024-11-29 15:41 | 7:03 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Matauil 132/33kV Grid Sub-Station | GT-1 HT | 2024-11-29 10:14 | 2024-11-29 20:22 | 10:08 | S/O | Due to Mainteance work | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2024-11-30 08:58 | 2024-11-30 12:52 | 3:54 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | 230kV Bus-02 | 2024-11-30 09:31 | 2024-11-30 16:12 | 6:41 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bus-1 | 2024-11-30 10:10 | 2024-11-30 15:25 | 5:15 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
|  |  | Total : | 388:27 |  | Unserved Energy: |  | 249.5833
Chattogram Grid Circle :
Agrabad 132/33kV Grid Sub-Station | Auxiliary Transformer-02 HT | 2024-11-02 07:00 | 2024-11-02 13:35 | 6:35 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Agrabad 132/33kV Grid Sub-Station | MTR-02 (416T) HT | 2024-11-02 07:08 | 2024-11-02 13:57 | 6:49 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | 415T-T2 HT | 2024-11-02 07:11 | 2024-11-02 17:20 | 10:09 | S/O | Project Work | 40 | 406 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2024-11-02 09:18 | 2024-11-02 13:24 | 4:06 | S/O | Due to Annual Maintenance by PDB | 45 | 184.5 | Power interruption
Juldah 132/33kV Grid Sub-Station | 406T T-1 HT | 2024-11-03 07:37 | 2024-11-03 12:46 | 5:09 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bus-B | 2024-11-03 08:10 | 2024-11-03 14:32 | 6:22 | S/O | Project Work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | T-2 416T LT | 2024-11-04 08:12 | 2024-11-04 13:02 | 4:50 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2024-11-04 15:22 | 2024-11-04 16:48 | 1:26 | S/O | Due to Red hot maintenance. | 45 | 64.5 | Power interruption
Khulshi 132/33kV Grid Sub-Station | 415T (T2) HT | 2024-11-05 06:02 | 2024-11-05 07:16 | 1:14 | S/O | Due to Red hot maintenance. | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 406T LT | 2024-11-05 07:13 | 2024-11-05 13:44 | 6:31 | S/O | Due to Red hot maintenance. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2024-11-06 14:38 | 2024-11-06 16:14 | 1:36 | S/O | Due to Red hot maintenance. | 40 | 64 | Power interruption
Matarbari 132/33kV Grid Sub-Station | T2 | 2024-11-12 12:05 | 2024-11-12 15:13 | 3:08 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Bus-B | 2024-11-24 08:45 | 2024-11-24 15:18 | 6:33 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
|  |  | Total : | 64:28 |  |  |  | 719
Cumilla Grid Circle :
Shahjibazar 132/33kV Grid Sub-Station | TR-02 HT | 2024-11-02 07:17 | 2024-11-02 10:07 | 2:50 | S/O | Maintenance work by PBS | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2024-11-02 08:32 | 2024-11-02 08:32 | 0:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T LT | 2024-11-02 08:46 | 2024-11-02 15:48 | 7:02 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2024-11-02 08:48 | 2024-11-02 19:10 | 10:22 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sreemongal 132/33kV Grid Sub-Station | T-3 LT | 2024-11-02 13:25 | 2024-11-02 13:43 | 0:18 | S/O | Due to For 33 kV GCB gas refill | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T LT | 2024-11-03 08:46 | 2024-11-03 15:48 | 7:02 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2024-11-04 07:28 | 2024-11-04 08:45 | 1:17 | S/O | Maintenance work BY PDB | 40 | 51.3333 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T HT | 2024-11-04 09:11 | 2024-11-04 15:57 | 6:46 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 LT | 2024-11-04 09:49 | 2024-11-04 12:39 | 2:50 | S/O | Due to PRD cover Installation | 4 | 11.3333 | Power interruption
Sreemongal 132/33kV Grid Sub-Station | T-1AB LT | 2024-11-05 08:29 | 2024-11-05 16:28 | 7:59 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2024-11-05 09:04 | 2024-11-05 12:24 | 3:20 | S/O | Due to For under frequency relay setting by SPMD Comilla. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2024-11-05 12:39 | 2024-11-05 14:42 | 2:03 | S/O | Due to For under frequency relay setting by SPMD Comilla. | 0 | 0 | No interruption
Sreemongal 132/33kV Grid Sub-Station | T-1AB LT | 2024-11-06 08:39 | 2024-11-06 16:20 | 7:41 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Trafo-1 LT | 2024-11-06 09:35 | 2024-11-06 18:18 | 8:43 | S/O | Due to PDB 2D bay extension | 0 | 0 | No interruption
Sylhet(S)132/33kV Grid Sub-Station | Bus Bar 132 KV -1 | 2024-11-06 09:45 | 2024-11-06 18:17 | 8:32 | S/O | Due to PDB 33 kv 2D bay extension | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-90MW P/S | 2024-11-06 10:14 | 2024-11-06 15:14 | 5:00 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2024-11-07 06:55 | 2024-11-07 12:29 | 5:34 | S/O | Maintenance work | 0 | 0 | No interruption
Sreemongal 132/33kV Grid Sub-Station | T-1AB LT | 2024-11-07 08:44 | 2024-11-07 17:02 | 8:18 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sylhet(S)132/33kV Grid Sub-Station | Trafo-1 LT | 2024-11-07 08:55 | 2024-11-07 19:55 | 11:00 | S/O | Project Work | 0 | 0 | No interruption
Sylhet(S)132/33kV Grid Sub-Station | Trafo-2 LT | 2024-11-08 09:59 | 2024-11-08 11:30 | 1:31 | S/O | Project Work | 15 | 22.75 | Power interruption
Chandpur132/33kV Grid Sub-Station | 422T LT | 2024-11-09 06:25 | 2024-11-09 09:53 | 3:28 | S/O | Due to 33 Kv Bus section T3 shutdown | 15 | 52 | Power interruption
Sreemongal 132/33kV Grid Sub-Station | T-2 LT | 2024-11-09 08:40 | 2024-11-12 16:37 | 79:57 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sreemongal 132/33kV Grid Sub-Station | T-3 LT | 2024-11-09 08:40 | 2024-11-12 16:37 | 79:57 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-06 LT | 2024-11-11 12:15 | 2024-11-11 14:55 | 2:40 | S/O | Due to Required by PBS | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-11-12 08:14 | 2024-11-12 14:12 | 5:58 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 HT | 2024-11-13 08:17 | 2024-11-13 13:37 | 5:20 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Chandpur132/33kV Grid Sub-Station | 402T LT | 2024-11-13 09:20 | 2024-11-13 13:35 | 4:15 | S/O | Due to Relay testing by SPMD | 0 | 0 | No interruption
Cumilla(S132/33kV Grid Sub-Station | TR-3 LT | 2024-11-13 12:04 | 2024-11-13 13:21 | 1:17 | S/O | Due to 33 KV kaliajuri feeder red hot maintenance by PDB. | 10 | 12.8333 | Power interruption
Chandpur132/33kV Grid Sub-Station | 422T LT | 2024-11-13 13:40 | 2024-11-13 16:24 | 2:44 | S/O | Due to Relay testing by SPMD | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-11-14 08:06 | 2024-11-14 15:16 | 7:10 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Beanibazar 132/33kV Grid Sub-Station | Transformer TR-01 HT | 2024-11-16 07:35 | 2024-11-16 14:00 | 6:25 | S/O | Project Work | 22 | 141.1667 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-2 HT | 2024-11-16 08:28 | 2024-11-16 13:40 | 5:12 | S/O | Project Work | 8 | 41.6 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-1 HT | 2024-11-16 08:32 | 2024-11-16 19:36 | 11:04 | S/O | Project Work | 8 | 88.5333 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2024-11-16 08:50 | 2024-11-16 16:08 | 7:18 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-1 HT | 2024-11-16 08:50 | 2024-11-16 11:53 | 3:03 | S/O | Due to PBS project work-33KV BUS | 2 | 6.1 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 LT | 2024-11-16 08:54 | 2024-11-16 14:25 | 5:31 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bibiana 132/33kV Grid Sub-Station | ICT-01 HT | 2024-11-17 08:42 | 2024-11-17 16:35 | 7:53 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T HT | 2024-11-17 08:55 | 2024-11-17 16:13 | 7:18 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 LT | 2024-11-17 08:56 | 2024-11-17 15:30 | 6:34 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bibiana 400/230/kV Grid Sub-Station | ICT-01 HT | 2024-11-18 08:23 | 2024-11-18 16:01 | 7:38 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2024-11-18 09:22 | 2024-11-18 14:34 | 5:12 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2024-11-19 08:31 | 2024-11-19 14:16 | 5:45 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-11-19 15:15 | 2024-11-19 18:26 | 3:11 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2024-11-21 08:36 | 2024-11-21 13:19 | 4:43 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2-425T LT | 2024-11-21 11:04 | 2024-11-21 12:30 | 1:26 | S/O | Due to Annual Maintenence | 30 | 43 | Power interruption
Sreemongal 132/33kV Grid Sub-Station | T-1AB LT | 2024-11-23 07:12 | 2024-11-23 09:28 | 2:16 | S/O | Due to PBS work | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-06 LT | 2024-11-23 08:14 | 2024-11-23 14:05 | 5:51 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2024-11-23 08:40 | 2024-11-23 16:38 | 7:58 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bibiana 400/230/kV Grid Sub-Station | ICT-02 LT | 2024-11-23 09:18 | 2024-11-23 15:35 | 6:17 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-06 LT | 2024-11-24 08:13 | 2024-11-24 13:50 | 5:37 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Bibiana 400/230/kV Grid Sub-Station | ICT-02 LT | 2024-11-24 09:00 | 2024-11-24 15:58 | 6:58 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2024-11-24 08:53 | 2024-11-24 16:35 | 7:42 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2024-11-25 09:20 | 2024-11-25 16:50 | 7:30 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2024-11-26 07:20 | 2024-11-26 08:30 | 1:10 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-1 HT | 2024-11-26 08:33 | 2024-11-26 16:14 | 7:41 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T LT | 2024-11-26 08:41 | 2024-11-26 13:27 | 4:46 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sylhet(S)132/33kV Grid Sub-Station | South Trafo-1 LT | 2024-11-26 08:49 | 2024-11-26 17:52 | 9:03 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2024-11-26 14:13 | 2024-11-26 17:49 | 3:36 | S/O | Due to Ten Delta test. | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-1 LT | 2024-11-27 08:45 | 2024-11-27 16:27 | 7:42 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sylhet(S)132/33kV Grid Sub-Station | Trafo-1 LT | 2024-11-27 09:12 | 2024-11-27 13:28 | 4:16 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-11-28 08:14 | 2024-11-28 11:59 | 3:45 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | 230KV ATR-03 LT | 2024-11-30 07:39 | 2024-11-30 07:39 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2024-11-30 08:29 | 2024-11-30 13:19 | 4:50 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sylhet(S)132/33kV Grid Sub-Station | Trafo-1 LT | 2024-11-30 08:31 | 2024-11-30 15:59 | 7:28 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 LT | 2024-11-30 08:46 | 2024-11-30 16:42 | 7:56 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | TR-02 HT | 2024-11-30 09:23 | 2024-11-30 16:02 | 6:39 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
Sylhet(S)132/33kV Grid Sub-Station | Trafo-2 LT | 2024-11-30 10:51 | 2024-11-30 17:35 | 6:44 | S/O | Due to Annual Maintenence | 0 | 0 | No interruption
|  |  | Total : | 514:52 |  | Unserved Energy: |  | 470.65
Khulna Grid Circle :
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2024-11-01 05:54 | 2024-11-01 05:54 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T LT | 2024-11-01 05:55 | 2024-11-01 05:55 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Tr-3 (426T) LT | 2024-11-01 06:46 | 2024-11-01 08:59 | 2:13 | S/O | Due to Red hot maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-11-01 08:00 | 2024-11-05 12:11 | 100:11 | S/O | Maintenance work | 0 | 0 | No interruption
Barisal 132/33kV Grid Sub-Station | 132 kV Capacitor Bank | 2024-11-02 07:22 | 2024-11-02 16:55 | 9:33 | S/O | Project Work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T LT | 2024-11-02 07:41 | 2024-11-02 16:54 | 9:13 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 HT | 2024-11-02 08:20 | 2024-11-02 15:58 | 7:38 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-03 07:12 | 2024-11-03 08:50 | 1:38 | S/O | Due to Annual Maintenance | 25 | 40.8333 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T LT | 2024-11-03 07:37 | 2024-11-03 17:14 | 9:37 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 LT | 2024-11-03 07:45 | 2024-11-03 17:16 | 9:31 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) LT | 2024-11-04 07:26 | 2024-11-04 17:15 | 9:49 | S/O | Maintenance work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2024-11-04 07:42 | 2024-11-04 17:16 | 9:34 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Gopalpara 132/33kV Grid Sub-Station | Bus 1 | 2024-11-04 09:58 | 2024-11-04 16:04 | 6:06 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) LT | 2024-11-05 07:25 | 2024-11-05 16:31 | 9:06 | S/O | Due to Annual Maintenance | 25 | 227.5 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2024-11-05 07:35 | 2024-11-05 17:47 | 10:12 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2024-11-05 08:26 | 2024-11-05 15:19 | 6:53 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Gopalpara 132/33kV Grid Sub-Station | Bus 1 | 2024-11-05 08:40 | 2024-11-05 15:50 | 7:10 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2024-11-06 07:15 | 2024-11-06 08:15 | 1:00 | S/O | Due to Red hot maintenance. | 16 | 16 | Power interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-2 | 2024-11-06 08:32 | 2024-11-06 15:03 | 6:31 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2024-11-06 08:37 | 2024-11-06 16:46 | 8:09 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Capacitor Bank | 2024-11-06 08:56 | 2024-11-06 17:20 | 8:24 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) LT | 2024-11-06 09:48 | 2024-11-06 20:13 | 10:25 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Barisal 132/33kV Grid Sub-Station | Bus B | 2024-11-07 07:16 | 2024-11-07 16:57 | 9:41 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-07 07:19 | 2024-11-07 16:28 | 9:09 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | (T-2) LT | 2024-11-07 07:37 | 2024-11-07 16:27 | 8:50 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Madaripur 230/132kV Grid Sub-Station | Aux Tr-01 HT | 2024-11-07 09:27 | 2024-11-07 09:27 | 0:00 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-11-09 07:07 | 2024-11-09 10:35 | 3:28 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Chuadanga 230/132kV Grid Sub-Station | Tr. T2(426T) LT | 2024-11-09 07:16 | 2024-11-09 15:41 | 8:25 | S/O | Due to Annual maintenance work. | 9 | 75.75 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2024-11-09 07:45 | 2024-11-09 16:31 | 8:46 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) LT | 2024-11-09 08:09 | 2024-11-09 16:25 | 8:16 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2024-11-09 08:11 | 2024-11-09 15:43 | 7:32 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 2024-11-09 08:40 | 2024-11-09 16:41 | 8:01 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2024-11-09 10:47 | 2024-11-09 12:33 | 1:46 | S/O | Due to Annual maintenance work. | 10 | 17.6667 | Power interruption
Payra 400/132/33kV Grid Sub-Station | GSUT-02 HT | 2024-11-09 23:34 | 2024-11-09 23:34 | 0:00 | S/O | Due to overhaul inspection | 622 | 0 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) LT | 2024-11-10 08:10 | 2024-11-10 16:48 | 8:38 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2024-11-10 08:10 | 2024-11-10 14:20 | 6:10 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2024-11-10 08:11 | 2024-11-10 08:11 | 0:00 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 2024-11-10 08:52 | 2024-11-10 17:04 | 8:12 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Gopalpara 132/33kV Grid Sub-Station | Bus 2 | 2024-11-10 09:21 | 2024-11-10 14:08 | 4:47 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-11-11 07:29 | 2024-11-11 16:49 | 9:20 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2024-11-11 07:45 | 2024-11-11 17:09 | 9:24 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-11-12 07:25 | 2024-11-12 17:11 | 9:46 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2024-11-12 07:40 | 2024-11-12 14:39 | 6:59 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2024-11-12 07:57 | 2024-11-12 15:51 | 7:54 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | ATR-04 LT | 2024-11-12 08:42 | 2024-11-12 15:08 | 6:26 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-11-13 07:17 | 2024-11-13 16:56 | 9:39 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2024-11-13 08:10 | 2024-11-13 16:41 | 8:31 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-13 08:39 | 2024-11-13 15:16 | 6:37 | S/O | Due to Annual Maintenance. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-04 LT | 2024-11-13 08:55 | 2024-11-13 16:55 | 8:00 | S/O | Due to Completion of Bus Coupler Breaker CT | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2024-11-13 10:14 | 2024-11-13 15:13 | 4:59 | S/O | Due to Relay Testing. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T LT | 2024-11-13 15:18 | 2024-11-13 16:22 | 1:04 | S/O | Due to Relay Testing. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2024-11-13 16:30 | 2024-11-13 18:50 | 2:20 | S/O | Due to Relay Testing. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-11-14 07:13 | 2024-11-14 13:28 | 6:15 | S/O | Due to Annual maintenance | 20 | 125 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2024-11-14 08:01 | 2024-11-14 16:59 | 8:58 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-14 08:45 | 2024-11-14 15:38 | 6:53 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-11-14 10:43 | 2024-11-14 10:59 | 0:16 | S/O | Due to Annual maintenance | 59 | 15.7333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-15 06:20 | 2024-11-15 10:07 | 3:47 | S/O | Project Work | 24 | 90.8 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-11-15 06:24 | 2024-11-15 06:24 | 0:00 | S/O | Project Work | 24 | 0 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T1(416T) LT | 2024-11-16 07:16 | 2024-11-16 15:12 | 7:56 | S/O | Project Work | 55 | 436.3333 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | Tr. T3 LT | 2024-11-16 07:17 | 2024-11-16 15:14 | 7:57 | S/O | Project Work | 55 | 437.25 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | Tr. T2(426T) LT | 2024-11-16 07:17 | 2024-11-16 15:14 | 7:57 | S/O | Project Work | 55 | 437.25 | Power interruption
Narial 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2024-11-16 07:44 | 2024-11-16 15:51 | 8:07 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-05 HT | 2024-11-16 08:40 | 2024-11-16 14:56 | 6:16 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2024-11-16 08:48 | 2024-11-16 16:02 | 7:14 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) LT | 2024-11-16 08:48 | 2024-11-16 14:48 | 6:00 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-11-16 08:54 | 2024-11-16 15:20 | 6:26 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | Main Bus | 2024-11-16 09:02 | 2024-11-16 13:37 | 4:35 | S/O | Due to Annual maintenance | 20 | 91.6667 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-11-16 09:14 | 2024-11-16 10:48 | 1:34 | S/O | Due to 33 kV Bus maintenance | 36 | 56.4 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-11-16 09:20 | 2024-11-16 15:15 | 5:55 | S/O | Due to 33 kV Bus maintenance | 20 | 118.3333 | Power interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | 230 KV Main Bus 1 | 2024-11-16 10:31 | 2024-11-16 17:40 | 7:09 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulna(C) 230/ 132/33kV Grid Sub-Station | TR-1 425T LT | 2024-11-16 14:02 | 2024-11-16 17:16 | 3:14 | S/O | Due to 33 kV Bus maintenance | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2024-11-17 07:53 | 2024-11-17 15:44 | 7:51 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-11-17 09:03 | 2024-11-17 14:30 | 5:27 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-05 HT | 2024-11-17 09:20 | 2024-11-17 14:47 | 5:27 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-11-18 07:10 | 2024-11-18 17:07 | 9:57 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Bus-A | 2024-11-18 08:18 | 2024-11-18 16:53 | 8:35 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | Rampal Ckt-2 | 2024-11-18 08:25 | 2024-11-18 15:51 | 7:26 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-11-18 08:57 | 2024-11-18 16:50 | 7:53 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | 230 KV Main Bus 2 | 2024-11-18 09:00 | 2024-11-18 16:10 | 7:10 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Payra 400/230/ 132/33kV Grid Sub-Station | Auto Transformer-02 HT | 2024-11-18 09:25 | 2024-11-18 09:25 | 0:00 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Bus-01 | 2024-11-18 09:43 | 2024-11-18 14:41 | 4:58 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-11-19 06:00 | 2024-11-19 13:53 | 7:53 | S/O | Due to G2G project work. | 25 | 197.0833 | Power interruption
Barguna 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-11-19 07:02 | 2024-11-19 15:05 | 8:03 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Bus-B | 2024-11-19 08:22 | 2024-11-19 16:01 | 7:39 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | 230 KV Main Bus 2 | 2024-11-19 08:29 | 2024-11-19 14:47 | 6:18 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Bus-01 | 2024-11-19 09:30 | 2024-11-19 19:21 | 9:51 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | Capacitor Bank | 2024-11-20 08:19 | 2024-11-20 16:36 | 8:17 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | 230 KV Main Bus 1 | 2024-11-20 08:58 | 2024-11-20 15:17 | 6:19 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-20 09:08 | 2024-11-20 14:19 | 5:11 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Bus-02 | 2024-11-20 09:24 | 2024-11-20 13:12 | 3:48 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 LT | 2024-11-20 10:22 | 2024-11-20 13:19 | 2:57 | S/O | Project Work | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2024-11-21 08:11 | 2024-11-21 16:32 | 8:21 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | ATR-1 LT | 2024-11-21 09:20 | 2024-11-21 15:44 | 6:24 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2024-11-21 09:56 | 2024-11-21 13:19 | 3:23 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-11-23 09:09 | 2024-11-23 16:33 | 7:24 | S/O | Due to 33kV BUS Section DS installation. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | ATR-2 LT | 2024-11-23 09:27 | 2024-11-23 14:42 | 5:15 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Bus-01 | 2024-11-23 09:42 | 2024-11-23 14:41 | 4:59 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Tr-1(403T) LT | 2024-11-24 09:10 | 2024-11-24 14:32 | 5:22 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Bus-B | 2024-11-26 11:15 | 2024-11-26 16:21 | 5:06 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 230 kV Bus-01 | 2024-11-27 10:03 | 2024-11-27 17:14 | 7:11 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-11-27 16:36 | 2024-11-27 17:14 | 0:38 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 230 kV Bus-02 | 2024-11-28 08:18 | 2024-11-28 14:56 | 6:38 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-11-28 10:06 | 2024-11-28 11:12 | 1:06 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 734:49 |  | Unserved Energy : |  | 2383.6
HVDC Grid Circle
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-11-01 07:17 | 2024-11-01 07:17 | 0:00 | S/O | Due to Red hot maintenance work at 33 kV | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 LT | 2024-11-01 08:29 | 2024-11-01 11:43 | 3:14 | S/O | Due to OTI meter i installation | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 LT | 2024-11-01 08:44 | 2024-11-01 12:54 | 4:10 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 20DF11 | 2024-11-02 10:19 | 2024-11-02 17:39 | 7:20 | S/O | Due to For Annual rectification work | 0 | 0 | No interruption
BIPTC | 20DF12 | 2024-11-03 09:27 | 2024-11-03 16:33 | 7:06 | S/O | Maintenance work | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Bus-A | 2024-11-04 08:30 | 2024-11-04 09:07 | 0:37 | S/O | Project Work | 0 | 0 | No interruption
BIPTC | 20DF21 | 2024-11-04 09:31 | 2024-11-04 09:31 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
BIPTC | 20DF22 | 2024-11-05 09:21 | 2024-11-05 16:52 | 7:31 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Bus-B | 2024-11-05 09:40 | 2024-11-05 18:10 | 8:30 | S/O | Due toLoop connection. | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | 132 KV Bus1 | 2024-11-06 08:31 | 2024-11-06 14:22 | 5:51 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 20DF23 | 2024-11-06 09:36 | 2024-11-06 16:11 | 6:35 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 20DF31 | 2024-11-07 09:32 | 2024-11-07 09:32 | 0:00 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | T-2 HT | 2024-11-08 08:24 | 2024-11-08 16:13 | 7:49 | S/O | Due to oil centrifuse | 0 | 0 | No interruption
BIPTC | 20DF32 | 2024-11-09 10:40 | 2024-11-09 16:16 | 5:36 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 20DF41 | 2024-11-10 10:56 | 2024-11-10 17:40 | 6:44 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 20DF42 | 2024-11-11 09:51 | 2024-11-11 16:15 | 6:24 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | 230 kV Bus | 2024-11-11 10:50 | 2024-11-11 15:33 | 4:43 | S/O | Maintenance work | 0 | 0 | No interruption
BIPTC | 20DF43 | 2024-11-12 09:54 | 2024-11-12 16:07 | 6:13 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 10CF13 | 2024-11-13 09:12 | 2024-11-13 16:26 | 7:14 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 10CF14 | 2024-11-14 09:24 | 2024-11-14 15:20 | 5:56 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | T-2 LT | 2024-11-14 15:20 | 2024-11-14 16:37 | 1:17 | S/O | Due to 33 kv bus-2 loop maintenance | 25 | 32.0833 | Power interruption
BIPTC | 10CF15 | 2024-11-16 09:35 | 2024-11-16 15:50 | 6:15 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 10CF16 | 2024-11-17 10:12 | 2024-11-17 15:32 | 5:20 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-1(405T) HT | 2024-11-18 07:37 | 2024-11-18 16:10 | 8:33 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 10CF23 | 2024-11-18 09:51 | 2024-11-18 15:53 | 6:02 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-1 HT | 2024-11-19 07:44 | 2024-11-19 07:44 | 0:00 | S/O | Due to oil centrifuge | 0 | 0 | No interruption
BIPTC | 10CF24 | 2024-11-19 09:56 | 2024-11-19 14:30 | 4:34 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 10CF25 | 2024-11-20 09:50 | 2024-11-20 15:30 | 5:40 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
BIPTC | 10CF26 | 2024-11-21 09:29 | 2024-11-21 16:56 | 7:27 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 LT | 2024-11-23 07:42 | 2024-11-23 16:31 | 8:49 | S/O | Due to Annual maintenance | 21 | 185.15 | Power interruption
Magura 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-11-23 08:12 | 2024-11-23 14:53 | 6:41 | S/O | Due to 33kV Feeder connection | 10 | 66.8333 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) LT | 2024-11-27 07:28 | 2024-11-27 16:06 | 8:38 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-11-28 10:52 | 2024-11-28 12:27 | 1:35 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 172:24 |  | Unserved Energy : |  | 284.0667
Bogura Grid Circle:
Niamatpur132/33kV Grid Sub-Station | Transformer-1(407T) LT | 2024-11-02 06:21 | 2024-11-02 06:21 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Niamatpur132/33kV Grid Sub-Station | Transformer-2(407T) LT | 2024-11-02 06:22 | 2024-11-02 06:22 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
Niamatpur132/33kV Grid Sub-Station | Transformer-2 (417T) HT | 2024-11-02 06:24 | 2024-11-02 13:59 | 7:35 | S/O | Project Work | 14 | 106.1667 | No interruption
Niamatpur132/33kV Grid Sub-Station | Transformer-1(407T) HT | 2024-11-02 06:24 | 2024-11-02 13:58 | 7:34 | S/O | Project Work | 27 | 204.3 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2024-11-02 08:03 | 2024-11-02 08:03 | 0:00 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2024-11-02 08:13 | 2024-11-02 10:57 | 2:44 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | ATR-01 HT | 2024-11-02 08:33 | 2024-11-02 17:19 | 8:46 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2024-11-02 08:34 | 2024-11-02 08:34 | 0:00 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132kv bus coupler | 2024-11-02 08:35 | 2024-11-02 08:35 | 0:00 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) LT | 2024-11-02 09:30 | 2024-11-02 16:22 | 6:52 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) HT | 2024-11-03 07:56 | 2024-11-03 17:00 | 9:04 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | 100MW PPP | 2024-11-03 08:12 | 2024-11-03 16:06 | 7:54 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | 132KV Bus A | 2024-11-03 09:46 | 2024-11-03 14:20 | 4:34 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | 132KV Bus-B | 2024-11-03 11:16 | 2024-11-03 14:20 | 3:04 | S/O | Maintenance work | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | 132KV Bus-2 | 2024-11-04 07:21 | 2024-11-04 07:21 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2024-11-04 08:12 | 2024-11-04 16:27 | 8:15 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-02 HT | 2024-11-04 08:50 | 2024-11-04 16:46 | 7:56 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) HT | 2024-11-04 09:06 | 2024-11-04 17:05 | 7:59 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2024-11-05 08:01 | 2024-11-05 18:01 | 10:00 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-2 Transformer (413T) LT | 2024-11-05 09:44 | 2024-11-05 17:35 | 7:51 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-06 07:11 | 2024-11-06 17:08 | 9:57 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-1 (406T) LT | 2024-11-06 08:10 | 2024-11-06 17:38 | 9:28 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-03 HT | 2024-11-06 08:29 | 2024-11-06 17:30 | 9:01 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-1 (406T) LT | 2024-11-07 07:46 | 2024-11-07 16:52 | 9:06 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) LT | 2024-11-07 10:32 | 2024-11-07 12:51 | 2:19 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-11-08 06:55 | 2024-11-08 08:40 | 1:45 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-11-08 09:05 | 2024-11-08 09:05 | 0:00 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-2 (416T) LT | 2024-11-08 07:51 | 2024-11-08 16:47 | 8:56 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-2 (416T) HT | 2024-11-09 08:20 | 2024-11-09 16:25 | 8:05 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | 132KV Bus-A | 2024-11-10 09:54 | 2024-11-10 09:54 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-4 Transformer LT | 2024-11-10 10:07 | 2024-11-10 15:00 | 4:53 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | T-3, 404T LT | 2024-11-11 08:09 | 2024-11-11 09:35 | 1:26 | S/O | Due to Annual maintenance. | 12 | 17.2 | Power interruption
Amnura 132/33kV Grid Sub-Station | T-3 (426T) LT | 2024-11-11 08:15 | 2024-11-11 16:24 | 8:09 | S/O | Due to Maintenance Work | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-3 (426T) HT | 2024-11-11 08:23 | 2024-11-11 15:24 | 7:01 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | T-01, 703T LT | 2024-11-11 10:03 | 2024-11-11 15:31 | 5:28 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | 132 KV Bus A | 2024-11-11 10:09 | 2024-11-11 15:36 | 5:27 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-3 (426T) HT | 2024-11-12 07:54 | 2024-11-12 07:54 | 0:00 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | T-01, 703T LT | 2024-11-12 09:02 | 2024-11-12 15:49 | 6:47 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Niamatpur132/33kV Grid Sub-Station | Transformer-1(407T) LT | 2024-11-13 08:04 | 2024-11-13 16:23 | 8:19 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | TR-3 (425 T) LT | 2024-11-13 08:18 | 2024-11-13 16:40 | 8:22 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) LT | 2024-11-13 08:21 | 2024-11-13 16:04 | 7:43 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | T-02, 713T LT | 2024-11-13 09:05 | 2024-11-13 16:43 | 7:38 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | Bus B | 2024-11-13 09:09 | 2024-11-13 16:36 | 7:27 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Bus-1 | 2024-11-13 09:39 | 2024-11-13 09:39 | 0:00 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Sirajganj 230/132kV Grid Sub-Station | T4-(445) LT | 2024-11-13 10:05 | 2024-11-13 10:05 | 0:00 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) LT | 2024-11-14 08:19 | 2024-11-14 17:41 | 9:22 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Niamatpur132/33kV Grid Sub-Station | Transformer-1(407T) LT | 2024-11-14 08:41 | 2024-11-14 16:20 | 7:39 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | T-02, 713T LT | 2024-11-14 08:42 | 2024-11-14 19:18 | 10:36 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-11-15 09:53 | 2024-11-15 09:53 | 0:00 | S/O | Due to Up gradation work. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-1 (406T) HT | 2024-11-16 08:31 | 2024-11-16 08:31 | 0:00 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | Main BUS-01 | 2024-11-16 08:49 | 2024-11-16 14:02 | 5:13 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | T-06, 723T HT | 2024-11-16 09:02 | 2024-11-16 17:16 | 8:14 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | 132 KV Bus B | 2024-11-16 09:06 | 2024-11-16 17:11 | 8:05 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | 132KV Bus-B | 2024-11-16 13:50 | 2024-11-16 13:50 | 0:00 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Bus sec-1 | 2024-11-17 07:57 | 2024-11-17 07:57 | 0:00 | S/O | upgradtion work | 0 | 0 | No interruption
Niamatpur132/33kV Grid Sub-Station | Transformer-2 (417T) LT | 2024-11-17 08:25 | 2024-11-17 16:14 | 7:49 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | T-06, 723T HT | 2024-11-17 09:56 | 2024-11-17 15:58 | 6:02 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2024-11-17 10:08 | 2024-11-17 13:13 | 3:05 | S/O | Due to Tan Delta test | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) HT | 2024-11-17 13:19 | 2024-11-17 16:18 | 2:59 | S/O | Due to Tan Delta test | 0 | 0 | No interruption
Niamatpur132/33kV Grid Sub-Station | Transformer-2 (417T) LT | 2024-11-18 08:22 | 2024-11-18 16:09 | 7:47 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | 132 kV Main BUS-02 | 2024-11-18 09:07 | 2024-11-18 16:57 | 7:50 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2024-11-18 09:35 | 2024-11-18 11:27 | 1:52 | S/O | Due to Tan Delta test | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-11-18 11:37 | 2024-11-18 14:03 | 2:26 | S/O | Due to Tan Delta test | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Main BUS-02 | 2024-11-19 08:26 | 2024-11-19 15:54 | 7:28 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | ATR-01 (704T) LT | 2024-11-19 08:33 | 2024-11-19 11:38 | 3:05 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 LT | 2024-11-19 08:55 | 2024-11-19 16:35 | 7:40 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | ATR-02 (714T) HT | 2024-11-19 11:39 | 2024-11-19 15:51 | 4:12 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | T-02 (416T) LT | 2024-11-19 13:30 | 2024-11-19 16:34 | 3:04 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | T-01 (406T) LT | 2024-11-19 16:35 | 2024-11-19 18:23 | 1:48 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2024-11-20 07:52 | 2024-11-20 17:07 | 9:15 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 HT | 2024-11-20 08:32 | 2024-11-20 17:06 | 8:34 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2024-11-21 08:20 | 2024-11-21 16:34 | 8:14 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Sirajganj 230/132kV Grid Sub-Station | Bus-2 | 2024-11-21 08:49 | 2024-11-21 15:42 | 6:53 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-11-23 08:09 | 2024-11-23 16:48 | 8:39 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-11-24 08:12 | 2024-11-24 15:39 | 7:27 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | ATR-01 (704T) LT | 2024-11-25 08:24 | 2024-11-25 16:30 | 8:06 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | TR-01 HT | 2024-11-25 09:39 | 2024-11-25 16:41 | 7:02 | S/O | Due to Annual Maintenance by NESCO. | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | Bus A | 2024-11-25 09:39 | 2024-11-25 15:00 | 5:21 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | ATR-01 (704T) LT | 2024-11-26 08:23 | 2024-11-26 16:50 | 8:27 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bhangura 132/11kV Grid Sub-Station | Tr-2(413T) LT | 2024-11-26 09:17 | 2024-11-26 13:39 | 4:22 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-03 HT | 2024-11-27 08:00 | 2024-11-28 14:00 | 30:00 | S/O | Project Work | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | ATR-02 (714T) HT | 2024-11-28 08:12 | 2024-11-28 17:05 | 8:53 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | TR-02 LT | 2024-11-28 09:05 | 2024-11-28 16:24 | 7:19 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
Rajshahi 230/132kV Grid Sub-Station | T-01 (406T) LT | 2024-11-30 08:12 | 2024-11-30 16:11 | 7:59 | S/O | Due to Annual maintenance. | 0 | 0 | No interruption
|  |  | Total : | 490:12 |  | Unserved Energy : |  | 327.6667
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 3077:41 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:November 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV Grid Sub-Station | Mymensingh 132 kV Ckt-1 | 2024-11-02 08:52 | 2024-11-02 17:08 | 8:16 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Agargaon 230/132/33kV Grid Sub-Station | Satmasjid 132kV Ckt-1 | 2024-11-02 09:14 | 2024-11-02 15:48 | 6:34 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Kishoreganj 132kV Ckt-2 | 2024-11-03 06:13 | 2024-11-03 06:13 | 0:00 | S/O | Due to 132kv GIS work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh 132 kV Ckt-1 | 2024-11-03 09:00 | 2024-11-03 09:00 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh 132 kV Ckt-1 | 2024-11-04 07:43 | 2024-11-04 16:48 | 9:05 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh 132 kV Ckt-2 | 2024-11-05 08:12 | 2024-11-05 17:10 | 8:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-1 | 2024-11-05 08:35 | 2024-11-05 17:02 | 8:27 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Lalbag 132kV Ckt-2 | 2024-11-05 09:36 | 2024-11-05 17:14 | 7:38 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur United (20MW) | Sherpur 132kV Ckt-2 | 2024-11-05 12:02 | 2024-11-05 16:29 | 4:27 | S/O | Due to C.T Den-Delta Test | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-2 | 2024-11-06 08:30 | 2024-11-06 17:13 | 8:43 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh 132 kV Ckt-2 | 2024-11-06 08:48 | 2024-11-06 16:46 | 7:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh 132 kV Ckt-2 | 2024-11-07 07:28 | 2024-11-07 07:28 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh 132 kV Ckt-2 | 2024-11-07 07:31 | 2024-11-07 07:31 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-1 | 2024-11-07 08:53 | 2024-11-07 13:38 | 4:45 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132kV Grid Sub-Station | Bashundhara-1 | 2024-11-07 09:54 | 2024-11-07 11:09 | 1:15 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132kV Grid Sub-Station | Bashundhara-1 | 2024-11-07 11:16 | 2024-11-07 13:16 | 2:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132kV Grid Sub-Station | Tongi-Uttara Ckt | 2024-11-07 13:23 | 2024-11-07 15:17 | 1:54 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-2 | 2024-11-07 14:15 | 2024-11-07 15:55 | 1:40 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2024-11-07 15:19 | 2024-11-07 16:47 | 1:28 | S/O | Due to relay test | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-1 | 2024-11-09 09:30 | 2024-11-09 16:54 | 7:24 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132kV Grid Sub-Station | Tongi 132kV Ckt-1 | 2024-11-09 09:56 | 2024-11-09 14:22 | 4:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | BR Powergen Ckt- 01 | 2024-11-09 14:17 | 2024-11-09 20:55 | 6:38 | S/O | Project Work | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kodda 132kV Ckt-1 | 2024-11-10 07:45 | 2024-11-10 07:45 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-1 | 2024-11-10 09:30 | 2024-11-10 16:50 | 7:20 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-1 | 2024-11-11 09:37 | 2024-11-11 17:18 | 7:41 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-1 | 2024-11-12 09:08 | 2024-11-12 17:34 | 8:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Joydevpur 132/33kV Grid Sub-Station | Kodda B 132 kV Ckt-1 | 2024-11-12 10:00 | 2024-11-12 17:25 | 7:25 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-2 | 2024-11-12 11:08 | 2024-11-12 12:22 | 1:14 | S/O | Due to Relay Test | 0 | 0 | No interruption
Joydevpur 132/33kV Grid Sub-Station | Kodda B 132 kV Ckt-1 | 2024-11-13 09:11 | 2024-11-13 17:11 | 8:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-1 | 2024-11-13 09:18 | 2024-11-13 17:32 | 8:14 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-1 | 2024-11-14 09:28 | 2024-11-14 16:52 | 7:24 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Agargaon 132/33kV Grid Sub-Station | Satmasjid 132kV Ckt-2 | 2024-11-14 09:33 | 2024-11-14 16:19 | 6:46 | S/O | Due to 33kv Left bus annual maintenance by DPDC. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Lalbag 132kV Ckt-2 | 2024-11-14 11:13 | 2024-11-14 16:35 | 5:22 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132kV Grid Sub-Station | Bashundhara-2 | 2024-11-16 08:47 | 2024-11-16 19:50 | 11:03 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-2 | 2024-11-16 09:22 | 2024-11-16 16:50 | 7:28 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Joydevpur 132/33kV Grid Sub-Station | Kodda B 132 kV Ckt-2 | 2024-11-16 09:25 | 2024-11-16 16:00 | 6:35 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat 400kV Ckt-1 | 2024-11-16 09:34 | 2024-11-16 18:35 | 9:01 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat 400kV Ckt-2 | 2024-11-16 09:34 | 2024-11-16 16:49 | 7:15 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi(N) 230/132kV Grid Sub-Station | Tongi 132kV Ckt-2 | 2024-11-16 10:18 | 2024-11-16 12:44 | 2:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Kaliakoir 132 kV Ckt-2 | 2024-11-17 08:26 | 2024-11-17 08:26 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat 400kV Ckt-1 | 2024-11-17 08:41 | 2024-11-18 23:59 | 39:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Joydevpur 132/33kV Grid Sub-Station | Kodda B 132 kV Ckt-2 | 2024-11-17 09:12 | 2024-11-17 14:36 | 5:24 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-2 | 2024-11-17 09:36 | 2024-11-17 16:47 | 7:11 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi 230/132kV Grid Sub-Station | Bashundhara-2 | 2024-11-17 09:59 | 2024-11-17 15:18 | 5:19 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kodda 132kV Ckt-1 | 2024-11-18 07:25 | 2024-11-18 21:41 | 14:16 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-2 | 2024-11-18 08:57 | 2024-11-18 17:12 | 8:15 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat 400kV Ckt-2 | 2024-11-19 08:42 | 2024-11-19 16:56 | 8:14 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-2 | 2024-11-19 09:20 | 2024-11-19 17:19 | 7:59 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara 3PH 132kV Ckt-1 | 2024-11-20 07:41 | 2024-11-20 07:41 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Bhasantek 132kV Ckt-2 | 2024-11-20 08:10 | 2024-11-20 12:40 | 4:30 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bashundhara 132/33kV Grid Sub-Station | Tongi 132 kV Ckt-2 | 2024-11-20 08:53 | 2024-11-20 15:40 | 6:47 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh 132kV Ckt-2 | 2024-11-20 09:56 | 2024-11-20 09:56 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara 3PH 132kV Ckt-1 | 2024-11-21 07:41 | 2024-11-21 07:41 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi230/132kV Grid Sub-Station | Bashundhara-2 | 2024-11-22 04:25 | 2024-11-22 04:25 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mymensingh RPCL | Tangail 132kV Ckt-1 | 2024-11-22 06:36 | 2024-11-22 11:44 | 5:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Summit 149 MW PS | 2024-11-22 10:19 | 2024-11-22 15:16 | 4:57 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Rajendrapur 132kV Ckt-1 | 2024-11-22 16:47 | 2024-11-22 17:18 | 0:31 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-1 | 2024-11-23 10:05 | 2024-11-23 17:38 | 7:33 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-1 | 2024-11-24 07:16 | 2024-11-24 07:16 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara 132kV Ckt-1 | 2024-11-24 07:41 | 2024-11-24 16:22 | 8:41 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Rajendrapur 132kV Ckt-1 | 2024-11-24 09:17 | 2024-11-24 16:00 | 6:43 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh 132 kV Ckt-1 | 2024-11-24 10:00 | 2024-11-24 12:26 | 2:26 | S/O | Due to Relay Testing | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh 132 kV Ckt-2 | 2024-11-24 12:28 | 2024-11-24 14:26 | 1:58 | S/O | Due to Protection works | 0 | 0 | No interruption
Tongi230/132kV Grid Sub-Station | Kaliakoir-2 | 2024-11-24 09:14 | 2024-11-24 16:46 | 7:32 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara 132kV Ckt-1 | 2024-11-25 07:45 | 2024-11-25 17:03 | 9:18 | S/O | Maintenance work | 0 | 0 | No interruption
Tongi230/132kV Grid Sub-Station | Kaliakoir-2 | 2024-11-25 08:28 | 2024-11-25 16:46 | 8:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj 132kV Ckt-1 | 2024-11-25 08:42 | 2024-11-25 17:00 | 8:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Rajendrapur 132kV Ckt-2 | 2024-11-25 09:02 | 2024-11-25 16:54 | 7:52 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-1 | 2024-11-25 14:26 | 2024-11-25 16:45 | 2:19 | S/O | Due to Deed Line checking. | 0 | 0 | No interruption
Tongi230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-1 | 2024-11-26 08:26 | 2024-11-26 17:45 | 9:19 | S/O | Due to Deed Line checking. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-1 | 2024-11-26 09:12 | 2024-11-26 15:06 | 5:54 | S/O | Due to Annual Maintenance dead line checking. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-1 | 2024-11-26 09:16 | 2024-11-26 09:16 | 0:00 | S/O | Due to Annual Maintenance dead line checking. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tongi 230kV Ckt-2 | 2024-11-27 08:19 | 2024-11-27 18:02 | 9:43 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir 230kV Ckt-1 | 2024-11-27 08:23 | 2024-11-27 18:15 | 9:52 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj 132kV Ckt-1 | 2024-11-27 08:45 | 2024-11-27 16:17 | 7:32 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-1 | 2024-11-27 09:47 | 2024-11-27 17:15 | 7:28 | S/O | Due to Annual Maintenance dead line checking. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-2 | 2024-11-28 06:45 | 2024-11-28 16:20 | 9:35 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi 132kV Ckt-2 | 2024-11-28 07:14 | 2024-11-28 07:14 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-2 | 2024-11-28 07:44 | 2024-11-28 07:44 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj 132kV Ckt-1 | 2024-11-28 08:43 | 2024-11-28 16:54 | 8:11 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | RPCL 100 MW PS | 2024-11-29 07:09 | 2024-11-29 11:27 | 4:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Tongi230/132kV Grid Sub-Station | Tongi 132kV Ckt-1 | 2024-11-30 10:01 | 2024-11-30 11:09 | 1:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Airport(Old) 230kV Ckt-1 | 2024-11-30 10:33 | 2024-11-30 12:45 | 2:12 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keraniganj 230kV Ckt-2 | 2024-11-30 10:58 | 2024-11-30 13:28 | 2:30 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 479:45 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-11-01 10:44 | 2024-11-01 15:40 | 4:56 | S/O | Maintenance work | 0 | 0 | No interruption
Bhulta 132/33kV Grid Sub-Station | Rampura 230 kV Ckt-1 | 2024-11-03 09:20 | 2024-11-03 16:45 | 7:25 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-1 | 2024-11-03 09:45 | 2024-11-03 16:42 | 6:57 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | DPDC Char sayedpur 132k Ckt-1 | 2024-11-05 10:24 | 2024-11-05 13:09 | 2:45 | S/O | Project work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | DPDC Char sayedpur 132k Ckt-2 | 2024-11-05 13:22 | 2024-11-05 14:07 | 0:45 | S/O | Project work | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-2 | 2024-11-06 08:18 | 2024-11-06 18:01 | 9:43 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-2 | 2024-11-07 09:01 | 2024-11-07 09:01 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat 230kV Ckt-2 | 2024-11-08 06:14 | 2024-11-08 17:52 | 11:38 | S/O | Due to OPGW Changing Work. | 0 | 0 | No interruption
Ghorasal 132/33kV Grid Sub-Station | Joydeb-B 132kV Ckt-2 | 2024-11-08 08:24 | 2024-11-08 15:11 | 6:47 | S/O | Due to Evacuation of buildings adjacent to the line | 0 | 0 | No interruption
Keraniganj 230/132kV Grid Sub-Station | Nawabganj 132kV Ckt-1 | 2024-11-09 08:11 | 2024-11-09 16:30 | 8:19 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Haripur 230 kV Ckt-1 | 2024-11-09 08:22 | 2024-11-09 21:51 | 13:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Keraniganj 230/132kV Grid Sub-Station | Nawabganj 132kV Ckt-1 | 2024-11-10 07:31 | 2024-11-10 12:39 | 5:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 2024-11-10 08:40 | 2024-11-10 11:49 | 3:09 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Haripur 230 kV Ckt-1 | 2024-11-10 09:51 | 2024-11-10 15:42 | 5:51 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-3 | 2024-11-11 08:10 | 2024-11-11 18:28 | 10:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-3 | 2024-11-11 08:55 | 2024-11-11 18:25 | 9:30 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Haripur 230 kV Ckt-1 | 2024-11-11 09:53 | 2024-11-11 17:05 | 7:12 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Haripur 230 kV Ckt-1 | 2024-11-11 10:27 | 2024-11-11 17:05 | 6:38 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Keraniganj 230/132kV Grid Sub-Station | Nawabganj 132kV Ckt-2 | 2024-11-12 07:43 | 2024-11-12 16:55 | 9:12 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | Shyampur(New) 132 kV Ckt-1 | 2024-11-12 08:22 | 2024-11-12 17:08 | 8:46 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | Shyampur(New) 132 kV Ckt-1 | 2024-11-12 08:40 | 2024-11-12 08:40 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Haripur 230 kV Ckt-2 | 2024-11-12 09:50 | 2024-11-12 16:27 | 6:37 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Haripur 230 kV Ckt-2 | 2024-11-12 10:20 | 2024-11-12 16:24 | 6:04 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Keraniganj 230/132kV Grid Sub-Station | Nawabganj 132kV Ckt-2 | 2024-11-13 07:33 | 2024-11-13 15:15 | 7:42 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | Shyampur(New) 132 kV Ckt-2 | 2024-11-13 07:41 | 2024-11-13 16:52 | 9:11 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Haripur 230 kV Ckt-2 | 2024-11-13 08:37 | 2024-11-13 16:25 | 7:48 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | EGCB 412MW | 2024-11-13 08:50 | 2024-11-13 15:40 | 6:50 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Haripur 230 kV Ckt-2 | 2024-11-13 09:42 | 2024-11-13 16:24 | 6:42 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-4 | 2024-11-13 09:52 | 2024-11-13 17:03 | 7:11 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-4 | 2024-11-13 10:23 | 2024-11-13 17:01 | 6:38 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gulsan 132/33kV Grid Sub-Station | Rampura 132kV Ckt-2 | 2024-11-13 11:43 | 2024-11-13 16:34 | 4:51 | S/O | Due to Distance relay installation work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Shitalakhya 132 kv Ckt | 2024-11-15 18:16 | 2024-11-15 18:16 | 0:00 | S/O | Maintenance work | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-4 | 2024-11-16 08:28 | 2024-11-16 16:27 | 7:59 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddirganj 230kV Ckt-1 | 2024-11-16 09:00 | 2024-11-16 09:00 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bashundhara Line | 2024-11-16 09:45 | 2024-11-16 15:49 | 6:04 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -2 | 2024-11-17 08:45 | 2024-11-17 08:45 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddirganj 230kV Ckt-2 | 2024-11-17 09:32 | 2024-11-17 17:13 | 7:41 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Haripur (360MW) 230kV Ckt-2 | 2024-11-17 16:03 | 2024-11-17 16:03 | 0:00 | S/O | Due to Oil leakage of bay PT. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Shyampur(New) 132kV Ckt-1 | 2024-11-18 09:22 | 2024-11-18 18:36 | 9:14 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Keraniganj 230/132kV Grid Sub-Station | 132 kV Hasnabad Ckt. 1 | 2024-11-19 07:24 | 2024-11-19 15:39 | 8:15 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Hanabad 132/33kV Grid Sub-Station | Keraniganj-1 (Pre- Lalbag) | 2024-11-19 07:30 | 2024-11-24 19:22 | 131:52 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Shyampur(New) 132kV Ckt-2 | 2024-11-19 10:54 | 2024-11-19 17:04 | 6:10 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Keraniganj 230/132kV Grid Sub-Station | Aggreko-1 | 2024-11-20 06:52 | 2024-11-20 20:55 | 14:03 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Nawabganj 230/132kV Grid Sub-Station | 132kV Main Bus-1 | 2024-11-20 07:40 | 2024-11-20 07:40 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 2024-11-21 11:08 | 2024-11-21 17:06 | 5:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -2 | 2024-11-21 13:09 | 2024-11-21 14:53 | 1:44 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulsan-2 | 2024-11-22 04:35 | 2024-11-22 04:35 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Powerpac 100MW) 132kV Ckt-2 | 2024-11-22 08:56 | 2024-11-22 16:31 | 7:35 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Motijheel Ckt-1 | 2024-11-22 09:56 | 2024-11-22 17:05 | 7:09 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Keraniganj 230/132kV Grid Sub-Station | Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 | 2024-11-23 08:57 | 2024-11-23 17:40 | 8:43 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | Shyampur(New) 132kV Ckt-2 | 2024-11-25 09:34 | 2024-11-25 15:23 | 5:49 | S/O | Due to Maintenance work of DPDC. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-4 | 2024-11-25 10:10 | 2024-11-25 11:35 | 1:25 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 2 | 2024-11-25 15:03 | 2024-11-25 17:58 | 2:55 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj 132kV Ckt-1 | 2024-11-26 08:52 | 2024-11-26 16:50 | 7:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-1 | 2024-11-26 09:52 | 2024-11-26 18:30 | 8:38 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-1 | 2024-11-26 10:59 | 2024-11-26 18:29 | 7:30 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-2 | 2024-11-27 10:00 | 2024-11-27 17:28 | 7:28 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Haripur 132 kV Ckt-1 | 2024-11-28 08:32 | 2024-11-28 16:32 | 8:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bhulta 400/230/kV Grid Sub-Station | Rampura 230 kV Ckt-2 | 2024-11-28 10:09 | 2024-11-28 16:55 | 6:46 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Siddhirganj 230kV Ckt-1 | 2024-11-30 09:11 | 2024-11-30 16:09 | 6:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 493:56 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
BSRM 230/132kV Sub-Station | Mirsharai 230 kV Ckt-1 | 2024-11-01 08:23 | 2024-11-01 08:23 | 0:00 | S/O | Project Work | 0 | 0 | No interruption
BSRM 230/132/33kV Grid Sub-Station | Cumilla(N) 230 kV Ckt-1 | 2024-11-02 08:52 | 2024-11-02 16:43 | 7:51 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-1 | 2024-11-02 09:22 | 2024-11-02 16:54 | 7:32 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-1 | 2024-11-03 08:18 | 2024-11-03 16:37 | 8:19 | S/O | Due to Dead line ckecking. | 0 | 0 | No interruption
Mirsorai 230/132/33kV Grid Sub-Station | 150 MW Power Station -01 | 2024-11-03 08:42 | 2024-11-03 13:08 | 4:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mirsorai 230/132/33kV Grid Sub-Station | 150 MW Power Station -02 | 2024-11-03 14:32 | 2024-11-03 16:57 | 2:25 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-1 | 2024-11-04 08:14 | 2024-11-04 15:57 | 7:43 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-1 | 2024-11-04 09:54 | 2024-11-04 16:28 | 6:34 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-1 | 2024-11-05 10:49 | 2024-11-05 16:45 | 5:56 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-1 | 2024-11-06 08:22 | 2024-11-06 16:35 | 8:13 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Julda power plant unit-1 | 2024-11-07 08:15 | 2024-11-07 13:37 | 5:22 | S/O | Maintenance work | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-1 | 2024-11-07 09:44 | 2024-11-07 16:31 | 6:47 | S/O | Due to Annual Deadline Checking | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-2 | 2024-11-09 10:03 | 2024-11-09 16:32 | 6:29 | S/O | Maintenance work | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Julda 132kV Ckt-1 | 2024-11-10 06:21 | 2024-11-10 10:52 | 4:31 | S/O | Maintenance work | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-2 | 2024-11-10 08:33 | 2024-11-10 18:02 | 9:29 | S/O | Due to Annual Deadline Checking | 0 | 0 | No interruption
Khagrachari 132/33kV Grid Sub-Station | Rangamati 132kV Ckt-1 | 2024-11-10 08:35 | 2024-11-10 16:04 | 7:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Sikalbaha 132kV Ckt-1 | 2024-11-11 07:28 | 2024-11-11 10:50 | 3:22 | S/O | Due to Dead line checking | 0 | 0 | No interruption
Khagrachari 132/132kV Grid Sub-Station | Rangamati 132kV Ckt-2 | 2024-11-11 08:23 | 2024-11-11 16:42 | 8:19 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-2 | 2024-11-11 08:50 | 2024-11-11 16:54 | 8:04 | S/O | Due to Dead line checking | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Shahmirpur 132kV Ckt-1 | 2024-11-12 07:18 | 2024-11-12 12:50 | 5:32 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-2 | 2024-11-12 08:22 | 2024-11-12 16:41 | 8:19 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Feni 132 kV Ckt-2 | 2024-11-13 08:07 | 2024-11-13 17:14 | 9:07 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-2 | 2024-11-13 09:20 | 2024-11-13 16:47 | 7:27 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | PHP 132 kV Ckt-1 | 2024-11-14 07:27 | 2024-11-14 15:30 | 8:03 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-2 | 2024-11-14 10:01 | 2024-11-14 17:23 | 7:22 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Cox'sbazar 132/33kV Grid Sub-Station | Dohazari 132 kV Ckt-2 | 2024-11-16 09:03 | 2024-11-16 17:11 | 8:08 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Sikalbaha 132kV Ckt-2 | 2024-11-16 15:57 | 2024-11-16 17:10 | 1:13 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-1 | 2024-11-17 08:32 | 2024-11-17 15:56 | 7:24 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | AKSML-1 | 2024-11-17 08:51 | 2024-11-17 15:04 | 6:13 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Baraulia Circuit-2 | 2024-11-18 07:31 | 2024-11-18 14:16 | 6:45 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Rangamati 132 kV Ckt-2 | 2024-11-18 08:38 | 2024-11-18 16:05 | 7:27 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Cox'sbazar 132/33kV Grid Sub-Station | Dohazari 132 kV Ckt-2 | 2024-11-19 10:17 | 2024-11-19 17:07 | 6:50 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Madunaghat 132kV Ckt-2 | 2024-11-20 07:35 | 2024-11-20 12:09 | 4:34 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Cox'sbazar 132/33kV Grid Sub-Station | Dohazari 132 kV Ckt-2 | 2024-11-20 08:15 | 2024-11-20 18:47 | 10:32 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Rampur 230/132kV Grid Sub-Station | Halishahar-2 | 2024-11-21 08:29 | 2024-11-21 12:43 | 4:14 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Khulshi 132kV Ckt-2 | 2024-11-21 08:30 | 2024-11-21 12:45 | 4:15 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Hathazari 230/132kV Grid Sub-Station | Kaptai 132kV Ckt-1 | 2024-11-21 09:07 | 2024-11-21 15:04 | 5:57 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Madunaghat 132kV Ckt-1 | 2024-11-22 09:03 | 2024-11-22 09:03 | 0:00 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Halishahar Ckt-3 | 2024-11-23 07:23 | 2024-11-23 07:23 | 0:00 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Cox'sbazar 132/33kV Grid Sub-Station | Dohazari 132 kV Ckt-2 | 2024-11-23 08:35 | 2024-11-23 17:20 | 8:45 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Hathazari 230/132kV Grid Sub-Station | Kaptai 132kV Ckt-2 | 2024-11-23 09:18 | 2024-11-23 13:03 | 3:45 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Cox'sbazar 132/33kV Grid Sub-Station | Dohazari 132 kV Ckt-2 | 2024-11-24 08:25 | 2024-11-24 16:58 | 8:33 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Halishahai 132/33kV Grid Sub-Station | Khulshi 132kV Ckt-1 | 2024-11-24 09:32 | 2024-11-24 13:57 | 4:25 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Rampur 230/132kV Grid Sub-Station | Halishahar-1 | 2024-11-24 09:01 | 2024-11-24 14:21 | 5:20 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Rampur 230/132kV Grid Sub-Station | Khulshi-1 | 2024-11-24 09:28 | 2024-11-24 13:50 | 4:22 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Cox'sbazar 132/33kV Grid Sub-Station | Dohazari 132 kV Ckt-2 | 2024-11-25 08:15 | 2024-11-25 16:48 | 8:33 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bakulia-132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-1 | 2024-11-26 07:40 | 2024-11-26 07:40 | 0:00 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Cox'sbazar 132/33kV Grid Sub-Station | Dohazari 132 kV Ckt-2 | 2024-11-26 08:24 | 2024-11-26 16:52 | 8:28 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bakulia-132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-2 | 2024-11-27 07:18 | 2024-11-27 07:18 | 0:00 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bakulia-132/33kV Grid Sub-Station | Sikalbaha 132 kV Ckt-2 | 2024-11-27 07:30 | 2024-11-27 07:30 | 0:00 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Cox'sbazar 132/33kV Grid Sub-Station | Dohazari 132 kV Ckt-2 | 2024-11-27 08:16 | 2024-11-27 16:00 | 7:44 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
GPH 230/132kV Grid Sub-Station | HATHAZARI-2 | 2024-11-28 06:01 | 2024-11-28 06:01 | 0:00 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bakulia-132/33kV Grid Sub-Station | Khulshi 132 kV Ckt-1 | 2024-11-28 07:43 | 2024-11-28 15:21 | 7:38 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Bakulia-132/33kV Grid Sub-Station | MSML 132 kV Ckt-2 | 2024-11-30 07:50 | 2024-11-30 07:50 | 0:00 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Hathazari 230/132kV Grid Sub-Station | Madunaghat 132kV Ckt-1 | 2024-11-30 08:24 | 2024-11-30 17:17 | 8:53 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 314:39 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj 132/33kV Grid Sub-Station | Shahjibazar 132kV Ckt-1 | 2024-11-01 08:34 | 2024-11-01 17:22 | 8:48 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Shahjibazar 132kV Ckt-1 | 2024-11-01 08:46 | 2024-11-01 17:21 | 8:35 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Kishoreganj 132kV Ckt-2 | 2024-11-02 06:10 | 2024-11-02 06:10 | 0:00 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Meghnaghat 230 kV Ckt-1 | 2024-11-02 08:20 | 2024-11-02 15:22 | 7:02 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Shahjibazar 132kV Ckt-1 | 2024-11-02 08:33 | 2024-11-02 08:33 | 0:00 | S/O | Due to 132kv GIS work | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sunamganj 132 kV Ckt-1 | 2024-11-02 09:01 | 2024-11-02 14:42 | 5:41 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/33kV Grid Sub-Station | Fenchuganj 132 kV Ckt-2 | 2024-11-02 09:10 | 2024-11-02 15:30 | 6:20 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/33kV Grid Sub-Station | Fenchuganj 132 kV Ckt-2 | 2024-11-03 08:18 | 2024-11-03 17:36 | 9:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132kV Grid Sub-Station | Shahjibazar 132kV Ckt-1 | 2024-11-03 08:30 | 2024-11-03 08:30 | 0:00 | S/O | project work | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sunamganj 132 kV Ckt-1 | 2024-11-03 09:06 | 2024-11-03 16:54 | 7:48 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sunamganj 1 | 2024-11-03 09:08 | 2024-11-03 16:53 | 7:45 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | BSRM-1 | 2024-11-03 09:14 | 2024-11-03 17:18 | 8:04 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Narsinghdi 132 kV Ckt-1 | 2024-11-03 10:34 | 2024-11-03 20:19 | 9:45 | S/O | Due to NLDC work | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Meghnaghat 230 kV Ckt-1 | 2024-11-04 08:30 | 2024-11-04 16:40 | 8:10 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Shahjibazar 132kV Ckt-1 | 2024-11-04 08:57 | 2024-11-04 16:55 | 7:58 | S/O | project work | 0 | 0 | No interruption
BSRM 230/132kV Grid Sub-Station | Cumilla(N) 230 kV Ckt-1 | 2024-11-04 08:59 | 2024-11-04 19:42 | 10:43 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sunamganj 132 kV Ckt-1 | 2024-11-04 09:16 | 2024-11-04 16:54 | 7:38 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sunamganj 132 kV Ckt-1 | 2024-11-04 09:17 | 2024-11-04 16:53 | 7:36 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Meghnaghat 230 kV Ckt-2 | 2024-11-05 08:24 | 2024-11-05 20:14 | 11:50 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132kV Grid Sub-Station | Brahmanbaria 132kV Ckt-1 | 2024-11-05 08:30 | 2024-11-05 08:30 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-90MW | 2024-11-05 08:31 | 2024-11-05 16:27 | 7:56 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
BSRM 230/132kV Grid Sub-Station | Cumilla(N) 230 kV Ckt-1 | 2024-11-05 08:57 | 2024-11-05 20:24 | 11:27 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/33kV Grid Sub-Station | Fenchuganj 132 kV Ckt-4 | 2024-11-05 08:58 | 2024-11-05 17:15 | 8:17 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
BSRM 230/132kV Grid Sub-Station | Cumilla(N) 230 kV Ckt-1 | 2024-11-05 09:07 | 2024-11-05 09:07 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Brahmanbaria 132kV Ckt-1 | 2024-11-06 08:37 | 2024-11-06 16:39 | 8:02 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Meghnaghat 230 kV Ckt-2 | 2024-11-06 09:07 | 2024-11-06 09:07 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Meghnaghat 230 kV Ckt-2 | 2024-11-07 08:29 | 2024-11-07 17:21 | 8:52 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Brahmanbaria 132kV Ckt-1 | 2024-11-07 08:57 | 2024-11-07 16:18 | 7:21 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-90MW P/S | 2024-11-07 08:59 | 2024-11-07 12:24 | 3:25 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
BSRM 230/132kV Grid Sub-Station | Cumilla(N) 230 kV Ckt-2 | 2024-11-07 09:32 | 2024-11-07 17:05 | 7:33 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
BSRM 230/132kV Grid Sub-Station | Cumilla(N) 230 kV Ckt-2 | 2024-11-09 08:47 | 2024-11-09 16:13 | 7:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132kV Grid Sub-Station | Brahmanbaria 132kV Ckt-2 | 2024-11-09 09:09 | 2024-11-09 09:09 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Beanibazar 132/33kV Grid Sub-Station | Sylhet-132kV Ckt-1 | 2024-11-09 09:10 | 2024-11-09 16:36 | 7:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/33kV Grid Sub-Station | Sylhet (T at Bianibazar) 132kV Ckt-2 | 2024-11-09 09:53 | 2024-11-09 09:53 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 132/33kV Grid Sub-Station | Brahmanbaria 132kV Ckt-2 | 2024-11-10 08:45 | 2024-11-10 12:29 | 3:44 | S/O | Due to As per instruction of NLDC | 0 | 0 | No interruption
BSRM 230/132kV Grid Sub-Station | Cumilla(N) 230 kV Ckt-2 | 2024-11-10 09:17 | 2024-11-10 09:17 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132kV Grid Sub-Station | Brahmanbaria 132kV Ckt-2 | 2024-11-11 08:57 | 2024-11-11 14:47 | 5:50 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Beanibazar 132/33kV Grid Sub-Station | Sylhet132kV Ckt-1 | 2024-11-11 09:25 | 2024-11-11 16:06 | 6:41 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
BSRM 230/132kV Grid Sub-Station | Cumilla(N) 230 kV Ckt-2 | 2024-11-11 09:27 | 2024-11-11 09:27 | 0:00 | S/O | Due to Deadline Checking | 0 | 0 | No interruption
BSRM 230/132kV Grid Sub-Station | Mirsharai 230 kV Ckt-2 | 2024-11-12 07:26 | 2024-11-12 07:26 | 0:00 | S/O | project work | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sylhet 132 kV Ckt-2 | 2024-11-12 08:20 | 2024-11-12 17:09 | 8:49 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Kulaura 132 kV Ckt-1 | 2024-11-12 08:35 | 2024-11-12 17:12 | 8:37 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Shahmirpur-2 | 2024-11-13 07:29 | 2024-11-13 07:29 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sylhet 132 kV Ckt-2 | 2024-11-13 08:21 | 2024-11-13 14:52 | 6:31 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 132/33kV Grid Sub-Station | Kulaura 132 kV Ckt-1 | 2024-11-13 08:38 | 2024-11-13 17:04 | 8:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Ashuganj-1 | 2024-11-13 09:31 | 2024-11-13 19:20 | 9:49 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18 | 0:12 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sylhet 132 kV Ckt-2 | 2024-11-14 08:22 | 2024-11-14 14:51 | 6:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Kulaura 132 kV Ckt-1 | 2024-11-14 09:02 | 2024-11-14 16:49 | 7:47 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Kachua 132kV Ckt-1 & 2 | 2024-11-15 07:36 | 2024-11-15 17:04 | 9:28 | S/O | project work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Kachua 132 kV Ckt-1 | 2024-11-15 07:45 | 2024-11-15 16:49 | 9:04 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Kachua 132kV Ckt-1 | 2024-11-16 08:14 | 2024-11-16 13:45 | 5:31 | S/O | project work | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Kachua 132kV Ckt-2 | 2024-11-16 08:14 | 2024-11-16 13:46 | 5:32 | S/O | project work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Kachua 132 kV Ckt-1 | 2024-11-16 08:21 | 2024-11-16 13:36 | 5:15 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Kachua 132 kV Ckt-2 | 2024-11-16 08:33 | 2024-11-16 13:46 | 5:13 | S/O | project work | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sreemangal 132kV Ckt-1 | 2024-11-16 08:46 | 2024-11-16 16:30 | 7:44 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sreemangal 132kV Ckt-1 | 2024-11-17 08:38 | 2024-11-17 15:44 | 7:06 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Ashuganj-1 | 2024-11-17 09:07 | 2024-11-17 17:33 | 8:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sylhet (T at Bianibazar) 132kV Ckt-2 | 2024-11-17 11:23 | 2024-11-17 15:30 | 4:07 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sreemangal 132kV Ckt-1 | 2024-11-18 08:50 | 2024-11-18 16:19 | 7:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sylhet (T at Bianibazar) 132kV Ckt-2 | 2024-11-18 09:29 | 2024-11-18 14:09 | 4:40 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sreemangal 132kV Ckt-2 | 2024-11-19 08:38 | 2024-11-19 16:43 | 8:05 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sunamgonj CKT-2 | 2024-11-19 08:46 | 2024-11-19 16:59 | 8:13 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Ashuganj-2 | 2024-11-19 08:51 | 2024-11-19 16:29 | 7:38 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Ashuganj-2 | 2024-11-20 08:40 | 2024-11-20 16:38 | 7:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chattak 132/33kV Grid Sub-Station | Sunamgonj CKT-2 | 2024-11-21 08:43 | 2024-11-21 16:12 | 7:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sreemangal 132kV Ckt-2 | 2024-11-21 08:48 | 2024-11-21 16:37 | 7:49 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sylhet-132kV Ckt-1 | 2024-11-23 08:30 | 2024-11-23 16:56 | 8:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Kulaura 132 kV Ckt-2 | 2024-11-23 08:55 | 2024-11-23 20:08 | 11:13 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Daudkandi 132 kV Ckt-1 | 2024-11-23 09:32 | 2024-11-23 14:56 | 5:24 | S/O | Project work | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-2 | 2024-11-23 09:34 | 2024-11-23 17:47 | 8:13 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Daudkandi 132 kV Ckt-2 | 2024-11-23 14:57 | 2024-11-23 17:12 | 2:15 | S/O | Project work | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Kachua 132 kV Ckt-1 | 2024-11-24 08:41 | 2024-11-24 15:49 | 7:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Kulaura 132 kV Ckt-2 | 2024-11-24 09:08 | 2024-11-24 20:08 | 11:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Kachua 132 kV Ckt-1 | 2024-11-25 08:20 | 2024-11-25 16:14 | 7:54 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sylhet 132kV Ckt-1 | 2024-11-25 08:32 | 2024-11-25 16:23 | 7:51 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Kachua 132 kV Ckt-2 | 2024-11-25 08:48 | 2024-11-25 16:14 | 7:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Kulaura 132 kV Ckt-2 | 2024-11-25 08:50 | 2024-11-25 17:08 | 8:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Tripura Ckt-2 | 2024-11-27 17:14 | 2024-11-27 18:16 | 1:02 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Daudkandi 132 kV Ckt-2 | 2024-11-28 06:52 | 2024-11-28 06:52 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Cumilla(N) 230/132kV Grid Sub-Station | Daudkandi 132 kV Ckt-1 & 2 | 2024-11-28 06:52 | 2024-11-28 06:52 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Fenchuganj 230/132kV Grid Sub-Station | Sreemangal 132kV Ckt-1 | 2024-11-30 08:23 | 2024-11-30 15:50 | 7:27 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 504:05 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Mongla 132 kV Ckt-1 | 2024-11-02 08:16 | 2024-11-02 16:56 | 8:40 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-11-03 08:51 | 2024-11-03 17:14 | 8:23 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-2 | 2024-11-03 08:53 | 2024-11-03 17:16 | 8:23 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Mongla 132 kV Ckt-1 | 2024-11-03 08:54 | 2024-11-03 14:49 | 5:55 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-11-04 09:05 | 2024-11-04 17:26 | 8:21 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-2 | 2024-11-04 09:06 | 2024-11-04 17:27 | 8:21 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Mongla 132 kV Ckt-1 | 2024-11-04 09:10 | 2024-11-04 16:22 | 7:12 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-11-05 08:59 | 2024-11-05 15:50 | 6:51 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-2 | 2024-11-05 09:00 | 2024-11-05 15:51 | 6:51 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Mongla 132 kV Ckt-2 | 2024-11-05 09:02 | 2024-11-05 15:53 | 6:51 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-11-06 08:30 | 2024-11-06 15:02 | 6:32 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Mongla 132 kV Ckt-2 | 2024-11-07 08:23 | 2024-11-07 17:55 | 9:32 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-11-07 09:02 | 2024-11-07 15:31 | 6:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-2 | 2024-11-07 09:02 | 2024-11-07 15:32 | 6:30 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-11-09 08:52 | 2024-11-09 15:00 | 6:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Gopalganj(N) 132 kV Ckt-2 | 2024-11-12 13:48 | 2024-11-12 18:01 | 4:13 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | 100MW ERBL Solar PS | 2024-11-16 08:10 | 2024-11-16 13:40 | 5:30 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | UPPL (150MW) 132kV LINE | 2024-11-16 08:21 | 2024-11-16 15:56 | 7:35 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | (Barguna T at Bakergonj) 132 kV Ckt | 2024-11-16 08:23 | 2024-11-16 14:42 | 6:19 | S/O | Due to Annual Maintenance work. | 6 | 37.9 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Mongla 132 kV Ckt-1 | 2024-11-16 08:32 | 2024-11-16 13:38 | 5:06 | S/O | Due to Annual Maintenance work. | 5 | 25.5 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Mongla 132 kV Ckt-2 | 2024-11-16 08:32 | 2024-11-16 13:38 | 5:06 | S/O | Due to Annual Maintenance work. | 20 | 102 | Power interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-11-16 08:47 | 2024-11-16 15:33 | 6:46 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | Rampal Ckt-2 | 2024-11-16 08:41 | 2024-11-16 18:14 | 9:33 | S/O | Due to Annual maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | Payra 132kV Ckt-2 | 2024-11-16 08:56 | 2024-11-16 14:41 | 5:45 | S/O | Due to Annual maintenance | 17 | 97.75 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | Payra 132kV Ckt-1 | 2024-11-16 08:56 | 2024-11-16 14:40 | 5:44 | S/O | Due to Annual maintenance | 17 | 97.4667 | Power interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | Rampal Ckt-2 | 2024-11-17 08:19 | 2024-11-17 16:10 | 7:51 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-11-17 08:22 | 2024-11-17 15:50 | 7:28 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | (Barguna T at Bakergonj) 132 kV Ckt | 2024-11-17 09:00 | 2024-11-17 13:52 | 4:52 | S/O | Due to PT terminal disconnect. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2024-11-17 09:42 | 2024-11-17 09:42 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj 100 MW PS | 2024-11-17 11:05 | 2024-11-17 17:34 | 6:29 | S/O | Due to BCU faulty relay change | 0 | 0 | No interruption
Barisha 132/33kV Grid Sub-Station | 132 kv Summit power | 2024-11-18 06:19 | 2024-11-18 16:48 | 10:29 | S/O | Maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-11-18 08:30 | 2024-11-18 16:37 | 8:07 | S/O | Maintenance work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2024-11-18 09:34 | 2024-11-18 16:12 | 6:38 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj 100 MW PS | 2024-11-18 10:34 | 2024-11-18 15:54 | 5:20 | S/O | Project work | 0 | 0 | No interruption
Barisha 132/33kV Grid Sub-Station | Bhandaria 132 kV Ckt-1 | 2024-11-19 06:04 | 2024-11-19 13:49 | 7:45 | S/O | Maintenance work | 25 | 193.75 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Bhandaria 132 kV Ckt-1 | 2024-11-19 06:10 | 2024-11-19 13:53 | 7:43 | S/O | Project work | 25 | 192.9167 | Power interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | Rampal Ckt-1 | 2024-11-19 08:12 | 2024-11-19 15:28 | 7:16 | S/O | Maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-2 | 2024-11-19 09:50 | 2024-11-19 16:39 | 6:49 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj 100 MW PS | 2024-11-19 10:24 | 2024-11-19 18:07 | 7:43 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | Rampal Ckt-1 | 2024-11-20 08:33 | 2024-11-20 15:32 | 6:59 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj 100 MW PS | 2024-11-21 10:57 | 2024-11-21 10:57 | 0:00 | S/O | Due to NLDC testing for PDB 100 MW PS | 0 | 0 | No interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | Rampal Ckt-1 | 2024-11-21 07:54 | 2024-11-21 16:33 | 8:39 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Narail 132kV Ckt-1 | 2024-11-21 08:13 | 2024-11-21 16:30 | 8:17 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-2 | 2024-11-21 08:35 | 2024-11-21 14:46 | 6:11 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-2 | 2024-11-21 09:16 | 2024-11-21 12:45 | 3:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-1 | 2024-11-21 14:35 | 2024-11-21 16:40 | 2:05 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rampal 400/132kV Grid Sub-Station | Gopalganj Line-1 | 2024-11-21 14:36 | 2024-11-21 15:17 | 0:41 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj(N) 400/132kV Grid Sub-Station | Rampal Ckt-1 | 2024-11-21 14:37 | 2024-11-21 16:39 | 2:02 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Khulna (C) 132kV Ckt-1 | 2024-11-23 08:34 | 2024-11-23 15:09 | 6:35 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj(N) 400/132kV Grid Sub-Station | Gopalgan (N) Ckt-1 | 2024-11-24 08:44 | 2024-11-24 16:13 | 7:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Khulna (C) 132kV Ckt-1 | 2024-11-24 09:46 | 2024-11-24 15:36 | 5:50 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Khulna(S) 230/ 132/33kV Grid Sub-Station | Khulna (C) 132kV Ckt-1 | 2024-11-25 08:24 | 2024-11-25 15:50 | 7:26 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Khulna(C) 230/ 132/33kV Grid Sub-Station | Khulna (S) 132kV Ckt-1 | 2024-11-25 08:40 | 2024-11-25 15:50 | 7:10 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj (O) 132/33kV Grid Sub-Station | Gopalgan (N) Ckt-1 | 2024-11-25 08:42 | 2024-11-25 16:21 | 7:39 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj (O) 132/33kV Grid Sub-Station | Gopalgan (N) Ckt-2 | 2024-11-25 08:43 | 2024-11-25 16:22 | 7:39 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj (O) 132/33kV Grid Sub-Station | Gopalgan (N) Ckt-1 | 2024-11-26 08:20 | 2024-11-26 17:29 | 9:09 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj (O) 132/33kV Grid Sub-Station | Gopalgan (N) Ckt-2 | 2024-11-26 08:21 | 2024-11-26 17:29 | 9:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Khulna(C) 230/ 132/33kV Grid Sub-Station | Khulna (S) 132kV Ckt-1 | 2024-11-26 08:38 | 2024-11-26 14:40 | 6:02 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj(N) 400/132kV Grid Sub-Station | Gopalgan (N) Ckt-1 | 2024-11-27 08:15 | 2024-11-27 17:11 | 8:56 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Khulna(C) 230/ 132/33kV Grid Sub-Station | Khulna (S) 132kV Ckt-2 | 2024-11-27 08:30 | 2024-11-27 14:30 | 6:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Khulna(C) 230/ 132/33kV Grid Sub-Station | Khulna (S) 132kV Ckt-2 | 2024-11-28 08:13 | 2024-11-28 14:26 | 6:13 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | Gopalganj(N) 132kV Ckt-2 | 2024-11-28 08:56 | 2024-11-28 17:00 | 8:04 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Patuakhali-1 | 2024-11-28 10:07 | 2024-11-28 12:54 | 2:47 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barishal 230132kV Grid Sub-Station | Barishal(N) 132 kV Ckt-1 | 2024-11-30 08:15 | 2024-11-30 16:50 | 8:35 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | Gopalganj(N) 132kV Ckt-2 | 2024-11-30 08:23 | 2024-11-30 18:08 | 9:45 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Gopalganj (O) 132/33kV Grid Sub-Station | Gopalganj 100 MW PS | 2024-11-30 14:42 | 2024-11-30 16:24 | 1:42 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kv Summit power | 2024-11-30 15:33 | 2024-11-30 16:48 | 1:15 | S/O | Due to SF6 Gas leakage repair. | 0 | 0 | No interruption
|  |  | Total : | 432:53 |  | Unserved Energy: |  | 747.2833
HVDC Grid Circle :
HVDC Bheramera | Jhenaidah 230kV Ckt-1 | 2024-11-02 08:19 | 2024-11-02 18:11 | 9:52 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-2 | 2024-11-03 08:53 | 2024-11-03 17:18 | 8:25 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-21 | 2024-11-03 08:54 | 2024-11-03 17:16 | 8:22 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | Ullahpara 132kV Ckt-1 | 2024-11-05 07:44 | 2024-11-05 07:44 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-1 | 2024-11-05 09:07 | 2024-11-05 15:50 | 6:43 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-2 | 2024-11-05 09:08 | 2024-11-05 15:50 | 6:42 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Jhenaidah 230kV Ckt-2 | 2024-11-05 09:13 | 2024-11-05 16:47 | 7:34 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
HVDC Bheramera | Jhenaidah 230kV Ckt-2 | 2024-11-05 09:37 | 2024-11-05 16:47 | 7:10 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Jhenaidah New-2 | 2024-11-05 09:41 | 2024-11-05 12:01 | 2:20 | S/O | Project work | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (Old) Ckt-2 | 2024-11-05 09:42 | 2024-11-05 12:01 | 2:19 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-2 | 2024-11-06 08:40 | 2024-11-06 15:05 | 6:25 | S/O | Maintenance work | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-1 | 2024-11-06 08:40 | 2024-11-06 15:05 | 6:25 | S/O | Maintenance work | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-1 | 2024-11-07 09:03 | 2024-11-07 15:31 | 6:28 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-2 | 2024-11-07 09:03 | 2024-11-07 15:32 | 6:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2024-11-08 18:52 | 2024-11-08 22:45 | 3:53 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ishwardi- 132/33kV Grid Sub-Station | Rooppur 132kV Ckt-1 | 2024-11-09 08:30 | 2024-11-09 16:32 | 8:02 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Khulna 230kV Ckt-1 | 2024-11-09 08:53 | 2024-11-09 15:54 | 7:01 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Khulna 230kV Ckt-1 | 2024-11-10 08:12 | 2024-11-10 17:20 | 9:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ishwardi- 132/33kV Grid Sub-Station | Rooppur132kV Ckt-1 | 2024-11-10 08:20 | 2024-11-10 16:08 | 7:48 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ishwardi- 132/33kV Grid Sub-Station | Rooppur 132kV Ckt-1 | 2024-11-11 08:00 | 2024-11-11 16:25 | 8:25 | S/O | Maintenance work | 0 | 0 | No interruption
Ishwardi- 132/33kV Grid Sub-Station | Rooppur132kV Ckt-2 | 2024-11-11 08:13 | 2024-11-11 16:42 | 8:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Khulna 230kV Ckt-1 | 2024-11-11 08:20 | 2024-11-11 16:08 | 7:48 | S/O | Due to As per ALDC order. | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Khulna 230kV Ckt-2 | 2024-11-12 08:28 | 2024-11-12 16:01 | 7:33 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Shahjadpur 132 kV Ckt-2 | 2024-11-13 07:40 | 2024-11-13 07:40 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Khulna 230kV Ckt-2 | 2024-11-13 08:12 | 2024-11-13 16:02 | 7:50 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Khulna 230kV Ckt-2 | 2024-11-14 08:09 | 2024-11-14 16:01 | 7:52 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Shahjadpur 132kV Ckt-1 | 2024-11-16 07:24 | 2024-11-16 16:38 | 9:14 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah(New) 132kV Ckt-3 | 2024-11-16 07:37 | 2024-11-16 15:20 | 7:43 | S/O | Project work | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-1 | 2024-11-16 08:48 | 2024-11-16 15:31 | 6:43 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Shahjadpur 132kV Ckt-1 | 2024-11-17 07:45 | 2024-11-17 19:21 | 11:36 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara P/S | Faridpur 132 kV Ckt-1 | 2024-11-17 08:22 | 2024-11-17 15:50 | 7:28 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Sirajganj 230 kV Ckt-2 | 2024-11-18 13:08 | 2024-11-18 16:32 | 3:24 | S/O | Project work | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Ishurdi 230 kV Ckt-1 | 2024-11-19 08:34 | 2024-11-19 17:03 | 8:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-2 | 2024-11-20 08:20 | 2024-11-20 15:05 | 6:45 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Faridpur 132 kV Ckt-2 | 2024-11-21 08:35 | 2024-11-21 14:46 | 6:11 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara P/S | Kustia 132 kV Ckt-1 | 2024-11-23 08:17 | 2024-11-23 14:33 | 6:16 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Ishurdi 230 kV Ckt-2 | 2024-11-23 08:20 | 2024-11-23 16:21 | 8:01 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Shahjadpur 132 kV Ckt-1 | 2024-11-24 07:38 | 2024-11-24 17:35 | 9:57 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bheramara P/S | Kustia 132 kV Ckt-2 | 2024-11-26 08:14 | 2024-11-26 15:16 | 7:02 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-2(L1) | 2024-11-29 06:47 | 2024-11-29 06:47 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jashore Ckt-2 | 2024-11-29 06:48 | 2024-11-29 06:48 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Ishwardi- 132/33kV Grid Sub-Station | Natore 132kV Ckt-2 | 2024-11-29 09:06 | 2024-11-29 12:04 | 2:58 | S/O | Due to request by ALDC bogura | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | HVDC Bheramara 230 kV Ckt-1 | 2024-11-30 09:27 | 2024-11-30 13:34 | 4:07 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 274:57 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Sherpur(Bogura) 132/33kV Grid Sub-Station | Sirajgonj 132 kV Ckt-1 | 2024-11-01 08:04 | 2024-11-01 18:28 | 10:24 | S/O | Project work | 0 | 0 | No interruption
Sherpur(Bogura) 132/33kV Grid Sub-Station | Sirajgonj 132 kV Ckt-2 | 2024-11-01 08:05 | 2024-11-01 18:28 | 10:23 | S/O | Project work | 0 | 0 | No interruption
Barapukuria 230/132kV Grid Sub-Station | Bogura 230 kV Ckt-2 | 2024-11-01 15:53 | 2024-11-01 15:53 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Naogaon Ckt.-2 | 2024-11-02 06:12 | 2024-11-02 06:31 | 0:19 | S/O | Project work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Niyamatpur 132kV Ckt-1 | 2024-11-02 06:14 | 2024-11-02 06:14 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-1 | 2024-11-02 06:22 | 2024-11-02 13:54 | 7:32 | S/O | Project work | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-2 | 2024-11-02 06:22 | 2024-11-02 13:56 | 7:34 | S/O | Project work | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-1 | 2024-11-02 08:18 | 2024-11-02 16:15 | 7:57 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | 50MW RPP | 2024-11-02 08:26 | 2024-11-02 18:07 | 9:41 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | 100MW PPP | 2024-11-02 09:52 | 2024-11-02 16:13 | 6:21 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-1 | 2024-11-03 07:48 | 2024-11-03 16:10 | 8:22 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullahpara 132KV Ckt-1 | 2024-11-04 06:54 | 2024-11-04 16:12 | 9:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullahpara 132KV Ckt-2 | 2024-11-04 06:55 | 2024-11-04 16:13 | 9:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-2 | 2024-11-05 08:17 | 2024-11-05 17:32 | 9:15 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(new) 230/132/33kV Grid Sub-Station | Bogura(Sherpur) 132 kV Ckt-1 | 2024-11-06 08:07 | 2024-11-06 15:34 | 7:27 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi 132kV Ckt-1 | 2024-11-06 08:15 | 2024-11-06 18:24 | 10:09 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-2 | 2024-11-06 08:18 | 2024-11-06 16:27 | 8:09 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi 132kV Ckt-1 | 2024-11-07 08:15 | 2024-11-07 18:01 | 9:46 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-2 | 2024-11-07 08:25 | 2024-11-07 15:53 | 7:28 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 kV Ckt-2 | 2024-11-09 07:21 | 2024-11-09 19:42 | 12:21 | S/O | Project work | 0 | 0 | No interruption
Bogura(new) 230/132/33kV Grid Sub-Station | Bogura(Sherpur) 132 kV Ckt-2 | 2024-11-09 08:07 | 2024-11-09 16:23 | 8:16 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi 132kV Ckt-2 | 2024-11-09 08:16 | 2024-11-09 16:58 | 8:42 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(new) 132/33kV Grid Sub-Station | Bogura(Sherpur) 132 kV Ckt-2 | 2024-11-10 07:56 | 2024-11-10 17:04 | 9:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mithapukur132/33kV Grid Sub-Station | Rangpur Confidence( 100MW ) 132kV Ckt-1 | 2024-11-11 09:28 | 2024-11-11 16:25 | 6:57 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(Sherpur) 132/33kV Grid Sub-Station | Sirajgonj 132 kV Ckt-1 | 2024-11-12 08:15 | 2024-11-12 15:48 | 7:33 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur Confidence( 100MW ) 132kV Ckt-1 | 2024-11-12 09:24 | 2024-11-12 16:32 | 7:08 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV PPP 50 Mw | 2024-11-13 08:13 | 2024-11-13 16:14 | 8:01 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Sherpur(Bogura) 132/33kV Grid Sub-Station | Sirajgonj 132 kV Ckt-1 | 2024-11-13 08:18 | 2024-11-13 16:42 | 8:24 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(new) 230/132/33kV Grid Sub-Station | Naogaon 132 kV Ckt-1 | 2024-11-13 08:21 | 2024-11-13 08:21 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mithapukur132/33kV Grid Sub-Station | Rangpur Confidence( 100MW ) 132kV Ckt-2 | 2024-11-13 09:25 | 2024-11-13 16:25 | 7:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(new) 230/132/33kV Grid Sub-Station | Naogaon 132 kV Ckt-2 | 2024-11-13 10:38 | 2024-11-13 10:38 | 0:00 | S/O | Due to developing work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV PPP 50 Mw | 2024-11-14 08:24 | 2024-11-14 16:14 | 7:50 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(new) 230/132/33kV Grid Sub-Station | Rangpur 132 kV Ckt-2 | 2024-11-15 06:14 | 2024-11-15 06:14 | 0:00 | S/O | Due to Conductor stringing | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Saidpur 132 kV Ckt-1 | 2024-11-15 06:22 | 2024-11-15 15:49 | 9:27 | S/O | Project work | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Naogaon Ckt.-2 | 2024-11-16 08:07 | 2024-11-16 15:34 | 7:27 | S/O | Due to Annual Maintenance work. | 15 | 111.75 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Naogaon 132kV Ckt-1 | 2024-11-16 08:12 | 2024-11-16 15:33 | 7:21 | S/O | Due to Annual Maintenance work. | 30 | 220.5 | Power interruption
Chapainawabganj 132/33kV Grid Sub-Station | Rahanpur 132kV Ckt-1 | 2024-11-16 08:21 | 2024-11-16 15:01 | 6:40 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-1 | 2024-11-16 08:49 | 2024-11-16 15:04 | 6:15 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Chapainawabganj 132/33kV Grid Sub-Station | Rahanpur 132kV Ckt-1 | 2024-11-17 08:19 | 2024-11-17 14:51 | 6:32 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Sherpur(Bogura) 132/33kV Grid Sub-Station | Sirajgonj 132 kV Ckt-2 | 2024-11-17 08:33 | 2024-11-17 16:19 | 7:46 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-1 | 2024-11-17 08:33 | 2024-11-17 16:06 | 7:33 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Sherpur(Bogura) 132/33kV Grid Sub-Station | Sirajgonj 132 kV Ckt-2 | 2024-11-18 08:35 | 2024-11-18 14:23 | 5:48 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-1 | 2024-11-18 08:40 | 2024-11-18 15:40 | 7:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Naogaon ckt-2 | 2024-11-18 08:53 | 2024-11-18 08:53 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Mahasthangar 132/33kV Grid Sub-Station | Palashbari 132kV Ckt-2 | 2024-11-18 14:35 | 2024-11-18 15:17 | 0:42 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 kV Ckt-2 & 1 | 2024-11-19 06:59 | 2024-11-19 15:40 | 8:41 | S/O | Project work | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 2 | 2024-11-19 08:20 | 2024-11-19 15:43 | 7:23 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rahanpur 400/132/kV Grid Sub-Station | Chapainawabganj 132 KV Line Ckt-02 | 2024-11-19 08:23 | 2024-11-19 15:45 | 7:22 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-2 | 2024-11-19 08:38 | 2024-11-19 16:23 | 7:45 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajshahi- 230/132/33kV Grid Sub-Station | Rajshahi(New) 132kV Ckt-1 | 2024-11-20 08:11 | 2024-11-20 16:09 | 7:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-2 | 2024-11-20 09:04 | 2024-11-20 15:52 | 6:48 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Rajshahi(New) 132kV Ckt-1 | 2024-11-21 08:21 | 2024-11-21 17:48 | 9:27 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur 132kV Ckt-2 | 2024-11-21 08:48 | 2024-11-21 15:54 | 7:06 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 kV Ckt-1 | 2024-11-23 08:04 | 2024-11-23 12:14 | 4:10 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 kV Ckt-2 | 2024-11-23 08:04 | 2024-11-23 12:20 | 4:16 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 kV Ckt-2 | 2024-11-23 08:28 | 2024-11-23 12:16 | 3:48 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Rajshahi(New) 132kV Ckt-1 | 2024-11-23 08:40 | 2024-11-23 16:33 | 7:53 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon-EPV 132kV Ckt-1 | 2024-11-23 08:56 | 2024-11-23 16:55 | 7:59 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 2024-11-23 09:10 | 2024-11-23 14:32 | 5:22 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(new) 230/132/33kV Grid Sub-Station | Naogaon 132 kV Ckt-1 | 2024-11-24 07:45 | 2024-11-24 07:45 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon-EPV 132kV Ckt-1 | 2024-11-24 08:56 | 2024-11-24 16:10 | 7:14 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon-EPV 132kV Ckt-1 | 2024-11-24 09:10 | 2024-11-24 16:05 | 6:55 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(new) 230/132/33kV Grid Sub-Station | Naogaon 132 kV Ckt-1 | 2024-11-25 08:14 | 2024-11-25 14:32 | 6:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 kV Ckt-1 | 2024-11-25 09:03 | 2024-11-25 16:50 | 7:47 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon-EPV 132kV Ckt-1 | 2024-11-25 09:10 | 2024-11-25 17:08 | 7:58 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(new) 230/132/33kV Grid Sub-Station | Naogaon 132 kV Ckt-2 | 2024-11-26 08:17 | 2024-11-26 16:51 | 8:34 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 kV Ckt-1 | 2024-11-26 08:37 | 2024-11-26 16:00 | 7:23 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon-EPV 132kV Ckt-2 | 2024-11-26 08:57 | 2024-11-26 16:59 | 8:02 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon-EPV 132kV Ckt-2 | 2024-11-26 09:10 | 2024-11-26 16:57 | 7:47 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(new) 230/132/33kV Grid Sub-Station | Naogaon 132 kV Ckt-2 | 2024-11-27 07:56 | 2024-11-27 07:56 | 0:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon-EPV 132kV Ckt-2 | 2024-11-27 09:08 | 2024-11-27 16:26 | 7:18 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 kV Ckt-1 | 2024-11-27 09:08 | 2024-11-27 16:48 | 7:40 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon-EPV 132kV Ckt-1 | 2024-11-28 07:50 | 2024-11-29 11:30 | 27:40 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 kV Ckt-2 | 2024-11-28 08:42 | 2024-11-28 16:58 | 8:16 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 kV Ckt-2 | 2024-11-30 08:50 | 2024-11-30 16:40 | 7:50 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-SPPP Ckt-1 | 2024-11-30 09:10 | 2024-11-30 17:04 | 7:54 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi 132kV Ckt-1 | 2024-11-30 09:26 | 2024-11-30 14:37 | 5:11 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Bogura(new) 230/132/33kV Grid Sub-Station | Bogura (W) CKT-1 | 2024-11-30 10:54 | 2024-11-30 12:23 | 1:29 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi 132kV Ckt-2 | 2024-11-30 14:51 | 2024-11-30 15:51 | 1:00 | S/O | Due to Annual Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 541:28 |  | Unserved Energy: |  | 332.25
Others :Nil
No interruption
|  |  | Total : | 0:00 |  |  |  | 0:00
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 3041:43 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:November 2024
| Area | Previous Month (October' 2024) |  |  |  | Current Month (November '2024)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 19 | 14 | 118 | 151 | 7 | 9 | 218 | 234
2 | Dhaka (South) Grid Circle. | 19 | 18 | 35 | 72 | 24 | 17 | 120 | 161
3 | Chattogram Grid Circle. | - | 9 | 65 | 74 | - | 2 | 68 | 70
4 | Cumilla Grid Circle. | 7 | 6 | 64 | 77 | 7 | 7 | 149 | 163
5 | Khulna Grid Circle. | 13 | 2 | 107 | 122 | 8 | 9 | 171 | 188
6 | HVDC Grid Circle | 7 | 3 | 20 | 30 | 1 | 7 | 76 | 84
7 | Bogura Grid Circle. | 10 | 6 | 77 | 93 | 7 | 4 | 163 | 174
8 | Others | bar: Total number of T to Total number of S/O
9 | Total | 75 | 58 | 487 | 620 | 54 | 55 | 965 | 1074
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:November 2024
| Area | Previous Month (October' 2024) |  |  |  | Current Month (November '2024)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 157.12 | 733.83 | 301.32 | 1192.27 | 22.38 | 16.15 | 1001.6 | 1040.13
2 | Dhaka (South) Grid Circle. | 1107.65 | 661.67 | 375.4 | 2144.72 | 97.42 | 103.34 | 249.58 | 450.34
3 | Chattogram Grid Circle. | 100.93 | 92.22 | 118.05 | 311.2 | - | - | 719 | 719
4 | Cumilla Grid Circle. | 319.92 | 57.33 | 540.03 | 917.28 | 10 | 133.35 | 470.65 | 614
5 | Khulna Grid Circle. | 114.01 | 119 | 807.2 | 1040.21 | 61.64 | 76.2 | 3130.88 | 3268.72
6 | HVDC Grid Circle | 31.17 | 55.27 | 12.33 | 98.77 | 14.5 | - | 284.07 | 298.57
7 | Bogura Grid Circle. | 55.8 | 280.01 | 233.27 | 569.08 | 11.17 | - | 659.92 | 671.09
8 | Others | - | - | - | 0 | - | - | - | 0
9 | Total | 1886.6 | 1999.33 | 2387.6 | 6273.53 | 217.11 | 329.04 | 6515.7 | 7061.85
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:November 2024
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 3 | 9 | 12 | 3 | 1 | 8 | 1025.5
2 | Dhaka (South) | 5031.6 | 3 | 2 | 5 | 1 | 2 | 2 | 337.71
3 | Chattogram | 2042 | - | 4 | 4 | - | - | 4 | 719
4 | Khulna | 2434 | 7 | 15 | 22 | 4 | 2 | 16 | 2521.45
5 | HVDC | 5954.3 | 1 | 3 | 4 | 1 | - | 3 | 298.57
6 | Bogura | 3145.6 | 2 | 3 | 5 | 2 | - | 3 | 338.84
7 | Cumilla | 2981 | 5 | 10 | 15 | 2 | - | 13 | 614
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 5855.07
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 100%
4 | Khulna | 99.98%
5 | HVDC | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.98% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:November 2024
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 |  | 2 | 2 | - | 1 | 14.63
2 | Dhaka (South) | 990.29 | - | 5 | - | 5 | 4 | 1 | - | 112.62
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | - | 7 | 7 | - | - | 7 | 747.28
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | - | 2 | 2 | - | - | 2 | 332.25
7 | Cumilla | 1648.16 | - | - | - | - | - | - | - | -
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 1206.78
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 100%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 100%
7 | Cumilla | 100% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:November 2024
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2024-11-01 | 7 | - | - | - | 1 | 20 min | - | - |  |  | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:November 2024
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Mirzapur 132/33kV Grid Sub-Station | 3 | 1:27 | 23.9
Mirpur 132/33kV Grid Sub-Station | 1 | 0:03 | 3.3
Bhaluka 132/33kV Grid Sub-Station | 1 | 0:10 | 11.3333
Kodda 132/33kV Grid Sub-Station | 1 | 1:16 | 31.6667
Kishoreganj 132/33kV Grid Sub-Station | 2 | 6:39 | 205.6
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:36 | 16
Kabirpur 132/33kV Grid Sub-Station | 2 | 3:09 | 221.58
Sherpur 132/33kV Grid Sub-Station | 1 | 7:28 | 261.3333
Aminbazar 400/230/132kV Grid Sub-Station | 1 | 6:00 | 150
Gatail 132/33kV Grid Sub-Station | 1 | 4:37 | 115.4167
Keranigonj 230/132kV Grid Sub-Station | 1 | 0:12 | 2.8
Narsingdi 132/33kV Grid Sub-Station | 1 | 0:56 | 46.6667
Sonargaon 132/33kV Grid Sub-Station | 1 | 0:58 | 38.6667
Gulshan 132/33kV Grid Sub-Station | 2 | 0:38 | 31.87
Hasnabad 132/33kV Grid Sub-Station | 1 | 0:15 | 16
Siddhirganj 132/33kV Grid Sub-Station | 1 | 0:20 | 18
Hasnabad 132/33kV Grid Sub-Station | 1 | 0:51 | 46.75
Narshingdi 132/33kV Grid Sub-Station | 2 | 8:26 | 249.58
Coxsbazar 132/33kV Grid Sub-Station | 1 | 10:09 | 406
Dohazari 132/33kV Grid Sub-Station | 3 | 7:08 | 313
Sunamganj 132/33kV Grid Sub-Station | 2 | 0:30 | 10
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 3:24 | 119
Chhatak 132/33kV Grid Sub-Station | 2 | 2:03 | 14.35
Shahjibazar 132/33kV Grid Sub-Station | 1 | 1:17 | 51.3333
Sunamganj 132/33kV Grid Sub-Station | 1 | 2:50 | 11.3333
Sreemongal 132/33kV Grid Sub-Station | 1 | 7:59 | 0
Sylhet(S)132/33kV Grid Sub-Station | 1 | 1:31 | 22.75
Chandpur132/33kV Grid Sub-Station | 1 | 3:28 | 52
Cumilla(S132/33kV Grid Sub-Station | 1 | 1:17 | 12.8333
Chandpur132/33kV Grid Sub-Station | 1 | 2:44 | 0
Shahjibazar 132/33kV Grid Sub-Station | 1 | 7:10 | 0
Beanibazar 132/33kV Grid Sub-Station | 1 | 6:25 | 141.1667
Kachua 132/33kV Grid Sub-Station | 2 | 16:16 | 130.13
Chhatak 132/33kV Grid Sub-Station | 1 | 3:03 | 6.1
Chowmuhani 132/33kV Grid Sub-Station | 1 | 1:26 | 43
Satkhira 132/33kV Grid Sub-Station | 1 | 1:18 | 52
Barguna132/33kV Grid Sub-Station | 1 | 11:20 | 25.83
Barishal 132/33kV Grid Sub-Station | 1 | 0:28 | 27.5333
Khulna(C) 230/ 132/33kV Grid Sub-Station | 1 | 1:41 | 0
Barishal 230/132kV Grid Sub-Station | 1 | 2:52 | 17.2
Mongla 132/33kV Grid Sub-Station | 1 | 0:40 | 3.3333
Barishal 230/132kV Grid Sub-Station | 1 | 0:11 | 4.95
Satkhira 132/33kV Grid Sub-Station | 1 | 0:21 | 7
Faridpur 132/33kV Grid Sub-Station | 1 | 1:38 | 40.8333
Patuakhali 132/33kV Grid Sub-Station | 1 | 9:06 | 227.5
Narail 132/33kV Grid Sub-Station | 1 | 1:00 | 16
Chuadanga 230/132kV Grid Sub-Station | 1 | 8:25 | 75.75
Noapara 132/33kV Grid Sub-Station | 1 | 1:46 | 17.6667
Barishal 132/33kV Grid Sub-Station | 2 | 6:31 | 140.73
Bhandaria 132/33kV Grid Sub-Station | 1 | 3:47 | 90.8
Chuadanga 132/33kV Grid Sub-Station | 3 | 23:50 | 1310.83
Mongla 132/33kV Grid Sub-Station | 1 | 4:35 | 91.6667
Barishal 132/33kV Grid Sub-Station | 2 | 7:29 | 174.73
Bhandaria 132/33kV Grid Sub-Station | 1 | 7:53 | 197.0833
Patuakhali 132/33kV Grid Sub-Station | 1 | 6:19 | 37.9
Bagerhat 132/33kV Grid Sub-Station | 2 | 10:12 | 127.5
Patuakhali 132/33kV Grid Sub-Station | 2 | 11:29 | 195.22
Barisha 132/33kV Grid Sub-Station | 1 | 7:45 | 193.75
Bagerhat 132/33kV Grid Sub-Station | 1 | 7:43 | 192.9167
Ishurdi 230/132 Grid Sub-Station | 2 | 1:46 | 46.58
Jhenaidah 132/33kV Grid Sub-Station | 1 | 8:49 | 185.15
Magura 132/33kV Grid Sub-Station | 1 | 6:41 | 66.8333
Niamatpur132/33kV Grid Sub-Station | 1 | 0:20 | 6.6667
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 0:18 | 4.5
Niamatpur132/33kV Grid Sub-Station | 2 | 15:09 | 310.47
Barapukuria 230/132kV Grid Sub-Station | 1 | 1:26 | 17.2
Joypurhat 132/33kV Grid Sub-Station | 2 | 14:48 | 332.25
Total Unserved energy : | 87 | 311:17 | 7061.8333
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: November 2024
Sl. No | Sub-station | Load (MW) | Time
1 | AKS | 21 | 2024-11-30 06:00
2 | AKSML | 156 | 2024-11-28 04:00
3 | Aftabnagar | 58 | 2024-11-03 15:00
4 | Agargaon | 117 | 2024-11-04 13:00
5 | Agrabad | 102 | 2024-11-11 18:30
6 | Amnura | 51 | 2024-11-01 18:00
7 | Ashuganj | 94.5 | 2024-11-26 19:00
8 | BSRM | 145 | 2024-11-29 20:00
9 | Bagerhat | 77 | 2024-11-01 18:00
10 | Bajitpur | N/A | N/A
11 | Bakulia | 107 | 2024-11-11 18:30
12 | Banani | 70.2 | 2024-11-03 13:00
13 | Bangabhaban | 24 | 2024-11-03 10:00
14 | Barapukuria | 50 | 2024-11-05 18:30
15 | Barguna | 20 | 2024-11-01 20:00
16 | Barishal | 105 | 2024-11-02 19:00
17 | Barishal-230 | 92 | 2024-11-02 19:00
18 | Baroaulia | 69 | 2024-11-30 07:00
19 | Baroirhat | 58 | 2024-11-11 18:30
20 | Bashundhara | 175 | 2024-11-03 18:00
21 | BashundharaCement | 12 | 2024-11-01 00:00
22 | Beanibazar | 64 | 2024-11-01 18:00
23 | Benapole | 60 | 2024-11-07 18:00
24 | Bhaluka | 150 | 2024-11-03 12:00
25 | Bhandaria | 52 | 2024-11-11 18:00
26 | Bhangura | 51 | 2024-11-03 05:00
27 | Bheramara(GK) | 53 | 2024-11-01 18:00
28 | Bhulta | 280 | 2024-11-07 19:00
29 | Bog-Sherpur | 66 | 2024-11-08 18:00
30 | Bogura | 142 | 2024-11-01 18:30
31 | Borhanuddin | 80 | 2024-11-01 21:00
32 | Brahmanbaria | 190 | 2024-11-02 20:00
33 | Cantonment | 115 | 2024-11-05 13:00
34 | Chandpur | 70 | 2024-11-02 20:00
35 | Chandraghona | 35 | 2024-11-11 18:00
36 | Chapai | 54 | 2024-11-01 20:00
37 | Charsaidpur | 43 | 2024-11-01 04:00
38 | Chauddagram | 64 | 2024-11-02 21:00
39 | Chhatak | 30 | 2024-11-01 18:30
40 | Chowmuhani | 219 | 2024-11-01 22:00
41 | Chuadanga | 96 | 2024-11-02 21:00
42 | Coxsbazar | 120 | 2024-11-05 18:00
43 | Cumilla(N) | 161 | 2024-11-04 18:00
44 | Cumilla(S) | 159 | 2024-11-04 18:30
45 | Daudkandi | 148 | 2024-11-03 21:00
46 | Dhaka | 40 | 2024-11-03 12:00
47 | Dhamrai | 134 | 2024-11-28 17:00
48 | Dhanmondi | 149 | 2024-11-03 13:00
49 | Dohazari | 110 | 2024-11-02 18:30
50 | Faridpur | 148 | 2024-11-02 21:00
51 | Fatullah | 88 | 2024-11-02 15:00
52 | Fenchuganj | 38 | 2024-11-03 18:00
53 | Feni | 110 | 2024-11-04 18:00
54 | GPH | 101 | 2024-11-05 06:00
55 | Ghatail | 60 | 2024-11-01 18:00
56 | Ghorashal | 59 | 2024-11-09 18:00
57 | Ghorashal-230 | N/A | N/A
58 | Goalpara | 36 | 2024-11-07 13:00
59 | Gollamari | 100 | 2024-11-09 12:00
60 | Gopalganj | 99 | 2024-11-02 21:00
61 | Gulshan | 102 | 2024-11-12 15:00
62 | Halishahar | 87 | 2024-11-13 07:00
63 | HaripurSBU | 180 | 2024-11-13 11:00
64 | Hasnabad | 99 | 2024-11-04 19:00
65 | Hathazari | 75 | 2024-11-03 18:30
66 | Ishurdi | 69 | 2024-11-06 18:00
67 | Jaldhaka | 67 | 2024-11-05 18:00
68 | Jamalpur | 108 | 2024-11-01 18:00
69 | Jashore | 120 | 2024-11-03 19:30
70 | Jhenaidah | 113 | 2024-11-01 18:30
71 | Joydebpur | 184 | 2024-11-04 18:30
72 | Joypurhat | 56 | 2024-11-02 20:00
73 | Juldah | 17 | 2024-11-02 12:00
74 | KSRM | 52 | 2024-11-17 12:00
75 | Kabirpur | 316 | 2024-11-06 18:30
76 | Kachua | 82 | 2024-11-03 22:00
77 | Kallyanpur | 108 | 2024-11-02 18:00
78 | Kalurghat | 40 | 2024-11-05 18:00
79 | Kamrangirchar | 65 | 2024-11-05 13:00
80 | Kaptai | N/A | N/A
81 | Kazla | 109 | 2024-11-05 16:00
82 | Keranigonj | 83 | 2024-11-02 16:00
83 | Khagrachori | 32 | 2024-11-02 18:00
84 | Khulna | 79 | 2024-11-05 18:00
85 | Khulshi | 158 | 2024-11-02 13:00
86 | Kishoreganj | 148 | 2024-11-02 21:00
87 | Kodda | 313 | 2024-11-06 18:00
88 | Kulaura | 44 | 2024-11-04 18:00
89 | Kurigram | 62 | 2024-11-04 18:00
90 | Kushtia | 138 | 2024-11-05 18:30
91 | Lalbag | 78 | 2024-11-01 00:00
92 | Lalmonirhat | 47 | 2024-11-09 18:00
93 | MI_Cement | 17.8 | 2024-11-01 13:00
94 | Madanganj | 40 | 2024-11-02 18:00
95 | Madaripur | 92 | 2024-11-01 23:00
96 | Madartek | 92 | 2024-11-01 00:00
97 | Madunaghat | 99 | 2024-11-24 18:00
98 | Magura | 55 | 2024-11-01 18:00
99 | Mahasthangarh | 70 | 2024-11-05 18:00
100 | Manikganj | 128 | 2024-11-02 18:00
101 | Maniknagar | 70 | 2024-11-03 13:00
102 | Matarbari | 48 | 2024-11-05 21:00
103 | Matuail | 70 | 2024-11-02 11:00
104 | Millgate | 124 | 2024-11-04 12:00
105 | Mirpur | 138 | 2024-11-05 18:00
106 | Mirsorai | 56 | 2024-11-01 20:00
107 | Mirzapur | 48 | 2024-11-16 18:00
108 | Mithapukur | 90 | 2024-11-05 08:00
109 | Modern | 0 | 2024-11-01 00:00
110 | Mogbazar | 129.4 | 2024-11-04 12:00
111 | Mongla | 44 | 2024-11-05 15:00
112 | Motijheel | 47 | 2024-11-04 13:00
113 | Munshiganj | 102 | 2024-11-01 23:00
114 | Mymensingh | 224 | 2024-11-05 18:30
115 | Naogaon | 109 | 2024-11-04 18:00
116 | Narail | 52 | 2024-11-04 19:00
117 | Narinda | 78 | 2024-11-05 13:00
118 | Narshingdi | 180 | 2024-11-01 18:30
119 | Natore | 127 | 2024-11-05 18:00
120 | Nawabganj | 43.6 | 2024-11-01 21:00
121 | Netrakona | 120 | 2024-11-02 21:00
122 | New | 54.4 | 2024-11-05 18:00
123 | Niamatpur | 54 | 2024-11-01 22:00
124 | Noapara | 48 | 2024-11-23 21:00
125 | PHP | 11 | 2024-11-23 15:00
126 | Pabna | 110 | 2024-11-06 18:00
127 | Palashbari | 106 | 2024-11-05 18:00
128 | Panchagarh | 49 | 2024-11-04 18:00
129 | Patuakhali | 72.1 | 2024-11-01 21:00
130 | Payra | 38 | 2024-11-01 22:00
131 | Postogola | 52 | 2024-11-01 00:00
132 | Purbachal | 13 | 2024-11-07 13:00
133 | Purbasadipur | 103 | 2024-11-06 18:00
134 | Rahanpur | N/A | N/A
135 | Rahim | 52 | 2024-11-27 22:00
136 | Rajbari | 70 | 2024-11-06 18:00
137 | Rajendrapur | 106 | 2024-11-03 21:00
138 | Rajshahi | 101 | 2024-11-06 18:00
139 | Rajshahi-230 | 84 | 2024-11-04 13:00
140 | Ramganj | 116 | 2024-11-02 20:00
141 | Rampur | 42 | 2024-11-05 00:00
142 | Rangamati | 16 | 2024-11-02 18:00
143 | Rangpur | 130 | 2024-11-06 18:00
144 | Ruppur | 6.8 | 2024-11-06 15:00
145 | SSM | 15 | 2024-11-05 23:00
146 | Saidpur | 96 | 2024-11-09 18:00
147 | Satkhira | 112 | 2024-11-02 18:00
148 | Satmasjid | 103 | 2024-11-02 13:00
149 | Savar | 212 | 2024-11-04 16:00
150 | SevenRings | 17.32 | 2024-11-27 06:00
151 | ShahCement | 35 | 2024-11-30 00:00
152 | Shahjadpur | 93 | 2024-11-05 11:00
153 | Shahjibazar | 128 | 2024-11-02 19:00
154 | Shahmirpur | 59 | 2024-11-10 16:00
155 | Shariatpur | 80 | 2024-11-02 21:00
156 | Sherpur | 118 | 2024-11-07 18:00
157 | Shikalbaha | 32 | 2024-11-03 18:30
158 | Shitalakhya | 81 | 2024-11-04 13:00
159 | Sholosohor | 47 | 2024-11-04 16:00
160 | Shyampur | 170 | 2024-11-03 15:00
161 | Siddhirganj | 144 | 2024-11-09 18:00
162 | Sirajganj | 86 | 2024-11-03 18:30
163 | Sonargaon | 98 | 2024-11-04 12:00
164 | Sreemongol | 72 | 2024-11-03 18:30
165 | Sreepur | 90 | 2024-11-08 23:00
166 | Srinagar | 58 | 2024-11-06 17:00
167 | Sunamganj | 54 | 2024-11-05 18:00
168 | Sylhet | 54 | 2024-11-07 22:00
169 | Sylhet-132 | 128 | 2024-11-04 12:00
170 | TK | 32.5 | 2024-11-03 18:30
171 | Tangail | 180 | 2024-11-01 18:00
172 | Thakurgaon | 82 | 2024-11-05 18:00
173 | Tongi | 153 | 2024-11-05 12:00
174 | Ullahpara | 36 | 2024-11-02 18:00
175 | Ullon | 53 | 2024-11-01 12:00
176 | Uttara | 89 | 2024-11-05 13:00
177 | UttaraNew | 60 | 2024-11-07 09:00
178 | Zigatola | 93 | 2024-11-11 18:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: November 2024
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5124.38 | 2024-11-04 | 18:30
Chattogram | 1354.5 | 2024-11-04 | 14:00
Cumilla | 1343 | 2024-11-02 | 20:00
Mymensingh | 1051 | 2024-11-02 | 21:00
Sylhet | 577 | 2024-11-04 | 18:00
Khulna | 1517.6 | 2024-11-05 | 18:30
Barishal | 433.5 | 2024-11-02 | 22:00
Rajshahi | 1205.6 | 2024-11-05 | 18:30
Rangpur | 802 | 2024-11-06 | 18:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: November 2024
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 415 | 2024-11-30 03:00 | 370 | 2024-11-05 12:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 413 | 2024-11-22 08:00 | 374 | 2024-11-30 12:00
4 | Bibiana | 400 | 401 | 2024-11-20 22:00 | 380 | 2024-11-08 23:00
5 | BIPTC | 400 | 409 | 2024-11-29 03:00 | 390 | 2024-11-21 18:00
6 | Bogura | 400 | 414 | 2024-11-29 04:00 | 374 | 2024-11-24 13:00
7 | Gopalganj | 400 | 417 | 2024-11-27 06:00 | 385 | 2024-11-04 12:00
8 | Kaliakoir | 400 | 389 | 2024-11-22 08:00 | 354 | 2024-11-05 11:00
9 | Madunaghat | 400 | 424 | 2024-11-28 14:00 | 383 | 2024-11-06 13:00
10 | Meghnaghat | 400 | 412 | 2024-11-27 07:30 | 366 | 2024-11-09 11:30
11 | Payra | 400 | 421 | 2024-11-27 03:00 | 402 | 2024-11-05 12:00
12 | Rahanpur | 400 | 416 | 2024-11-30 04:00 | 379 | 2024-11-24 12:00
13 | Rampal | 400 | 416 | 2024-11-29 06:00 | 386 | 2024-11-05 12:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 260 | 2024-11-01 18:00 | 231 | 2024-11-01 19:30
2 | AKSML | 230 | 245 | 2024-11-16 18:00 | 220 | 2024-11-27 12:00
3 | Aminbazar | 230 | 244 | 2024-11-22 08:00 | 219 | 2024-11-04 15:00
4 | Ashuganj | 230 | 244 | 2024-11-20 22:00 | 224 | 2024-11-04 12:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 240 | 2024-11-22 04:00 | 223 | 2024-11-05 11:00
7 | Barapukuria | 230 | 237 | 2024-11-26 02:00 | 215 | 2024-11-28 18:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 247 | 2024-11-29 04:00 | 230 | 2024-11-05 12:00
10 | Bheramara | 230 | 240 | 2024-11-19 05:00 | 222 | 2024-11-05 12:00
11 | Bhulta | 230 | 244 | 2024-11-24 03:00 | 220 | 2024-11-04 12:00
12 | Bibiana | 230 | 232 | 2024-11-19 05:00 | 218 | 2024-11-03 11:00
13 | BIPTC | 230 | 243 | 2024-11-19 06:00 | 223 | 2024-11-05 12:00
14 | Bogura | 230 | 244 | 2024-11-23 09:00 | 228 | 2024-11-25 13:00
15 | Bogura-400 | 230 | 244 | 2024-11-23 09:00 | 227 | 2024-11-27 18:00
16 | Borhanuddin | 230 | 248 | 2024-11-29 09:00 | 234 | 2024-11-02 00:00
17 | BSRM | 230 | 243 | 2024-11-10 22:00 | 221 | 2024-11-27 12:00
18 | Cumilla(N) | 230 | 240 | 2024-11-26 04:00 | 219 | 2024-11-04 14:00
19 | Faridpur | 230 | 247 | 2024-11-27 04:00 | 224 | 2024-11-30 18:00
20 | Fenchuganj | 230 | 235 | 2024-11-25 07:00 | 221 | 2024-11-02 11:00
22 | Ghorashal | 230 | 246 | 2024-11-22 04:00 | 228 | 2024-11-04 17:00
23 | Ghorashal-230 | 230 | 242 | 2024-11-24 05:00 | 218 | 2024-11-04 12:00
24 | Gopalganj | 230 | 247 | 2024-11-29 04:00 | 227 | 2024-11-04 12:00
25 | GPH | 230 | 243 | 2024-11-10 22:00 | 219 | 2024-11-27 12:00
26 | Haripur | 230 | 243 | 2024-11-20 20:00 | 236 | 2024-11-17 07:00
27 | Hasnabad | 230 | 245 | 2024-11-25 01:00 | 223 | 2024-11-11 20:00
28 | Hathazari | 230 | 245 | 2024-11-17 20:00 | 227 | 2024-11-20 03:00
29 | Ishurdi | 230 | 243 | 2024-11-19 06:00 | 222 | 2024-11-09 02:00
30 | Jhenaidah | 230 | 239 | 2024-11-28 04:00 | 215 | 2024-11-05 12:00
31 | Kaliakoir | 230 | 244 | 2024-11-22 08:00 | 223 | 2024-11-08 19:30
32 | Keranigonj | 230 | 244 | 2024-11-25 04:00 | 218 | 2024-11-04 12:00
33 | Khulna(S) | 230 | 242 | 2024-11-22 03:00 | 219 | 2024-11-05 12:00
34 | Madunaghat | 230 | 244 | 2024-11-29 06:00 | 220 | 2024-11-27 13:00
35 | Madunaghat-400 | 230 | 249 | 2024-11-27 12:00 | 223 | 2024-11-03 20:00
37 | Maniknagar | 230 | 242 | 2024-11-20 21:00 | 230 | 2024-11-06 00:00
38 | Meghnaghat | 230 | 241 | 2024-11-14 06:00 | 221 | 2024-11-11 15:00
39 | Meghnaghat-400 | 230 | 245 | 2024-11-20 20:00 | 232 | 2024-11-07 04:00
40 | Mirsorai | 230 | 245 | 2024-11-05 18:30 | 221 | 2024-11-27 13:00
41 | Rajshahi | 230 | 241 | 2024-11-19 05:00 | 224 | 2024-11-05 12:00
42 | Rampal | 230 | 240 | 2024-11-28 05:00 | 218 | 2024-11-05 12:00
43 | Rampur | 230 | N/A | N/A | N/A | N/A
44 | Rampura | 230 | 243 | 2024-11-22 06:00 | 218 | 2024-11-04 12:00
45 | Shikalbaha | 230 | 243 | 2024-11-20 17:00 | 219 | 2024-11-27 13:00
46 | Shyampur | 230 | 245 | 2024-11-26 06:00 | 220 | 2024-11-04 12:00
47 | Siddhirganj | 230 | 244 | 2024-11-22 08:00 | 221 | 2024-11-05 12:00
48 | Sirajgonj | 230 | 249 | 2024-11-23 03:00 | 234 | 2024-11-25 12:00
49 | Sreepur | 230 | 241 | 2024-11-24 04:00 | 223 | 2024-11-04 15:00
50 | Tongi | 230 | 240 | 2024-11-23 05:00 | 215 | 2024-11-04 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 140 | 2024-11-02 05:00 | 113 | 2024-11-24 13:00
2 | Agargaon | 132 | 169 | 2024-11-22 18:30 | 1 | 2024-11-04 06:00
3 | Agrabad | 132 | 139 | 2024-11-17 19:30 | 114 | 2024-11-25 18:30
4 | AKS | 132 | 137 | 2024-11-16 19:00 | 123 | 2024-11-27 12:00
5 | Aminbazar | 132 | 144 | 2024-11-24 06:00 | 129 | 2024-11-05 12:00
6 | Amnura | 132 | 159 | 2024-11-24 16:00 | 137 | 2024-11-08 22:00
7 | Ashuganj | 132 | 142 | 2024-11-08 09:00 | 135 | 2024-11-03 11:00
8 | Bagerhat | 132 | 140 | 2024-11-17 05:00 | 125 | 2024-11-01 21:00
9 | Bajitpur | 132 | N/A | N/A | N/A | N/A
10 | Bakulia | 132 | 140 | 2024-11-19 18:00 | 124 | 2024-11-27 12:00
11 | Banani | 132 | 141 | 2024-11-02 03:00 | 125 | 2024-11-06 12:00
12 | Bangabhaban | 132 | 139 | 2024-11-26 04:00 | 121 | 2024-11-04 12:00
13 | Barapukuria | 132 | 140 | 2024-11-11 21:00 | 126 | 2024-11-17 10:00
14 | Barguna | 132 | 142 | 2024-11-17 20:00 | 131 | 2024-11-01 14:00
15 | Barishal | 132 | 137 | 2024-11-29 04:00 | 125 | 2024-11-02 12:00
16 | Barishal-230 | 132 | 137 | 2024-11-26 04:00 | 127 | 2024-11-01 21:00
17 | Baroaulia | 132 | 141 | 2024-11-21 18:00 | 125 | 2024-11-27 13:00
18 | Baroirhat | 132 | 140 | 2024-11-21 18:00 | 118 | 2024-11-08 13:00
19 | Bashundhara | 132 | 141 | 2024-11-19 04:00 | 120 | 2024-11-26 09:00
20 | BashundharaCement | 132 | 133 | 2024-11-29 01:00 | 127 | 2024-11-06 11:00
21 | Beanibazar | 132 | 135 | 2024-11-25 04:00 | 120 | 2024-11-01 19:30
22 | Benapole | 132 | 140 | 2024-11-17 04:00 | 125 | 2024-11-01 21:00
23 | Bhaluka | 132 | 136 | 2024-11-24 06:00 | 122 | 2024-11-03 12:00
24 | Bhandaria | 132 | 136 | 2024-11-14 06:00 | 120 | 2024-11-01 22:00
25 | Bhangura | 132 | 143 | 2024-11-19 04:00 | 114 | 2024-11-30 07:00
26 | Bheramara | 132 | 141 | 2024-11-20 22:00 | 130 | 2024-11-23 18:00
27 | Bheramara(GK) | 132 | 140 | 2024-11-18 04:00 | 129 | 2024-11-23 18:00
28 | Bhulta | 132 | 160 | 2024-11-30 17:00 | 110 | 2024-11-04 11:00
29 | Bog-Sherpur | 132 | 141 | 2024-11-01 12:00 | 135 | 2024-11-04 16:00
30 | Bogura | 132 | 142 | 2024-11-01 03:00 | 131 | 2024-11-25 12:00
31 | Bogura-230 | 132 | 142 | 2024-11-01 03:00 | 129 | 2024-11-30 20:00
32 | Brahmanbaria | 132 | 138 | 2024-11-06 02:00 | 111 | 2024-11-15 11:00
33 | Cantonment | 132 | 142 | 2024-11-14 06:00 | 127 | 2024-11-04 12:00
34 | Chandpur | 132 | 141 | 2024-11-17 18:00 | 116 | 2024-11-15 10:00
35 | Chandraghona | 132 | 140 | 2024-11-16 18:30 | 136 | 2024-11-29 14:00
36 | Chapai | 132 | 139 | 2024-11-28 02:00 | 125 | 2024-11-24 13:00
37 | Charsaidpur | 132 | 137 | 2024-11-22 08:00 | 122 | 2024-11-04 12:00
38 | Chauddagram | 132 | 139 | 2024-11-18 18:00 | 114 | 2024-11-25 19:30
39 | Chhatak | 132 | 135 | 2024-11-26 06:00 | 118 | 2024-11-01 19:30
40 | Chowmuhani | 132 | 139 | 2024-11-21 23:00 | 130 | 2024-11-22 13:00
41 | Chuadanga | 132 | 140 | 2024-11-18 03:00 | 120 | 2024-11-02 21:00
42 | Coxsbazar | 132 | 131 | 2024-11-27 06:00 | 110 | 2024-11-29 18:00
43 | Cumilla(N) | 132 | 140 | 2024-11-20 20:00 | 126 | 2024-11-02 11:00
44 | Cumilla(S) | 132 | 140 | 2024-11-21 18:00 | 125 | 2024-11-02 10:00
45 | Daudkandi | 132 | 137 | 2024-11-22 07:00 | 119 | 2024-11-16 12:00
46 | Dhaka | 132 | 139 | 2024-11-01 17:00 | 126 | 2024-11-06 12:00
47 | Dhamrai | 132 | 140 | 2024-11-23 02:00 | 122 | 2024-11-04 12:00
48 | Dhanmondi | 132 | 140.3 | 2024-11-05 20:00 | 126 | 2024-11-06 12:00
49 | Dohazari | 132 | 138 | 2024-11-20 18:00 | 121 | 2024-11-27 13:00
50 | Faridpur | 132 | 138 | 2024-11-27 05:00 | 127 | 2024-11-04 16:00
51 | Fatullah | 132 | 141 | 2024-11-15 05:00 | 114 | 2024-11-24 05:00
52 | Fenchuganj | 132 | 139 | 2024-11-22 18:30 | 129 | 2024-11-04 11:00
53 | Feni | 132 | 139 | 2024-11-21 18:00 | 121 | 2024-11-08 13:00
54 | Ghatail | 132 | 134 | 2024-11-11 02:00 | 118 | 2024-11-03 19:00
55 | Ghorashal | 132 | 144 | 2024-11-25 04:00 | 130 | 2024-11-04 14:00
56 | Goalpara | 132 | 144 | 2024-11-19 05:00 | 127 | 2024-11-05 12:00
57 | Gollamari | 132 | 142 | 2024-11-18 06:00 | 129 | 2024-11-05 12:00
58 | Gopalganj | 132 | 139 | 2024-11-27 06:00 | 128 | 2024-11-04 12:00
59 | Gopalganj-400 | 132 | 139 | 2024-11-27 06:00 | 127 | 2024-11-05 12:00
60 | Gulshan | 132 | 140 | 2024-11-19 06:00 | 125 | 2024-11-30 13:00
61 | Halishahar | 132 | 140 | 2024-11-17 20:00 | 124 | 2024-11-27 12:00
62 | Haripur | 132 | 137 | 2024-11-20 20:00 | 123 | 2024-11-04 11:00
63 | HaripurSBU | 132 | 142 | 2024-11-19 17:00 | 123 | 2024-11-04 11:00
64 | Hasnabad | 132 | 144 | 2024-11-06 02:00 | 130 | 2024-11-13 03:00
65 | Hathazari | 132 | 143 | 2024-11-21 18:00 | 128 | 2024-11-27 12:00
66 | Ishurdi | 132 | 142 | 2024-11-18 03:00 | 132 | 2024-11-05 12:00
67 | Jaldhaka | 132 | 136 | 2024-11-11 22:00 | 119 | 2024-11-15 07:00
68 | Jamalpur | 132 | 142 | 2024-11-03 09:00 | 120 | 2024-11-27 14:00
69 | Jashore | 132 | 142 | 2024-11-06 15:00 | 125 | 2024-11-02 12:00
70 | Jhenaidah | 132 | 143 | 2024-11-15 20:00 | 113 | 2024-11-28 10:00
71 | Jhenaidah-230 | 132 | 143 | 2024-11-19 04:00 | 127 | 2024-11-02 12:00
72 | Joydebpur | 132 | 144 | 2024-11-29 08:00 | 127 | 2024-11-03 08:00
73 | Joypurhat | 132 | 139 | 2024-11-25 04:00 | 122 | 2024-11-01 19:30
74 | Juldah | 132 | 140 | 2024-11-16 18:30 | 125 | 2024-11-27 12:00
75 | Kabirpur | 132 | 139 | 2024-11-18 04:00 | 119 | 2024-11-05 11:00
76 | Kachua | 132 | 140 | 2024-11-17 18:00 | 121 | 2024-11-02 00:00
77 | Kaliakoir | 132 | 142 | 2024-11-22 08:00 | 113 | 2024-11-20 00:00
78 | Kallyanpur | 132 | 148 | 2024-11-27 08:00 | 113 | 2024-11-23 05:00
79 | Kalurghat | 132 | 141 | 2024-11-18 18:30 | 126 | 2024-11-27 13:00
80 | Kamrangirchar | 132 | 141 | 2024-11-06 03:00 | 121 | 2024-11-05 12:00
81 | Kaptai | 132 | N/A | N/A | N/A | N/A
82 | Kazla | 132 | 165 | 2024-11-16 00:00 | 131 | 2024-11-09 09:00
83 | Keranigonj | 132 | 142 | 2024-11-06 03:00 | 126 | 2024-11-30 13:00
84 | Khagrachori | 132 | 139 | 2024-11-05 18:30 | 125 | 2024-11-27 13:00
85 | Khulna | 132 | 142 | 2024-11-19 05:00 | 129 | 2024-11-05 12:00
86 | Khulna(S) | 132 | 144 | 2024-11-19 05:00 | 130 | 2024-11-05 12:00
87 | Khulshi | 132 | 138 | 2024-11-17 20:00 | 131 | 2024-11-25 12:00
88 | Kishoreganj | 132 | 137 | 2024-11-24 05:00 | 113 | 2024-11-24 12:00
89 | Kodda | 132 | 139 | 2024-11-08 18:00 | 128 | 2024-11-25 18:30
90 | KSRM | 132 | 141 | 2024-11-20 20:00 | 124 | 2024-11-27 13:00
91 | Kulaura | 132 | 138 | 2024-11-25 04:00 | 126 | 2024-11-04 18:00
92 | Kurigram | 132 | 136 | 2024-11-04 03:00 | 116 | 2024-11-27 18:00
93 | Kushtia | 132 | 141 | 2024-11-20 22:00 | 137 | 2024-11-07 06:00
94 | Lalbag | 132 | 141 | 2024-11-06 02:00 | 125 | 2024-11-30 13:00
95 | Lalmonirhat | 132 | 136 | 2024-11-11 22:00 | 119 | 2024-11-19 07:00
96 | Madanganj | 132 | 137 | 2024-11-20 20:00 | 121 | 2024-11-04 12:00
97 | Madaripur | 132 | 138 | 2024-11-30 06:00 | 124 | 2024-11-17 01:00
98 | Madartek | 132 | 140 | 2024-11-04 07:00 | 125 | 2024-11-06 12:00
99 | Madunaghat | 132 | 141 | 2024-11-19 18:30 | 126 | 2024-11-27 12:00
100 | Magura | 132 | 142 | 2024-11-19 04:00 | 126 | 2024-11-02 12:00
101 | Mahasthangarh | 132 | 140 | 2024-11-02 00:00 | 127 | 2024-11-28 18:00
102 | Manikganj | 132 | 138 | 2024-11-08 18:00 | 118 | 2024-11-03 15:00
103 | Maniknagar | 132 | 139 | 2024-11-26 04:00 | 112 | 2024-11-05 12:00
104 | Matarbari | 132 | 221 | 2024-11-10 07:00 | 124 | 2024-11-21 09:00
105 | Matuail | 132 | 137.4 | 2024-11-29 09:00 | 128 | 2024-11-14 05:00
106 | Millgate | 132 | 156 | 2024-11-22 15:00 | 122 | 2024-11-04 11:00
107 | Mirpur | 132 | 144 | 2024-11-27 02:00 | 139 | 2024-11-14 19:30
108 | Mirzapur | 132 | 133 | 2024-11-10 22:00 | 118 | 2024-11-05 12:00
109 | Mithapukur | 132 | 139 | 2024-11-11 22:00 | 113 | 2024-11-18 15:00
110 | MI_Cement | 132 | 143 | 2024-11-06 02:00 | 126 | 2024-11-02 12:00
111 | Modern | 132 | 139 | 2024-11-05 21:00 | 124 | 2024-11-27 12:00
112 | Mogbazar | 132 | 141 | 2024-11-04 05:00 | 139 | 2024-11-28 07:00
113 | Mongla | 132 | 139 | 2024-11-17 01:00 | 125 | 2024-11-01 21:00
114 | Motijheel | 132 | 139 | 2024-11-26 04:00 | 121 | 2024-11-04 12:00
115 | Munshiganj | 132 | 136 | 2024-11-19 05:00 | 122 | 2024-11-04 11:00
116 | Mymensingh | 132 | 138 | 2024-11-16 22:00 | 113 | 2024-11-24 12:00
117 | Naogaon | 132 | 140 | 2024-11-01 12:00 | 122 | 2024-11-01 20:00
118 | Narail | 132 | 143 | 2024-11-19 05:00 | 125 | 2024-11-02 12:00
119 | Narinda | 132 | 0 | 2024-11-01 00:00 | N/A | N/A
120 | Narshingdi | 132 | 136 | 2024-11-18 07:00 | 113 | 2024-11-04 12:00
121 | Natore | 132 | 167 | 2024-11-29 16:00 | 129 | 2024-11-25 13:00
122 | Nawabganj | 132 | 141 | 2024-11-06 02:00 | 127 | 2024-11-30 12:00
123 | Netrakona | 132 | 136 | 2024-11-06 09:00 | 118 | 2024-11-06 18:00
124 | New | 132 | 141 | 2024-11-17 22:00 | 123 | 2024-11-04 12:00
125 | Niamatpur | 132 | 141 | 2024-11-28 05:00 | 127 | 2024-11-24 13:00
126 | Noapara | 132 | 142 | 2024-11-19 05:00 | 127 | 2024-11-05 12:00
127 | Pabna | 132 | 142 | 2024-11-19 05:00 | 131 | 2024-11-05 12:00
128 | Palashbari | 132 | 137 | 2024-11-01 06:00 | 121 | 2024-11-28 18:00
129 | Panchagarh | 132 | 139 | 2024-11-11 03:00 | 115 | 2024-11-19 11:00
130 | Patuakhali | 132 | 142 | 2024-11-30 18:00 | 130 | 2024-11-01 15:00
131 | Payra | 132 | 139 | 2024-11-18 18:30 | 136 | 2024-11-20 00:00
132 | PHP | 132 | 138 | 2024-11-19 18:00 | 120 | 2024-11-08 12:00
133 | Postogola | 132 | 143 | 2024-11-15 18:00 | 113 | 2024-11-18 16:00
134 | Purbachal | 132 | 142 | 2024-11-19 04:00 | 122 | 2024-11-04 12:00
135 | Purbasadipur | 132 | 137 | 2024-11-11 22:00 | 116 | 2024-11-17 10:00
136 | Rahanpur | 132 | N/A | N/A | N/A | N/A
137 | Rahanpur-400 | 132 | 141 | 2024-11-27 03:00 | 128 | 2024-11-24 12:00
138 | Rahim | 132 | 136 | 2024-11-20 20:00 | 122 | 2024-11-04 11:00
139 | Rajbari | 132 | 138 | 2024-11-27 05:00 | 113 | 2024-11-13 12:00
140 | Rajendrapur | 132 | 136 | 2024-11-16 18:30 | 122 | 2024-11-13 15:00
141 | Rajshahi | 132 | 140 | 2024-11-22 02:00 | 130 | 2024-11-06 12:00
142 | Rajshahi-230 | 132 | 141 | 2024-11-22 05:00 | 137 | 2024-11-25 00:00
143 | Ramganj | 132 | 139 | 2024-11-21 17:00 | 114 | 2024-11-08 13:00
144 | Rampur | 132 | 139 | 2024-11-16 18:30 | 130 | 2024-11-08 12:00
145 | Rampura | 132 | 140 | 2024-11-19 06:00 | 112 | 2024-11-05 11:00
146 | Rangamati | 132 | 139 | 2024-11-05 18:00 | 126 | 2024-11-27 12:00
147 | Rangpur | 132 | 138 | 2024-11-11 21:00 | 124 | 2024-11-28 04:00
148 | Ruppur | 132 | 142 | 2024-11-18 02:00 | 114 | 2024-11-26 16:00
149 | Saidpur | 132 | 138 | 2024-11-12 08:00 | 115 | 2024-11-02 02:00
150 | Satkhira | 132 | 142 | 2024-11-19 05:00 | 125 | 2024-11-01 21:00
151 | Satmasjid | 132 | 167 | 2024-11-30 19:30 | 114 | 2024-11-19 06:00
152 | Savar | 132 | 142 | 2024-11-26 02:00 | 123 | 2024-11-30 12:00
153 | SevenRings | 132 | 148 | 2024-11-10 00:00 | 130 | 2024-11-04 12:00
154 | ShahCement | 132 | 137 | 2024-11-22 08:00 | 122 | 2024-11-04 12:00
155 | Shahjadpur | 132 | 147 | 2024-11-20 21:00 | 136 | 2024-11-02 12:00
156 | Shahjibazar | 132 | 138 | 2024-11-18 08:00 | 123 | 2024-11-02 20:00
157 | Shahmirpur | 132 | 140 | 2024-11-16 19:00 | 120 | 2024-11-01 23:00
158 | Shariatpur | 132 | 138 | 2024-11-28 03:00 | 125 | 2024-11-01 22:00
159 | Sherpur | 132 | 139 | 2024-11-15 22:00 | 118 | 2024-11-30 00:00
160 | Shikalbaha | 132 | 129 | 2024-11-21 17:00 | 115 | 2024-11-27 12:00
161 | Shikalbaha-230 | 132 | 142 | 2024-11-17 20:00 | 131 | 2024-11-21 21:00
162 | Shitalakhya | 132 | 143 | 2024-11-06 02:00 | 126 | 2024-11-02 12:00
163 | Sholosohor | 132 | 139 | 2024-11-16 18:00 | 126 | 2024-11-27 12:00
164 | Shyampur | 132 | 139 | 2024-11-15 18:00 | 125 | 2024-11-05 12:00
165 | Shyampur-230 | 132 | 143 | 2024-11-19 06:00 | 131 | 2024-11-07 10:00
166 | Siddhirganj | 132 | 137 | 2024-11-15 18:00 | 123 | 2024-11-04 12:00
167 | Sirajganj | 132 | 142 | 2024-11-23 09:00 | 131 | 2024-11-04 12:00
168 | Sonargaon | 132 | 136 | 2024-11-22 08:00 | 126 | 2024-11-02 08:00
169 | Sreemongol | 132 | 137 | 2024-11-18 08:00 | 124 | 2024-11-04 18:00
170 | Sreepur | 132 | 137 | 2024-11-17 05:00 | 113 | 2024-11-24 08:00
171 | Srinagar | 132 | 140 | 2024-11-06 02:00 | 126 | 2024-11-30 12:00
172 | SSM | 132 | 142 | 2024-11-15 18:00 | 131 | 2024-11-09 12:00
173 | Sunamganj | 132 | 133 | 2024-11-23 09:00 | 114 | 2024-11-07 15:00
174 | Sylhet | 132 | 136 | 2024-11-23 09:00 | 127 | 2024-11-01 05:00
175 | Sylhet-132 | 132 | 135 | 2024-11-26 04:00 | 122 | 2024-11-05 12:00
176 | Tangail | 132 | 132 | 2024-11-10 22:00 | 118 | 2024-11-05 12:00
177 | Thakurgaon | 132 | 141 | 2024-11-11 03:00 | 115 | 2024-11-17 10:00
178 | TK | 132 | 140 | 2024-11-16 18:30 | 126 | 2024-11-27 12:00
179 | Tongi | 132 | 142 | 2024-11-18 04:00 | 126 | 2024-11-03 15:00
180 | Ullahpara | 132 | 148 | 2024-11-06 06:00 | 114 | 2024-11-05 11:00
181 | Ullon | 132 | 139 | 2024-11-01 17:00 | 125 | 2024-11-06 12:00
182 | Uttara | 132 | 146 | 2024-11-27 05:00 | 114 | 2024-11-08 02:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: November 2024
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 27-11-2024 | 18:00 | 358 | 71 | 70.187
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 28-11-2024 | 19:30 | 402 | 402 | 109.3296
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 03-11-2024 | 17:00 | 393 | 105 | 78.2279
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 28-11-2024 | 19:30 | 266 | 31 | 82.4001
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 02-11-2024 | 12:00 | -288 | -120 | 60
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 19-11-2024 | 11:00 | -321 | -115 | 65.5727
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 24-11-2024 | 12:00 | -276 | 55 | 54.1205
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 17-11-2024 | 14:00 | -250 | 12 | 48.1323
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 27-11-2024 | 22:00 | 299 | 8 | 39.8809
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 27-11-2024 | 22:00 | 299 | 8 | 39.8809
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 02-11-2024 | 10:00 | 293 | 82 | 40.5677
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 30-11-2024 | 18:00 | -93 | 27 | 12.912
Gopalganj 400/230kV Grid Sub-Station | ATR-05 | 400/230 | 750 | 30-11-2024 | 18:00 | -93 | 27 | 12.912
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 05-11-2024 | 21:00 | -118 | -20 | 36.8255
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 05-11-2024 | 21:00 | -118 | -20 | 36.8255
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 05-11-2024 | 21:00 | -118 | -20 | 36.8255
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 07-11-2024 | 13:00 | 227 | 134 | 50.6923
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 07-11-2024 | 18:30 | 272 | 52 | 53.255
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 28-11-2024 | 07:00 | 309 | 47 | 96.1705
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 28-11-2024 | 07:00 | 309 | 47 | 96.1705
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 30-11-2024 | 19:00 | -452 | -273 | 70.4062
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 30-11-2024 | 19:00 | -452 | -273 | 70.4062
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 04-11-2024 | 19:30 | -217 | -42 | 42.5052
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 03-11-2024 | 09:00 | -412 | -28 | 79.4135
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 05-11-2024 | 07:00 | -134 | -134 | 58.3091
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 26-11-2024 | 02:00 | -61 | -6 | 18.8598
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 01-11-2024 | 21:00 | 142 | 57 | 29.4256
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 01-11-2024 | 21:00 | 142 | 57 | 29.4256
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 05-11-2024 | 13:00 | 192 | 55 | 66.5741
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 04-11-2024 | 12:00 | 165 | 61 | 58.6383
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 13-11-2024 | 15:00 | 188 | 40 | 85.4259
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 13-11-2024 | 15:00 | 188 | 40 | 85.4259
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 12-11-2024 | 09:00 | 196 | 44 | 89.2791
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 01-11-2024 | 19:30 | 224 | 120 | 84.706
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 09-11-2024 | 18:00 | 200 | 50 | 68.7184
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 23-11-2024 | 18:00 | 113 | 57 | 42.1874
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 23-11-2024 | 18:00 | 84 | 41 | 41.5431
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 16-11-2024 | 17:00 | 170 | 22 | 76.1856
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 16-11-2024 | 17:00 | 155 | 35 | 70.6233
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 14-11-2024 | 18:00 | 203 | 13 | 67.8053
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 02-11-2024 | 21:00 | 114 | 20 | 38.5804
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 02-11-2024 | 21:00 | 114 | 20 | 38.5804
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 23-11-2024 | 18:00 | -78 | 52 | 41.6641
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 23-11-2024 | 18:00 | -78 | 52 | 41.6641
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 19-11-2024 | 14:00 | 110 | 20 | 49.6904
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 21-11-2024 | 19:00 | 105 | 8 | 46.8019
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 04-11-2024 | 16:00 | 178 | 23 | 59.8266
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 19-11-2024 | 14:00 | 148 | 28 | 50.2085
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 14-11-2024 | 03:00 | 174 | 57 | 81.377
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 14-11-2024 | 03:00 | 173 | 55 | 80.6811
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 14-11-2024 | 03:00 | 184 | 57 | 85.6118
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 01-11-2024 | 19:30 | 174 | 69 | 62.3939
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 01-11-2024 | 19:30 | 213 | 91 | 77.2082
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 07-11-2024 | 00:00 | 95 | 0 | 76
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 07-11-2024 | 00:00 | 95 | 0 | 76
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 13-11-2024 | 11:00 | 138 | 20 | 61.9741
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 09-11-2024 | 19:00 | 167 | 26 | 75.1164
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 13-11-2024 | 12:00 | 151 | 25 | 68.0247
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 16-11-2024 | 11:00 | 116 | 86 | 64.1788
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 16-11-2024 | 11:00 | 116 | 86 | 64.1788
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 16-11-2024 | 11:00 | 116 | 86 | 64.1788
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 16-11-2024 | 12:00 | 112 | 44 | 80.2219
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 16-11-2024 | 12:00 | 112 | 44 | 80.2219
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 16-11-2024 | 12:00 | 112 | 44 | 80.2219
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 16-11-2024 | 12:00 | 112 | 44 | 80.2219
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 22-11-2024 | 18:00 | 72 | 42 | 37.0465
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 22-11-2024 | 18:00 | 72 | 42 | 37.0465
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 22-11-2024 | 18:00 | 72 | 42 | 37.0465
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 05-11-2024 | 18:30 | -164 | -48 | 56.96
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 01-11-2024 | 09:00 | -179 | -71 | 64.189
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 28-11-2024 | 16:00 | 136 | 52 | 48.5341
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 28-11-2024 | 13:00 | 127 | 35 | 43.9115
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 25-11-2024 | 13:00 | 128 | 37 | 44.4135
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 25-11-2024 | 13:00 | 128 | 37 | 44.4135
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 03-11-2024 | 01:00 | 133 | 0 | 59.1111
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 03-11-2024 | 19:30 | -125 | -44 | 58.8969
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 03-11-2024 | 19:30 | -162 | -50 | 56.5135
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 29-11-2024 | 11:00 | 166 | 51 | 57.8859
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 30-11-2024 | 12:00 | 228 | 85 | 81.1097
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 27-11-2024 | 13:00 | -83 | -8 | 27.7949
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 25-11-2024 | 09:00 | -69 | 0 | 23
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 08-11-2024 | 12:00 | 133 | 1 | 44.3346
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-11-2024 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 14-11-2024 | 13:00 | 278 | 35 | 62.2655
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 03-11-2024 | 14:00 | 324 | 32 | 72.3503
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 03-11-2024 | 14:00 | 324 | 32 | 72.3503
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 11-11-2024 | 18:00 | 238 | 101 | 86.1813
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 11-11-2024 | 18:00 | 238 | 101 | 86.1813
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 16-11-2024 | 11:00 | 203 | 77 | 72.371
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 09-11-2024 | 13:00 | 174 | 42 | 59.6657
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 30-10-2024 | 19:30 | 226 | 116 | 84.6772
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 23-10-2024 | 04:00 | -214 | -65 | 74.5513
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 18-11-2024 | 16:00 | 236 | 24 | 79.0724
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 18-11-2024 | 16:00 | 236 | 24 | 79.0724
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 04-11-2024 | 18:30 | 208 | 38 | 93.9745
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 04-11-2024 | 18:30 | 190 | 46 | 86.8841
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 04-11-2024 | 18:30 | 190 | 46 | 86.8841
Executive Engineer
Information Management Division
[5 empty] | LDC, Power Grid, Dhaka. |  |  |  | 270

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [11 empty] | Report on load shedding
Month: November 2024 |  |  |  | (For Evening Peak) | [10 empty] | Month: November 2024 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2024-11-01 | 12302 | 12302 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-01 | 11199 | 11199 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-02 | 13195 | 13195 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-02 | 11305 | 11305 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-03 | 13041 | 13041 | 343 | 19:00 | 0 | 0 | 145 | 50 | 100 | 41 | 7 | 0 | 0 | - | 2024-11-03 | 11422 | 11422 | 647 | 12:00 | 265 | 75 | 91 | 0 | 165 | 51 | 0 | 0 | 0 | -
2024-11-04 | 13253 | 13253 | 102 | 19:30 | 20 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 37 | - | 2024-11-04 | 11947 | 11947 | 98 | 12:00 | 68 | 0 | 10 | 0 | 5 | 15 | 0 | 0 | 0 | -
2024-11-05 | 12750 | 12750 | 67 | 18:00 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | - | 2024-11-05 | 11963 | 11963 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-06 | 12536 | 12536 | 42 | 18:00 | 17 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | - | 2024-11-06 | 10719 | 10719 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-07 | 12630 | 12630 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-07 | 11095 | 11095 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-08 | 10899 | 10899 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-08 | 9603 | 9603 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-09 | 12270 | 12270 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-09 | 10293 | 10293 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-10 | 12195 | 12195 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-10 | 11126 | 11126 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-11 | 12314 | 12314 | 44 | 20:00 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 7 | 0 | - | 2024-11-11 | 10878 | 10878 | 403 | 12:00 | 189 | 94 | 12 | 0 | 102 | 6 | 0 | 0 | 0 | -
2024-11-12 | 12505 | 12505 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-12 | 10768 | 10768 | 413 | 12:00 | 143 | 47 | 51 | 0 | 111 | 61 | 0 | 0 | 0 | -
2024-11-13 | 12414 | 12414 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-13 | 11037 | 11037 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-14 | 12251 | 12251 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-14 | 10905 | 10905 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-15 | 10277 | 10277 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-15 | 9308 | 9308 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-16 | 11246 | 11246 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-16 | 9431 | 9431 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-17 | 11186 | 11186 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-17 | 9431 | 9431 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-18 | 10934 | 10934 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-18 | 9704 | 9704 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-19 | 11273 | 11273 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-19 | 9599 | 9599 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-20 | 11087 | 11087 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-20 | 9693 | 9693 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-21 | 11166 | 11166 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-21 | 9875 | 9875 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-22 | 9183 | 9183 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-22 | 8530 | 8530 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-23 | 10471 | 10471 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-23 | 8993 | 8993 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-24 | 10624 | 10624 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-24 | 9361 | 9361 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-25 | 10545 | 10545 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-25 | 9398 | 9398 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-26 | 10676 | 10676 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-26 | 9465 | 9465 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-27 | 10666 | 10666 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-27 | 9652 | 9652 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-28 | 10800 | 10800 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-11-28 | 9675 | 9675 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-11-29 | 9366 | 9366 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2024-11-29 | 8936 | 8936 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-11-30 | 10812 | 10812 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2024-11-30 | 9424 | 9424 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | - | - | - | [11 empty] | - | -
98
30
68

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: November 2024
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13253 | 2024-11-04 | 19:30
2 | Maximum Day Peak Genaration | MW | 11963 | 2024-11-05 | 12:00
3 | Maximum Evening Peak Demand | MW | 13253 | 2024-11-03 | 19:00
4 | Minimum Generation | MW | 6915 | 2024-11-23 | 6:00
5 | Average of the daily evening peak Genaration | MW | 11495.5667 | - | -
6 | Average of the daily day peak Genaration | MW | 10157.8333 | - | -
7 | Maximum load shed (Evening Peak) | MW | 343 | 2024-11-03 | 19:00
8 | Minimum load shed | MW | 0 | 2024-11-01 | 19:00
9 | Total nos. of load shed days | Day | 5 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 19.9333 | - | -
11 | Total Generation | MkWh | 7159.2125 | - | -
12 | Total Generation by BPDB | MkWh | 1293.3147 | % of total Gen. | 18.07%
13 | Total Generation by IPP | MkWh | 2454.9734 | '' | 34.29%
14 | A) Total Generation by Generation Companies | MkWh | 2098.615 | '' | 29.31%
| B) Total Generation by REB | MkWh | 89.5936 | " | 1.251%
| C) Total Generation by RENTAL | MkWh | 78.2023 | " | 1.092%
| D) Total Imported from India (BIPTC) | MkWh | 653.4545 | " | 9.127%
| E) Total Imported from Tripura, India (A.C) | MkWh | 38.4115 | " | 0.5365%
| F) Total Imported from Nepal | MkWh | 0.45308 | " | 0.006329%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 452.1943 | " | 6.316%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3635.3513 | % of total Gen. | 50.78%
| B) Oil | MkWh | 708.8986 | '' | 9.902%
| C) Hydro | MkWh | 83.5571 | '' | 1.167%
| D) Solar | MkWh | 108.5987 | '' | 1.517%
| E) Coal | MkWh | 1475.3202 | '' | 20.61%
| F) BIPTC (Import from India) | MkWh | 653.4545 | '' | 9.127%
| G) A.C (Import from Tripura, India) | MkWh | 38.4115 | '' | 0.5365%
| H) Total Imported from Nepal | MkWh | 0.45308 | '' | 0.006329%
| I) Adani (Import from India) | MkWh | 452.1943 | '' | 6.317%
| J) Wind | MkWh | 2.9731 | '' | 0.04153%
16 | Maximun of the daily total Generation . | MkWh | 282.6523 | 2024-11-04
17 | Monthly Load factor | % | 75.0272 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 39899.0739 | - | -
| A) Gas | M.Taka | 10354.8687 | - | -
| B) Liquid fuel | M.Taka | 12867.7784 | - | -
| C) Coal | M.Taka | 10443.8558 | - | -
| D) BIPTC (Import from India) | M.Taka | 2875.2 | - | -
| E) Tripura(Import from India) | M.Taka | 368.3665 | - | -
| F) Nepal (Import) | M.Taka | 0 | - | -
| G) Adani (Import from India) | M.Taka | 2989.0046 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1889.1734 | 2024-11-04
| A) Gas | M.Taka | 384.4368 | 2024-11-02
| B) Liquid fuel | M.Taka | 935.3146 | 2024-11-10
| C) Coal | M.Taka | 458.492 | 2024-11-05
| D) BIPTC (Import from India) | M.Taka | 102.096 | 2024-11-14
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.5731
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 5.7293
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 106.1 | 30/11/2024 | 06:00
b) | Actual | FT (MSL) | 96.17 | 31/11/2024 | 06:00
22 | Peak Genaration of November 2023 | MW | 12608 | 2023-11-02 | 18:00
23 | Peak Demand of November 2023 | MW | 12650 | 2023-11-30 | 18:00
24 | Maximum peak Generation recorded upto 30/11/2024 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 30/11/2024 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 30/11/2024 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: November 2024
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
9 | Meghnaghat CCPP(Summit) | IPP | 335
10 | Ashuganj 225 MW CCPP | APSCL | 221 | [13 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400 | √
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable | [18 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable | [18 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable | [16 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | [13 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable |  | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable | [16 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | [13 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant