## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-01-2025 | during | 17-01-2025 | during | 17-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 374 | 405 | 400.37 | 400.37 | 400 | 400 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 380 | 450 | 450 | 380 | 380 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 294 | 296 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 260 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 50 | 50 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 16 | 149.36 | 149.36 | 149 | 149 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 21 | 17 | 30 | 30 | 25 | 25 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 30 | 30 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 26 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 26 | 26 | 52.19 | 52.19 | 52 | 52 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 32 | 93 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 25 | 0 | 29 | 0 | 29 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 36 | 36 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6257.05 | 5842.27 | 1607 | 2015 | 4009.99 | 3988.99 | 2728.92 | 2707.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 115 | 115 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25 | 25 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 228 | 227 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 24 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 74 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 0 | 2 | 10 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 0 | 0 | 3.83 | 0 | 3.83 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 35 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159 | 159 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 590 | 612 | 1224 | 1224 | 612 | 612 | network constraint
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 0 | 4 | 0 | 8 | 0 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 1056 | 1052 | 1150 | 1150 | 1055 | 1055 | -
Chattogram Area Total |  |  |  |  | 4917.36 | 4873.22 | 1988 | 2179 | 4154.55 | 4139.72 | 3332.56 | 3317.73
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 205 | 185 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 28 | 37 | 46.94 | 46.94 | 45 | 45 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 197 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 10 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 51 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 44 | 62 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52 | 52 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 105 | 113 | 113 | 113 | 113 | Fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 50 | 95 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 777 | 881 | 1660.97 | 1600.97 | 1526.2 | 1466.2
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 6 | 10 | 210 | 210 | 10 | 10 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 58 | 200 | 200 | 58 | 58 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 115 | 115 | 19 | 19 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.6 | 0 | 44.5 | 0 | 44.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54 | 54 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 145.6 | 128 | 648 | 601.5 | 210 | 163.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 10 | 27 | 44 | 44 | 10 | 10 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 20 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 61 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 207 | 207 | 210 | 210 | 210 | 210 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 0 | 0 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 370 | 337 | 395 | 395 | 340 | 340 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1491 | 1484 | 1611.5 | 1611.5 | 1481.01 | 1481.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 918 | 917 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 310 | 278 | 410 | 410 | 280 | 280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 77 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1305 | 1195 | 3246 | 3174 | 1442.01 | 1370.01
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 135 | 135 | 140 | 140 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1130 | 1192 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 150 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.55 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1836.55 | 2016 | 2177.12 | 2176.12 | 2139 | 2138
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 50 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | availability is 47MW but unable to submit to web
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 185 | 179 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 181 | 220 | 220 | 180 | 180 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 174 | 180 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 16 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 0 | 0 | 4.1 | 0 | 4.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 0 | 0 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.87 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 711.87 | 725 | 2107.3 | 1953.2 | 1993.3 | 1839.2
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 72 | 72 | 72 | 72 | 72 | 72 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 210 | 210 | 210 | 210 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.6 | 0 | 4.4 | 0 | 4.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 20.5 | 0 | 20.5 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 130 | 0 | 130.33 | 0 | 130.33 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 481.6 | 317 | 699.23 | 544 | 665.23 | 510
System Total |  |  |  |  | 27734.66 | 27025.248 | 10343.62 | 10940 | 20314.66 | 19790 | 15518.23 | 14993.57
Forecast Scenario (17-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8900 |  | 0 |  | 8900
|  |  |  | 1:00 | 8350 |  | 0 |  | 8350
|  |  |  | 2:00 | 8000 |  | 0 |  | 8000
|  |  |  | 3:00 | 7620 |  | 0 |  | 7620
|  |  |  | 4:00 | 7250 |  | 0 |  | 7250
|  |  |  | 5:00 | 7180 |  | 0 |  | 7180
|  |  |  | 6:00 | 7400 |  | 0 |  | 7400
|  |  |  | 7:00 | 7450 |  | 0 |  | 7450
|  |  |  | 8:00 | 7800 |  | 0 |  | 7800
|  |  |  | 9:00 | 8400 |  | 0 |  | 8400
|  |  |  | 10:00 | 8250 |  | 0 |  | 8250
|  |  |  | 11:00 | 8500 |  | 0 |  | 8500
|  |  |  | 12:00 | 9030 |  | 0 |  | 9030
|  |  |  | 13:00 | 9800 |  | 0 |  | 9800
|  |  |  | 14:00 | 8300 |  | 0 |  | 8300
|  |  |  | 15:00 | 7600 |  | 0 |  | 7600
|  |  |  | 16:00 | 7300 |  | 0 |  | 7300
|  |  |  | 17:00 | 7700 |  | 0 |  | 7700
|  |  |  | 18:00 | 8980 |  | 0 |  | 8980
|  |  |  | 18:30 | 9000 |  | 0 |  | 9000
|  |  |  | 19:00 | 9200 |  | 0 |  | 9200
|  |  |  | 19:30 | 9400 |  | 0 |  | 9400
|  |  |  | 20:00 | 9300 |  | 0 |  | 9300
|  |  |  | 21:00 | 9200 |  | 0 |  | 9200
|  |  |  | 22:00 | 8950 |  | 0 |  | 8950
|  |  |  | 23:00 | 8580 |  | 0 |  | 8580
Probable Maximum Temperature: |  |  | 27.90°C
Probable Maximum Demand at Day Peak: |  |  | 9030.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 9400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 9400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 199.04 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (16-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 28.50°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 839.3
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 20.8422 | Peak Hour Flow: |  | 917.00 MW at 19:00 hrs.
Energy Flow from West to East |  | 4249454.585 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 0.66702 | Peak Hour Flow: |  | 0
Power Flow during Peak Demand |  | 88 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.2 | Peak Hour Flow: |  | 62.00 MW at 19:00 hrs.
Maximum Power Flow |  | 504 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 22.7092 | Peak Hour Flow: |  | 979.00 MW at 19:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-01-2025 | [28 empty] | Date: | 16-01-2025 | [28 empty] | Date: | 16-01-2025 | [28 empty] | Date: | 16-01-2025 | [28 empty] | Date: | 16-01-2025 | [18 empty] | Date: | 16-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [18 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 150.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 0.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 17 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 263 | 0 | 0 | 0 | 28 | 260 | 0 | 0 | 0 | 0 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 1132 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 43 | 0 | 50 | 0 | 0 | 14 | 0 | 50 | 0 | 0 | 0 | 280 | 305 | 380 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 209 | 0 | 19 | 48 | 13 | 0 | 0 | 24 | 5457.5 | 915 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 202 | 0 | 199 | 0 | 0 | 0 | 0 | 8.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 960 | 0 | 3607.5 | 9065 | 93.05
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 269 | 0 | 0 | 0 | 29 | 260 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 1055 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 400 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 182 | 43 | 0 | 50 | 0 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 280 | 305 | 380 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 208 | 0 | 0 | 48 | 12 | 0 | 13.21 | 0 | 5163.21 | 914 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 140 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 208 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 880 | 0 | 3403.5 | 8566.71 | 93.04
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 284 | 0 | 0 | 0 | 29 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 1005 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 353 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 181 | 40 | 0 | 50 | 0 | 0 | 16 | 0 | 50 | 0 | 0 | 0 | 275 | 305 | 379 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 208 | 0 | 0 | 28 | 20 | 0 | 0 | 0 | 4997.5 | 727 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 140 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 220 | 0 | 780 | 0 | 3064.5 | 8062 | 93.04
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 271 | 0 | 0 | 0 | 29 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 32 | 905 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 305 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 188 | 37 | 0 | 50 | 0 | 0 | 14 | 0 | 44 | 0 | 0 | 0 | 300 | 305 | 380 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 0 | 0 | 0 | 208 | 0 | 9 | 18 | 20 | 0 | 0 | 0 | 4768.5 | 728 | 289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 140 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 209 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 700 | 0 | 2982.5 | 7751 | 93.03
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 286 | 0 | 0 | 0 | 30 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 905 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 301 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 198 | 37 | 0 | 50 | 0 | 0 | 10 | 0 | 40 | 0 | 0 | 0 | 310 | 305 | 380 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 0 | 0 | 0 | 208 | 0 | 9 | 9 | 20 | 0 | 0 | 0 | 4788.5 | 634 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 140 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 140 | 220 | 0 | 600 | 0 | 2790.5 | 7579 | 93.03
05:00 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 271 | 0 | 0 | 0 | 30 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 903 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 301 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 183 | 37 | 0 | 50 | 0 | 0 | 10 | 0 | 40 | 0 | 0 | 0 | 300 | 305 | 379 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 0 | 0 | 0 | 208 | 0 | 9 | 9 | 20 | 0 | 0 | 0 | 4742.5 | 634 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 140 | 0 | 150 | 0 | 0 | 0 | 0 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 140 | 220 | 0 | 600 | 0 | 2783.5 | 7526 | 93.02
06:00 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 314 | 0 | 0 | 0 | 30 | 260 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 1000 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 350 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 192 | 37 | 0 | 50 | 0 | 0 | 10 | 0 | 50 | 0 | 0 | 0 | 305 | 305 | 333 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 0 | 0 | 0 | 208 | 0 | 9 | 18 | 20 | 0 | 0 | 0 | 4939 | 727 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 172 | 0 | 167 | 0 | 0 | 0 | 0 | 5.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 220 | 0 | 630 | 0 | 2988.5 | 7927.5 | 93.02
07:00 | 0 | 23 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 30 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 309 | 0 | 0 | 0 | 30 | 260 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 1100 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 456 | 1 | 43 | 0 | 195 | 0 | 0 | 0 | 29 | 203 | 37 | 0 | 51 | 0 | 0 | 14 | 0 | 50 | 0 | 2 | 0 | 310 | 300 | 353 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 0 | 0 | 0 | 209 | 0 | 19 | 45 | 13 | 0 | 0.68 | 3 | 5338.68 | 915 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 151 | 0 | 170 | 0 | 169 | 0 | 0 | 0 | 0.08 | 5.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.01 | 0 | 200 | 6 | 140 | 220 | 0 | 780 | 0 | 3367.7 | 8706.38 | 93.01
08:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 5 | 16 | 0 | 53 | 32 | 0 | 0 | 0 | 40 | 14 | 0 | 300 | 320 | 0 | 0 | 0 | 30 | 260 | 0 | 0 | 5 | 0 | 21.6 | 22 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 0 | 1100 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 561 | 7 | 43 | 0 | 195 | 0 | 0 | 0 | 29 | 209 | 40 | 9 | 51 | 0 | 2 | 16 | 0 | 46 | 0 | 9 | 0 | 315 | 320 | 369 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 211 | 0 | 18 | 45 | 11 | 0 | 4.07 | 24 | 5695.67 | 917 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 3.44 | 151 | 0 | 162 | 0 | 173 | 0 | 0 | 0 | 0.34 | 5.5 | 210 | 71 | 0 | 5 | 0 | 0 | 0 | 0.7 | 29 | 0.11 | 0 | 307 | 5 | 140 | 220 | 0 | 1060 | 17 | 3846.09 | 9541.76 | 93.01
09:00 | 0 | 55 | 26 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 25 | 36 | 0 | 65 | 32 | 0 | 0 | 0 | 80 | 25 | 0 | 300 | 266 | 0 | 0 | 10 | 16.5 | 260 | 0 | 0 | 11 | 0 | 21 | 22 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 12 | 1064 | 0 | 0 | 9 | 0 | 2 | 229 | 0 | 0 | 0 | 604 | 13 | 43 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 29 | 50 | 50 | 2 | 19 | 16 | 0 | 42 | 0 | 38 | 0 | 300 | 320 | 368 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 211 | 0 | 19 | 46 | 6 | 0 | 10.45 | 24 | 5864.95 | 918 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 16.63 | 149 | 0 | 148 | 0 | 169 | 0 | 0 | 0 | 0.84 | 5.5 | 210 | 70 | 28 | 18 | 0 | 0 | 0 | 0 | 92 | 0.18 | 0 | 307 | 4 | 140 | 220 | 0 | 1200 | 72 | 4163.15 | 10028.1 | 93
10:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 37 | 36 | 0 | 64 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 284 | 0 | 0 | 17 | 16.5 | 260 | 0 | 0 | 18 | 0 | 21 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 6 | 1065 | 0 | 0 | 24 | 0 | 17 | 229 | 0 | 0 | 0 | 590 | 17 | 43 | 0 | 178 | 0 | 0 | 0 | 29 | 181 | 31 | 60 | 50 | 17 | 28 | 16 | 0 | 54 | 0 | 55 | 0 | 275 | 320 | 307 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 61 | 0 | 0 | 0 | 211 | 0 | 19 | 46 | 6 | 2 | 27.87 | 24 | 5820.37 | 916 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 31.6 | 152 | 0 | 148 | 0 | 164 | 0 | 0 | 0 | 2.79 | 5.5 | 210 | 70 | 34 | 27 | 0 | 0 | 0 | 2.2 | 112 | 0.41 | 0 | 270 | 4 | 100 | 180 | 0 | 1100 | 54 | 3978.5 | 9798.87 | 93
11:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 36 | 0 | 40 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 263 | 0 | 0 | 17 | 0 | 260 | 0 | 0 | 23 | 0 | 21 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 5 | 1067 | 0 | 0 | 19 | 0 | 17 | 228 | 0 | 0 | 0 | 540 | 19 | 43 | 0 | 178 | 0 | 0 | 0 | 29 | 184 | 34 | 50 | 50 | 17 | 28 | 16 | 0 | 60 | 0 | 65 | 0 | 300 | 320 | 307 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 61 | 0 | 0 | 0 | 209 | 0 | 19 | 48 | 6 | 2 | 46.01 | 24 | 5805.01 | 918 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 88 | 0 | 58.72 | 172 | 0 | 166 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 210 | 72 | 34 | 28 | 0 | 0 | 0 | 2.2 | 122 | 0.52 | 0 | 270 | 4 | 100 | 180 | 0 | 1100 | 35 | 4086.44 | 9891.45 | 92.99
12:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 35 | 36 | 0 | 32 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 294 | 0 | 0 | 17 | 0 | 260 | 0 | 0 | 25 | 0 | 21 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 1056 | 0 | 0 | 19 | 0 | 17 | 228 | 0 | 0 | 0 | 590 | 19 | 43 | 0 | 197 | 0 | 0 | 0 | 29 | 205 | 28 | 50 | 50 | 17 | 28 | 17 | 0 | 44 | 0 | 69 | 0 | 315 | 320 | 370 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 61 | 0 | 0 | 0 | 207 | 0 | 19 | 48 | 6 | 2 | 46.6 | 24 | 6008.6 | 918 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 93 | 0 | 57.87 | 185 | 0 | 194 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 210 | 72 | 35 | 32 | 0 | 0 | 0 | 2.6 | 130 | 0.55 | 0 | 307 | 4 | 140 | 220 | 0 | 1130 | 35 | 4335.02 | 10343.62 | 92.99
13:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 47 | 36 | 0 | 32 | 16 | 0 | 6 | 0 | 90 | 25 | 0 | 300 | 270 | 0 | 0 | 35 | 0 | 260 | 0 | 0 | 24 | 0 | 16 | 22 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 12 | 5 | 1051 | 0 | 0 | 38 | 0 | 28 | 227 | 0 | 0 | 0 | 610 | 19 | 43 | 12 | 197 | 0 | 0 | 0 | 29 | 186 | 35 | 74 | 50 | 26 | 43 | 17 | 0 | 58 | 0 | 66 | 0 | 320 | 320 | 351 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 82 | 0 | 0 | 0 | 207 | 15 | 19 | 48 | 6 | 2 | 42.93 | 24 | 6165.93 | 917 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 53.5 | 192 | 0 | 206 | 0 | 177 | 0 | 0 | 0 | 1.48 | 5.5 | 210 | 71 | 50 | 24 | 0 | 0 | 0 | 2.4 | 120 | 0.5 | 0 | 307 | 4 | 140 | 220 | 0 | 1244 | 90 | 4499.38 | 10665.31 | 92.98
14:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 35 | 36 | 0 | 32 | 16 | 0 | 15 | 0 | 72 | 25 | 0 | 300 | 273 | 0 | 0 | 17 | 22 | 260 | 0 | 0 | 22 | 0 | 17 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 4 | 1058 | 0 | 0 | 38 | 0 | 17 | 226 | 0 | 0 | 0 | 610 | 16 | 43 | 20 | 197 | 0 | 0 | 0 | 28 | 183 | 39 | 0 | 50 | 17 | 74 | 17 | 0 | 52 | 0 | 57 | 0 | 295 | 320 | 338 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 82 | 0 | 0 | 0 | 204 | 0 | 19 | 48 | 6 | 2 | 40.13 | 24 | 6043.13 | 917 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 42.54 | 192 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 3.89 | 8.5 | 210 | 72 | 0 | 18 | 0 | 0 | 0 | 2.2 | 119 | 0.46 | 0 | 250 | 4 | 140 | 220 | 0 | 1244 | 90 | 4287.59 | 10330.72 | 92.98
15:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 35 | 36 | 0 | 33 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 230 | 0 | 0 | 17 | 24 | 260 | 0 | 0 | 16 | 0 | 17 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 1057 | 0 | 0 | 38 | 0 | 0 | 225 | 0 | 0 | 0 | 610 | 13 | 43 | 0 | 197 | 0 | 0 | 0 | 29 | 223 | 36 | 0 | 50 | 17 | 75 | 17 | 0 | 46 | 0 | 44 | 0 | 280 | 320 | 338 | 0 | 15 | 0 | 2 | 120 | 13 | 0 | 82 | 0 | 0 | 0 | 203 | 0 | 19 | 48 | 5 | 1 | 30.88 | 24 | 5886.88 | 918 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 26.54 | 192 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 2.38 | 8.5 | 210 | 71 | 0 | 9 | 0 | 0 | 0 | 1.7 | 92 | 0.34 | 0 | 250 | 4 | 140 | 220 | 0 | 1244 | 19 | 4115.46 | 10002.34 | 92.97
16:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 36 | 0 | 22 | 16 | 0 | 0 | 0 | 17 | 25 | 0 | 300 | 268 | 0 | 0 | 0 | 24 | 260 | 0 | 0 | 9 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 1053 | 0 | 0 | 21 | 0 | 0 | 225 | 0 | 0 | 0 | 610 | 8 | 43 | 0 | 197 | 0 | 0 | 0 | 29 | 184 | 42 | 32 | 50 | 17 | 27 | 17 | 0 | 50 | 0 | 25 | 0 | 290 | 320 | 337 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 204 | 0 | 19 | 48 | 5 | 1 | 13.21 | 24 | 5703.21 | 918 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 11.36 | 193 | 0 | 160 | 0 | 197 | 0 | 0 | 0 | 1.19 | 5.5 | 210 | 71 | 0 | 11 | 0 | 0 | 0 | 0.6 | 59 | 0 | 0 | 250 | 3 | 140 | 220 | 0 | 1100 | 17 | 3901.65 | 9604.86 | 92.97
17:00 | 0 | 75 | 26 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 18 | 36 | 0 | 17 | 37 | 0 | 3 | 14 | 45 | 25 | 0 | 300 | 241 | 0 | 0 | 20 | 24 | 260 | 0 | 0 | 2 | 0 | 16.5 | 22 | 0 | 0 | 0 | 16 | 0 | 0 | 1 | 7 | 0 | 0 | 15 | 12 | 0 | 40 | 9 | 7 | 1050 | 35 | 0 | 20 | 2 | 6 | 226 | 0 | 0 | 0 | 610 | 1 | 43 | 10 | 197 | 0 | 0 | 0 | 28 | 184 | 37 | 60 | 50 | 18 | 37 | 17 | 0 | 48 | 5 | 4 | 0 | 305 | 320 | 337 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 203 | 13 | 19 | 48 | 6 | 0 | 1.92 | 22 | 5918.42 | 918 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 2.49 | 192 | 0 | 160 | 0 | 203 | 0 | 0 | 0 | 0.21 | 5.5 | 210 | 72 | 0 | 2 | 0 | 0 | 0 | 0.1 | 7 | 0.32 | 0 | 250 | 4 | 140 | 220 | 0 | 1100 | 45 | 3830.62 | 9749.04 | 92.96
18:00 | 0 | 105 | 26 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 37 | 34 | 0 | 57 | 48 | 0 | 32 | 35 | 120 | 25 | 0 | 300 | 267 | 0 | 0 | 35 | 12 | 260 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 30 | 16 | 11 | 0 | 4 | 32 | 24 | 0 | 50 | 50 | 0 | 40 | 17 | 6 | 1050 | 53 | 0 | 33 | 8 | 48 | 227 | 0 | 0 | 0 | 600 | 0 | 43 | 48 | 195 | 0 | 0 | 0 | 29 | 183 | 37 | 95 | 50 | 50 | 84 | 17 | 17 | 48 | 18 | 0 | 49 | 295 | 320 | 312 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 207 | 47 | 19 | 57 | 6 | 0 | 0 | 23 | 6704 | 918 | 250 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 102 | 35 | 27 | 8 | 0 | 30 | 0 | 156 | 0 | 181 | 0 | 159 | 0 | 0 | 0 | 0 | 11 | 210 | 72 | 68 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 7 | 100 | 180 | 0 | 1060 | 150 | 4086 | 10790 | 92.96
19:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 54 | 36 | 0 | 93 | 16 | 0 | 0 | 17 | 162 | 25 | 0 | 380 | 296 | 0 | 0 | 35 | 26 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 74 | 24 | 0 | 0 | 0 | 0 | 40 | 17 | 10 | 1052 | 0 | 0 | 33 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 0 | 43 | 10 | 197 | 0 | 0 | 0 | 29 | 185 | 37 | 95 | 50 | 51 | 105 | 17 | 0 | 62 | 0 | 0 | 0 | 280 | 320 | 337 | 27 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 207 | 17 | 19 | 58 | 10 | 0 | 0 | 24 | 6687 | 917 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 0 | 0 | 8 | 0 | 16 | 0 | 179 | 0 | 181 | 0 | 180 | 0 | 0 | 0 | 0 | 11 | 210 | 72 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1192 | 150 | 4253 | 10940 | 92.95
19:30 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 54 | 36 | 0 | 105 | 0 | 0 | 0 | 17 | 162 | 25 | 0 | 380 | 295 | 0 | 0 | 35 | 26 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 4 | 78 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 13 | 1053 | 0 | 0 | 33 | 0 | 51 | 227 | 0 | 0 | 0 | 612 | 0 | 43 | 10 | 197 | 0 | 0 | 0 | 29 | 186 | 36 | 95 | 50 | 51 | 105 | 17 | 0 | 58 | 0 | 0 | 0 | 310 | 320 | 337 | 30 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 207 | 0 | 19 | 58 | 10 | 0 | 0 | 24 | 6663 | 918 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 34 | 0 | 0 | 0 | 181 | 0 | 181 | 0 | 180 | 0 | 0 | 0 | 0 | 11 | 210 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1202 | 150 | 4225 | 10888
20:00 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 54 | 36 | 0 | 105 | 0 | 0 | 0 | 0 | 162 | 25 | 0 | 380 | 259 | 0 | 0 | 35 | 26 | 335 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 7 | 80 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 1058 | 0 | 0 | 33 | 0 | 51 | 229 | 0 | 0 | 0 | 610 | 0 | 43 | 10 | 199 | 0 | 0 | 0 | 29 | 182 | 40 | 95 | 50 | 51 | 107 | 17 | 0 | 56 | 0 | 0 | 0 | 295 | 320 | 337 | 30 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 206 | 0 | 19 | 58 | 10 | 0 | 0 | 24 | 6584.5 | 917 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 52.2 | 0 | 0 | 0 | 181 | 0 | 181 | 0 | 181 | 0 | 0 | 0 | 0 | 11 | 210 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1202 | 150 | 4244.2 | 10828.7 | 92.95
21:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 17 | 0 | 78 | 0 | 0 | 0 | 0 | 162 | 25 | 0 | 300 | 276 | 0 | 0 | 35 | 26 | 260 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 1054 | 0 | 0 | 28 | 0 | 17 | 230 | 0 | 0 | 0 | 612 | 0 | 43 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 44 | 95 | 50 | 51 | 105 | 17 | 0 | 56 | 0 | 0 | 0 | 290 | 320 | 337 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 206 | 0 | 19 | 58 | 10 | 0 | 0 | 24 | 6244.5 | 918 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 16 | 0 | 0 | 0 | 181 | 0 | 181 | 0 | 181 | 0 | 0 | 0 | 0 | 11 | 210 | 70 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1202 | 150 | 4266 | 10510.5 | 92.94
22:00 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 17 | 0 | 69 | 0 | 0 | 0 | 0 | 108 | 25 | 0 | 300 | 263 | 0 | 0 | 0 | 26 | 260 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 1055 | 0 | 0 | 18 | 0 | 0 | 229 | 0 | 0 | 0 | 610 | 0 | 43 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 41 | 95 | 50 | 0 | 55 | 17 | 0 | 54 | 0 | 0 | 0 | 285 | 320 | 337 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 205 | 0 | 19 | 58 | 10 | 0 | 0 | 24 | 5947.5 | 917 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 181 | 0 | 181 | 0 | 0 | 0 | 0 | 11 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 1202 | 150 | 4184 | 10131.5 | 92.94
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 271 | 0 | 0 | 0 | 26 | 260 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 1055 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 540 | 0 | 43 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 45 | 0 | 50 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 280 | 320 | 337 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 208 | 0 | 19 | 35 | 13 | 0 | 0 | 24 | 5514 | 917 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 181 | 0 | 179 | 0 | 0 | 0 | 0 | 11 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 7 | 140 | 220 | 0 | 1160 | 0 | 3968 | 9482 | 92.93
Total KWH | 0 | 1116480 | 388320 | 0 | 0 | 0 | 0 | 0 | 8924400 | 0 | 0 | 573480 | 543600 | 0 | 1034208 | 287040 | 0 | 111475 | 107411 | 1291680 | 499320 | 0 | 7642500 | 6784582 | 0 | 0 | 328148 | 553800 | 6445230 | 0 | 0 | 156423 | 0 | 420000 | 525600 | 0 | 0 | 417764 | 37636 | 25920 | 0 | 103200 | 189824 | 53664 | 0 | 69120 | 56640 | 20520 | 970320 | 118760 | 475200 | 25003636.36 | 83636 | 0 | 391680 | 13676.4 | 376363 | 5418960 | 0 | 0 | 0 | 12425453 | 131625 | 1061736 | 184000 | 4248727 | 0 | 0 | 0 | 694080 | 4642000 | 924984 | 976320 | 1189500 | 437280 | 913920 | 374880 | 17100 | 1200000 | 36912 | 435536 | 63152 | 7230000 | 7531800 | 8689000 | 294336 | 701000 | 0 | 58176 | 3833264 | 335328 | 0 | 1384320 | 131040 | 0 | 0 | 5239460 | 133560 | 369600 | 1008000 | 236160 | 10600 | 260780 | 425760 | 139389605.76 | 20842181 | 7115616 | 0 | 20160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 475200 | 0 | 0 | 667025 | 0 | 0 | 39587 | 0 | 40032 | 0 | 427872 | 36096 | 34112 | 115421 | 552720 | 50909 | 299252 | 4204818 | 0 | 4189073 | 0 | 4314018 | 0 | 0 | 0 | 12000 | 162054 | 5100000 | 1706181 | 343589 | 169397 | 42067 | 0 | 0 | 17624.76 | 823680 | 3321 | 0 | 6022000 | 132938 | 3112000 | 5287170 | 0 | 25175272.73 | 1252800 | 92786186.49 | 232175792.25

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 16-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 10343.62 | MW | 12:00 Hr. | Energy Generated |  |  | 232175.7922 |  | MWHr
Day Peak Demand |  |  | 10343.62 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MWHr
Evening Peak Generation |  |  | 10940 | MW | 19:00 Hr. | Energy Demand |  |  | 232175.7922 |  | MWHr
Evening Peak Demand |  |  | 10940 | MW | 19:00 Hr.
Minimum Generation of the Day |  |  | 7526 | MW | 05:00 Hr.
Maximum Generation of the Day |  |  | 10940 | MW | 19:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 31795.432 | 0 | 5781.842 | 0 | 0 | 156.423 | 0 | 0 | 37733.697 | Gas | 115007.07 | Gas | 408813802.32
Chattogram Zone |  |  | 5894.16 | 37429.0894 | 1834.6834 | 0 | 970.32 | 152.145 | 0 | 103.2 | 46383.5978 | Coal | 75432.5431 | Coal | 530982179.2977
Cumilla Zone |  |  | 13135.907 | 0 | 2628.684 | 0 | 0 | 435.536 | 1200 | 0 | 17400.127 | HFO | 14584.7744 | HFO | 266051598.79
Mymensingh Zone |  |  | 236.16 | 0 | 1936.92 | 0 | 0 | 271.38 | 0 | 0 | 2444.46 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 35427.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35427.724 | Hydro | 970.32 | Hydro | 97032
Khulna Zone |  |  | 7115.616 | 0 | 20.16 | 0 | 0 | 475.2 | 20842.181 | 0 | 28453.157 | Solar | 3368.6788 | Solar | 52359288.466
Barishal Zone |  |  | 8532.108 | 31197.2727 | 1252.8 | 0 | 0 | 3.321 | 0 | 0 | 40985.5017 | Import | 22709.206 | Import | 72100412.21
Rajshahi Zone |  |  | 12869.963 | 0 | 744.029 | 0 | 0 | 863.972 | 667.025 | 0 | 15144.989 | Wind | 103.2 | Wind | 1609920
Rangpur Zone |  |  | 0 | 6806.181 | 385.656 | 0 | 0 | 1010.7018 | 0 | 0 | 8202.5388
Total |  |  | 115007.07 | 75432.5431 | 14584.7744 | 0 | 970.32 | 3368.6788 | 22709.206 | 103.2 | 232175.7922
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 408813802.32 |  | Hydro | 97032
|  |  | Coal | 530982179.2977 |  | Solar | 52359288.466
|  |  | HFO | 266051598.79 |  | Import | 72100412.21
|  |  | HSD | 0 |  | Wind | 1609920
|  |  |  | Total: | 1332014233.0837 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
| 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
| 4 | Barapukuria TPP Unit-2 |  |  | 85
| 5 | Khulna 330 MW CCPP GT |  |  | 220
| 6 | Khulna 330 MW CCPP ST |  |  | 110
| 7 | Siddhirgonj 210 MW TPP |  |  | 115
| 8 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 9 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1404 |  |  |  | Total | 435.09
|  |  | Total Unavailable Capacity |  |  |  | 1839.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3977
|  |  | Chattogram |  | 0 |  | 1174
|  |  | Cumilla |  | 0 |  | 897
|  |  | Mymensingh |  | 0 |  | 914
|  |  | Sylhet |  | 0 |  | 381
|  |  | Khulna |  | 0 |  | 1198
|  |  | Barishal |  | 0 |  | 297
|  |  | Rajshahi |  | 0 |  | 984
|  |  | Rangpur |  | 0 |  | 651
|  |  | Total |  | 0 |  | 10473
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:19 | 15:51 | Barishal(N)-Madaripur 132 kV Ckt-1 Scheduled S/D from Barishal 230/132kV end. and from
Madaripur 132/33kV end Due to Annual maintenance
08:20 | 15:11 | Feni-PHP 132kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to Annual Maintenance
08:24 | 13:40 | Bogura-Bogura (New)) 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to Annual
maintenance and from Bogura 230/132kVend.
08:42 | 16:33 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-2 Scheduled S/D Due to Annual Maintenance
08:42 | 16:45 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Annual Maintenance
08:46 | 09:30 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Project Work S/D Due to Old T1 Shifting Work by
Project
08:46 | 09:27 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Project Work S/D Due to Old T1 Shifting Work by
Project
08:50 | 15:01 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to AM
08:52 |  | Kallyanpur 132/33kV S/S Main bus Scheduled S/D Due to ANNUAL MAINTANENCE
08:57 | 15:15 | Sylhet (South) S/S Trafo-1 LT Scheduled S/D Due to Annual maintenance work
08:57 | 15:14 | Sylhet (South) S/S Trafo-1 HT Scheduled S/D Due to Annual maintenance work
09:00 | 09:37 | Kishoreganj 132/33kV S/S Bus-A Project Work S/D Due to Old T1 Shifting Work by Project
09:01 |  | Kushtia 132/33kV S/S T2 LT Scheduled S/D Due to Annual Maintenance | [7 empty] | 10.0MW load
interrup.
09:02 |  | Kushtia 132/33kV S/S T2 HT Scheduled S/D Due to Annual Maintenance | [7 empty] | 10.0MW load
interrup.
09:16 | 15:08 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Scheduled S/D from Srinagar
132/33kV end Due to Dead line checking of 132KV Keraniganj line-02 and from Keranigonj
230/132/33kV end Due to Dead line check from srinagar end.
09:16 | 15:08 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Scheduled S/D from Srinagar
132/33kV end Due to Deadline checking purpose. and from Keranigonj 230/132/33kV end Due
to Dead line check from srinagar end.
09:25 | 16:46 | Patuakhali-Payra 132kV Ckt-2 Scheduled S/D from Payra 400/132/33kV end Due to Annual
Maintrnancr and from Patuakhali 132/33kV end Due to Annual Maintenance-2025
09:50 | 15:05 | Ruppur 132/11kV S/S 132kv BUS-1 Scheduled S/D Due to A/M
09:52 |  | Bibiyana-III 400 MW CCPP, FGMO is OFF with remarks:-
09:56 | 15:17 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual maintenance
10:04 | 16:30 | Sonargaon 132/33kV S/S OPSL(IEL-2) Scheduled S/D Due to Annual maintenance Deadline
chaking work.
10:12 | 17:41 | BIPTC S/S 20D09C 20MVA HT Scheduled S/D Due to Fire Fighting Pipe Painting
10:18 | 17:53 | BIPTC S/S 20DF44 Scheduled S/D Due to Fire Fighting Pipe Painting
12:00 |  | Day peak Generation is 10341 MW
12:16 | 12:36 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance
Protection 21/1: (Z1,BN) relays Due to Unknown
13:57 | 15:06 | Shahjibazar-Sreemangal 132kV Ckt-1 Tripped from Sreemongol 132/33kV end showing Distance
relay . relays Due to LA blast of shajirbazar ckt 1 blue phase. and from Shahjibazar
132/33kV end showing Distance Realy . relays Due to Shahjibazar-Sreemongal ckt-01 Blue
phase LA Blast at Sreemongal grid S/S.
14:00 | 15:05 | Shahjibazar-Sreemangal 132kV Ckt-1 Forced S/D from Sreemongol 132/33kV end Due to LA
Change of shajirbazar ckt 1 blue phase.
14:36 | 16:39 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Project Work S/D Due to 50/75 MVA
transformer shifting
14:37 | 16:38 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Project Work S/D
| 16:25 | Bagerhat-Labanchura 132 kV Ckt-2 is restored.
| 16:50 | Sylhet 132/33kV S/S T1 HT is restored.
| 18:00 | Mymensingh RPCL -Mymensingh 132kV Ckt-2 is restored.
18:21 | 18:44 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Instant o/c,definite O/C,instant E/F | [7 empty] | 71.0MW load
|  | relays Due to 33 kv padma blowing feeder fault loop disconnect. | [7 empty] | interrup.
18:21 | 18:44 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Instant O/c,defenite O/C,Instant E/F. | [7 empty] | 71.0MW load
|  | relays Due to 33 kv padma blowing feeder loop disconnect. | [7 empty] | interrup.
| 18:44 | Barishal 132/33kV S/S T-2 (415T) LT is restored.
19:00 |  | Evening Peak Generation: 10940 MW.
| 19:13 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 is restored.
19:31 |  | Adani Power Jharkhand Ltd. Unit-2 was sync.
| 19:32 | Cumilla(N) 230/132/33kV S/S 132KV T-05 HT is restored.
| 19:33 | Cumilla(N) 230/132/33kV S/S 132KV T-05 LT is restored.
05:00 |  | Min. Gen. 7469 MW
06:42 |  | Dohazari 132/33 kv T-2 was shut down for 33 kv bus development work
06:44 |  | Dohazari 132/33 T-1 was shut down for 33 kv bus development work. | [7 empty] | 45MW load interrup.
07:35 |  | Hasnabad-Sitalakhya 132kV Ckt-1 Scheduled S/D from Shitalakhya 132/33kV end Due to Annual
maintenance
07:46 |  | Shahjibazar-Sreemangal 132kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to
shutdown taken by Sreemongal grid
07:52 |  | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D
07:55 |  | Fatullah 132/33kV S/S 132 kV Hasnabad Scheduled S/D
07:57 |  | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Scheduled S/D Due to Deadline checking
07:58 |  | Jashore-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end.
07:59 |  | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Scheduled S/D Due to As per order of
ALDC
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 405 | 8924400 | DP High
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 7642500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 296 | 6784582 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 111475 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6445230 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 573480 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 287040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 107411 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 328148 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 420000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 525600 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 499320 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 26 | 553800 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 26 | 388320 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 93 | 1034208 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1116480 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1291680 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 156423 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 36 | 543600 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 2015 | 37733697
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 13676.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 131625 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 391680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 970320 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 5418960 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 376363 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 24 | 53664 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 74 | 189824 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 69120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 0 | 10 | 475200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 25920 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 37636 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 118760 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 56640 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 417764 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 83636 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 12425453 | network constraint
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 4 | 103200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 1052 | 25003636.36 | -
Chattogram Area Total |  |  |  |  | 4873.22 | 2179 | 46383597.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 185 | 4642000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 37 | 924984 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 694080 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 4248727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 1061736 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 10 | 184000 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 63152 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1189500 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 437280 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 62 | 1200000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 36912 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 374880 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 17100 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 913920 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 976320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 435536 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 881 | 17400127
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 10 | 236160 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1008000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 369600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 260780 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 425760 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 133560 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 128 | 2444460
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 701000 | Gas shortage
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3833264 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 27 | 294336 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 58176 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 20 | 131040 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1384320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 207 | 5239460 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 335328 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7230000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 337 | 8689000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7531800 | FGMO
Sylhet Area Total |  |  |  |  | 2368.568 | 1484 | 35427724
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 917 | 20842181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 20160 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 278 | 7115616 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 475200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1195 | 28453157
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 132938 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 3112000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1192 | 25175272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5287170 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1252800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6022000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3321 | -
Barishal Area Total |  |  |  |  | 2265.1 | 2016 | 40985501.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 50 | 39587 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 34112 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 179 | 4204818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 181 | 4189073 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 180 | 4314018 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 16 | 50909 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 11 | 162054 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 115421 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 427872 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 40032 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 36096 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 12000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 0 | 667025 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 299252 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 552720 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 725 | 15144989
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 72 | 1706181 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 5100000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 42067 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 17624.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 343589 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 169397 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 823680 | -
Rangpur Area Total |  |  |  |  | 950 | 317 | 8202538.76
Eastern Grid Total |  |  |  |  | 16730.748 | 6687 | 139389605.76
Western Grid Total |  |  |  |  | 10294.5 | 4253 | 92786186.49
National Grid Total |  |  |  |  | 27025.248 | 10940 | 232175792.25
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7342.72 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3130 | MW
i) Dhaka area |  |  | 3977.22 |  | MW | i) Khulna area |  |  |  | 1198 | MW
ii) Chattogram area |  |  | 1173.5 |  | MW | ii) Barishal area |  |  |  | 297 | MW
iii) Cumilla area |  |  | 897 |  | MW | iii) Rajshahi area |  |  |  | 984 | MW
iv) Mymensingh area |  |  | 914 |  | MW | iv) Rangpur area |  |  |  | 651 | MW
v) Sylhet area |  |  | 381 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10472.72 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 16 | 16:00 | 67 | Jaldhaka | 56 | 18:30 | 133 | Purbachal | 15 | 13:00
2 | AKSML | 101 | 09:00 | 68 | Jamalpur | 97 | 08:00 | 134 | Purbasadipur | 100 | 13:00
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 100 | 08:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 73 | 13:00 | 70 | Jhenaidah | 93 | 18:00 | 136 | Rahim | 33 | 16:00
5 | Agrabad | 66 | 18:00 | 71 | Joydebpur | 137 | 10:00 | 137 | Rajbari | 56 | 18:30
6 | Amnura | 49 | 12:00 | 72 | Joypurhat | 42 | 20:00 | 138 | Rajendrapur | 98 | 13:00
7 | Ashuganj | 84 | 18:30 | 73 | Juldah | 11 | 00:00 | 139 | Rajshahi | 94 | 21:00
8 | BSRM | 197 | 14:00 | 74 | KSRM | 20 | 00:00 | 140 | Rajshahi-230 | 38 | 13:00
9 | Bagerhat | 62 | 18:30 | 75 | Kabirpur | 209 | 18:00 | 141 | Ramganj | 76 | 18:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 50 | 21:00 | 142 | Rampur | 26 | 18:00
11 | Bakulia | 86 | 12:00 | 77 | Kallyanpur | 69 | 13:00 | 143 | Rangamati | 12 | 18:00
12 | Banani | 37.4 | 12:00 | 78 | Kalurghat | 12 | 12:00 | 144 | Rangpur | 106 | 13:00
13 | Bangabhaban | 8 | 10:00 | 79 | Kamrangirchar | 57.9 | 13:00 | 145 | Ruppur | 4.4 | 16:00
14 | Barapukuria | 53 | 18:30 | 80 | Kaptai | N/A | N/A | 146 | SSM | 16 | 07:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 98 | 12:00 | 147 | Saidpur | 93 | 09:00
16 | Barishal | 82 | 13:00 | 82 | Keranigonj | 58 | 13:00 | 148 | Satkhira | 85 | 18:30
17 | Barishal-230 | 72 | 21:00 | 83 | Khagrachori | 24 | 18:00 | 149 | Satmasjid | 81 | 13:00
18 | Baroaulia | 67 | 12:00 | 84 | Khulna | 68 | 13:00 | 150 | Savar | 162 | 15:00
19 | Baroirhat | 49 | 13:00 | 85 | Khulshi | 136 | 13:00 | 151 | SevenRings | 15.58 | 00:00
20 | Bashundhara | 130 | 13:00 | 86 | Kishoreganj | 124 | 18:30 | 152 | ShahCement | 36 | 10:00
21 | BashundharaCement | 12 | 12:00 | 87 | Kodda | 252 | 18:00 | 153 | Shahjadpur | 52 | 19:00
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 27 | 18:30 | 154 | Shahjibazar | 91 | 18:30
23 | Benapole | 54 | 08:00 | 89 | Kurigram | 48 | 18:00 | 155 | Shahmirpur | 47 | 00:00
24 | Bhaluka | 134 | 08:00 | 90 | Kushtia | 106 | 18:00 | 156 | Shariatpur | 53 | 21:00
25 | Bhandaria | 34 | 21:00 | 91 | Lalbag | 56 | 18:00 | 157 | Sherpur | 118 | 18:00
26 | Bhangura | 23 | 18:00 | 92 | Lalmonirhat | 41 | 18:00 | 158 | Shikalbaha | 23 | 13:00
27 | Bheramara(GK) | 40 | 18:00 | 93 | MI_Cement | 18 | 17:00 | 159 | Shitalakhya | 61.2 | 12:00
28 | Bhulta | 242.5 | 10:00 | 94 | Madanganj | 14 | 12:00 | 160 | Sholosohor | 33 | 13:00
29 | Bog-Sherpur | 52 | 09:00 | 95 | Madaripur | 66 | 13:00 | 161 | Shyampur | 154 | 13:00
30 | Bogura | 101 | 18:00 | 96 | Madartek | 46.24 | 13:00 | 162 | Siddhirganj | 93 | 12:00
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 37 | 18:00 | 163 | Sirajganj | 66 | 12:00
32 | Brahmanbaria | 102 | 19:30 | 98 | Magura | 45 | 18:00 | 164 | Sonargaon | 76 | 10:00
33 | Cantonment | 80 | 13:00 | 99 | Mahasthangarh | 58 | 18:00 | 165 | Sreemongol | 47 | 20:00
34 | Chandpur | 46 | 18:00 | 100 | Manikganj | 106 | 18:30 | 166 | Sreepur | 75 | 15:00
35 | Chandraghona | 26 | 18:30 | 101 | Maniknagar | 48 | 13:00 | 167 | Srinagar | 30 | 20:00
36 | Chapai | 47 | 09:00 | 102 | Matarbari | 38 | 18:00 | 168 | Sunamganj | 36 | 19:30
37 | Charsaidpur | 44 | 18:30 | 103 | Matuail | 51 | 15:00 | 169 | Sylhet | 28 | 19:00
38 | Chauddagram | 46 | 13:00 | 104 | Millgate | 70 | 11:00 | 170 | Sylhet-132 | 78 | 13:00
39 | Chhatak | 21 | 18:30 | 105 | Mirpur | 94 | 18:30 | 171 | TK | 21 | 19:30
40 | Chowmuhani | 152 | 18:00 | 106 | Mirsorai | 8 | 18:00 | 172 | Tangail | 146 | 07:00
41 | Chuadanga | 76 | 13:00 | 107 | Mirzapur | 36 | 20:00 | 173 | Thakurgaon | 74 | 18:30
42 | Coxsbazar | 106 | 18:00 | 108 | Mithapukur | 43 | 18:00 | 174 | Tongi | 113 | 11:00
43 | Cumilla(N) | 125 | 13:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 24 | 06:00
44 | Cumilla(S) | 119 | 11:00 | 110 | Mogbazar | 97 | 15:00 | 176 | Ullon | 34 | 13:00
45 | Daudkandi | 102 | 19:00 | 111 | Mongla | 34 | 12:00 | 177 | Uttara | 59 | 13:00
46 | Dhaka | 32 | 12:00 | 112 | Motijheel | 26 | 13:00 | 178 | UttaraNew | 33 | 13:00
47 | Dhamrai | 94 | 09:00 | 113 | Muktagacha | 25 | 13:00 | 179 | Zigatola | 55 | 13:00
48 | Dhanmondi | 98 | 13:00 | 114 | Munshiganj | 70 | 21:00
49 | Dohazari | 69 | 18:00 | 115 | Mymensingh | 143 | 13:00
50 | Faridpur | 106 | 20:00 | 116 | Naogaon | 87 | 09:00
51 | Fatullah | 77 | 15:00 | 117 | Narail | 42 | 18:30
52 | Fenchuganj | 25 | 12:00 | 118 | Narinda | 57 | 13:00
53 | Feni | 70 | 18:00 | 119 | Narshingdi | 153 | 20:00
54 | GPH | 101 | 01:00 | 120 | Natore | 103 | 18:30
55 | Ghatail | 32 | 08:00 | 121 | Nawabganj | 37.06 | 13:00
56 | Ghorashal | 10 | 20:00 | 122 | Netrakona | 135 | 18:00
57 | Ghorashal-230 | 56 | 09:00 | 123 | New | 70.1 | 12:00
58 | Goalpara | 26 | 13:00 | 124 | Niamatpur | 72 | 08:00
59 | Gollamari | 52 | 13:00 | 125 | Noapara | 32 | 18:30
60 | Gopalganj | 78.6 | 18:30 | 126 | PHP | 8 | 10:00
61 | Gulshan | 64 | 17:00 | 127 | Pabna | 81 | 18:30
62 | Halishahar | 48 | 16:00 | 128 | Palashbari | 74 | 18:30
63 | HaripurSBU | 172 | 09:00 | 129 | Panchagarh | 41 | 18:00
64 | Hasnabad | 66 | 12:00 | 130 | Patuakhali | 56 | 20:00
65 | Hathazari | 51 | 13:00 | 131 | Payra | 14 | 12:00
66 | Ishurdi | 57 | 18:30 | 132 | Postogola | 38 | 18:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9065 | 0 |  | 9065
1:00 | 8566.71 | 0 |  | 8566.71
2:00 | 8062 | 0 |  | 8062
3:00 | 7751 | 0 |  | 7751
4:00 | 7579 | 0 |  | 7579
5:00 | 7526 | 0 |  | 7526
6:00 | 7927.5 | 0 |  | 7927.5
7:00 | 8706.38 | 0 |  | 8706.38
8:00 | 9541.76 | 0 |  | 9541.76
9:00 | 10028.1 | 0 |  | 10028.1
10:00 | 9798.87 | 0 |  | 9798.87
11:00 | 9891.45 | 0 |  | 9891.45
12:00 | 10343.62 | 0 |  | 10343.62
13:00 | 10665.31 | 0 |  | 10665.31
14:00 | 10330.72 | 0 |  | 10330.72
15:00 | 10002.34 | 0 |  | 10002.34
16:00 | 9604.86 | 0 |  | 9604.86
17:00 | 9749.04 | 0 |  | 9749.04
18:00 | 10790 | 0 |  | 10790
19:00 | 10940 | 0 |  | 10940
19:30 | 10888 | 0 |  | 10888
20:00 | 10828.7 | 0 |  | 10828.7
21:00 | 10510.5 | 0 |  | 10510.5
22:00 | 10131.5 | 0 |  | 10131.5
23:00 | 9482 | 0 |  | 9482
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 16-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3043 | 1735 | 915 | 0 | 50 | 0 | 40 | 3073 | 0 | 25 | 175 | 0 | 0 | 9 | 0 | DAILY ENERGY CURVE
00:30 | 2982 | 1702.25 | 914.5 | 0 | 51 | 0 | 40 | 2944 | 6.605 | 25 | 142.5 | 0 | 0 | 8 | 0 | 16-01-2025
01:00 | 2921 | 1669.5 | 914 | 0 | 52 | 0 | 40 | 2815 | 13.21 | 25 | 110 | 0 | 0 | 7 | 0
01:30 | 2920.5 | 1674.25 | 820.5 | 0 | 51 | 0 | 40 | 2692.5 | 6.605 | 12.5 | 88.5 | 0 | 0 | 8 | 0 |  | Total Energy | 232.1758 |  | MKWHr
02:00 | 2920 | 1679 | 727 | 0 | 50 | 0 | 40 | 2570 | 0 | 0 | 67 | 0 | 0 | 9 | 0 |  | Energy not Served | 0 |  | MKWHr
02:30 | 2922 | 1658 | 727.5 | 0 | 47 | 0 | 40 | 2455.5 | 0 | 0 | 47 | 0 | 0 | 9.5 | 0 |  | Energy Requirement | 232.1758 |  | MKWHr
03:00 | 2924 | 1637 | 728 | 0 | 44 | 0 | 40 | 2341 | 0 | 0 | 27 | 0 | 0 | 10 | 0
03:30 | 2929.5 | 1651 | 681 | 0 | 42 | 0 | 40 | 2290 | 0 | 0 | 22.5 | 0 | 0 | 9 | 0
04:00 | 2935 | 1665 | 634 | 0 | 40 | 0 | 40 | 2239 | 0 | 0 | 18 | 0 | 0 | 8 | 0
04:30 | 2924 | 1652 | 634 | 0 | 40 | 0 | 40 | 2237.5 | 0 | 1 | 18.5 | 0 | 0 | 5.5 | 0
05:00 | 2913 | 1639 | 634 | 0 | 40 | 0 | 40 | 2236 | 0 | 2 | 19 | 0 | 0 | 3 | 0
05:30 | 2910.5 | 1664.75 | 680.5 | 0 | 45 | 0 | 40 | 2348.5 | 0 | 9 | 24 | 0 | 0 | 4.5 | 0
06:00 | 2908 | 1690.5 | 727 | 0 | 50 | 0 | 40 | 2461 | 0 | 16 | 29 | 0 | 0 | 6 | 0
06:30 | 2936.5 | 1721 | 821 | 0 | 50 | 0 | 40 | 2639 | 4.44 | 36 | 63 | 0 | 0 | 6 | 0
07:00 | 2965 | 1751.5 | 915 | 0 | 50 | 0 | 40 | 2817 | 8.88 | 56 | 97 | 0 | 0 | 6 | 0
07:30 | 2988.5 | 1768.3 | 916 | 0 | 48 | 0 | 40 | 3063 | 55.77 | 73.5 | 167 | 0 | 0 | 4 | 0
08:00 | 3012 | 1785.1 | 917 | 0 | 46 | 0 | 40 | 3309 | 102.66 | 91 | 237 | 0 | 0 | 2 | 0
08:30 | 2971 | 1756.55 | 917.5 | 0 | 44 | 0 | 40 | 3382 | 192.38 | 102 | 378.5 | 0 | 0 | 1 | 0
09:00 | 2930 | 1728 | 918 | 0 | 42 | 0 | 40 | 3455 | 282.1 | 113 | 520 | 0 | 0 | 0 | 0
09:30 | 2864.5 | 1669.5 | 917 | 0 | 48 | 0 | 40 | 3380 | 347.985 | 112.5 | 534 | 0 | 0 | 0 | 0
10:00 | 2799 | 1611 | 916 | 0 | 54 | 0 | 40 | 3305 | 413.87 | 112 | 548 | 0 | 0 | 0 | 0
10:30 | 2841 | 1601.5 | 917 | 0 | 57 | 0 | 40 | 3282 | 471.66 | 112 | 523 | 0 | 0 | 0 | 0
11:00 | 2883 | 1592 | 918 | 0 | 60 | 0 | 40 | 3259 | 529.45 | 112 | 498 | 0 | 0 | 0 | 0
11:30 | 2982 | 1665 | 918 | 0 | 52 | 0 | 40 | 3312 | 542.035 | 112 | 494.5 | 0 | 0 | 0 | 0
12:00 | 3081 | 1738 | 918 | 0 | 44 | 0 | 40 | 3365 | 554.62 | 112 | 491 | 0 | 0 | 0 | 0
12:30 | 3075.5 | 1719.25 | 917.5 | 0 | 51 | 0 | 40 | 3429 | 538.215 | 112 | 622 | 0 | 0 | 0 | 0
13:00 | 3070 | 1700.5 | 917 | 0 | 58 | 0 | 40 | 3493 | 521.81 | 112 | 753 | 0 | 0 | 0 | 0
13:30 | 3038.5 | 1701.5 | 917 | 0 | 55 | 0 | 40 | 3468.5 | 494.515 | 112 | 671 | 0 | 0 | 0 | 0
14:00 | 3007 | 1702.5 | 917 | 0 | 52 | 0 | 40 | 3444 | 467.22 | 112 | 589 | 0 | 0 | 0 | 0
14:30 | 3012 | 1669 | 917.5 | 0 | 49 | 0 | 40 | 3443 | 404.53 | 112 | 519.5 | 0 | 0 | 0 | 0
15:00 | 3017 | 1635.5 | 918 | 0 | 46 | 0 | 40 | 3442 | 341.84 | 112 | 450 | 0 | 0 | 0 | 0
15:30 | 3027 | 1660.5 | 918 | 0 | 48 | 0 | 40 | 3368 | 266.1 | 102 | 373.5 | 0 | 0 | 0.5 | 0
16:00 | 3037 | 1685.5 | 918 | 0 | 50 | 0 | 40 | 3294 | 190.36 | 92 | 297 | 0 | 0 | 1 | 0
16:30 | 3038 | 1685.25 | 918 | 0 | 49 | 0 | 40 | 3293 | 110.7 | 121 | 421 | 0 | 0 | 1 | 0
17:00 | 3039 | 1685 | 918 | 0 | 48 | 0 | 40 | 3292 | 31.04 | 150 | 545 | 0 | 0 | 1 | 0
17:30 | 2969 | 1692 | 918 | 0 | 48 | 0 | 40 | 3284 | 15.52 | 307.5 | 993 | 0 | 0 | 2.5 | 0
18:00 | 2899 | 1699 | 918 | 0 | 48 | 0 | 40 | 3276 | 0 | 465 | 1441 | 0 | 0 | 4 | 0
18:30 | 3010 | 1784.5 | 917.5 | 0 | 55 | 0 | 40 | 3360.5 | 0 | 420.5 | 1273 | 0 | 0 | 4 | 0
19:00 | 3121 | 1870 | 917 | 0 | 62 | 0 | 40 | 3445 | 0 | 376 | 1105 | 0 | 0 | 4 | 0
19:30 | 3129 | 1905 | 918 | 0 | 58 | 0 | 40 | 3454 | 0 | 254 | 1126 | 0 | 0 | 4 | 0
20:00 | 3127 | 1865.5 | 917 | 0 | 56 | 0 | 40 | 3457 | 0 | 247 | 1112.2 | 0 | 0 | 7 | 0
20:30 | 3090.5 | 1825.5 | 917.5 | 0 | 56 | 37 | 40 | 3456 | 0 | 202.5 | 1038.1 | 0 | 0 | 6.5 | 0
21:00 | 3054 | 1785.5 | 918 | 0 | 56 | 74 | 40 | 3455 | 0 | 158 | 964 | 0 | 0 | 6 | 0
21:30 | 3050.5 | 1776.5 | 917.5 | 0 | 55 | 100.5 | 40 | 3454.5 | 0 | 104 | 814.5 | 0 | 0 | 8 | 0
22:00 | 3047 | 1767.5 | 917 | 0 | 54 | 127 | 40 | 3454 | 0 | 50 | 665 | 0 | 0 | 10 | 0
22:30 | 3051.5 | 1770.25 | 917 | 0 | 56 | 155.5 | 40 | 3358.5 | 0 | 42 | 406 | 0 | 0 | 10 | 0
23:00 | 3056 | 1773 | 917 | 0 | 58 | 184 | 40 | 3263 | 0 | 34 | 147 | 0 | 0 | 10 | 0
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5457.5 | 3607.5 | 9065 | DAILY LOAD CURVE
00:30 | 5310.355 | 3505.5 | 8815.855
01:00 | 5163.21 | 3403.5 | 8566.71 | 16-01-2025
01:30 | 5080.355 | 3234 | 8314.355
02:00 | 4997.5 | 3064.5 | 8062
02:30 | 4883 | 3023.5 | 7906.5
03:00 | 4768.5 | 2982.5 | 7751
03:30 | 4778.5 | 2886.5 | 7665
04:00 | 4788.5 | 2790.5 | 7579
04:30 | 4765.5 | 2787 | 7552.5
05:00 | 4742.5 | 2783.5 | 7526
05:30 | 4840.75 | 2886 | 7726.75
06:00 | 4939 | 2988.5 | 7927.5
06:30 | 5138.84 | 3178.1 | 8316.94
07:00 | 5338.68 | 3367.7 | 8706.38
07:30 | 5517.175 | 3606.895 | 9124.07
08:00 | 5695.67 | 3846.09 | 9541.76
08:30 | 5780.31 | 4004.62 | 9784.93
09:00 | 5864.95 | 4163.15 | 10028.1
09:30 | 5842.66 | 4070.825 | 9913.485
10:00 | 5820.37 | 3978.5 | 9798.87
10:30 | 5812.69 | 4032.47 | 9845.16
11:00 | 5805.01 | 4086.44 | 9891.45
11:30 | 5906.805 | 4210.73 | 10117.535
12:00 | 6008.6 | 4335.02 | 10343.62
12:30 | 6087.265 | 4417.2 | 10504.465
13:00 | 6165.93 | 4499.38 | 10665.31
13:30 | 6104.53 | 4393.485 | 10498.015
14:00 | 6043.13 | 4287.59 | 10330.72
14:30 | 5965.005 | 4201.525 | 10166.53
15:00 | 5886.88 | 4115.46 | 10002.34
15:30 | 5795.045 | 4008.555 | 9803.6
16:00 | 5703.21 | 3901.65 | 9604.86
16:30 | 5810.815 | 3866.135 | 9676.95
17:00 | 5918.42 | 3830.62 | 9749.04
17:30 | 6311.21 | 3958.31 | 10269.52
18:00 | 6704 | 4086 | 10790
18:30 | 6695.5 | 4169.5 | 10865
19:00 | 6687 | 4253 | 10940
19:30 | 6663 | 4225 | 10888
20:00 | 6584.5 | 4244.2 | 10828.7
20:30 | 6414.5 | 4255.1 | 10669.6 |  | Executive Engineer
21:00 | 6244.5 | 4266 | 10510.5 |  | Network Operation Division
21:30 | 6096 | 4225 | 10321
22:00 | 5947.5 | 4184 | 10131.5
22:30 | 5730.75 | 4076 | 9806.75
23:00 | 5514 | 3968 | 9482

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 415 | 05:00 | 389 | 11:00 | Kaliakoir | 375 | 04:00 | 348 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 410 | 5:00 | 382 | 12:00 | Madunaghat | 409 | 04:00 | 395 | 13:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 409 | 05:00 | 384 | 12:00 | Meghnaghat | 411 | 05:00 | 386 | 12:00
| Bibiana | 396 | 00:00 | 386 | 11:00 | Payra | 419 | 05:00 | 406 | 12:00
| BIPTC | 407 | 02:00 | 390 | 10:00 | Rahanpur | 418 | 23:00 | 381 | 08:00
| Bogura | 414 | 23:00 | 383 | 08:00 | Rampal | 415 | 04:00 | 384 | 13:00
| Gopalganj | 419 | 05:00 | 393 | 12:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 236 | 04:00 | 221 | 12:00 | Haripur | 238 | 04:00 | 223 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 233 | 18:30 | 223 | 12:00 | Hasnabad | 235 | 05:00 | 222 | 12:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 235 | 02:00 | 221 | 11:00 | Hathazari | 236 | 18:00 | 226 | 12:00
| Ashuganj | 238 | 03:00 | 228 | 12:00 | Ishurdi | 244 | 04:00 | 229 | 08:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 03:00 | 228 | 12:00 | Jhenaidah | 241 | 04:00 | 224 | 13:00
| Baghabari | 241 | 23:00 | 231 | 07:00 | Kaliakoir | 236 | 04:00 | 218 | 12:00 | 230 kV MAX | 248 |  | 248 | 216
| Barapukuria | 225 | 11:00 | 216 | 08:00 | Keranigonj | 235 | 04:00 | 220 | 12:00 | 230 kV MIN | 216 |  | 244 | 218 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 225 | 11:00 | 216 | 08:00 | Khulna(S) | 242 | 04:00 | 225 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 246 | 04:00 | 235 | 12:00 | Madunaghat | 232 | 17:00 | 224 | 01:00 | 132 kV MAX | 143 |  | 142 | 112 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 242 | 04:00 | 226 | 08:00 | Madunaghat-400 | 234 | 04:00 | 225 | 13:00 | 132 kV MIN | 110 |  | 143 | 110 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 239 | 05:00 | 223 | 12:00 | Maniknagar | 236 | 01:00 | 224 | 12:00 | [35 empty] | 6:00
| Bibiana | 228 | 04:00 | 223 | 16:00 | Meghnaghat | 241 | 23:00 | 230 | 10:00 |  | 400 | [33 empty] | 392
| BIPTC | 244 | 04:00 | 226 | 08:00 | Meghnaghat-400 | 239 | 03:00 | 226 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 239 | 03:00 | 224 | 08:00 | Mirsorai | 233 | 18:00 | 221 | 12:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 238 | 23:00 | 222 | 08:00 | Rajshahi | 242 | 05:00 | 225 | 08:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 248 | 01:00 | 242 | 12:00 | Rampal | 240 | 03:00 | 221 | 13:00 |  | 132 |  |  | Ash 400-299274
| BSRM | 233 | 18:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 233 | 05:00 | 221 | 12:00 | Rampura | 238 | 04:00 | 224 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 247 | 03:00 | 233 | 12:00 | Shikalbaha | 232 | 03:00 | 223 | 12:00 |  | kaptai by call 399528
| Fenchuganj | 234 | 18:30 | 218 | 01:00 | Shyampur | 237 | 05:00 | 221 | 12:00
| Ghorashal | 240 | 00:00 | 230 | 14:00 | Siddhirganj | 237 | 00:00 | 225 | 12:00
| Ghorashal-230 | 236 | 04:00 | 222 | 12:00 | Sirajgonj | 246 | 04:00 | 235 | 08:00
| Gopalganj | 247 | 05:00 | 233 | 12:00 | Sreepur | 238 | 05:00 | 229 | 08:00
| GPH | 232 | 18:00 | 222 | 12:00 | Tongi | 234 | 01:00 | 217 | 11:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 137 | 06:00 | 127 | 12:00 | Kurigram | 130 | 04:00 | 115 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 138 | 05:00 | 127 | 12:00 | Kushtia | 140 | 02:00 | 132 | 08:00
| Agrabad | 133 | 01:00 | 127 | 12:00 | Lalbag | 136 | 00:00 | 129 | 12:00
| AKS | 130 | 09:00 | 125 | 12:00 | Lalmonirhat | 130 | 04:00 | 121 | 23:00
| Aminbazar | 136 | 02:00 | 126 | 14:00 | Madanganj | 135 | 04:00 | 129 | 12:00
| Amnura | 141 | 18:00 | 128 | 08:00 | Madaripur | 134 | 03:00 | 130 | 14:00
| Ashuganj | 140 | 03:00 | 135 | 12:00 | Madartek | 136 | 03:00 | 127 | 11:00
| Bagerhat | 138 | 01:00 | 124 | 13:00 | Madunaghat | 134 | 19:30 | 129 | 12:00
| Bajitpur | 134 | 17:00 | 129 | 12:00 | Magura | 141 | 03:00 | 129 | 13:00
| Bakulia | 134 | 04:00 | 128 | 12:00 | Mahasthangarh | 134 | 04:00 | 125 | 08:00
| Banani | 138 | 02:00 | 127 | 11:00 | Manikganj | 131 | 18:00 | 124 | 12:00
| Bangabhaban | 136 | 04:00 | 126 | 12:00 | Maniknagar | 135 | 05:00 | 126 | 12:00
| Barapukuria | 135 | 02:00 | 127 | 08:00 | Matarbari | 129 | 00:00 | 119 | 12:00
| Barguna | 141 | 22:00 | 134 | 23:00 | Matuail | 133.5 | 03:00 | 127 | 12:00
| Barishal | 136 | 04:00 | 128 | 12:00 | Millgate | 138 | 04:00 | 124 | 12:00
| Barishal-230 | 137 | 04:00 | 130 | 12:00 | Mirpur | 134 | 00:00 | 125 | 12:00
| Baroaulia | 134 | 18:00 | 128 | 12:00 | Mirzapur | 131 | 23:00 | 122 | 12:00
| Baroirhat | 134 | 18:00 | 125 | 12:00 | Mithapukur | 134 | 04:00 | 128 | 07:00
| Bashundhara | 138 | 05:00 | 125 | 12:00 | MI_Cement | 137 | 04:00 | 128 | 12:00
| BashundharaCement | 135 | 04:00 | 125 | 03:00 | Modern | 135 | 05:00 | 126 | 12:00
| Beanibazar | 135 | 03:00 | 131 | 14:00 | Mogbazar | 137 | 03:00 | 128 | 14:00
| Benapole | 139 | 03:00 | 124 | 13:00 | Mongla | 135 | 04:00 | 124 | 13:00
| Bhaluka | 130 | 04:00 | 121 | 08:00 | Motijheel | 136 | 04:00 | 126 | 12:00
| Bhandaria | 135 | 03:00 | 126 | 12:00 | Muktagacha | 127 | 16:00 | 118 | 18:00
| Bhangura | 141 | 04:00 | 133 | 12:00 | Munshiganj | 135 | 05:00 | 127 | 12:00
| Bheramara | 141 | 04:00 | 133 | 08:00 | Mymensingh | 128 | 00:00 | 116 | 18:00
| Bheramara(GK) | 141 | 03:00 | 135 | 08:00 | Naogaon | 134 | 04:00 | 128 | 08:00
| Bhulta | 125 | 18:00 | 116 | 12:00 | Narail | 140 | 03:00 | 129 | 08:00
| Bog-Sherpur | 136 | 23:00 | 126 | 08:00 | Narinda | 135 | 05:00 | 126 | 12:00
| Bogura | 136 | 05:00 | 126 | 08:00 | Narshingdi | 136 | 00:00 | 122 | 11:00
| Bogura-230 | 138 | 03:00 | 127 | 08:00 | Natore | 138 | 02:00 | 130 | 08:00
| Brahmanbaria | 136 | 00:00 | 130 | 12:00 | Nawabganj | 138 | 02:00 | 128 | 12:00
| Cantonment | 138 | 05:00 | 127 | 12:00 | Netrakona | 127 | 01:00 | 117 | 13:00
| Chandpur | 139 | 18:00 | 126 | 12:00 | New | 138 | 03:00 | 126 | 12:00
| Chandraghona | 135 | 18:00 | 129 | 12:00 | Niamatpur | 142 | 22:00 | 132 | 00:00
| Chapai | 140 | 20:00 | 134 | 06:00 | Noapara | 140 | 01:00 | 128 | 12:00
| Charsaidpur | 136 | 04:00 | 128 | 12:00 | Pabna | 141 | 04:00 | 131 | 08:00
| Chauddagram | 132 | 01:00 | 125 | 12:00 | Palashbari | 132 | 03:00 | 125 | 08:00
| Chhatak | 135 | 04:00 | 130 | 11:00 | Panchagarh | 135 | 04:00 | 121 | 08:00
| Chowmuhani | 134 | 18:30 | 123 | 12:00 | Patuakhali | 140 | 19:30 | 134 | 05:00
| Chuadanga | 140 | 02:00 | 128 | 08:00 | Payra | 137 | 01:00 | 134 | 12:00
| Coxsbazar | 124 | 00:00 | 119 | 12:00 | PHP | 133 | 18:00 | 125 | 12:00
| Cumilla(N) | 136 | 01:00 | 128 | 12:00 | Postogola | 139 | 03:00 | 130 | 12:00
| Cumilla(S) | 136 | 18:00 | 127 | 12:00 | Purbachal | 138 | 04:00 | 127 | 12:00
| Daudkandi | 133 | 01:00 | 125 | 12:00 | Purbasadipur | 132 | 18:00 | 122 | 08:00
| Dhaka | 137 | 03:00 | 127 | 12:00 | Rahanpur | 142 | 20:00 | 131 | 07:00
| Dhamrai | 133 | 00:00 | 125 | 12:00 | Rahanpur-400 | 142 | 22:00 | 129 | 08:00
| Dhanmondi | 137 | 03:00 | 127 | 12:00 | Rahim | 135 | 05:00 | 127 | 13:00
| Dohazari | 131 | 17:00 | 124 | 12:00 | Rajbari | 137 | 04:00 | 128 | 13:00
| Faridpur | 137 | 02:00 | 129 | 13:00 | Rajendrapur | 134 | 00:00 | 126 | 13:00
| Fatullah | 138 | 04:00 | 129 | 12:00 | Rajshahi | 138 | 01:00 | 132 | 08:00
| Fenchuganj | 139 | 01:00 | 135 | 11:00 | Rajshahi-230 | 140 | 05:00 | 126 | 08:00
| Feni | 133 | 19:00 | 124 | 12:00 | Ramganj | 136 | 18:00 | 123 | 14:00
| Ghatail | 128 | 00:00 | 121 | 09:00 | Rampur | 134 | 04:00 | 126 | 11:00
| Ghorashal | 140 | 01:00 | 135 | 13:00 | Rampura | 137 | 05:00 | 127 | 12:00
| Goalpara | 141 | 01:00 | 127 | 13:00 | Rangamati | 135 | 05:00 | 128 | 12:00
| Gollamari | 140 | 04:00 | 129 | 12:00 | Rangpur | 132 | 04:00 | 120 | 08:00
| Gopalganj | 139 | 04:00 | 128 | 12:00 | Ruppur | 142 | 04:00 | 135 | 08:00
| Gopalganj-400 | 139 | 05:00 | 130 | 13:00 | Saidpur | 133 | 04:00 | 122 | 08:00
| Gulshan | 136 | 03:00 | 126 | 12:00 | Satkhira | 139 | 03:00 | 126 | 08:00
| Halishahar | 134 | 18:30 | 124 | 12:00 | Satmasjid | 137 | 04:00 | 126 | 13:00
| Haripur | 135 | 05:00 | 128 | 12:00 | Savar | 133 | 00:00 | 124 | 12:00
| HaripurSBU | 135 | 04:00 | 128 | 12:00 | SevenRings | 141 | 04:00 | 133 | 12:00
| Hasnabad | 138 | 00:00 | 130 | 12:00 | ShahCement | 136 | 04:00 | 128 | 12:00
| Hathazari | 136 | 18:00 | 130 | 15:00 | Shahjadpur | 143 | 04:00 | 136 | 07:00
| Ishurdi | 142 | 03:00 | 134 | 08:00 | Shahjibazar | 138 | 00:00 | 131 | 12:00
| Jaldhaka | 131 | 04:00 | 117 | 08:00 | Shahmirpur | 134 | 02:00 | 128 | 12:00
| Jamalpur | 129 | 10:00 | 112 | 08:00 | Shariatpur | 138 | 04:00 | 129 | 12:00
| Jashore | 137 | 01:00 | 126 | 08:00 | Sherpur | 126 | 10:00 | 110 | 08:00
| Jhenaidah | 141 | 01:00 | 130 | 12:00 | Shikalbaha | 123 | 06:00 | 117 | 12:00
| Jhenaidah-230 | 142 | 04:00 | 131 | 08:00 | Shikalbaha-230 | 135 | 18:00 | 128 | 12:00
| Joydebpur | 140 | 17:00 | 129 | 12:00 | Shitalakhya | 139 | 02:00 | 128 | 12:00
| Joypurhat | 136 | 02:00 | 124 | 08:00 | Sholosohor | 134 | 05:00 | 128 | 12:00
| Juldah | 133 | 18:00 | 128 | 13:00 | Shyampur | 136 | 01:00 | 133 | 08:00
| Kabirpur | 135 | 01:00 | 124 | 12:00 | Shyampur-230 | 140 | 05:00 | 128 | 12:00
| Kachua | 137 | 18:00 | 125 | 13:00 | Siddhirganj | 135 | 01:00 | 128 | 12:00
| Kaliakoir | 138 | 04:00 | 127 | 12:00 | Sirajganj | 138 | 01:00 | 127 | 08:00
| Kallyanpur | 137 | 04:00 | 127 | 12:00 | Sonargaon | 132 | 17:00 | 125 | 12:00
| Kalurghat | 135 | 18:00 | 129 | 12:00 | Sreemongol | 136 | 00:00 | 131 | 11:00
| Kamrangirchar | 139 | 02:00 | 125 | 12:00 | Sreepur | 130 | 05:00 | 123 | 08:00
| Kaptai | 137 | 4:00 | 133 | 15:00 | Srinagar | 137 | 02:00 | 128 | 12:00
| Kazla | 136 | 05:00 | 125 | 13:00 | SSM | 139 | 18:00 | 132 | 08:00
| Keranigonj | 138 | 03:00 | 129 | 12:00 | Sunamganj | 133 | 04:00 | 130 | 12:00
| Khagrachori | 134 | 05:00 | 127 | 12:00 | Sylhet | 136 | 04:00 | 132 | 13:00
| Khulna | 139 | 01:00 | 126 | 13:00 | Sylhet-132 | 135 | 02:00 | 131 | 12:00
| Khulna(S) | 141 | 04:00 | 129 | 13:00 | Tangail | 128 | 00:00 | 120 | 08:00
| Khulshi | 133 | 18:30 | 126 | 12:00 | Thakurgaon | 133 | 05:00 | 117 | 08:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 133 | 04:00 | 125 | 08:00 | TK | 133 | 00:00 | 128 | 12:00 |  |  | Nos | Nos | Nos
| Kodda | 136 | 17:00 | 124 | 12:00 | Tongi | 138 | 01:00 | 128 | 11:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 134 | 00:00 | 128 | 12:00 | Ullahpara | 139 | 23:00 | 129 | 07:00
| Kulaura | 138 | 00:00 | 134 | 14:00 | Ullon | 136 | 01:00 | 128 | 12:00
| UttaraNew | 137 | 03:00 | 122 | 12:00 | Uttara | 136 | 03:00 | 125 | 12:00
| Zigatola | 138 | 00:00 | 124 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.