## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-01-2025 | during | 18-01-2025 | during | 18-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 370 | 406 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 350 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 262 | 150 | 335 | 335 | 150 | 150 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 260 | 300 | 335 | 335 | 310 | 310 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 0 | 0 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 17 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 0 | 0 | 52.19 | 52.19 | 27 | 27 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 27 | 0 | 27 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 0 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6257.05 | 5842.27 | 1292 | 1295 | 3833.19 | 3814.19 | 2503.72 | 2484.72
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 227 | 228 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 0 | 30 | 40 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.86 | 0 | 3.86 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 390 | 410 | 1224 | 1224 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 3 | 6 | 7 | 40 | 7 | 40 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 1007 | 1035 | 1150 | 1150 | 1050 | 1050 | -
Chattogram Area Total |  |  |  |  | 4917.36 | 4873.22 | 1711 | 1749 | 4046.58 | 4056.72 | 3334.58 | 3344.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 184 | 195 | 221 | 221 | 190 | 190 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 44 | 41 | 46.94 | 46.94 | 46.94 | 46.94 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 28 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 195 | 194 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 0 | 0 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 44 | 52 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 16 | 7.34 | 20.83 | 7.34 | 20.83 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 675 | 619 | 1484.48 | 1437.97 | 1453.48 | 1406.97
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 24 | 210 | 210 | 10 | 10 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 66 | 200 | 200 | 60 | 60 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 115 | 115 | 45 | 45 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.34 | 0 | 46.6 | 0 | 46.6 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 142.34 | 109 | 650.1 | 601.5 | 240.1 | 191.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | -
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 10 | 10 | 0 | 0 | 0 | 0 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 25 | 20 | 0 | 0 | 20 | 20 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 206 | 206 | 210 | 210 | 210 | 210 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 0 | 0 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 336 | 344 | 385 | 385 | 340 | 340 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1470 | 1508 | 1527.5 | 1527.5 | 1448.01 | 1448.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 917 | 916 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 335 | 341 | 0 | 0 | 350 | 350 | -
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 76.75 | 0 | 72 | 0 | 72 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1328.75 | 1257 | 2786 | 2714 | 1462.01 | 1390.01
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 140 | 135 | 135 | 135 | 135 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 800 | 1000 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 180 | 250 | 307 | 307 | 250 | 250 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1305.51 | 1617 | 2176.12 | 2176.12 | 2076 | 2076
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 149 | 193 | 214 | 214 | 190 | 190 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 129 | 201 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 155 | 201 | 220 | 220 | 200 | 200 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5.5 | 8.5 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52 | 52 | 52 | 52 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.16 | 0 | 4.1 | 0 | 4.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 564.01 | 564 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.9 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 89 | 0 | 96 | 0 | 96 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1148.57 | 1167.5 | 2031.1 | 1881 | 1967.1 | 1817
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 70 | 72 | 72 | 72 | 72 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 171 | 210 | 210 | 210 | 210 | 210 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.7 | 0 | 4.4 | 0 | 4.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 14 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 136 | 0 | 125 | 0 | 125 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 393.7 | 280 | 689.4 | 530 | 669.41 | 510.01
System Total |  |  |  |  | 27734.66 | 27025.248 | 9466.87 | 9601.5 | 19224.47 | 18739 | 15154.41 | 14668.94
Forecast Scenario (18-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8250 |  | 0 |  | 8250
|  |  |  | 1:00 | 7790 |  | 0 |  | 7790
|  |  |  | 2:00 | 7430 |  | 0 |  | 7430
|  |  |  | 3:00 | 7220 |  | 0 |  | 7220
|  |  |  | 4:00 | 6990 |  | 0 |  | 6990
|  |  |  | 5:00 | 6840 |  | 0 |  | 6840
|  |  |  | 6:00 | 7220 |  | 0 |  | 7220
|  |  |  | 7:00 | 7780 |  | 0 |  | 7780
|  |  |  | 8:00 | 8830 |  | 0 |  | 8830
|  |  |  | 9:00 | 9100 |  | 0 |  | 9100
|  |  |  | 10:00 | 8900 |  | 0 |  | 8900
|  |  |  | 11:00 | 9050 |  | 0 |  | 9050
|  |  |  | 12:00 | 9650 |  | 0 |  | 9650
|  |  |  | 13:00 | 10030 |  | 0 |  | 10030
|  |  |  | 14:00 | 9860 |  | 0 |  | 9860
|  |  |  | 15:00 | 9210 |  | 0 |  | 9210
|  |  |  | 16:00 | 8990 |  | 0 |  | 8990
|  |  |  | 17:00 | 9180 |  | 0 |  | 9180
|  |  |  | 18:00 | 10850 |  | 0 |  | 10850
|  |  |  | 18:30 | 10900 |  | 0 |  | 10900
|  |  |  | 19:00 | 10970 |  | 0 |  | 10970
|  |  |  | 19:30 | 10720 |  | 0 |  | 10720
|  |  |  | 20:00 | 10660 |  | 0 |  | 10660
|  |  |  | 21:00 | 10530 |  | 0 |  | 10530
|  |  |  | 22:00 | 9930 |  | 0 |  | 9930
|  |  |  | 23:00 | 9540 |  | 0 |  | 9540
Probable Maximum Temperature: |  |  | 26.00°C
Probable Maximum Demand at Day Peak: |  |  | 9650.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 10970.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10970.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 214.80 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (17-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 28.10°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 819.37
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 19.9607 | Peak Hour Flow: |  | 916.00 MW at 19:30 hrs.
Energy Flow from West to East |  | 8842018.255 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 11.3314 | Peak Hour Flow: |  | 564.00 MW at 19:30 hrs.
Power Flow during Peak Demand |  | 526 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.1347 | Peak Hour Flow: |  | 52.00 MW at 19:30 hrs.
Maximum Power Flow |  | 766 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 32.4269 | Peak Hour Flow: |  | 1532.00 MW at 19:30 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [9 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [9 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-01-2025 | [28 empty] | Date: | 17-01-2025 | [28 empty] | Date: | 17-01-2025 | [28 empty] | Date: | 17-01-2025 | [28 empty] | Date: | 17-01-2025 | [18 empty] | Date: | 17-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [18 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 150.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 0.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 265 | 0 | 0 | 0 | 26 | 260 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 910 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 476 | 0 | 43 | 0 | 195 | 0 | 0 | 0 | 29 | 183 | 41 | 0 | 50 | 0 | 0 | 17 | 0 | 56 | 0 | 0 | 0 | 295 | 320 | 312 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 207 | 0 | 19 | 35 | 13 | 0 | 0 | 0 | 5200 | 918 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 181 | 0 | 177 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 900 | 0 | 3802.5 | 9002.5 | 92.93
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 288 | 0 | 0 | 0 | 28 | 260 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 802 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 350 | 0 | 43 | 0 | 108 | 0 | 0 | 0 | 29 | 190 | 43 | 0 | 50 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 295 | 320 | 310 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 209 | 0 | 0 | 35 | 13 | 0 | 0 | 0 | 4850 | 917 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 174 | 0 | 170 | 0 | 0 | 0 | 0 | 5.5 | 209 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49 | 0 | 150 | 7 | 140 | 220 | 0 | 700 | 0 | 3596.99 | 8446.99 | 92.92
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 298 | 0 | 0 | 0 | 30 | 260 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 802 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 108 | 0 | 0 | 0 | 29 | 194 | 47 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 305 | 320 | 310 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 20 | 0 | 0 | 208 | 0 | 0 | 18 | 19 | 0 | 0 | 0 | 4683 | 752 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 165 | 0 | 162 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0 | 150 | 7 | 140 | 220 | 0 | 700 | 0 | 3428.94 | 8111.94 | 92.92
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 284 | 0 | 0 | 0 | 30 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 804 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 108 | 0 | 0 | 0 | 29 | 196 | 47 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 305 | 320 | 319 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 10 | 20 | 0 | 0 | 208 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 4618.5 | 727 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 159 | 0 | 162 | 0 | 0 | 0 | 0 | 5.5 | 209 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 100 | 220 | 0 | 600 | 0 | 3243.5 | 7862 | 92.91
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 287 | 0 | 0 | 0 | 8.5 | 260 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 804 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 12 | 183 | 47 | 0 | 50 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 300 | 320 | 319 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 10 | 20 | 0 | 0 | 209 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 4487.5 | 728 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 153 | 0 | 154 | 0 | 0 | 0 | 0 | 5.5 | 210 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 100 | 180 | 0 | 600 | 0 | 3136.5 | 7624 | 92.91
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 277 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 0 | 0 | 14 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 803 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 5 | 183 | 47 | 0 | 50 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 295 | 320 | 301 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 10 | 20 | 0 | 0 | 208 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 4435 | 633 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 149 | 0 | 148 | 0 | 0 | 0 | 0 | 5.5 | 210 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 600 | 0 | 3034.5 | 7469.5 | 92.9
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 291 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 800 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 107 | 0 | 0 | 0 | 5 | 202 | 47 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 305 | 320 | 380 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 20 | 0 | 0 | 208 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 4612.5 | 633 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 142 | 0 | 137 | 0 | 0 | 0 | 0 | 5.5 | 210 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 600 | 0 | 3136.5 | 7749 | 92.9
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 272 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 800 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 300 | 1 | 5 | 0 | 130 | 0 | 0 | 0 | 5 | 222 | 47 | 0 | 50 | 0 | 0 | 17 | 0 | 40 | 0 | 2 | 0 | 300 | 300 | 376 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 20 | 0 | 0 | 208 | 0 | 19 | 24 | 22 | 0 | 0.69 | 0 | 4634.19 | 726 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54 | 130 | 0 | 137 | 0 | 134 | 0 | 0 | 0 | 0.03 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 150 | 6 | 140 | 220 | 0 | 600 | 0 | 3249.22 | 7883.41 | 92.89
08:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 262 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 2 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 38 | 900 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 300 | 7 | 34 | 0 | 190 | 0 | 0 | 0 | 19 | 183 | 48 | 0 | 50 | 0 | 0 | 17 | 0 | 38 | 0 | 21 | 0 | 315 | 320 | 375 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 208 | 0 | 19 | 27 | 22 | 0 | 5.48 | 0 | 4956.98 | 727 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.81 | 0 | 0 | 416.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 3.11 | 130 | 0 | 132 | 0 | 134 | 0 | 0 | 0 | 0.31 | 5.5 | 210 | 69 | 0 | 0 | 0 | 0 | 0 | 0.4 | 25 | 0.1 | 0 | 220 | 5 | 140 | 220 | 0 | 710 | 0 | 3515.7 | 8472.68 | 92.89
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 265 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 5 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 30 | 900 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 300 | 14 | 43 | 0 | 192 | 0 | 0 | 0 | 29 | 183 | 47 | 0 | 50 | 0 | 0 | 17 | 0 | 34 | 0 | 42 | 0 | 295 | 320 | 375 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 208 | 0 | 19 | 47 | 18 | 1 | 15.24 | 17 | 5072.24 | 822 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.75 | 0 | 0 | 412.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 6.29 | 123 | 0 | 126 | 0 | 128 | 0 | 0 | 0 | 0.55 | 5.5 | 173 | 70 | 0 | 5 | 0 | 0 | 0 | 1.1 | 50 | 0.25 | 0 | 220 | 5 | 140 | 220 | 0 | 800 | 0 | 3722.83 | 8795.07 | 92.88
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 270 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 15 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 30 | 0 | 32 | 806 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 300 | 17 | 43 | 0 | 194 | 0 | 0 | 0 | 29 | 196 | 41 | 0 | 50 | 0 | 0 | 17 | 0 | 34 | 0 | 57 | 0 | 280 | 320 | 336 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 20 | 0 | 0 | 209 | 0 | 19 | 47 | 18 | 2 | 34.8 | 24 | 4942.8 | 823 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.4 | 0 | 0 | 416.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 20.74 | 123 | 0 | 125 | 0 | 124 | 0 | 0 | 0 | 1.89 | 5.5 | 173 | 70 | 0 | 7 | 0 | 0 | 0 | 2.9 | 111 | 0.4 | 0 | 180 | 5 | 100 | 180 | 0 | 720 | 0 | 3651.21 | 8594.01 | 92.88
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 265 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 30 | 0 | 30 | 807 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 300 | 19 | 43 | 0 | 195 | 0 | 0 | 0 | 29 | 183 | 43 | 0 | 50 | 0 | 0 | 17 | 0 | 37 | 0 | 67 | 0 | 285 | 320 | 336 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 20 | 0 | 0 | 210 | 0 | 19 | 47 | 16 | 2 | 40.57 | 24 | 4952.57 | 916 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.39 | 0 | 0 | 414.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 47.85 | 126 | 0 | 124 | 0 | 128 | 0 | 0 | 0 | 4.03 | 5.5 | 173 | 68 | 0 | 11 | 0 | 0 | 0 | 3.2 | 106 | 0.48 | 0 | 180 | 5 | 100 | 180 | 0 | 720 | 0 | 3802.19 | 8754.76 | 92.88
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 262 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 28 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 30 | 0 | 30 | 1007 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 390 | 20 | 43 | 0 | 195 | 0 | 0 | 0 | 29 | 184 | 44 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 69 | 0 | 280 | 320 | 336 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 25 | 0 | 0 | 206 | 0 | 19 | 56 | 11 | 2 | 42.34 | 12 | 5290.34 | 917 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.75 | 0 | 0 | 564.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 52.9 | 149 | 0 | 129 | 0 | 155 | 0 | 0 | 0 | 4.16 | 5.5 | 171 | 70 | 0 | 14 | 0 | 0 | 0 | 2.7 | 136 | 0.51 | 0 | 180 | 5 | 100 | 220 | 0 | 800 | 0 | 4176.53 | 9466.87 | 92.87
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 265 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 28 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 33 | 1067 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 450 | 18 | 43 | 0 | 195 | 0 | 0 | 0 | 29 | 183 | 43 | 0 | 50 | 0 | 0 | 17 | 0 | 64 | 0 | 64 | 0 | 305 | 316 | 370 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 25 | 0 | 0 | 207 | 0 | 19 | 48 | 11 | 2 | 42.19 | 12 | 5477.19 | 917 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.37 | 0 | 0 | 660.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 49.09 | 180 | 0 | 171 | 0 | 197 | 0 | 0 | 0 | 4.25 | 5.5 | 210 | 70 | 0 | 9 | 0 | 0 | 0 | 2.2 | 90 | 0 | 0 | 280 | 6 | 140 | 220 | 0 | 1010 | 0 | 4718.72 | 10195.91 | 92.87
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 156 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 23 | 0 | 11 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 30 | 0 | 20 | 908 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 354 | 17 | 43 | 0 | 88 | 0 | 0 | 0 | 29 | 183 | 44 | 0 | 50 | 0 | 0 | 17 | 0 | 54 | 0 | 55 | 0 | 270 | 320 | 324 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 10 | 20 | 0 | 0 | 205 | 0 | 19 | 58 | 12 | 2 | 33.21 | 0 | 4696.21 | 917 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.55 | 0 | 0 | 517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 41.47 | 140 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 3.31 | 5.5 | 210 | 68 | 0 | 8 | 0 | 0 | 0 | 2 | 137 | 0.44 | 0 | 150 | 4 | 100 | 180 | 0 | 800 | 0 | 3970.27 | 8666.48 | 92.87
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 155 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 16 | 0 | 11 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 0 | 29 | 756 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 350 | 13 | 43 | 0 | 86 | 0 | 0 | 0 | 29 | 183 | 44 | 0 | 50 | 0 | 0 | 16 | 0 | 48 | 0 | 42 | 0 | 285 | 320 | 323 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 10 | 20 | 0 | 0 | 205 | 0 | 19 | 45 | 18 | 1 | 25.89 | 0 | 4485.89 | 727 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.05 | 0 | 0 | 518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 33.94 | 140 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 2.57 | 5.5 | 210 | 70 | 0 | 5 | 0 | 0 | 0 | 1.5 | 62 | 0.33 | 0 | 150 | 4 | 100 | 180 | 0 | 650 | 0 | 3511.89 | 7997.78 | 92.86
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 142 | 0 | 0 | 0 | 7.5 | 240 | 0 | 0 | 9 | 0 | 11 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 0 | 31 | 757 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 350 | 8 | 43 | 0 | 78 | 0 | 0 | 0 | 10 | 184 | 43 | 0 | 50 | 0 | 0 | 15 | 0 | 46 | 0 | 23 | 0 | 300 | 320 | 310 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 20 | 0 | 0 | 202 | 0 | 19 | 45 | 20 | 0 | 11.93 | 0 | 4411.43 | 728 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.66 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 13.07 | 140 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 1.37 | 5.5 | 210 | 70 | 0 | 3 | 0 | 0 | 0 | 0.9 | 27 | 0.18 | 0 | 150 | 4 | 80 | 180 | 0 | 540 | 0 | 3126.68 | 7538.11 | 92.86
17:00 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 150 | 0 | 0 | 0 | 16 | 240 | 0 | 0 | 2 | 0 | 11.5 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 40 | 754 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 402 | 1 | 43 | 0 | 125 | 0 | 0 | 0 | 10 | 195 | 43 | 0 | 50 | 0 | 0 | 15 | 0 | 46 | 0 | 4 | 0 | 310 | 320 | 303 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 20 | 0 | 0 | 204 | 0 | 19 | 45 | 22 | 0 | 2.21 | 0 | 4590.71 | 727 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.05 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 3.78 | 140 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 0.24 | 5.5 | 210 | 70 | 0 | 1 | 0 | 0 | 0 | 0.2 | 6 | 0.31 | 0 | 150 | 4 | 80 | 220 | 0 | 680 | 0 | 3232.08 | 7822.79 | 92.86
18:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 145 | 0 | 0 | 0 | 14 | 300 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 35 | 1030 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 430 | 0 | 43 | 0 | 192 | 0 | 0 | 0 | 19 | 186 | 38 | 0 | 50 | 0 | 0 | 15 | 0 | 52 | 0 | 0 | 0 | 295 | 320 | 338 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 205 | 0 | 19 | 66 | 22 | 0 | 0 | 6 | 5282 | 915 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 200 | 0 | 186 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 140 | 220 | 0 | 900 | 0 | 4137.5 | 9419.5 | 92.85
19:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 148 | 0 | 0 | 0 | 16 | 300 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 40 | 1032 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 408 | 0 | 43 | 0 | 192 | 0 | 0 | 0 | 28 | 186 | 41 | 0 | 50 | 0 | 0 | 16 | 0 | 50 | 0 | 0 | 0 | 310 | 320 | 335 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 206 | 0 | 19 | 66 | 24 | 0 | 0 | 24 | 5268 | 916 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 204 | 0 | 200 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 140 | 220 | 0 | 1000 | 0 | 4315.5 | 9583.5 | 92.85
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 150 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 40 | 1035 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 410 | 0 | 43 | 0 | 194 | 0 | 0 | 0 | 28 | 195 | 41 | 0 | 50 | 0 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 315 | 320 | 344 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 206 | 0 | 19 | 66 | 24 | 0 | 0 | 0 | 5280 | 916 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 201 | 0 | 201 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 140 | 220 | 0 | 1000 | 0 | 4321.5 | 9601.5
20:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 148 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 42 | 1035 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 405 | 0 | 43 | 0 | 195 | 0 | 0 | 0 | 29 | 192 | 41 | 0 | 50 | 0 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 305 | 320 | 335 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 206 | 0 | 19 | 35 | 24 | 0 | 0 | 0 | 5232 | 916 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 201 | 0 | 203 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 140 | 220 | 0 | 1000 | 0 | 4321.5 | 9553.5 | 92.85
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 139 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 42 | 1032 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 504 | 0 | 43 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 47 | 0 | 50 | 0 | 0 | 16 | 0 | 52 | 0 | 0 | 0 | 300 | 320 | 337 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 199 | 0 | 19 | 35 | 24 | 0 | 0 | 0 | 5289 | 916 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 201 | 0 | 203 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226 | 7 | 140 | 220 | 0 | 980 | 0 | 4277.5 | 9566.5 | 92.85
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 150 | 0 | 0 | 0 | 33 | 300 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 42 | 1033 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 423 | 0 | 43 | 0 | 197 | 0 | 0 | 0 | 28 | 191 | 38 | 0 | 50 | 0 | 0 | 16 | 0 | 54 | 0 | 0 | 0 | 290 | 320 | 338 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 20 | 0 | 0 | 203 | 0 | 19 | 35 | 24 | 0 | 0 | 0 | 5214 | 917 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 201 | 0 | 203 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 900 | 0 | 4032.5 | 9246.5 | 92.85
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 148 | 0 | 0 | 0 | 25 | 300 | 0 | 0 | 0 | 0 | 12 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 42 | 950 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 320 | 0 | 43 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 44 | 0 | 50 | 0 | 0 | 16 | 0 | 54 | 0 | 0 | 0 | 280 | 320 | 288 | 10 | 30 | 0 | 2 | 130 | 13 | 0 | 85 | 20 | 0 | 0 | 205 | 0 | 19 | 18 | 24 | 0 | 0 | 0 | 4909 | 917 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 165 | 0 | 201 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 220 | 0 | 880 | 0 | 3905.5 | 8814.5 | 92.84
Total KWH | 0 | 237600 | 17280 | 0 | 0 | 0 | 0 | 0 | 8985600 | 0 | 0 | 0 | 0 | 0 | 39024 | 0 | 0 | 0 | 0 | 0 | 373800 | 0 | 7827500 | 5214895 | 0 | 0 | 0 | 488900 | 6518830 | 0 | 0 | 151734 | 0 | 279000 | 481680 | 0 | 0 | 0 | 0 | 0 | 0 | 87360 | 0 | 0 | 0 | 0 | 0 | 20879 | 815520 | 0 | 899520 | 21352727.27 | 0 | 0 | 0 | 0 | 0 | 5124429 | 0 | 0 | 0 | 8585453 | 136485 | 833188 | 0 | 3596364 | 0 | 0 | 0 | 550080 | 4627000 | 1068408 | 0 | 1192950 | 0 | 0 | 389310 | 0 | 1134720 | 0 | 450173 | 0 | 7241500 | 7635900 | 8359000 | 306648 | 716000 | 0 | 56736 | 3742936 | 342720 | 0 | 1285440 | 483072 | 0 | 0 | 4225040 | 0 | 322800 | 844800 | 448320 | 10950 | 260810 | 142080 | 117905161.27 | 19960727 | 7215552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451440 | 0 | 0 | 11331403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575460 | 0 | 276000 | 3698818 | 0 | 4052209 | 0 | 4153509 | 0 | 0 | 0 | 22860 | 152622 | 4969000 | 1605818 | 40145 | 61545 | 0 | 0 | 0 | 19744.56 | 653040 | 3250 | 0 | 4495000 | 141640 | 2880000 | 5195420 | 0 | 19294545.45 | 0 | 91249748.01 | 209154909.28

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 17-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 9466.87 | MW | 12:00 Hr. | Energy Generated |  |  | 209154.9093 |  | MWHr
Day Peak Demand |  |  | 9466.87 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MWHr
Evening Peak Generation |  |  | 9601.5 | MW | 19:30 Hr. | Energy Demand |  |  | 209154.9093 |  | MWHr
Evening Peak Demand |  |  | 9601.5 | MW | 19:30 Hr.
Minimum Generation of the Day |  |  | 7469.5 | MW | 05:00 Hr.
Maximum Generation of the Day |  |  | 10195.91 | MW | 13:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 30170.205 | 0 | 293.904 | 0 | 0 | 151.734 | 0 | 0 | 30615.843 | Gas | 110784.536 | Gas | 395664427.02
Chattogram Zone |  |  | 6023.949 | 29938.1803 | 0 | 0 | 815.52 | 157.364 | 0 | 87.36 | 37022.3733 | Coal | 60302.5437 | Coal | 427797027.0821
Cumilla Zone |  |  | 12257.3 | 0 | 0 | 0 | 0 | 450.173 | 1134.72 | 0 | 13842.193 | HFO | 1643.729 | HFO | 32351661.34
Mymensingh Zone |  |  | 448.32 | 0 | 1309.68 | 0 | 0 | 271.76 | 0 | 0 | 2029.76 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 34394.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34394.992 | Hydro | 815.52 | Hydro | 81552
Khulna Zone |  |  | 7215.552 | 0 | 0 | 0 | 0 | 451.44 | 19960.727 | 0 | 27627.719 | Solar | 3094.3706 | Solar | 47202730.806
Barishal Zone |  |  | 8217.06 | 23789.5455 | 0 | 0 | 0 | 3.25 | 0 | 0 | 32009.8554 | Import | 32426.85 | Import | 154775762.31
Rajshahi Zone |  |  | 12057.158 | 0 | 0 | 0 | 0 | 874.32 | 11331.403 | 0 | 24262.881 | Wind | 87.36 | Wind | 1362816
Rangpur Zone |  |  | 0 | 6574.818 | 40.145 | 0 | 0 | 734.3296 | 0 | 0 | 7349.2926
Total |  |  | 110784.536 | 60302.5437 | 1643.729 | 0 | 815.52 | 3094.3706 | 32426.85 | 87.36 | 209154.9093
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 395664427.02 |  | Hydro | 81552
|  |  | Coal | 427797027.0821 |  | Solar | 47202730.806
|  |  | HFO | 32351661.34 |  | Import | 154775762.31
|  |  | HSD | 0 |  | Wind | 1362816
|  |  |  | Total: | 1059235976.5581 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
| 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
| 4 | Barapukuria TPP Unit-2 |  |  | 85
| 5 | Khulna 330 MW CCPP GT |  |  | 220
| 6 | Khulna 330 MW CCPP ST |  |  | 110
| 7 | Siddhirgonj 210 MW TPP |  |  | 115
| 8 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 9 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1404 |  |  |  | Total | 435.09
|  |  | Total Unavailable Capacity |  |  |  | 1839.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3103
|  |  | Chattogram |  | 0 |  | 1080
|  |  | Cumilla |  | 0 |  | 818
|  |  | Mymensingh |  | 0 |  | 882
|  |  | Sylhet |  | 0 |  | 347
|  |  | Khulna |  | 0 |  | 1116
|  |  | Barishal |  | 0 |  | 281
|  |  | Rajshahi |  | 0 |  | 932
|  |  | Rangpur |  | 0 |  | 611
|  |  | Total |  | 0 |  | 9170
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:01 | 11:02 | Benapole-Jashore 132 kV Ckt-1 Forced S/D from Benapole 132/33kV end Due to Jessore SS | [7 empty] | 50.0MW load
|  | maintenance | [7 empty] | interrup. Benapole
132/33kV end
08:01 | 11:02 | Benapole-Jashore 132 kV Ckt-2 Forced S/D from Benapole 132/33kV end Due to Jessore SS | [7 empty] | 50.0MW load
|  | maintenance | [7 empty] | interrup. Benapole
132/33kV end
08:03 |  | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Scheduled S/D Due to As per order of
ALDC
08:03 | 17:28 | Jashore 132/33kV S/S JH-2(L1) Project Work S/D Due to For jack bus upgrade | [7 empty] | 30.0MW load
interrup.
08:17 | 10:59 | Jashore 132/33kV S/S 132 kV Bus-B Project Work S/D Due to For jack bus upgrade | [7 empty] | 80.0MW load
interrup.
08:18 | 10:58 | Jashore-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end.
08:18 |  | Ashuganj 420 MW CCPP(East) GT Planned Shutdown with remarks:- None
08:19 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
08:25 | 11:47 | Ghorasal- Ishwardi 230 kV Ckt-2 Project Work S/D from Ghorashal 230kV end Due to
Repairing of 230kV existing top conductor repair. and from Ishurdi 230/132kVend.
08:25 | 11:43 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to Annual maintenance work
08:25 | 11:40 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to Annual maintenance work
08:32 | 17:24 | Hasnabad-Sitalakhya 132kV Ckt-1 Scheduled S/D from Hasnabad 132/33kV end Due to Deadline
Checking
08:40 | 12:05 | Siddhirganj 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenance
08:40 | 12:06 | Siddhirganj 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenance
08:55 | 11:15 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T LT Scheduled S/D Due to Emergency
Maintenance work
08:56 | 11:14 | Barapukuria 230/132/33kV S/S 230/132 KV T-02, 713T HT Scheduled S/D Due to Emergency
Maintenance work
08:59 | 11:24 | Barapukuria 230/132/33kV S/S 132 KV Bus A Scheduled S/D Due to Emergency Maintenance work
| 09:16 | Dohazari 132/33kV S/S Power Transformer -T-2 LT is restored.
| 09:16 | Dohazari 132/33kV S/S Power Transformer -T-2 HT is restored.
09:17 | 10:55 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to
Incommer CB Problem
| 09:18 | Dohazari 132/33kV S/S Power Transformer -T-1 LT is restored.
| 09:18 | Dohazari 132/33kV S/S Power Transformer -T-1 HT is restored.
09:20 | 16:07 | Barishal(N)-Madaripur 132 kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end Due to
Annual maintenance and from Barishal 230/132kV end Due to Annual maintenance work
09:20 | 16:06 | Barishal(N)-Madaripur 132 kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to
Annual maintenance and from Barishal 230/132kV end Due to Annual maintenance work
09:27 | 20:15 | Rampura 230/132kV S/S Auto Transformer - 04 HT Project Work S/D Due to G2G Project Work
09:27 | 20:35 | Rampura 230/132kV S/S NLDC Trafo HT Project Work S/D Due to G2G Project Work
09:27 | 20:35 | Rampura 230/132kV S/S NLDC Trafo LT Project Work S/D Due to G2G Project Work
09:40 | 20:50 | Rampura 230/132kV S/S Aux Transformer-01 HT Project Work S/D Due to G2G Project Work
09:43 | 10:56 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to
Incommer CB Problem
09:44 | 09:58 | Chowmuhani 132/33kV S/S TR3 Forced S/D Due to Station Supply X-former Fuse fail . | [7 empty] | 15.0MW load
interrup.
09:50 | 20:50 | Rampura 230/132kV S/S Aux Transformer-01 LT Project Work S/D Due to G2G Project Work
| 10:57 | Jashore-Noapara 132kV Ckt-1 is restored.
| 11:04 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 is restored.
12:00 |  | Day peak generation 9463 MW
12:15 | 13:06 | Panchagarh 132/33kV S/S T-2(417T) LT Scheduled S/D Due to T-2 Transformer Maintenance
Work.
12:15 | 13:06 | Panchagarh 132/33kV S/S T-2(417T) HT Scheduled S/D Due to T-2 Transformer Maintenance
Work.
13:16 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT2
13:16 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT2 SD & GT-1 Running.
13:16 |  | Meghnaghat CCPP(Summit) GT-2 Shutdown with remarks:- GT-2 air intake filter change
| 13:17 | Shahjibazar-Sreemangal 132kV Ckt-1 is restored.
| 13:17 | Shahjibazar-Sreemangal 132kV Ckt-1 is restored.
| 14:45 | Rangpur 132/33kV S/S Rangpur-Teesta Solar-2 is restored.
15:10 | 17:31 | Benapole 132/33kV S/S Transformer-1(406T) LT Forced S/D Due to Jashore grid annual | [7 empty] | 50.0MW load
|  | maintenance | [7 empty] | interrup.
15:10 | 17:33 | Benapole 132/33kV S/S Transformer-2(416T) LT Forced S/D Due to Jashore grid annual | [7 empty] | 50.0MW load
|  | maintenance | [7 empty] | interrup.
15:17 | 16:58 | Panchagarh 132/33kV S/S T-2(417T) HT Forced S/D Due to T-2 Transformer Maintenance Work .
15:17 | 16:58 | Panchagarh 132/33kV S/S T-2(417T) LT Forced S/D Due to T-2 Transformer Maintenance Work .
15:23 | 17:36 | Benapole-Jashore 132 kV Ckt-2 Forced S/D from Benapole 132/33kV end Due to Jashore grid | [7 empty] | 50.0MW load
|  | annual maintenance | [7 empty] | interrup. Benapole
132/33kV end
15:23 | 17:29 | Benapole-Jashore 132 kV Ckt-1 Forced S/D from Benapole 132/33kV end Due to Jashore grid | [7 empty] | 50.0MW load
|  | annual maintenance | [7 empty] | interrup. Benapole
132/33kV end
15:24 | 17:25 | Jashore-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end Due to Jashore
sub-ststion work.
15:36 | 17:25 | Jashore-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end Due to Jashore
sub-station work.
15:51 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT-2 ( This is False SMS ).
16:16 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
| 16:44 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) is restored.
| 16:59 | Fatullah 132/33kV S/S 132 kV Hasnabad is restored.
| 17:45 | Jashore 132/33kV S/S 132 kV Bus-A is restored.
| 18:43 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) HT is restored.
| 19:12 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) LT is restored.
19:30 |  | Evening peak Generation is 9601 MW
00:47 |  | Siddhirganj GT-2 was sync.
02:10 |  | Siddhirganj GT-2 was shutdown.
02:22 |  | Siddhirganj GT-1 was sync.
03:36 |  | Siddhirganj GT-1 was shutdown.
04:00 |  | Minimum Generation: 6991 MW.
06:24 |  | SS Power Synchronized with remarks:- unit-2
06:51 |  | Rampura 230/132kV S/S 132 kV Busbar-2 Scheduled S/D Due to Project (G2G) work, BUS 2 &
Diameter 5 loop connection, and testing (SPMD).
07:04 |  | Cantonment 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D Due to Annual Maintenance
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 406 | 8985600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 7827500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 5214895 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6518830 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 0 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 279000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 481680 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 373800 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 33 | 488900 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 0 | 17280 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 0 | 39024 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 237600 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 151734 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 0 | 0 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 1295 | 30615843
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 136485 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 815520 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 228 | 5124429 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 0 | 40 | 899520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20879 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 410 | 8585453 | network constraint
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 6 | 87360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 1035 | 21352727.27 | -
Chattogram Area Total |  |  |  |  | 4873.22 | 1749 | 37022373.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 195 | 4627000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 41 | 1068408 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 28 | 550080 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 194 | 3596364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 833188 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1192950 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 52 | 1134720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 389310 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 0 | Fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 450173 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 619 | 13842193
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 24 | 448320 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 66 | 844800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 322800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 260810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 142080 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 109 | 2029760
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3742936 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 10 | 306648 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 56736 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 20 | 483072 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1285440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 206 | 4225040 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 342720 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7241500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 344 | 8359000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7635900 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1508 | 34394992
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 916 | 19960727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 341 | 7215552 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 451440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1257 | 27627719
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 141640 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2880000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1000 | 19294545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5195420 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 250 | 4495000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3250 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1617 | 32009855.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | availability is 47MW but unable to submit to web
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 193 | 3698818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 201 | 4052209 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 201 | 4153509 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 8.5 | 152622 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22860 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 564 | 11331403 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 276000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 575460 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1167.5 | 24262881
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 70 | 1605818 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4969000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 19744.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 40145 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 61545 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 653040 | -
Rangpur Area Total |  |  |  |  | 950 | 280 | 7349292.56
Eastern Grid Total |  |  |  |  | 16730.748 | 5280 | 117905161.27
Western Grid Total |  |  |  |  | 10294.5 | 4321.5 | 91249748.01
National Grid Total |  |  |  |  | 27025.248 | 9601.5 | 209154909.28
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-01-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6230.65 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 2939.3 | MW
i) Dhaka area |  |  | 3103.15 |  | MW | i) Khulna area |  |  |  | 1115.5 | MW
ii) Chattogram area |  |  | 1080.5 |  | MW | ii) Barishal area |  |  |  | 281 | MW
iii) Cumilla area |  |  | 818 |  | MW | iii) Rajshahi area |  |  |  | 931.8 | MW
iv) Mymensingh area |  |  | 882 |  | MW | iv) Rangpur area |  |  |  | 611 | MW
v) Sylhet area |  |  | 347 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9169.95 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 13:00 | 67 | Jaldhaka | 54 | 18:00 | 133 | Purbachal | 15 | 13:00
2 | AKSML | 96 | 10:00 | 68 | Jamalpur | 96 | 18:30 | 134 | Purbasadipur | 102 | 12:00
3 | Aftabnagar | 26 | 12:00 | 69 | Jashore | 111 | 18:30 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 73 | 13:00 | 70 | Jhenaidah | 94 | 08:00 | 136 | Rahim | 15 | 02:00
5 | Agrabad | 56 | 20:00 | 71 | Joydebpur | 93 | 12:00 | 137 | Rajbari | 48 | 18:30
6 | Amnura | 52 | 12:00 | 72 | Joypurhat | 40 | 08:00 | 138 | Rajendrapur | 90 | 13:00
7 | Ashuganj | 59 | 12:00 | 73 | Juldah | 9 | 00:00 | 139 | Rajshahi | 99 | 13:00
8 | BSRM | 189 | 11:00 | 74 | KSRM | 27 | 20:00 | 140 | Rajshahi-230 | 37 | 13:00
9 | Bagerhat | 55 | 18:30 | 75 | Kabirpur | 134 | 09:00 | 141 | Ramganj | 102 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 50 | 13:00 | 142 | Rampur | 25 | 13:00
11 | Bakulia | 68 | 13:00 | 77 | Kallyanpur | 72 | 01:00 | 143 | Rangamati | 12 | 18:00
12 | Banani | 29.4 | 19:30 | 78 | Kalurghat | 10 | 10:00 | 144 | Rangpur | 101 | 13:00
13 | Bangabhaban | 3 | 12:00 | 79 | Kamrangirchar | 42.2 | 00:00 | 145 | Ruppur | 4.2 | 11:00
14 | Barapukuria | 48 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 14 | 02:00
15 | Barguna | 12 | 00:00 | 81 | Kazla | 82 | 13:00 | 147 | Saidpur | 75 | 10:00
16 | Barishal | 70 | 13:00 | 82 | Keranigonj | 51 | 13:00 | 148 | Satkhira | 86 | 18:30
17 | Barishal-230 | 70 | 13:00 | 83 | Khagrachori | 24 | 18:00 | 149 | Satmasjid | 84 | 13:00
18 | Baroaulia | 58 | 10:00 | 84 | Khulna | 66 | 13:00 | 150 | Savar | 144 | 12:00
19 | Baroirhat | 53 | 13:00 | 85 | Khulshi | 129 | 18:30 | 151 | SevenRings | 18.41 | 02:00
20 | Bashundhara | 114 | 12:00 | 86 | Kishoreganj | 124 | 13:00 | 152 | ShahCement | 30 | 01:00
21 | BashundharaCement | 1 | 00:00 | 87 | Kodda | 186 | 00:00 | 153 | Shahjadpur | 44 | 07:00
22 | Beanibazar | 42 | 18:00 | 88 | Kulaura | 26 | 12:00 | 154 | Shahjibazar | 77 | 00:00
23 | Benapole | 62 | 13:00 | 89 | Kurigram | 42 | 08:00 | 155 | Shahmirpur | 39.5 | 08:00
24 | Bhaluka | 106 | 12:00 | 90 | Kushtia | 96 | 18:30 | 156 | Shariatpur | 53 | 13:00
25 | Bhandaria | 34 | 21:00 | 91 | Lalbag | 50 | 00:00 | 157 | Sherpur | 120 | 18:30
26 | Bhangura | 21 | 20:00 | 92 | Lalmonirhat | 39 | 18:00 | 158 | Shikalbaha | 20 | 19:30
27 | Bheramara(GK) | 36 | 18:30 | 93 | MI_Cement | 17.7 | 00:00 | 159 | Shitalakhya | 42.4 | 13:00
28 | Bhulta | 236 | 00:00 | 94 | Madanganj | 14 | 12:00 | 160 | Sholosohor | 25 | 12:00
29 | Bog-Sherpur | 52 | 18:30 | 95 | Madaripur | 63 | 21:00 | 161 | Shyampur | 148 | 10:00
30 | Bogura | 93 | 19:00 | 96 | Madartek | 57.85 | 13:00 | 162 | Siddhirganj | 69 | 13:00
31 | Borhanuddin | 51 | 19:30 | 97 | Madunaghat | 33 | 12:00 | 163 | Sirajganj | 52 | 18:00
32 | Brahmanbaria | 112 | 13:00 | 98 | Magura | 42 | 13:00 | 164 | Sonargaon | 74 | 00:00
33 | Cantonment | 78 | 13:00 | 99 | Mahasthangarh | 54 | 18:30 | 165 | Sreemongol | 48 | 18:00
34 | Chandpur | 42 | 20:00 | 100 | Manikganj | 92 | 21:00 | 166 | Sreepur | 62 | 12:00
35 | Chandraghona | 25 | 18:00 | 101 | Maniknagar | 38 | 13:00 | 167 | Srinagar | 32.41 | 13:00
36 | Chapai | 50 | 09:00 | 102 | Matarbari | 35 | 18:30 | 168 | Sunamganj | 36 | 18:00
37 | Charsaidpur | 44 | 00:00 | 103 | Matuail | 38 | 00:00 | 169 | Sylhet | 30 | 13:00
38 | Chauddagram | 49 | 13:00 | 104 | Millgate | 49 | 00:00 | 170 | Sylhet-132 | 68 | 13:00
39 | Chhatak | 25 | 13:00 | 105 | Mirpur | 94 | 13:00 | 171 | TK | 20 | 20:00
40 | Chowmuhani | 141 | 13:00 | 106 | Mirsorai | 7 | 18:00 | 172 | Tangail | 144 | 08:00
41 | Chuadanga | 73 | 13:00 | 107 | Mirzapur | 32 | 08:00 | 173 | Thakurgaon | 69 | 18:30
42 | Coxsbazar | 98 | 18:00 | 108 | Mithapukur | 40 | 18:00 | 174 | Tongi | 81 | 12:00
43 | Cumilla(N) | 102 | 11:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 25 | 18:30
44 | Cumilla(S) | 114 | 13:00 | 110 | Mogbazar | 78.8 | 12:00 | 176 | Ullon | 37 | 12:00
45 | Daudkandi | 84 | 20:00 | 111 | Mongla | 32 | 00:00 | 177 | Uttara | 58 | 13:00
46 | Dhaka | 18 | 12:00 | 112 | Motijheel | 24 | 13:00 | 178 | UttaraNew | 35 | 13:00
47 | Dhamrai | 82 | 00:00 | 113 | Muktagacha | 26 | 13:00 | 179 | Zigatola | 56 | 13:00
48 | Dhanmondi | 78.4 | 13:00 | 114 | Munshiganj | 72 | 13:00
49 | Dohazari | 66 | 13:00 | 115 | Mymensingh | 152 | 13:00
50 | Faridpur | 95 | 21:00 | 116 | Naogaon | 81 | 09:00
51 | Fatullah | 57 | 00:00 | 117 | Narail | 38 | 08:00
52 | Fenchuganj | 24 | 13:00 | 118 | Narinda | 41 | 13:00
53 | Feni | 65 | 13:00 | 119 | Narshingdi | 139 | 20:00
54 | GPH | 97 | 04:00 | 120 | Natore | 100 | 19:00
55 | Ghatail | 30 | 08:00 | 121 | Nawabganj | 41 | 12:00
56 | Ghorashal | 7 | 00:00 | 122 | Netrakona | 140 | 08:00
57 | Ghorashal-230 | 52 | 00:00 | 123 | New | 53 | 12:00
58 | Goalpara | 28 | 13:00 | 124 | Niamatpur | 74 | 09:00
59 | Gollamari | 52 | 13:00 | 125 | Noapara | 36 | 09:00
60 | Gopalganj | 74.8 | 18:30 | 126 | PHP | 8 | 12:00
61 | Gulshan | 52 | 12:00 | 127 | Pabna | 68 | 18:30
62 | Halishahar | 34 | 18:00 | 128 | Palashbari | 68 | 18:00
63 | HaripurSBU | 148 | 01:00 | 129 | Panchagarh | 38 | 18:00
64 | Hasnabad | 53 | 12:00 | 130 | Patuakhali | 53.5 | 21:00
65 | Hathazari | 51 | 12:00 | 131 | Payra | 14 | 13:00
66 | Ishurdi | 47 | 13:00 | 132 | Postogola | 30 | 14:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9002.5 | 0 |  | 9002.5
1:00 | 8446.99 | 0 |  | 8446.99
2:00 | 8111.94 | 0 |  | 8111.94
3:00 | 7862 | 0 |  | 7862
4:00 | 7624 | 0 |  | 7624
5:00 | 7469.5 | 0 |  | 7469.5
6:00 | 7749 | 0 |  | 7749
7:00 | 7883.41 | 0 |  | 7883.41
8:00 | 8472.68 | 0 |  | 8472.68
9:00 | 8795.07 | 0 |  | 8795.07
10:00 | 8594.01 | 0 |  | 8594.01
11:00 | 8754.76 | 0 |  | 8754.76
12:00 | 9466.87 | 0 |  | 9466.87
13:00 | 10195.91 | 0 |  | 10195.91
14:00 | 8666.48 | 0 |  | 8666.48
15:00 | 7997.78 | 0 |  | 7997.78
16:00 | 7538.11 | 0 |  | 7538.11
17:00 | 7822.79 | 0 |  | 7822.79
18:00 | 9419.5 | 0 |  | 9419.5
19:00 | 9583.5 | 0 |  | 9583.5
19:30 | 9601.5 | 0 |  | 9601.5
20:00 | 9553.5 | 0 |  | 9553.5
21:00 | 9566.5 | 0 |  | 9566.5
22:00 | 9246.5 | 0 |  | 9246.5
23:00 | 8814.5 | 0 |  | 8814.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5200 | 3802.5 | 9002.5 | DAILY LOAD CURVE
00:30 | 5025 | 3699.745 | 8724.745
01:00 | 4850 | 3596.99 | 8446.99 | 17-01-2025
01:30 | 4766.5 | 3512.965 | 8279.465
02:00 | 4683 | 3428.94 | 8111.94
02:30 | 4650.75 | 3336.22 | 7986.97
03:00 | 4618.5 | 3243.5 | 7862
03:30 | 4553 | 3190 | 7743
04:00 | 4487.5 | 3136.5 | 7624
04:30 | 4461.25 | 3085.5 | 7546.75
05:00 | 4435 | 3034.5 | 7469.5
05:30 | 4523.75 | 3085.5 | 7609.25
06:00 | 4612.5 | 3136.5 | 7749
06:30 | 4623.345 | 3192.86 | 7816.205
07:00 | 4634.19 | 3249.22 | 7883.41
07:30 | 4795.585 | 3382.46 | 8178.045
08:00 | 4956.98 | 3515.7 | 8472.68
08:30 | 5014.61 | 3619.265 | 8633.875
09:00 | 5072.24 | 3722.83 | 8795.07
09:30 | 5007.52 | 3687.02 | 8694.54
10:00 | 4942.8 | 3651.21 | 8594.01
10:30 | 4947.685 | 3726.7 | 8674.385
11:00 | 4952.57 | 3802.19 | 8754.76
11:30 | 5121.455 | 3989.36 | 9110.815
12:00 | 5290.34 | 4176.53 | 9466.87
12:30 | 5383.765 | 4447.625 | 9831.39
13:00 | 5477.19 | 4718.72 | 10195.91
13:30 | 5086.7 | 4344.495 | 9431.195
14:00 | 4696.21 | 3970.27 | 8666.48
14:30 | 4591.05 | 3741.08 | 8332.13
15:00 | 4485.89 | 3511.89 | 7997.78
15:30 | 4448.66 | 3319.285 | 7767.945
16:00 | 4411.43 | 3126.68 | 7538.11
16:30 | 4501.07 | 3179.38 | 7680.45
17:00 | 4590.71 | 3232.08 | 7822.79
17:30 | 4936.355 | 3684.79 | 8621.145
18:00 | 5282 | 4137.5 | 9419.5
18:30 | 5275 | 4226.5 | 9501.5
19:00 | 5268 | 4315.5 | 9583.5
19:30 | 5280 | 4321.5 | 9601.5
20:00 | 5232 | 4321.5 | 9553.5
20:30 | 5260.5 | 4299.5 | 9560 |  | Executive Engineer
21:00 | 5289 | 4277.5 | 9566.5 |  | Network Operation Division
21:30 | 5251.5 | 4155 | 9406.5
22:00 | 5214 | 4032.5 | 9246.5
22:30 | 5061.5 | 3969 | 9030.5
23:00 | 4909 | 3905.5 | 8814.5

## En-Curve
QF-LDC-12
Date | 17-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3022 | 1769.5 | 918 | 0 | 56 | 313 | 40 | 2766 | 0 | 17 | 90 | 0 | 0 | 11 | 0 | DAILY ENERGY CURVE
00:30 | 3012.5 | 1736.5 | 917.5 | 0 | 53 | 351.5 | 40 | 2523.5 | 0.245 | 8.5 | 71 | 0 | 0 | 10.5 | 0 | 17-01-2025
01:00 | 3003 | 1703.5 | 917 | 0 | 50 | 390 | 40 | 2281 | 0.49 | 0 | 52 | 0 | 0 | 10 | 0
01:30 | 2994 | 1658 | 834.5 | 0 | 49 | 403.5 | 40 | 2256.5 | 0.465 | 0 | 35 | 0 | 0 | 8.5 | 0 |  | Total Energy | 209.1549 |  | MKWHr
02:00 | 2985 | 1612.5 | 752 | 0 | 48 | 417 | 40 | 2232 | 0.44 | 0 | 18 | 0 | 0 | 7 | 0 |  | Energy not Served | 0 |  | MKWHr
02:30 | 2965 | 1582.25 | 739.5 | 0 | 46 | 415 | 40 | 2182 | 0.22 | 0 | 9 | 0 | 0 | 8 | 0 |  | Energy Requirement | 209.1549 |  | MKWHr
03:00 | 2945 | 1552 | 727 | 0 | 44 | 413 | 40 | 2132 | 0 | 0 | 0 | 0 | 0 | 9 | 0
03:30 | 2875.5 | 1497.5 | 727.5 | 0 | 48 | 413 | 40 | 2132 | 0 | 0 | 0 | 0 | 0 | 9.5 | 0
04:00 | 2806 | 1443 | 728 | 0 | 52 | 413 | 40 | 2132 | 0 | 0 | 0 | 0 | 0 | 10 | 0
04:30 | 2784 | 1438.25 | 680.5 | 0 | 51 | 414 | 40 | 2131.5 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0
05:00 | 2762 | 1433.5 | 633 | 0 | 50 | 415 | 40 | 2131 | 0 | 0 | 0 | 0 | 0 | 5 | 0
05:30 | 2842.5 | 1499.75 | 633 | 0 | 47 | 415 | 40 | 2129.5 | 0 | 0 | 0 | 0 | 0 | 2.5 | 0
06:00 | 2923 | 1566 | 633 | 0 | 44 | 415 | 40 | 2128 | 0 | 0 | 0 | 0 | 0 | 0 | 0
06:30 | 2919 | 1566 | 679.5 | 0 | 42 | 415.5 | 40 | 2129 | 3.705 | 0 | 21.5 | 0 | 0 | 0 | 0
07:00 | 2915 | 1566 | 726 | 0 | 40 | 416 | 40 | 2130 | 7.41 | 0 | 43 | 0 | 0 | 0 | 0
07:30 | 2927 | 1655.5 | 726.5 | 0 | 39 | 416.235 | 40 | 2269.5 | 51.31 | 8.5 | 44.5 | 0 | 0 | 0 | 0
08:00 | 2939 | 1745 | 727 | 0 | 38 | 416.47 | 40 | 2409 | 95.21 | 17 | 46 | 0 | 0 | 0 | 0
08:30 | 2949 | 1745.25 | 774.5 | 0 | 36 | 414.43 | 40 | 2436 | 157.195 | 17 | 64.5 | 0 | 0 | 0 | 0
09:00 | 2959 | 1745.5 | 822 | 0 | 34 | 412.39 | 40 | 2463 | 219.18 | 17 | 83 | 0 | 0 | 0 | 0
09:30 | 2928.5 | 1693 | 822.5 | 0 | 34 | 414.385 | 35 | 2356 | 307.655 | 17 | 86.5 | 0 | 0 | 0 | 0
10:00 | 2898 | 1640.5 | 823 | 0 | 34 | 416.38 | 30 | 2249 | 396.13 | 17 | 90 | 0 | 0 | 0 | 0
10:30 | 2889.5 | 1640 | 869.5 | 0 | 35.5 | 415.56 | 30 | 2248.5 | 438.825 | 17 | 90 | 0 | 0 | 0 | 0
11:00 | 2881 | 1639.5 | 916 | 0 | 37 | 414.74 | 30 | 2248 | 481.52 | 17 | 90 | 0 | 0 | 0 | 0
11:30 | 2906 | 1677 | 916.5 | 0 | 40.5 | 489.375 | 30 | 2433 | 511.44 | 17 | 88.5 | 0 | 0 | 1.5 | 0
12:00 | 2931 | 1714.5 | 917 | 0 | 44 | 564.01 | 30 | 2618 | 541.36 | 17 | 87 | 0 | 0 | 3 | 0
12:30 | 3022 | 1736.5 | 917 | 0 | 54 | 612.16 | 30 | 2852.5 | 505.73 | 17 | 83 | 0 | 0 | 1.5 | 0
13:00 | 3113 | 1758.5 | 917 | 0 | 64 | 660.31 | 30 | 3087 | 470.1 | 17 | 79 | 0 | 0 | 0 | 0
13:30 | 2946 | 1541 | 917 | 0 | 59 | 588.655 | 30 | 2788.5 | 466.04 | 17 | 78 | 0 | 0 | 0 | 0
14:00 | 2779 | 1323.5 | 917 | 0 | 54 | 517 | 30 | 2490 | 461.98 | 17 | 77 | 0 | 0 | 0 | 0
14:30 | 2775.5 | 1333.5 | 822 | 0 | 51 | 517.5 | 30 | 2338 | 384.63 | 8.5 | 70.5 | 0 | 0 | 1 | 0
15:00 | 2772 | 1343.5 | 727 | 0 | 48 | 518 | 30 | 2186 | 307.28 | 0 | 64 | 0 | 0 | 2 | 0
15:30 | 2717 | 1348.75 | 727.5 | 0 | 47 | 469 | 30 | 2131.5 | 229.695 | 0 | 64 | 0 | 0 | 3.5 | 0
16:00 | 2662 | 1354 | 728 | 0 | 46 | 420 | 30 | 2077 | 152.11 | 0 | 64 | 0 | 0 | 5 | 0
16:30 | 2703 | 1415.5 | 727.5 | 0 | 46 | 419 | 30 | 2171.5 | 94.45 | 2.5 | 64 | 0 | 0 | 7 | 0
17:00 | 2744 | 1477 | 727 | 0 | 46 | 418 | 30 | 2266 | 36.79 | 5 | 64 | 0 | 0 | 9 | 0
17:30 | 2931 | 1565.25 | 821 | 0 | 49 | 485.5 | 30 | 2578 | 18.395 | 37 | 96.5 | 0 | 0 | 9.5 | 0
18:00 | 3118 | 1653.5 | 915 | 0 | 52 | 553 | 30 | 2890 | 0 | 69 | 129 | 0 | 0 | 10 | 0
18:30 | 3167.5 | 1677.5 | 915.5 | 0 | 51 | 559 | 30 | 2930 | 0 | 43 | 119 | 0 | 0 | 9 | 0
19:00 | 3217 | 1701.5 | 916 | 0 | 50 | 565 | 30 | 2970 | 0 | 17 | 109 | 0 | 0 | 8 | 0
19:30 | 3240 | 1716.5 | 916 | 0 | 52 | 564 | 30 | 2975 | 0 | 17 | 85 | 0 | 0 | 6 | 0
20:00 | 3230 | 1719.5 | 916 | 0 | 52 | 563 | 30 | 2970 | 0 | 17 | 54 | 0 | 0 | 2 | 0
20:30 | 3225 | 1714 | 916 | 0 | 52 | 563.5 | 30 | 2996 | 0 | 8.5 | 54 | 0 | 0 | 1 | 0
21:00 | 3220 | 1708.5 | 916 | 0 | 52 | 564 | 30 | 3022 | 0 | 0 | 54 | 0 | 0 | 0 | 0
21:30 | 3219.5 | 1708.5 | 916.5 | 0 | 53 | 496 | 30 | 2929 | 0 | 0 | 54 | 0 | 0 | 0 | 0
22:00 | 3219 | 1708.5 | 917 | 0 | 54 | 428 | 30 | 2836 | 0 | 0 | 54 | 0 | 0 | 0 | 0
22:30 | 3171.5 | 1682.5 | 917 | 0 | 54 | 421.5 | 30 | 2708 | 0 | 0 | 45.5 | 0 | 0 | 0.5 | 0
23:00 | 3124 | 1656.5 | 917 | 0 | 54 | 415 | 30 | 2580 | 0 | 0 | 37 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 417 | 05:00 | 400 | 13:00 | Kaliakoir | 378 | 04:00 | 368 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 410 | 5:00 | 382 | 12:00 | Madunaghat | 410 | 03:00 | 401 | 13:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 410 | 05:00 | 397 | 12:00 | Meghnaghat | 409 | 05:00 | 399 | 13:00
| Bibiana | 396 | 05:00 | 390 | 04:00 | Payra | 419 | 05:00 | 409 | 13:00
| BIPTC | 408 | 04:00 | 391 | 11:00 | Rahanpur | 420 | 00:00 | 407 | 13:00
| Bogura | 416 | 00:00 | 402 | 13:00 | Rampal | 416 | 04:00 | 393 | 13:00
| Gopalganj | 418 | 04:00 | 403 | 13:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 237 | 04:00 | 228 | 13:00 | Haripur | 237 | 06:00 | 230 | 13:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 234 | 06:00 | 224 | 12:00 | Hasnabad | 235 | 00:00 | 44 | 18:30 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 236 | 04:00 | 226 | 13:00 | Hathazari | 236 | 05:00 | 231 | 12:00
| Ashuganj | 239 | 09:00 | 234 | 12:00 | Ishurdi | 244 | 03:00 | 234 | 13:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 239 | 09:00 | 234 | 13:00 | Jhenaidah | 242 | 05:00 | 226 | 13:00
| Baghabari | 242 | 01:00 | 234 | 12:00 | Kaliakoir | 237 | 04:00 | 229 | 12:00 | 230 kV MAX | 248 |  | 248 | 222
| Barapukuria | 227 | 03:00 | 222 | 19:00 | Keranigonj | 237 | 05:00 | 228 | 13:00 | 230 kV MIN | 44 |  | 245 | 44 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 227 | 14:00 | 222 | 19:00 | Khulna(S) | 243 | 04:00 | 228 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 247 | 04:00 | 236 | 13:00 | Madunaghat | 233 | 09:00 | 228 | 13:00 | 132 kV MAX | 143 |  | 142 | 112 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 243 | 04:00 | 231 | 13:00 | Madunaghat-400 | 234 | 03:00 | 228 | 13:00 | 132 kV MIN | 110 |  | 143 | 110 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 240 | 05:00 | 232 | 12:00 | Maniknagar | 237 | 04:00 | 228 | 12:00 | [35 empty] | 6:00
| Bibiana | 230 | 02:00 | 226 | 12:00 | Meghnaghat | 245 | 05:00 | 239 | 13:00 |  | 400 | [33 empty] | 392
| BIPTC | 244 | 04:00 | 231 | 13:00 | Meghnaghat-400 | 240 | 05:00 | 233 | 13:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 242 | 03:00 | 234 | 18:30 | Mirsorai | 234 | 05:00 | 224 | 13:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 240 | 00:00 | 233 | 13:00 | Rajshahi | 243 | 05:00 | 232 | 12:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 248 | 03:00 | 244 | 14:00 | Rampal | 241 | 04:00 | 225 | 13:00 |  | 132 |  |  | Ash 400-299274
| BSRM | 235 | 05:00 | 226 | 13:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 235 | 05:00 | 227 | 12:00 | Rampura | 239 | 04:00 | 136 | 00:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 247 | 05:00 | 238 | 13:00 | Shikalbaha | 233 | 02:00 | 226 | 19:00 |  | kaptai by call 399528
| Fenchuganj | 233 | 01:00 | 223 | 06:00 | Shyampur | 238 | 05:00 | 230 | 13:00
| Ghorashal | 240 | 01:00 | 238 | 00:00 | Siddhirganj | 240 | 23:00 | 232 | 12:00
| Ghorashal-230 | 238 | 05:00 | 228 | 13:00 | Sirajgonj | 248 | 05:00 | 242 | 13:00
| Gopalganj | 248 | 05:00 | 238 | 13:00 | Sreepur | 238 | 00:00 | 232 | 13:00
| GPH | 234 | 05:00 | 225 | 13:00 | Tongi | 233 | 19:30 | 224 | 09:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 137 | 06:00 | 127 | 12:00 | Kurigram | 130 | 04:00 | 115 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 138 | 05:00 | 127 | 12:00 | Kushtia | 140 | 02:00 | 132 | 08:00
| Agrabad | 133 | 01:00 | 127 | 12:00 | Lalbag | 136 | 00:00 | 129 | 12:00
| AKS | 130 | 09:00 | 125 | 12:00 | Lalmonirhat | 130 | 04:00 | 121 | 23:00
| Aminbazar | 136 | 02:00 | 126 | 14:00 | Madanganj | 135 | 04:00 | 129 | 12:00
| Amnura | 141 | 18:00 | 128 | 08:00 | Madaripur | 134 | 03:00 | 130 | 14:00
| Ashuganj | 140 | 03:00 | 135 | 12:00 | Madartek | 136 | 03:00 | 127 | 11:00
| Bagerhat | 138 | 01:00 | 124 | 13:00 | Madunaghat | 134 | 19:30 | 129 | 12:00
| Bajitpur | 134 | 17:00 | 129 | 12:00 | Magura | 141 | 03:00 | 129 | 13:00
| Bakulia | 134 | 04:00 | 128 | 12:00 | Mahasthangarh | 134 | 04:00 | 125 | 08:00
| Banani | 138 | 02:00 | 127 | 11:00 | Manikganj | 131 | 18:00 | 124 | 12:00
| Bangabhaban | 136 | 04:00 | 126 | 12:00 | Maniknagar | 135 | 05:00 | 126 | 12:00
| Barapukuria | 135 | 02:00 | 127 | 08:00 | Matarbari | 129 | 00:00 | 119 | 12:00
| Barguna | 141 | 22:00 | 134 | 23:00 | Matuail | 133.5 | 03:00 | 127 | 12:00
| Barishal | 136 | 04:00 | 128 | 12:00 | Millgate | 138 | 04:00 | 124 | 12:00
| Barishal-230 | 137 | 04:00 | 130 | 12:00 | Mirpur | 134 | 00:00 | 125 | 12:00
| Baroaulia | 134 | 18:00 | 128 | 12:00 | Mirzapur | 131 | 23:00 | 122 | 12:00
| Baroirhat | 134 | 18:00 | 125 | 12:00 | Mithapukur | 134 | 04:00 | 128 | 07:00
| Bashundhara | 138 | 05:00 | 125 | 12:00 | MI_Cement | 137 | 04:00 | 128 | 12:00
| BashundharaCement | 135 | 04:00 | 125 | 03:00 | Modern | 135 | 05:00 | 126 | 12:00
| Beanibazar | 135 | 03:00 | 131 | 14:00 | Mogbazar | 137 | 03:00 | 128 | 14:00
| Benapole | 139 | 03:00 | 124 | 13:00 | Mongla | 135 | 04:00 | 124 | 13:00
| Bhaluka | 130 | 04:00 | 121 | 08:00 | Motijheel | 136 | 04:00 | 126 | 12:00
| Bhandaria | 135 | 03:00 | 126 | 12:00 | Muktagacha | 127 | 16:00 | 118 | 18:00
| Bhangura | 141 | 04:00 | 133 | 12:00 | Munshiganj | 135 | 05:00 | 127 | 12:00
| Bheramara | 141 | 04:00 | 133 | 08:00 | Mymensingh | 128 | 00:00 | 116 | 18:00
| Bheramara(GK) | 141 | 03:00 | 135 | 08:00 | Naogaon | 134 | 04:00 | 128 | 08:00
| Bhulta | 125 | 18:00 | 116 | 12:00 | Narail | 140 | 03:00 | 129 | 08:00
| Bog-Sherpur | 136 | 23:00 | 126 | 08:00 | Narinda | 135 | 05:00 | 126 | 12:00
| Bogura | 136 | 05:00 | 126 | 08:00 | Narshingdi | 136 | 00:00 | 122 | 11:00
| Bogura-230 | 138 | 03:00 | 127 | 08:00 | Natore | 138 | 02:00 | 130 | 08:00
| Brahmanbaria | 136 | 00:00 | 130 | 12:00 | Nawabganj | 138 | 02:00 | 128 | 12:00
| Cantonment | 138 | 05:00 | 127 | 12:00 | Netrakona | 127 | 01:00 | 117 | 13:00
| Chandpur | 139 | 18:00 | 126 | 12:00 | New | 138 | 03:00 | 126 | 12:00
| Chandraghona | 135 | 18:00 | 129 | 12:00 | Niamatpur | 142 | 22:00 | 132 | 00:00
| Chapai | 140 | 20:00 | 134 | 06:00 | Noapara | 140 | 01:00 | 128 | 12:00
| Charsaidpur | 136 | 04:00 | 128 | 12:00 | Pabna | 141 | 04:00 | 131 | 08:00
| Chauddagram | 132 | 01:00 | 125 | 12:00 | Palashbari | 132 | 03:00 | 125 | 08:00
| Chhatak | 135 | 04:00 | 130 | 11:00 | Panchagarh | 135 | 04:00 | 121 | 08:00
| Chowmuhani | 134 | 18:30 | 123 | 12:00 | Patuakhali | 140 | 19:30 | 134 | 05:00
| Chuadanga | 140 | 02:00 | 128 | 08:00 | Payra | 137 | 01:00 | 134 | 12:00
| Coxsbazar | 124 | 00:00 | 119 | 12:00 | PHP | 133 | 18:00 | 125 | 12:00
| Cumilla(N) | 136 | 01:00 | 128 | 12:00 | Postogola | 139 | 03:00 | 130 | 12:00
| Cumilla(S) | 136 | 18:00 | 127 | 12:00 | Purbachal | 138 | 04:00 | 127 | 12:00
| Daudkandi | 133 | 01:00 | 125 | 12:00 | Purbasadipur | 132 | 18:00 | 122 | 08:00
| Dhaka | 137 | 03:00 | 127 | 12:00 | Rahanpur | 142 | 20:00 | 131 | 07:00
| Dhamrai | 133 | 00:00 | 125 | 12:00 | Rahanpur-400 | 142 | 22:00 | 129 | 08:00
| Dhanmondi | 137 | 03:00 | 127 | 12:00 | Rahim | 135 | 05:00 | 127 | 13:00
| Dohazari | 131 | 17:00 | 124 | 12:00 | Rajbari | 137 | 04:00 | 128 | 13:00
| Faridpur | 137 | 02:00 | 129 | 13:00 | Rajendrapur | 134 | 00:00 | 126 | 13:00
| Fatullah | 138 | 04:00 | 129 | 12:00 | Rajshahi | 138 | 01:00 | 132 | 08:00
| Fenchuganj | 139 | 01:00 | 135 | 11:00 | Rajshahi-230 | 140 | 05:00 | 126 | 08:00
| Feni | 133 | 19:00 | 124 | 12:00 | Ramganj | 136 | 18:00 | 123 | 14:00
| Ghatail | 128 | 00:00 | 121 | 09:00 | Rampur | 134 | 04:00 | 126 | 11:00
| Ghorashal | 140 | 01:00 | 135 | 13:00 | Rampura | 137 | 05:00 | 127 | 12:00
| Goalpara | 141 | 01:00 | 127 | 13:00 | Rangamati | 135 | 05:00 | 128 | 12:00
| Gollamari | 140 | 04:00 | 129 | 12:00 | Rangpur | 132 | 04:00 | 120 | 08:00
| Gopalganj | 139 | 04:00 | 128 | 12:00 | Ruppur | 142 | 04:00 | 135 | 08:00
| Gopalganj-400 | 139 | 05:00 | 130 | 13:00 | Saidpur | 133 | 04:00 | 122 | 08:00
| Gulshan | 136 | 03:00 | 126 | 12:00 | Satkhira | 139 | 03:00 | 126 | 08:00
| Halishahar | 134 | 18:30 | 124 | 12:00 | Satmasjid | 137 | 04:00 | 126 | 13:00
| Haripur | 135 | 05:00 | 128 | 12:00 | Savar | 133 | 00:00 | 124 | 12:00
| HaripurSBU | 135 | 04:00 | 128 | 12:00 | SevenRings | 141 | 04:00 | 133 | 12:00
| Hasnabad | 138 | 00:00 | 130 | 12:00 | ShahCement | 136 | 04:00 | 128 | 12:00
| Hathazari | 136 | 18:00 | 130 | 15:00 | Shahjadpur | 143 | 04:00 | 136 | 07:00
| Ishurdi | 142 | 03:00 | 134 | 08:00 | Shahjibazar | 138 | 00:00 | 131 | 12:00
| Jaldhaka | 131 | 04:00 | 117 | 08:00 | Shahmirpur | 134 | 02:00 | 128 | 12:00
| Jamalpur | 129 | 10:00 | 112 | 08:00 | Shariatpur | 138 | 04:00 | 129 | 12:00
| Jashore | 137 | 01:00 | 126 | 08:00 | Sherpur | 126 | 10:00 | 110 | 08:00
| Jhenaidah | 141 | 01:00 | 130 | 12:00 | Shikalbaha | 123 | 06:00 | 117 | 12:00
| Jhenaidah-230 | 142 | 04:00 | 131 | 08:00 | Shikalbaha-230 | 135 | 18:00 | 128 | 12:00
| Joydebpur | 140 | 17:00 | 129 | 12:00 | Shitalakhya | 139 | 02:00 | 128 | 12:00
| Joypurhat | 136 | 02:00 | 124 | 08:00 | Sholosohor | 134 | 05:00 | 128 | 12:00
| Juldah | 133 | 18:00 | 128 | 13:00 | Shyampur | 136 | 01:00 | 133 | 08:00
| Kabirpur | 135 | 01:00 | 124 | 12:00 | Shyampur-230 | 140 | 05:00 | 128 | 12:00
| Kachua | 137 | 18:00 | 125 | 13:00 | Siddhirganj | 135 | 01:00 | 128 | 12:00
| Kaliakoir | 138 | 04:00 | 127 | 12:00 | Sirajganj | 138 | 01:00 | 127 | 08:00
| Kallyanpur | 137 | 04:00 | 127 | 12:00 | Sonargaon | 132 | 17:00 | 125 | 12:00
| Kalurghat | 135 | 18:00 | 129 | 12:00 | Sreemongol | 136 | 00:00 | 131 | 11:00
| Kamrangirchar | 139 | 02:00 | 125 | 12:00 | Sreepur | 130 | 05:00 | 123 | 08:00
| Kaptai | 137 | 4:00 | 133 | 15:00 | Srinagar | 137 | 02:00 | 128 | 12:00
| Kazla | 136 | 05:00 | 125 | 13:00 | SSM | 139 | 18:00 | 132 | 08:00
| Keranigonj | 138 | 03:00 | 129 | 12:00 | Sunamganj | 133 | 04:00 | 130 | 12:00
| Khagrachori | 134 | 05:00 | 127 | 12:00 | Sylhet | 136 | 04:00 | 132 | 13:00
| Khulna | 139 | 01:00 | 126 | 13:00 | Sylhet-132 | 135 | 02:00 | 131 | 12:00
| Khulna(S) | 141 | 04:00 | 129 | 13:00 | Tangail | 128 | 00:00 | 120 | 08:00
| Khulshi | 133 | 18:30 | 126 | 12:00 | Thakurgaon | 133 | 05:00 | 117 | 08:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 133 | 04:00 | 125 | 08:00 | TK | 133 | 00:00 | 128 | 12:00 |  |  | Nos | Nos | Nos
| Kodda | 136 | 17:00 | 124 | 12:00 | Tongi | 138 | 01:00 | 128 | 11:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 134 | 00:00 | 128 | 12:00 | Ullahpara | 139 | 23:00 | 129 | 07:00
| Kulaura | 138 | 00:00 | 134 | 14:00 | Ullon | 136 | 01:00 | 128 | 12:00
| UttaraNew | 137 | 03:00 | 122 | 12:00 | Uttara | 136 | 03:00 | 125 | 12:00
| Zigatola | 138 | 00:00 | 124 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.