## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-01-2025 | during | 19-01-2025 | during | 19-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 375 | 351 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 350 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 125 | 239 | 170 | 335 | 300 | 300 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 250 | 335 | 335 | 280 | 280 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 19.5 | 18.5 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 33 | 30 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 26 | 26 | 52.19 | 52.19 | 27 | 27 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 35 | 70 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 0 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0.01 | 0.01 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6257.05 | 5842.27 | 1392.5 | 1535.5 | 3858.99 | 4001.99 | 2639.73 | 2617.73
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 225 | 227 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 32 | 32 | 32 | 32 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 6 | 14 | 2 | 10 | 2 | 10 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 50 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 35 | 35 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 680 | 1068 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 7 | 29 | 25 | 36 | 25 | 36 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 953 | 990 | 1150 | 1150 | 1050 | 1050 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1916 | 2358 | 4031.72 | 4030.72 | 3792.72 | 3791.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 182 | 182 | 221 | 221 | 180 | 180 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 48 | 48 | 46.94 | 46.94 | 46.94 | 46.94 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 0 | 5 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 195 | 199 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 43 | 43 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 54 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 16 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 17 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 69 | 0 | 69 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 645 | 638 | 1677.97 | 1608.97 | 1512.14 | 1443.14
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 25 | 18 | 210 | 210 | 15 | 15 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 18 | 18 | 200 | 200 | 18 | 18 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 14 | 115 | 115 | 49 | 49 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 41.37 | 0 | 42.34 | 0.11 | 42.34 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 9 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 135.37 | 59 | 645.84 | 601.61 | 202.84 | 158.61
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 10 | 10 | 44 | 44 | 10 | 10 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 20 | 20 | 0 | 0 | 20 | 20 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 207 | 204 | 0 | 0 | 210 | 210 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 0 | 0 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 303 | 348 | 395 | 395 | 340 | 340 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1449 | 1476 | 1401.5 | 1401.5 | 1501.01 | 1501.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 917 | 917 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 330 | 334 | 410 | 410 | 350 | 350 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 74.7 | 0 | 74.5 | 0 | 74.5 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1321.7 | 1251 | 3243.5 | 3169 | 1509.51 | 1435.01
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 6 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 140 | 135 | 135 | 135 | 135 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 800 | 1120 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 301 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1324.5 | 1787 | 2176.12 | 2176.12 | 2133 | 2133
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 150 | 189 | 214 | 214 | 200 | 200 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 220 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 220 | 220 | 220 | 200 | 200 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 8.5 | 8.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.51 | 0 | 4.12 | 0 | 4.12 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 511 | 753.5 | 1347.54 | 1347.54 | 800 | 800 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.33 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 93 | 0 | 93 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1099.34 | 1391 | 2699.11 | 2551.99 | 2097.57 | 1950.45
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 72 | 72 | 72 | 72 | 72 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 210 | 210 | 210 | 210 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.9 | 0 | 2.8 | 0 | 2.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 170 | 0 | 160 | 0 | 160 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 487.9 | 282 | 736.8 | 544 | 702.82 | 510.02
System Total |  |  |  |  | 27734.66 | 27067.248 | 9771.31 | 10777.5 | 20471.55 | 20085.9 | 16091.34 | 15540.69
Forecast Scenario (19-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9060 |  | 0 |  | 9060
|  |  |  | 1:00 | 8560 |  | 0 |  | 8560
|  |  |  | 2:00 | 8060 |  | 0 |  | 8060
|  |  |  | 3:00 | 7750 |  | 0 |  | 7750
|  |  |  | 4:00 | 7570 |  | 0 |  | 7570
|  |  |  | 5:00 | 7520 |  | 0 |  | 7520
|  |  |  | 6:00 | 7920 |  | 0 |  | 7920
|  |  |  | 7:00 | 8700 |  | 0 |  | 8700
|  |  |  | 8:00 | 9540 |  | 0 |  | 9540
|  |  |  | 9:00 | 10020 |  | 0 |  | 10020
|  |  |  | 10:00 | 9790 |  | 0 |  | 9790
|  |  |  | 11:00 | 9890 |  | 0 |  | 9890
|  |  |  | 12:00 | 10340 |  | 0 |  | 10340
|  |  |  | 13:00 | 10660 |  | 0 |  | 10660
|  |  |  | 14:00 | 10330 |  | 0 |  | 10330
|  |  |  | 15:00 | 10000 |  | 0 |  | 10000
|  |  |  | 16:00 | 9600 |  | 0 |  | 9600
|  |  |  | 17:00 | 9740 |  | 0 |  | 9740
|  |  |  | 18:00 | 10790 |  | 0 |  | 10790
|  |  |  | 18:30 | 10860 |  | 0 |  | 10860
|  |  |  | 19:00 | 10940 |  | 0 |  | 10940
|  |  |  | 19:30 | 10880 |  | 0 |  | 10880
|  |  |  | 20:00 | 10820 |  | 0 |  | 10820
|  |  |  | 21:00 | 10510 |  | 0 |  | 10510
|  |  |  | 22:00 | 10130 |  | 0 |  | 10130
|  |  |  | 23:00 | 9480 |  | 0 |  | 9480
Probable Maximum Temperature: |  |  | 23.60°C
Probable Maximum Demand at Day Peak: |  |  | 10340.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 10940.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10940.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 227.72 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (18-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 27.30°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 839.11
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 20.539 | Peak Hour Flow: |  | 917.00 MW at 19:00 hrs.
Energy Flow from West to East |  | 8938018.255 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 11.9757 | Peak Hour Flow: |  | 753.50 MW at 19:00 hrs.
Power Flow during Peak Demand |  | 582 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.1846 | Peak Hour Flow: |  | 54.00 MW at 19:00 hrs.
Maximum Power Flow |  | 888 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 33.6994 | Peak Hour Flow: |  | 1724.50 MW at 19:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 18-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 9771.31 | MW | 12:00 Hr. | Energy Generated |  |  | 220273.0085 |  | MWHr
Day Peak Demand |  |  | 9771.31 | MW | 12:00 Hr. | Energy Unserverd |  |  | 73 |  | MWHr
Evening Peak Generation |  |  | 10777.5 | MW | 19:00 Hr. | Energy Demand |  |  | 220346.0085 |  | MWHr
Evening Peak Demand |  |  | 10800.5 | MW | 19:00 Hr.
Minimum Generation of the Day |  |  | 6991.5 | MW | 04:00 Hr.
Maximum Generation of the Day |  |  | 10777.5 | MW | 19:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 29953.565 | 0 | 2210.995 | 0 | 0 | 172.512 | 0 | 0 | 32337.072 | Gas | 111942.514 | Gas | 398647690.52
Chattogram Zone |  |  | 5625.694 | 36310.9072 | 135.523 | 0 | 724.32 | 133.474 | 0 | 238.08 | 43167.9982 | Coal | 66346.7433 | Coal | 469462298.0381
Cumilla Zone |  |  | 12029.882 | 0 | 171.96 | 0 | 0 | 374.691 | 1184.64 | 0 | 13761.173 | HFO | 3788.078 | HFO | 73640267.8
Mymensingh Zone |  |  | 508.8 | 0 | 1246.8 | 0 | 0 | 263.09 | 0 | 0 | 2018.69 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 35266.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35266.653 | Hydro | 724.32 | Hydro | 72432
Khulna Zone |  |  | 7501.536 | 0 | 0 | 0 | 0 | 461.52 | 20539 | 0 | 28502.056 | Solar | 3533.9112 | Solar | 55570281.33
Barishal Zone |  |  | 8278.216 | 23498.9091 | 22.8 | 0 | 0 | 3.048 | 0 | 0 | 31802.9731 | Import | 33699.362 | Import | 161958096.46
Rajshahi Zone |  |  | 12778.168 | 0 | 0 | 0 | 0 | 918.012 | 11975.722 | 0 | 25671.902 | Wind | 238.08 | Wind | 3714048
Rangpur Zone |  |  | 0 | 6536.927 | 0 | 0 | 0 | 1207.5642 | 0 | 0 | 7744.4912
Total |  |  | 111942.514 | 66346.7433 | 3788.078 | 0 | 724.32 | 3533.9112 | 33699.362 | 238.08 | 220273.0085
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 398647690.52 |  | Hydro | 72432
|  |  | Coal | 469462298.0381 |  | Solar | 55570281.33
|  |  | HFO | 73640267.8 |  | Import | 161958096.46
|  |  | HSD | 0 |  | Wind | 3714048
|  |  |  | Total: | 1163065114.1481 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
| 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
| 4 | Barapukuria TPP Unit-2 |  |  | 85
| 5 | Khulna 330 MW CCPP GT |  |  | 220
| 6 | Khulna 330 MW CCPP ST |  |  | 110
| 7 | Siddhirgonj 210 MW TPP |  |  | 115
| 8 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 9 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1404 |  |  |  | Total | 435.09
|  |  | Total Unavailable Capacity |  |  |  | 1839.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3936
|  |  | Chattogram |  | 0 |  | 1008
|  |  | Cumilla |  | 0 |  | 883
|  |  | Mymensingh |  | 22 |  | 953
|  |  | Sylhet |  | 0 |  | 372
|  |  | Khulna |  | 0 |  | 1200
|  |  | Barishal |  | 0 |  | 291
|  |  | Rajshahi |  | 0 |  | 1012
|  |  | Rangpur |  | 0 |  | 688
|  |  | Total |  | 22 |  | 10343
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:03 | 17:13 | Bhaluka 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Annual maintenance | [7 empty] | 80.0MW load
interrup.
08:03 | 17:10 | Bhaluka 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Annual maintenance | [7 empty] | 80.0MW load
interrup.
08:03 | 17:07 | Cumilla(S) 132/33kV S/S Tripura Ckt-2 Scheduled S/D Due to Annual Maintenance
08:12 | 16:38 | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to 33kv bus loop connection by west zone
08:13 | 16:38 | Gopalganj 132/33kV S/S T1 HT Scheduled S/D Due to 33kv bus loop connection by west zone
08:14 | 15:28 | Daudkandi-Sonargaon 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to
shutdown for annual maintenance work and from Sonargaon 132/33kV end Due to Annual
maintenance by Daudkanti.
08:14 | 16:21 | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to Yearly
Maintenance and from Bagerhat 132/33kV end Due to Goalpara bay annual maintenance
08:18 | 09:25 | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to PDB will change 33kv PT | [7 empty] | 30.0MW load
interrup.
08:18 | 09:25 | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to Pdb will Change 33kv pt | [7 empty] | 30.0MW load
interrup.
08:20 | 15:48 | Pabna 132/33kV S/S Main Bus Scheduled S/D Due to Annual Maintenance | [7 empty] | 30.0MW load
interrup.
08:23 | 16:39 | Tangail 132/33kV S/S Tr-4 LT Scheduled S/D Due to Annual Maintenance
08:23 | 16:39 | Tangail 132/33kV S/S Tr-4 HT Scheduled S/D Due to Annual Maintenance
08:24 | 16:08 | Tangail 132/33kV S/S Tr-3 LT Scheduled S/D Due to Annual Maintenance
08:24 | 15:50 | Tangail 132/33kV S/S Tr-3 HT Scheduled S/D Due to Annual Maintenance
08:25 | 15:16 | Tangail 132/33kV S/S Tr-2 LT Scheduled S/D Due to Annual Maintenance
08:25 | 15:14 | Tangail 132/33kV S/S Tr-2 HT Scheduled S/D Due to Annual Maintenance
08:32 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
08:33 | 16:03 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-01 Scheduled S/D Due to Annual maintenance
08:33 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
08:34 | 16:39 | Tangail 132/33kV S/S RPCL-2 Scheduled S/D Due to Annual Maintenance
08:34 | 16:39 | Tangail 132/33kV S/S RPCL-1 Scheduled S/D Due to Annual Maintenance
08:35 | 14:57 | Tangail 132/33kV S/S Kaliakair-2 Scheduled S/D Due to Annual Maintenance
08:36 | 15:13 | Tangail 132/33kV S/S Tr-1 LT Scheduled S/D Due to Annual Maintenance
08:37 | 15:12 | Tangail 132/33kV S/S Tr-1 HT Scheduled S/D Due to Annual Maintenance
08:37 | 15:57 | Tangail 132/33kV S/S Kaliakair-1 Scheduled S/D Due to Annual Maintenance
08:38 | 14:56 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2A(E04) Scheduled S/D Due to S/D Take tangail
Grid
08:38 | 14:55 | Mirzapur 132/33kV S/S Mirzapur-Tangail-ckt-2B(E03) Scheduled S/D Due to S/D Take Tangail
Grid
08:39 | 16:22 | Mymensingh RPCL-Tangail 132kV Ckt-1 Scheduled S/D from Ghatail 132/33kV end Due to
Annual Maintenance Work on Tangail Grid.
08:40 | 16:22 | Mymensingh RPCL-Tangail 132kV Ckt-2 Scheduled S/D from Ghatail 132/33kV end Due to
Annual Maintenance Work on Tangail Grid.
08:42 | 12:52 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to
Annual Maintenance work and from Shahjibazar 132/33kV end Due to Line D/S Maintenece Work
08:44 | 16:03 | HVDC Bheramera- Rajshahi 230kV Ckt-1 Scheduled S/D from BIPTC end Due to Shutdown is
taken from Rajshahi end
08:45 | 16:31 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 HT Scheduled S/D Due to annual maintenance
08:45 | 16:31 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT Scheduled S/D Due to Annual maintenance
09:02 | 16:59 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-2 Scheduled S/D Due to Annual maintenance
09:17 | 17:06 | Mymensingh RPCL -Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due
to Annual maintenance works (2024-2025).
| 09:18 | Rampura 230/132kV S/S 132 kV Busbar-2 is restored.
09:21 | 16:05 | Kushtia 132/33kV S/S T-3 LT Scheduled S/D Due to A/M | [7 empty] | 25.0MW load
interrup.
09:22 | 16:04 | Kushtia 132/33kV S/S T-3 HT Scheduled S/D Due to A/M | [7 empty] | 25.0MW load
interrup.
09:30 | 16:20 | Haripur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to Annual Maintenance.
09:30 | 18:48 | Ashuganj-Bhulta 400 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to 400 kv
Bhulta-Ashugonj ckt-01 Shutdown taken for Dead line checking
09:30 | 16:20 | Haripur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to Annual Maintenance.
09:39 | 13:29 | Rampura 230/132kV S/S 132 kV Busbar-1 Scheduled S/D Due to Project (G2G) work, Jumper
connection between BUSBAR & Diameter 05.
09:40 | 14:37 | Sylhet 132/33kV S/S T4 HT Scheduled S/D Due to Ten Delta Test
09:41 | 14:38 | Sylhet 132/33kV S/S T4 LT Scheduled S/D Due to Ten Delta Test
09:58 | 12:46 | Ishurdi 132/33kV S/S 132 kV Bus-2 Scheduled S/D
10:20 | 18:58 | Aminbazar 400/230/132kV S/S ATR-02 LT Scheduled S/D Due to Annual maintenance
10:20 | 18:56 | Aminbazar 400/230/132kV S/S ATR-02 HT Scheduled S/D Due to Annual maintenance
10:21 | 18:47 | BIPTC S/S Baharampur-4 Scheduled S/D Due to Shutdown is taken for annual maintenance
work.
11:07 | 17:03 | BIPTC S/S 20DF44 Scheduled S/D Due to Shutdown is taken for the painting work of the fire
fighting pipes.
11:15 | 15:38 | Khulna (C) S/S TR-1 425T LT Project Work S/D Due to Due to 33kv bus section-1, bus PT
replacements work.
11:16 | 15:37 | Khulna (C) S/S TR-1 425T HT Project Work S/D Due to Due to 33kv bus section-1, bus PT
replacements work.
12:00 |  | Day Peak generation = 9,771MW
12:11 |  | Bibiyana-III 400 MW CCPP, FGMO is ON with remarks:-
| 13:05 | Sylhet 132/33kV S/S T1 LT is restored.
13:34 | 17:24 | BIPTC S/S 20D10A 20MVA LT Scheduled S/D Due to Shutdown is taken for the painting work of
the fire fighting pipes.
13:55 | 16:29 | Gopalganj 132/33kV S/S T2 LT Tripped showing Over current, Earth Fault relays Due to | [7 empty] | 57.0MW load
|  | Section ds flashing | [7 empty] | interrup.
14:40 | 16:48 | Sylhet 132/33kV S/S T2 HT Scheduled S/D Due to Due to Ten Delta Test.
14:42 | 16:48 | Sylhet 132/33kV S/S T2 LT Scheduled S/D Due to Due to Ten Delta Test.
14:57 | 16:29 | Gopalganj 132/33kV S/S T2 HT Forced S/D Due to Section ds flashing | [7 empty] | 57.0MW load
interrup.
15:53 |  | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- GT-2 synch done at 15:53 after
air intake filter replacement done
15:53 |  | Meghnaghat Summit CCPP 335 MW GT-2 was sync.
15:53 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2
16:38 | 19:55 | Keranigonj 230/132/33kV S/S Earthing Trafo-1 HT Tripped showing Trip relay 86 operated.
relays Due to 230 kV ATR-1 PRV-2 Trip
16:38 | 19:55 | Keranigonj 230/132/33kV S/S ATR-1 LT Tripped showing Trip relay 86 operated. relays Due
to PRV-2 Trip,Trip relay 86 operated.
16:38 | 19:55 | Keranigonj 230/132/33kV S/S ATR-1 HT Tripped showing Trip relay 86 operated. relays Due
to PRV-2 Trip,Trip relay 86 operated.
16:38 | 19:55 | Keranigonj 230/132/33kV S/S Earthing Trafo-1 LT Tripped showing Trip relay 86 operated.
relays Due to 230 kV ATR-1 PRV-2 Trip
| 19:12 | Cantonment 132/33kV S/S Transformer-2 (T-2) HT is restored.
| 19:55 | Keranigonj 230/132/33kV S/S ATR-1 HT is restored.
00:10 |  | Patuakhali 1320 MW (RNPL) unit-2 was sync. for the first time
00:10 |  | RNPL Unit-2 synch
05:00 |  | Minimum Generation is 7429 MW
07:36 |  | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to Relay
Change.
07:39 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
07:40 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 351 | 8838000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 7880500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 239 | 4341062 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 108000 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6819503 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 18360 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 386880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 32491 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18.5 | 396000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 531000 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 521900 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 30 | 517600 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 26 | 354240 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 70 | 687024 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 586560 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 113760 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 172512 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 0 | 31680 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 1535.5 | 32337072
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 132435 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 44160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 724320 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 227 | 5122654 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 25091 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 38672 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 14 | 503040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 1039 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 27600 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1068 | 15169089 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 29 | 238080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 990 | 21141818.18 | -
Chattogram Area Total |  |  |  |  | 4915.22 | 2358 | 43167998.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4468000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 48 | 1107216 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 113760 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 199 | 3947636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 910480 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1193360 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 24000 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 54 | 1184640 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 289430 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 17 | 79800 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 68160 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 374691 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 638 | 13761173
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 18 | 508800 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 18 | 309600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 14 | 775200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 251090 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 9 | 162000 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 59 | 2018690
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 715000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3637555 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | -
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 10 | 352008 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 56112 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 20 | 475968 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1654080 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 204 | 5231250 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 328080 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7171000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 7964000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7681600 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1476 | 35266653
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 917 | 20539000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 334 | 7501536 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 461520 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1251 | 28502056
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 6 | 134266 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2977000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 19122909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5166950 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 22800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 301 | 4376000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3048 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1787 | 31802973.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | -
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 189 | 4020818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 220 | 4152236 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 220 | 4429182 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 8.5 | 175932 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26700 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 753.5 | 11975722 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 317252 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 574060 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1391 | 25671902
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 72 | 1635927 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4901000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 27214.2 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 189630 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 990720 | -
Rangpur Area Total |  |  |  |  | 950 | 282 | 7744491.2
Eastern Grid Total |  |  |  |  | 16772.748 | 6066.5 | 126551586.18
Western Grid Total |  |  |  |  | 10294.5 | 4711 | 93721422.29
National Grid Total |  |  |  |  | 27067.248 | 10777.5 | 220273008.47
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7130.49 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3190.4 | MW
i) Dhaka area |  |  | 3936.49 |  | MW | i) Khulna area |  |  |  | 1200 | MW
ii) Chattogram area |  |  | 1008 |  | MW | ii) Barishal area |  |  |  | 290.8 | MW
iii) Cumilla area |  |  | 883 |  | MW | iii) Rajshahi area |  |  |  | 1011.6 | MW
iv) Mymensingh area |  |  | 931 |  | MW | iv) Rangpur area |  |  |  | 688 | MW
v) Sylhet area |  |  | 372 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10320.89 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 00:00 | 67 | Jaldhaka | 57 | 18:30 | 133 | Purbachal | 15 | 13:00
2 | AKSML | 109 | 00:00 | 68 | Jamalpur | 102 | 08:00 | 134 | Purbasadipur | 100 | 13:00
3 | Aftabnagar | 24 | 12:00 | 69 | Jashore | 113 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 71 | 13:00 | 70 | Jhenaidah | 94 | 08:00 | 136 | Rahim | 33 | 17:00
5 | Agrabad | 62 | 19:00 | 71 | Joydebpur | 120 | 18:00 | 137 | Rajbari | 56 | 18:30
6 | Amnura | 54 | 12:00 | 72 | Joypurhat | 41 | 09:00 | 138 | Rajendrapur | 96 | 18:30
7 | Ashuganj | 63 | 13:00 | 73 | Juldah | 11 | 10:00 | 139 | Rajshahi | 101 | 13:00
8 | BSRM | 194 | 04:00 | 74 | KSRM | 28 | 04:00 | 140 | Rajshahi-230 | 39 | 21:00
9 | Bagerhat | 59 | 18:00 | 75 | Kabirpur | 212 | 18:00 | 141 | Ramganj | 88 | 18:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 51 | 18:00 | 142 | Rampur | 26 | 18:00
11 | Bakulia | 65 | 18:00 | 77 | Kallyanpur | 75 | 13:00 | 143 | Rangamati | 13 | 18:00
12 | Banani | 34 | 13:00 | 78 | Kalurghat | 26 | 14:00 | 144 | Rangpur | 108 | 19:00
13 | Bangabhaban | 3 | 09:00 | 79 | Kamrangirchar | 54.3 | 12:00 | 145 | Ruppur | 3 | 14:00
14 | Barapukuria | 48 | 19:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 14 | 00:00
15 | Barguna | 14 | 20:00 | 81 | Kazla | 98 | 13:00 | 147 | Saidpur | 91 | 18:30
16 | Barishal | 72 | 13:00 | 82 | Keranigonj | 58 | 13:00 | 148 | Satkhira | 88 | 18:30
17 | Barishal-230 | 70 | 18:00 | 83 | Khagrachori | 24 | 18:00 | 149 | Satmasjid | 80 | 13:00
18 | Baroaulia | 63 | 10:00 | 84 | Khulna | 59 | 18:30 | 150 | Savar | 148 | 18:30
19 | Baroirhat | 55 | 18:00 | 85 | Khulshi | 145 | 15:00 | 151 | SevenRings | 7.78 | 20:00
20 | Bashundhara | 116 | 18:30 | 86 | Kishoreganj | 124 | 18:30 | 152 | ShahCement | 25 | 04:00
21 | BashundharaCement | 7 | 11:00 | 87 | Kodda | 260 | 18:30 | 153 | Shahjadpur | 51 | 18:30
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 28 | 18:00 | 154 | Shahjibazar | 84 | 18:00
23 | Benapole | 58 | 08:00 | 89 | Kurigram | 48 | 18:30 | 155 | Shahmirpur | 47 | 23:00
24 | Bhaluka | 100 | 08:00 | 90 | Kushtia | 102 | 18:30 | 156 | Shariatpur | 52 | 20:00
25 | Bhandaria | 33.5 | 20:00 | 91 | Lalbag | 53 | 17:00 | 157 | Sherpur | 114 | 08:00
26 | Bhangura | 22 | 18:30 | 92 | Lalmonirhat | 41 | 19:00 | 158 | Shikalbaha | 19 | 12:00
27 | Bheramara(GK) | 51 | 13:00 | 93 | MI_Cement | 17.7 | 11:00 | 159 | Shitalakhya | 61.3 | 12:00
28 | Bhulta | 231 | 11:00 | 94 | Madanganj | 22 | 18:00 | 160 | Sholosohor | 31 | 15:00
29 | Bog-Sherpur | 56 | 18:30 | 95 | Madaripur | 64 | 20:00 | 161 | Shyampur | 160 | 13:00
30 | Bogura | 100 | 18:30 | 96 | Madartek | 49.37 | 14:00 | 162 | Siddhirganj | 109 | 12:00
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 37 | 18:00 | 163 | Sirajganj | 66 | 19:00
32 | Brahmanbaria | 105 | 18:30 | 98 | Magura | 44 | 18:30 | 164 | Sonargaon | 77 | 12:00
33 | Cantonment | 78 | 13:00 | 99 | Mahasthangarh | 60 | 18:30 | 165 | Sreemongol | 50 | 22:00
34 | Chandpur | 42 | 20:00 | 100 | Manikganj | 102 | 19:00 | 166 | Sreepur | 81 | 12:00
35 | Chandraghona | 26 | 18:00 | 101 | Maniknagar | 38 | 13:00 | 167 | Srinagar | 30.29 | 13:00
36 | Chapai | 57 | 13:00 | 102 | Matarbari | 38 | 19:00 | 168 | Sunamganj | 40 | 18:00
37 | Charsaidpur | 40 | 11:00 | 103 | Matuail | 48 | 10:00 | 169 | Sylhet | 30 | 18:00
38 | Chauddagram | 46 | 13:00 | 104 | Millgate | 62 | 15:00 | 170 | Sylhet-132 | 77 | 18:00
39 | Chhatak | 21 | 18:00 | 105 | Mirpur | 92 | 18:30 | 171 | TK | 21.5 | 18:00
40 | Chowmuhani | 137 | 18:30 | 106 | Mirsorai | 8 | 18:00 | 172 | Tangail | 175 | 18:30
41 | Chuadanga | 81 | 13:00 | 107 | Mirzapur | 33 | 19:30 | 173 | Thakurgaon | 74 | 18:30
42 | Coxsbazar | 95 | 23:00 | 108 | Mithapukur | 40 | 18:00 | 174 | Tongi | 101 | 12:00
43 | Cumilla(N) | 115 | 13:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 23 | 19:00
44 | Cumilla(S) | 127 | 14:00 | 110 | Mogbazar | 92.7 | 14:00 | 176 | Ullon | 36 | 14:00
45 | Daudkandi | 104 | 19:00 | 111 | Mongla | 38 | 14:00 | 177 | Uttara | 58 | 13:00
46 | Dhaka | 28 | 13:00 | 112 | Motijheel | 26 | 13:00 | 178 | UttaraNew | 32 | 13:00
47 | Dhamrai | 102 | 11:00 | 113 | Muktagacha | 24 | 13:00 | 179 | Zigatola | 54 | 13:00
48 | Dhanmondi | 91 | 13:00 | 114 | Munshiganj | 66 | 13:00
49 | Dohazari | 72 | 19:00 | 115 | Mymensingh | 170 | 14:00
50 | Faridpur | 106 | 18:30 | 116 | Naogaon | 87 | 13:00
51 | Fatullah | 79 | 12:00 | 117 | Narail | 41 | 18:30
52 | Fenchuganj | 26 | 18:30 | 118 | Narinda | 56 | 13:00
53 | Feni | 63 | 18:30 | 119 | Narshingdi | 152 | 19:00
54 | GPH | 81 | 05:00 | 120 | Natore | 109 | 18:30
55 | Ghatail | 34 | 08:00 | 121 | Nawabganj | 37.2 | 13:00
56 | Ghorashal | 8 | 18:00 | 122 | Netrakona | 135 | 09:00
57 | Ghorashal-230 | 62 | 10:00 | 123 | New | 68 | 12:00
58 | Goalpara | 26 | 13:00 | 124 | Niamatpur | 84 | 11:00
59 | Gollamari | 62 | 13:00 | 125 | Noapara | 34 | 18:30
60 | Gopalganj | 88 | 18:30 | 126 | PHP | 8 | 10:00
61 | Gulshan | 58 | 13:00 | 127 | Pabna | 84 | 18:00
62 | Halishahar | 48 | 15:00 | 128 | Palashbari | 73 | 18:30
63 | HaripurSBU | 167 | 10:00 | 129 | Panchagarh | 41 | 18:30
64 | Hasnabad | 61 | 12:00 | 130 | Patuakhali | 54 | 21:00
65 | Hathazari | 49 | 18:30 | 131 | Payra | 14 | 12:00
66 | Ishurdi | 59 | 18:30 | 132 | Postogola | 41 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 8363.5 | 0 |  | 8363.5
1:00 | 8052.5 | 0 |  | 8052.5
2:00 | 7410.5 | 0 |  | 7410.5
3:00 | 7219.5 | 0 |  | 7219.5
4:00 | 6991.5 | 0 |  | 6991.5
5:00 | 6992.5 | 0 |  | 6992.5
6:00 | 7443.5 | 0 |  | 7443.5
7:00 | 8185.72 | 0 |  | 8185.72
8:00 | 8893.6 | 0 |  | 8893.6
9:00 | 9126.1 | 0 |  | 9126.1
10:00 | 9146.89 | 0 |  | 9146.89
11:00 | 9096.12 | 0 |  | 9096.12
12:00 | 9771.31 | 0 |  | 9771.31
13:00 | 10144.88 | 0 |  | 10144.88
14:00 | 9685.95 | 0 |  | 9685.95
15:00 | 9182.44 | 0 |  | 9182.44
16:00 | 8914.5 | 0 |  | 8914.5
17:00 | 9397.7 | 0 |  | 9397.7
18:00 | 10506.83 | 0 |  | 10506.83
19:00 | 10777.5 | 22 |  | 10800.5
19:30 | 10655.71 | 63 |  | 10721.71
20:00 | 10568.76 | 51 |  | 10621.76
21:00 | 10424.16 | 0 |  | 10424.16
22:00 | 9971.02 | 0 |  | 9971.02
23:00 | 9515.28 | 0 |  | 9515.28
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4770 | 3593.5 | 8363.5 | DAILY LOAD CURVE
00:30 | 4717.5 | 3490.5 | 8208
01:00 | 4665 | 3387.5 | 8052.5 | 18-01-2025
01:30 | 4488.5 | 3243 | 7731.5
02:00 | 4312 | 3098.5 | 7410.5
02:30 | 4295 | 3020 | 7315
03:00 | 4278 | 2941.5 | 7219.5
03:30 | 4189.5 | 2916 | 7105.5
04:00 | 4101 | 2890.5 | 6991.5
04:30 | 4101 | 2891 | 6992
05:00 | 4101 | 2891.5 | 6992.5
05:30 | 4254.5 | 2963.5 | 7218
06:00 | 4408 | 3035.5 | 7443.5
06:30 | 4674.3 | 3140.31 | 7814.61
07:00 | 4940.6 | 3245.12 | 8185.72
07:30 | 5095.865 | 3443.795 | 8539.66
08:00 | 5251.13 | 3642.47 | 8893.6
08:30 | 5291.95 | 3717.9 | 9009.85
09:00 | 5332.77 | 3793.33 | 9126.1
09:30 | 5229.08 | 3907.415 | 9136.495
10:00 | 5125.39 | 4021.5 | 9146.89
10:30 | 5158.25 | 3963.255 | 9121.505
11:00 | 5191.11 | 3905.01 | 9096.12
11:30 | 5364.49 | 4069.225 | 9433.715
12:00 | 5537.87 | 4233.44 | 9771.31
12:30 | 5532.72 | 4425.375 | 9958.095
13:00 | 5527.57 | 4617.31 | 10144.88
13:30 | 5425.645 | 4489.77 | 9915.415
14:00 | 5323.72 | 4362.23 | 9685.95
14:30 | 5262.625 | 4171.57 | 9434.195
15:00 | 5201.53 | 3980.91 | 9182.44
15:30 | 5210.18 | 3838.29 | 9048.47
16:00 | 5218.83 | 3695.67 | 8914.5
16:30 | 5430.71 | 3725.39 | 9156.1
17:00 | 5642.59 | 3755.11 | 9397.7
17:30 | 5943.045 | 4009.22 | 9952.265
18:00 | 6243.5 | 4263.33 | 10506.83
18:30 | 6155 | 4487.165 | 10642.165
19:00 | 6066.5 | 4711 | 10777.5
19:30 | 6107.5 | 4548.21 | 10655.71
20:00 | 6014.5 | 4554.26 | 10568.76
20:30 | 5959 | 4537.46 | 10496.46 |  | Executive Engineer
21:00 | 5903.5 | 4520.66 | 10424.16 |  | Network Operation Division
21:30 | 5821 | 4376.59 | 10197.59
22:00 | 5738.5 | 4232.52 | 9971.02
22:30 | 5612.5 | 4130.65 | 9743.15
23:00 | 5486.5 | 4028.78 | 9515.28

## En-Curve
QF-LDC-12
Date | 18-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3077 | 1647.5 | 726 | 0 | 48 | 416 | 30 | 2400 | 0 | 0 | 18 | 0 | 0 | 1 | 0 | DAILY ENERGY CURVE
00:30 | 3092.5 | 1638 | 726 | 0 | 46 | 417.5 | 30 | 2246.5 | 0 | 0 | 9 | 0 | 0 | 2.5 | 0 | 18-01-2025
01:00 | 3108 | 1628.5 | 726 | 0 | 44 | 419 | 30 | 2093 | 0 | 0 | 0 | 0 | 0 | 4 | 0
01:30 | 3012.5 | 1452.5 | 726 | 0 | 43 | 417.5 | 30 | 2045.5 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0 |  | Total Energy | 220.273 |  | MKWHr
02:00 | 2917 | 1276.5 | 726 | 0 | 42 | 416 | 30 | 1998 | 0 | 0 | 0 | 0 | 0 | 5 | 0 |  | Energy not Served | 0.073 |  | MKWHr
02:30 | 2864.5 | 1282 | 680 | 0 | 41 | 416 | 30 | 1994 | 0 | 0 | 0 | 0 | 0 | 7.5 | 0 |  | Energy Requirement | 220.346 |  | MKWHr
03:00 | 2812 | 1287.5 | 634 | 0 | 40 | 416 | 30 | 1990 | 0 | 0 | 0 | 0 | 0 | 10 | 0
03:30 | 2708.5 | 1279.5 | 634 | 0 | 40 | 416.5 | 30 | 1987 | 0 | 0 | 0 | 0 | 0 | 10 | 0
04:00 | 2605 | 1271.5 | 634 | 0 | 40 | 417 | 30 | 1984 | 0 | 0 | 0 | 0 | 0 | 10 | 0
04:30 | 2600 | 1276.5 | 634 | 0 | 39 | 417 | 30 | 1986.5 | 0 | 0 | 0 | 0 | 0 | 9 | 0
05:00 | 2595 | 1281.5 | 634 | 0 | 38 | 417 | 30 | 1989 | 0 | 0 | 0 | 0 | 0 | 8 | 0
05:30 | 2702.5 | 1393 | 634 | 0 | 39 | 417.5 | 30 | 1994 | 0 | 0 | 0 | 0 | 0 | 8 | 0
06:00 | 2810 | 1504.5 | 634 | 0 | 40 | 418 | 30 | 1999 | 0 | 0 | 0 | 0 | 0 | 8 | 0
06:30 | 2909.5 | 1569 | 680.5 | 0 | 40 | 416.5 | 30 | 2131 | 5.61 | 3 | 21 | 0 | 0 | 8.5 | 0
07:00 | 3009 | 1633.5 | 727 | 0 | 40 | 415 | 30 | 2263 | 11.22 | 6 | 42 | 0 | 0 | 9 | 0
07:30 | 3021 | 1628.75 | 774.5 | 0 | 39 | 414 | 30 | 2479 | 57.41 | 32.5 | 53.5 | 0 | 0 | 10 | 0
08:00 | 3033 | 1624 | 822 | 0 | 38 | 413 | 30 | 2695 | 103.6 | 59 | 65 | 0 | 0 | 11 | 0
08:30 | 3008 | 1591.75 | 822 | 0 | 43 | 413.5 | 30 | 2765 | 186.6 | 67.5 | 73 | 0 | 0 | 9.5 | 0
09:00 | 2983 | 1559.5 | 822 | 0 | 48 | 414 | 30 | 2835 | 269.6 | 76 | 81 | 0 | 0 | 8 | 0
09:30 | 3015 | 1472.5 | 869.5 | 0 | 51 | 414.5 | 30 | 2753 | 356.995 | 76 | 90.5 | 0 | 0 | 7.5 | 0
10:00 | 3047 | 1385.5 | 917 | 0 | 54 | 415 | 30 | 2671 | 444.39 | 76 | 100 | 0 | 0 | 7 | 0
10:30 | 2955 | 1421 | 917.5 | 0 | 53 | 415 | 30 | 2654 | 494.005 | 76 | 101 | 0 | 0 | 5 | 0
11:00 | 2863 | 1456.5 | 918 | 0 | 52 | 415 | 30 | 2637 | 543.62 | 76 | 102 | 0 | 0 | 3 | 0
11:30 | 2921.5 | 1525.75 | 917.5 | 0 | 55 | 463 | 30 | 2775 | 562.965 | 76 | 102 | 0 | 0 | 5 | 0
12:00 | 2980 | 1595 | 917 | 0 | 58 | 511 | 30 | 2913 | 582.31 | 76 | 102 | 0 | 0 | 7 | 0
12:30 | 3129 | 1587 | 917 | 0 | 53 | 540.5 | 30 | 2948.5 | 569.595 | 76 | 102 | 0 | 0 | 5.5 | 0
13:00 | 3278 | 1579 | 917 | 0 | 48 | 570 | 30 | 2984 | 556.88 | 76 | 102 | 0 | 0 | 4 | 0
13:30 | 3185 | 1561.75 | 917.5 | 0 | 54 | 566.775 | 30 | 2909.5 | 518.89 | 76 | 94 | 0 | 0 | 2 | 0
14:00 | 3092 | 1544.5 | 918 | 0 | 60 | 563.55 | 30 | 2835 | 480.9 | 76 | 86 | 0 | 0 | 0 | 0
14:30 | 3045.5 | 1552 | 917.5 | 0 | 58 | 515.665 | 30 | 2745 | 409.53 | 76 | 84.5 | 0 | 0 | 0.5 | 0
15:00 | 2999 | 1559.5 | 917 | 0 | 56 | 467.78 | 30 | 2655 | 338.16 | 76 | 83 | 0 | 0 | 1 | 0
15:30 | 2941.5 | 1541 | 917 | 0 | 51 | 465.045 | 30 | 2666.5 | 259.925 | 82 | 90 | 0 | 0 | 4.5 | 0
16:00 | 2884 | 1522.5 | 917 | 0 | 46 | 462.31 | 30 | 2678 | 181.69 | 88 | 97 | 0 | 0 | 8 | 0
16:30 | 2895.5 | 1551 | 917 | 0 | 54 | 503.295 | 30 | 2864.5 | 109.805 | 106.5 | 115.5 | 0 | 0 | 9 | 0
17:00 | 2907 | 1579.5 | 917 | 0 | 62 | 544.28 | 30 | 3051 | 37.92 | 125 | 134 | 0 | 0 | 10 | 0
17:30 | 2967 | 1698.25 | 917 | 0 | 59 | 652.555 | 30 | 3258.5 | 18.96 | 125 | 212.5 | 0 | 0 | 13.5 | 0
18:00 | 3027 | 1817 | 917 | 0 | 56 | 760.83 | 30 | 3466 | 0 | 125 | 291 | 0 | 0 | 17 | 0
18:30 | 3089 | 1787.5 | 917 | 0 | 55 | 757.165 | 30 | 3613.5 | 0 | 125.5 | 244.5 | 0 | 0 | 23 | 11
19:00 | 3151 | 1758 | 917 | 0 | 54 | 753.5 | 30 | 3761 | 0 | 126 | 198 | 0 | 0 | 29 | 22
19:30 | 3251 | 1831 | 917 | 0 | 54 | 657.71 | 30 | 3541 | 0 | 126 | 212 | 0 | 0 | 36 | 63
20:00 | 3228 | 1804 | 917 | 0 | 58 | 659.76 | 30 | 3544 | 0 | 126 | 168 | 0 | 0 | 34 | 51
20:30 | 3230 | 1801.5 | 917 | 0 | 57 | 663.46 | 30 | 3508.5 | 0 | 100 | 164.5 | 0 | 0 | 24.5 | 25.5
21:00 | 3232 | 1799 | 917 | 0 | 56 | 667.16 | 30 | 3473 | 0 | 74 | 161 | 0 | 0 | 15 | 0
21:30 | 3206.5 | 1797.5 | 917 | 0 | 55 | 620.09 | 30 | 3343 | 0 | 62 | 155 | 0 | 0 | 11.5 | 0
22:00 | 3181 | 1796 | 917 | 0 | 54 | 573.02 | 30 | 3213 | 0 | 50 | 149 | 0 | 0 | 8 | 0
22:30 | 3172.5 | 1770 | 917 | 0 | 56 | 546.65 | 30 | 3075 | 0 | 42 | 123.5 | 0 | 0 | 10.5 | 0
23:00 | 3164 | 1744 | 917 | 0 | 58 | 520.28 | 30 | 2937 | 0 | 34 | 98 | 0 | 0 | 13 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 18-01-2025 | 0 | [6 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 419 | 03:00 | 395 | 18:30 | Kaliakoir | 381 | 03:00 | 363 | 18:30 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 410 | 5:00 | 385 | 12:00 | Madunaghat | 413 | 04:00 | 397 | 19:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 412 | 01:00 | 387 | 12:00 | Meghnaghat | 414 | 01:00 | 392 | 18:30
| Bibiana | 401 | 01:00 | 386 | 18:30 | Payra | 421 | 05:00 | 407 | 19:00
| BIPTC | 407 | 00:00 | 387 | 11:00 | Rahanpur | 417 | 03:00 | 400 | 18:00
| Bogura | 416 | 02:00 | 395 | 18:00 | Rampal | 418 | 03:00 | 390 | 18:30
| Gopalganj | 420 | 02:00 | 398 | 18:30 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 239 | 03:00 | 225 | 12:00 | Haripur | 238 | 07:00 | 227 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 234 | 05:00 | 225 | 18:00 | Hasnabad | 237 | 00:00 | 224 | 12:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 238 | 04:00 | 223 | 12:00 | Hathazari | 235 | 05:00 | 229 | 13:00
| Ashuganj | 241 | 01:00 | 228 | 13:00 | Ishurdi | 245 | 01:00 | 24 | 02:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 8:00 | 232 | 12:00 | Jhenaidah | 242 | 01:00 | 225 | 13:00
| Baghabari | 244 | 03:00 | 232 | 13:00 | Kaliakoir | 239 | 03:00 | 226 | 18:00 | 230 kV MAX | 250 |  | 250 | 218
| Barapukuria | 227 | 01:00 | 218 | 18:00 | Keranigonj | 239 | 01:00 | 224 | 12:00 | 230 kV MIN | 24 |  | 245 | 24 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 225 | 12:00 | 220 | 19:00 | Khulna(S) | 245 | 04:00 | 226 | 18:30 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 247 | 03:00 | 236 | 18:30 | Madunaghat | 235 | 01:00 | 227 | 19:30 | 132 kV MAX | 143 |  | 143 | 114 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 243 | 01:00 | 230 | 13:00 | Madunaghat-400 | 236 | 04:00 | 227 | 13:00 | 132 kV MIN | 110 |  | 143 | 110 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 241 | 03:00 | 226 | 12:00 | Maniknagar | 239 | 01:00 | 225 | 12:00 | [35 empty] | 6:00
| Bibiana | 232 | 06:00 | 223 | 13:00 | Meghnaghat | 245 | 07:00 | 232 | 13:00 |  | 400 | [33 empty] | 392
| BIPTC | 244 | 01:00 | 230 | 13:00 | Meghnaghat-400 | 242 | 04:00 | 227 | 13:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 240 | 03:00 | 229 | 18:00 | Mirsorai | 235 | 04:00 | 224 | 18:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 241 | 04:00 | 229 | 18:00 | Rajshahi | 244 | 01:00 | 228 | 13:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 250 | 02:00 | 244 | 13:00 | Rampal | 241 | 03:00 | 225 | 13:00 |  | 132 |  |  | Ash 400-299274
| BSRM | 235 | 01:00 | 224 | 18:30 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 234 | 00:00 | 223 | 13:00 | Rampura | 241 | 01:00 | 226 | 13:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 249 | 03:00 | 236 | 18:00 | Shikalbaha | 234 | 04:00 | 225 | 16:00 |  | kaptai by call 399528
| Fenchuganj | 232 | 07:00 | 225 | 18:30 | Shyampur | 238 | 03:00 | 225 | 12:00
| Ghorashal | 242 | 00:00 | 234 | 15:00 | Siddhirganj | 240 | 00:00 | 230 | 15:00
| Ghorashal-230 | 239 | 01:00 | 224 | 13:00 | Sirajgonj | 248 | 02:00 | 239 | 18:00
| Gopalganj | 249 | 04:00 | 236 | 18:30 | Sreepur | 240 | 01:00 | 226 | 18:30
| GPH | 235 | 06:00 | 225 | 13:00 | Tongi | 236 | 08:00 | 225 | 13:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 139 | 03:00 | 129 | 12:00 | Kurigram | 133 | 04:00 | 121 | 18:00 |  | Gopalganj-230 | 599470
| Agargaon | 139 | 01:00 | 130 | 13:00 | Kushtia | 141 | 00:00 | 134 | 13:00
| Agrabad | 134 | 03:00 | 128 | 13:00 | Lalbag | 140 | 01:00 | 129 | 18:00
| AKS | 131 | 05:00 | 127 | 13:00 | Lalmonirhat | 129 | 05:00 | 120 | 18:00
| Aminbazar | 137 | 00:00 | 128 | 12:00 | Madanganj | 134 | 00:00 | 128 | 14:00
| Amnura | 140 | 00:00 | 132 | 13:00 | Madaripur | 137 | 05:00 | 131 | 12:00
| Ashuganj | 142 | 01:00 | 135 | 12:00 | Madartek | 139 | 06:00 | 129 | 13:00
| Bagerhat | 140 | 01:00 | 125 | 13:00 | Madunaghat | 136 | 04:00 | 130 | 12:00
| Bajitpur | 136 | 03:00 | 128 | 18:00 | Magura | 141 | 03:00 | 129 | 13:00
| Bakulia | 135 | 04:00 | 129 | 13:00 | Mahasthangarh | 137 | 01:00 | 129 | 18:00
| Banani | 139 | 05:00 | 129 | 13:00 | Manikganj | 133 | 04:00 | 126 | 15:00
| Bangabhaban | 138 | 04:00 | 128 | 12:00 | Maniknagar | 137 | 04:00 | 129 | 17:00
| Barapukuria | 137 | 01:00 | 128 | 18:30 | Matarbari | 126 | 02:00 | 119 | 18:00
| Barguna | 139 | 04:00 | 133 | 13:00 | Matuail | 137.5 | 06:00 | 130 | 12:00
| Barishal | 137 | 04:00 | 131 | 13:00 | Millgate | 141 | 02:00 | 129 | 13:00
| Barishal-230 | 138 | 03:00 | 132 | 13:00 | Mirpur | 138 | 03:00 | 128 | 12:00
| Baroaulia | 134 | 00:00 | 129 | 17:00 | Mirzapur | 134 | 09:00 | 126 | 16:00
| Baroirhat | 132 | 09:00 | 123 | 19:30 | Mithapukur | 136 | 03:00 | 125 | 18:00
| Bashundhara | 140 | 04:00 | 128 | 13:00 | MI_Cement | 139 | 04:00 | 130 | 12:00
| BashundharaCement | 134 | 00:00 | 128 | 14:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 135 | 03:00 | 131 | 18:00 | Mogbazar | 141 | 06:00 | 129 | 13:00
| Benapole | 140 | 01:00 | 125 | 13:00 | Mongla | 138 | 03:00 | 125 | 13:00
| Bhaluka | 130 | 00:00 | 117 | 18:00 | Motijheel | 138 | 04:00 | 128 | 12:00
| Bhandaria | 135 | 03:00 | 127 | 18:00 | Muktagacha | 128 | 22:00 | 118 | 13:00
| Bhangura | 139 | 01:00 | 134 | 13:00 | Munshiganj | 138 | 03:00 | 129 | 12:00
| Bheramara | 141 | 01:00 | 135 | 13:00 | Mymensingh | 128 | 00:00 | 117 | 18:00
| Bheramara(GK) | 141 | 00:00 | 136 | 12:00 | Naogaon | 137 | 04:00 | 128 | 18:00
| Bhulta | 132 | 09:00 | 120 | 12:00 | Narail | 141 | 01:00 | 130 | 13:00
| Bog-Sherpur | 138 | 01:00 | 130 | 18:00 | Narinda | 137 | 4:00 | 129 | 17:00
| Bogura | 138 | 02:00 | 131 | 18:00 | Narshingdi | 132 | 00:00 | 124 | 19:00
| Bogura-230 | 139 | 03:00 | 131 | 18:00 | Natore | 140 | 02:00 | 132 | 18:30
| Brahmanbaria | 136 | 06:00 | 128 | 18:00 | Nawabganj | 140 | 03:00 | 129 | 18:00
| Cantonment | 139 | 01:00 | 130 | 12:00 | Netrakona | 129 | 00:00 | 110 | 18:00
| Chandpur | 130 | 05:00 | 120 | 13:00 | New | 141 | 03:00 | 130 | 18:00
| Chandraghona | 136 | 02:00 | 130 | 18:00 | Niamatpur | 139 | 00:00 | 134 | 11:00
| Chapai | 140 | 05:00 | 134 | 12:00 | Noapara | 141 | 03:00 | 128 | 13:00
| Charsaidpur | 139 | 03:00 | 131 | 19:30 | Pabna | 142 | 01:00 | 133 | 18:00
| Chauddagram | 132 | 00:00 | 122 | 13:00 | Palashbari | 134 | 04:00 | 123 | 18:00
| Chhatak | 134 | 00:00 | 130 | 18:00 | Panchagarh | 137 | 04:00 | 124 | 18:00
| Chowmuhani | 128 | 02:00 | 117 | 13:00 | Patuakhali | 137 | 02:00 | 133 | 13:00
| Chuadanga | 141 | 01:00 | 127 | 13:00 | Payra | 139 | 15:00 | 134 | 18:30
| Coxsbazar | 126 | 05:00 | 121 | 13:00 | PHP | 132 | 02:00 | 122 | 13:00
| Cumilla(N) | 136 | 00:00 | 127 | 13:00 | Postogola | 142 | 03:00 | 132 | 12:00
| Cumilla(S) | 136 | 03:00 | 124 | 12:00 | Purbachal | 139 | 02:00 | 129 | 13:00
| Daudkandi | 136 | 01:00 | 127 | 12:00 | Purbasadipur | 133 | 03:00 | 121 | 18:30
| Dhaka | 139 | 01:00 | 129 | 13:00 | Rahanpur | 141 | 00:00 | 135 | 18:00
| Dhamrai | 137 | 06:00 | 128 | 18:00 | Rahanpur-400 | 142 | 03:00 | 136 | 18:00
| Dhanmondi | 140 | 05:00 | 130 | 12:00 | Rahim | 137 | 05:00 | 128 | 13:00
| Dohazari | 132 | 03:00 | 126 | 18:00 | Rajbari | 138 | 03:00 | 128 | 18:30
| Faridpur | 138 | 03:00 | 131 | 13:00 | Rajendrapur | 137 | 04:00 | 126 | 13:00
| Fatullah | 140 | 04:00 | 131 | 12:00 | Rajshahi | 141 | 01:00 | 132 | 13:00
| Fenchuganj | 139 | 00:00 | 135 | 18:00 | Rajshahi-230 | 141 | 01:00 | 131 | 13:00
| Feni | 132 | 05:00 | 124 | 13:00 | Ramganj | 128 | 01:00 | 118 | 13:00
| Ghatail | 129 | 05:00 | 114 | 13:00 | Rampur | 135 | 04:00 | 128 | 15:00
| Ghorashal | 142 | 00:00 | 134 | 13:00 | Rampura | 140 | 06:00 | 129 | 13:00
| Goalpara | 143 | 03:00 | 130 | 13:00 | Rangamati | 136 | 04:00 | 129 | 18:00
| Gollamari | 141 | 02:00 | 131 | 13:00 | Rangpur | 133 | 07:00 | 121 | 18:30
| Gopalganj | 140 | 04:00 | 130 | 18:00 | Ruppur | 142 | 04:00 | 136 | 12:00
| Gopalganj-400 | 139 | 01:00 | 132 | 13:00 | Saidpur | 136 | 06:00 | 122 | 18:00
| Gulshan | 138 | 02:00 | 129 | 12:00 | Satkhira | 140 | 05:00 | 128 | 13:00
| Halishahar | 133 | 00:00 | 130 | 07:00 | Satmasjid | 139 | 04:00 | 128 | 13:00
| Haripur | 136 | 00:00 | 129 | 12:00 | Savar | 136 | 00:00 | 127 | 13:00
| HaripurSBU | 136 | 00:00 | 129 | 12:00 | SevenRings | 143 | 04:00 | 133 | 13:00
| Hasnabad | 139 | 00:00 | 132 | 12:00 | ShahCement | 139 | 03:00 | 129 | 12:00
| Hathazari | 136 | 05:00 | 133 | 14:00 | Shahjadpur | 142 | 00:00 | 138 | 10:00
| Ishurdi | 143 | 01:00 | 136 | 18:00 | Shahjibazar | 139 | 00:00 | 130 | 18:00
| Jaldhaka | 133 | 01:00 | 119 | 18:00 | Shahmirpur | 134 | 01:00 | 129 | 13:00
| Jamalpur | 126 | 10:00 | 115 | 18:00 | Shariatpur | 139 | 02:00 | 130 | 19:00
| Jashore | 138 | 00:00 | 126 | 13:00 | Sherpur | 124 | 22:00 | 110 | 18:00
| Jhenaidah | 141 | 01:00 | 131 | 13:00 | Shikalbaha | 124 | 01:00 | 118 | 13:00
| Jhenaidah-230 | 142 | 01:00 | 131 | 13:00 | Shikalbaha-230 | 136 | 04:00 | 130 | 11:00
| Joydebpur | 137 | 00:00 | 131 | 12:00 | Shitalakhya | 139 | 04:00 | 130 | 12:00
| Joypurhat | 138 | 04:00 | 128 | 18:00 | Sholosohor | 135 | 01:00 | 129 | 18:00
| Juldah | 133 | 03:00 | 129 | 16:00 | Shyampur | 138 | 07:00 | 130 | 12:00
| Kabirpur | 136 | 02:00 | 127 | 18:00 | Shyampur-230 | 140 | 03:00 | 130 | 12:00
| Kachua | 132 | 01:00 | 121 | 13:00 | Siddhirganj | 138 | 01:00 | 130 | 12:00
| Kaliakoir | 140 | 03:00 | 130 | 16:00 | Sirajganj | 140 | 03:00 | 132 | 13:00
| Kallyanpur | 137 | 04:00 | 128 | 13:00 | Sonargaon | 134 | 00:00 | 127 | 12:00
| Kalurghat | 135 | 02:00 | 130 | 14:00 | Sreemongol | 138 | 00:00 | 132 | 12:00
| Kamrangirchar | 139 | 06:00 | 128 | 12:00 | Sreepur | 131 | 04:00 | 121 | 18:00
| Kaptai | N/A | N/A | N/A | N/A | Srinagar | 139 | 01:00 | 129 | 18:00
| Kazla | 138 | 04:00 | 126 | 13:00 | SSM | 139 | 06:00 | 132 | 12:00
| Keranigonj | 140 | 01:00 | 129 | 18:30 | Sunamganj | 133 | 00:00 | 130 | 18:00
| Khagrachori | 135 | 02:00 | 129 | 13:00 | Sylhet | 136 | 01:00 | 132 | 18:00
| Khulna | 140 | 05:00 | 128 | 13:00 | Sylhet-132 | 135 | 01:00 | 132 | 12:00
| Khulna(S) | 143 | 04:00 | 130 | 18:30 | Tangail | 129 | 05:00 | 122 | 19:00
| Khulshi | 133 | 01:00 | 127 | 13:00 | Thakurgaon | 135 | 03:00 | 119 | 18:30 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 131 | 00:00 | 121 | 18:00 | TK | 135 | 06:00 | 130 | 11:00 |  |  | Nos | Nos | Nos
| Kodda | 137 | 05:00 | 126 | 15:00 | Tongi | 140 | 04:00 | 133 | 12:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 135 | 01:00 | 130 | 14:00 | Ullahpara | 140 | 00:00 | 134 | 18:00
| Kulaura | 139 | 01:00 | 134 | 13:00 | Ullon | 138 | 02:00 | 128 | 12:00
| UttaraNew | 137 | 03:00 | 122 | 12:00 | Uttara | 136 | 03:00 | 125 | 12:00
| Zigatola | 138 | 00:00 | 124 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.