## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-01-2025 | during | 21-01-2025 | during | 21-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.5 | 174.5 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 373 | 340 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 255 | 262 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 250 | 335 | 335 | 250 | 300 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 16 | 16 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 22 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 26 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 32 | 70 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 18 | 36 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0.01 | 0.01 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0.01 | 0.01 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6257.05 | 5842.27 | 1448 | 1495 | 4607.69 | 4585.69 | 2635.93 | 2663.93
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 0 | 0 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 226 | 226 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 24 | 24 | 24 | 24 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 22 | 2 | 14 | 2 | 14 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.78 | 0 | 3.78 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 780 | 1205 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 1 | 2 | 3 | 18 | 3 | 18 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 993 | 997 | 1150 | 1150 | 1050 | 1050 | Machine Problem
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2056 | 2482 | 3964.5 | 3968.72 | 3864.5 | 3868.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 182 | 221 | 221 | 190 | 190 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 42 | 45 | 46.69 | 46.69 | 46.69 | 46.69 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 133 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 45 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 5 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 59 | 54 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 5 | 26 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 29 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 67 | 0 | 67 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 629 | 675 | 1675.72 | 1608.72 | 1527.89 | 1460.89
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 5 | 210 | 210 | 11 | 11 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 59 | 58 | 200 | 200 | 60 | 60 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 115 | 115 | 19 | 19 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 40.73 | 0 | 46.75 | 0 | 46.75 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 149.73 | 106 | 650.25 | 601.5 | 215.25 | 166.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 43 | 42 | 44 | 44 | 44 | 44 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 0 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 209 | 203 | 210 | 210 | 210 | 210 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 25 | 25 | 13 | 13 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 300 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 365 | 382 | 380 | 380 | 370 | 370 | FGMO not available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 392 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1587 | 1540 | 1621.5 | 1621.5 | 1579.01 | 1579.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 920 | 919 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 250 | 260 | 410 | 410 | 330 | 330 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78.41 | 0 | 75 | 0 | 75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1248.41 | 1179 | 3244 | 3169 | 1490.01 | 1415.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 76 | 0 | 330 | 330 | 330 | 330 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 135 | 135 | 135 | 135 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 860 | 1190 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 1500.6 | 1824 | 2507.12 | 2506.12 | 2464 | 2463
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 150 | 189 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 219 | 197 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 215 | 190 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 8.5 | 8.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.14 | 0 | 4.55 | 0 | 4.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 559 | 754 | 1347.54 | 1347.54 | 800 | 800 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 49.77 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 96 | 0 | 96 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1305.41 | 1338.5 | 2773.54 | 2622.99 | 2121 | 1970.45
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 72 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 200 | 200 | 210 | 210 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5 | 0 | 3.8 | 0 | 3.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 162 | 0 | 162 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 455 | 317 | 727.8 | 532 | 703.82 | 508.02
System Total |  |  |  |  | 29054.66 | 28387.248 | 10379.15 | 10956.5 | 21772.12 | 21216.24 | 16601.41 | 16095.53
Forecast Scenario (21-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9010 |  | 0 |  | 9010
|  |  |  | 1:00 | 8430 |  | 0 |  | 8430
|  |  |  | 2:00 | 8090 |  | 0 |  | 8090
|  |  |  | 3:00 | 7750 |  | 0 |  | 7750
|  |  |  | 4:00 | 7550 |  | 0 |  | 7550
|  |  |  | 5:00 | 7520 |  | 0 |  | 7520
|  |  |  | 6:00 | 7960 |  | 0 |  | 7960
|  |  |  | 7:00 | 8750 |  | 0 |  | 8750
|  |  |  | 8:00 | 9610 |  | 0 |  | 9610
|  |  |  | 9:00 | 10030 |  | 0 |  | 10030
|  |  |  | 10:00 | 9750 |  | 0 |  | 9750
|  |  |  | 11:00 | 9780 |  | 0 |  | 9780
|  |  |  | 12:00 | 10370 |  | 0 |  | 10370
|  |  |  | 13:00 | 10660 |  | 0 |  | 10660
|  |  |  | 14:00 | 10330 |  | 0 |  | 10330
|  |  |  | 15:00 | 10000 |  | 0 |  | 10000
|  |  |  | 16:00 | 9600 |  | 0 |  | 9600
|  |  |  | 17:00 | 9750 |  | 0 |  | 9750
|  |  |  | 18:00 | 10790 |  | 0 |  | 10790
|  |  |  | 18:30 | 10860 |  | 0 |  | 10860
|  |  |  | 19:00 | 10940 |  | 0 |  | 10940
|  |  |  | 19:30 | 10880 |  | 0 |  | 10880
|  |  |  | 20:00 | 10820 |  | 0 |  | 10820
|  |  |  | 21:00 | 10510 |  | 0 |  | 10510
|  |  |  | 22:00 | 10130 |  | 0 |  | 10130
|  |  |  | 23:00 | 9480 |  | 0 |  | 9480
Probable Maximum Temperature: |  |  | 25.40°C
Probable Maximum Demand at Day Peak: |  |  | 10370.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 10940.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10940.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 227.61 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (20-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 24.40°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 827.31
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 20.9411 | Peak Hour Flow: |  | 919.00 MW at 19:00 hrs.
Energy Flow from West to East |  | 7638790000 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 12.3342 | Peak Hour Flow: |  | 754.00 MW at 19:00 hrs.
Power Flow during Peak Demand |  | 492 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.2422 | Peak Hour Flow: |  | 54.00 MW at 19:00 hrs.
Maximum Power Flow |  | 760 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 34.5175 | Peak Hour Flow: |  | 1727.00 MW at 19:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-01-2025 | [28 empty] | Date: | 20-01-2025 | [28 empty] | Date: | 20-01-2025 | [28 empty] | Date: | 20-01-2025 | [28 empty] | Date: | 20-01-2025 | [19 empty] | Date: | 20-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [19 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 150.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 300 | 278 | 0 | 0 | 0 | 26 | 250 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 29 | 850 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 748 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 183 | 47 | 0 | 45 | 0 | 0 | 16 | 0 | 54 | 0 | 0 | 0 | 285 | 320 | 375 | 5 | 30 | 0 | 2 | 120 | 8 | 0 | 5 | 0 | 0 | 0 | 207 | 0 | 59 | 18 | 12 | 0 | 0 | 0 | 5213 | 917 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 179 | 0 | 190 | 0 | 0 | 0 | 0 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 180 | 0 | 0 | 900 | 0 | 3803.33 | 9016.33 | 92.75
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 278 | 0 | 0 | 0 | 26 | 250 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 30 | 750 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 645 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 29 | 183 | 47 | 0 | 45 | 0 | 0 | 16 | 0 | 46 | 0 | 0 | 0 | 280 | 320 | 375 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 0 | 0 | 0 | 207 | 0 | 18 | 8 | 13 | 0 | 0 | 0 | 4817 | 917 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 180 | 0 | 195 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 140 | 180 | 0 | 0 | 700 | 0 | 3621.65 | 8438.65 | 92.74
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 286 | 0 | 0 | 0 | 28 | 250 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 39 | 756 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 600 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 16 | 183 | 46 | 0 | 45 | 0 | 0 | 16 | 0 | 42 | 0 | 0 | 0 | 290 | 320 | 375 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 0 | 0 | 0 | 207 | 0 | 9 | 8 | 13 | 0 | 0 | 0 | 4769 | 730 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 177 | 0 | 185 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 140 | 180 | 0 | 0 | 600 | 0 | 3328.01 | 8097.01 | 92.74
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 272 | 0 | 0 | 0 | 28 | 250 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 39 | 758 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 602 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 5 | 183 | 46 | 0 | 45 | 0 | 0 | 16 | 0 | 44 | 0 | 0 | 0 | 285 | 320 | 322 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 4640 | 730 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 180 | 0 | 0 | 580 | 0 | 3115.16 | 7755.16 | 92.74
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 289 | 0 | 0 | 0 | 29 | 250 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 39 | 753 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 601 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 5 | 183 | 10 | 0 | 50 | 0 | 0 | 15 | 0 | 46 | 0 | 0 | 0 | 300 | 320 | 323 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 4601 | 730 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 180 | 0 | 0 | 500 | 0 | 2950.56 | 7551.56 | 92.74
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 277 | 0 | 0 | 0 | 29 | 250 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 41 | 752 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 601 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 5 | 183 | 10 | 0 | 50 | 0 | 0 | 11 | 0 | 40 | 0 | 0 | 0 | 285 | 320 | 323 | 5 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 4566 | 730 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 0 | 500 | 0 | 2956.01 | 7522.01 | 92.73
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 296 | 0 | 0 | 0 | 29 | 250 | 0 | 0 | 0 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 41 | 753 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 604 | 0 | 5 | 0 | 128 | 0 | 0 | 0 | 6 | 183 | 44 | 0 | 50 | 0 | 0 | 11 | 0 | 46 | 0 | 0 | 0 | 295 | 320 | 366 | 5 | 30 | 0 | 2 | 163 | 13 | 0 | 5 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 4798 | 730 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 137 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 0 | 500 | 0 | 3167.07 | 7965.07 | 92.73
07:00 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 308 | 0 | 0 | 0 | 29 | 250 | 0 | 0 | 1 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 34 | 853 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 675 | 1 | 17 | 0 | 184 | 0 | 0 | 0 | 18 | 191 | 40 | 0 | 50 | 0 | 0 | 11 | 0 | 46 | 0 | 2 | 0 | 295 | 320 | 367 | 35 | 30 | 0 | 2 | 163 | 13 | 0 | 82 | 0 | 0 | 0 | 206 | 0 | 19 | 56 | 18 | 0 | 0.72 | 5 | 5343.72 | 824 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0 | 0 | 417.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54 | 173 | 0 | 130 | 0 | 144 | 0 | 0 | 0 | 0.03 | 8.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.02 | 0 | 192 | 6 | 140 | 220 | 0 | 0 | 540 | 0 | 3406.88 | 8750.6 | 92.73
08:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 258 | 0 | 0 | 0 | 28 | 250 | 0 | 0 | 7 | 0 | 16.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 0 | 10 | 950 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 747 | 6 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 182 | 44 | 0 | 50 | 0 | 0 | 15 | 0 | 46 | 0 | 17 | 0 | 280 | 320 | 367 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 0 | 0 | 0 | 206 | 0 | 19 | 56 | 11 | 0 | 8.31 | 24 | 5595.81 | 919 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.11 | 0 | 0 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8.92 | 172 | 0 | 190 | 0 | 187 | 0 | 0 | 0 | 0.84 | 8.5 | 210 | 70 | 0 | 4 | 0 | 0 | 0 | 0.4 | 27 | 0.12 | 0 | 200 | 4 | 140 | 220 | 0 | 0 | 800 | 0 | 4020.89 | 9616.7 | 92.73
09:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 68 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 275 | 0 | 0 | 0 | 28 | 250 | 0 | 0 | 15 | 0 | 16.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 0 | 2 | 950 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 800 | 12 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 182 | 47 | 0 | 50 | 0 | 0 | 16 | 0 | 44 | 0 | 36 | 0 | 270 | 320 | 270 | 37 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 5 | 0 | 0.04 | 0 | 5503.54 | 919 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.42 | 0 | 0 | 557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 22.93 | 173 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 2 | 8.5 | 210 | 71 | 0 | 11 | 0 | 0 | 0 | 1 | 67 | 0.28 | 0 | 200 | 4 | 100 | 180 | 0 | 0 | 870 | 0 | 4056.13 | 9559.67 | 92.73
10:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 68 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 278 | 0 | 0 | 0 | 26 | 250 | 0 | 0 | 22 | 0 | 16.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 3 | 30 | 0 | 2 | 1012 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 800 | 17 | 51 | 0 | 148 | 0 | 0 | 0 | 29 | 182 | 44 | 0 | 45 | 0 | 0 | 17 | 0 | 50 | 0 | 52 | 0 | 275 | 320 | 304 | 43 | 30 | 0 | 2 | 120 | 0 | 0 | 50 | 0 | 0 | 0 | 207 | 0 | 19 | 56 | 5 | 1 | 31.83 | 16 | 5677.33 | 919 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.37 | 0 | 0 | 558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 36.05 | 140 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 3.05 | 8.5 | 210 | 71 | 0 | 19 | 0 | 0 | 0 | 1.3 | 105 | 0.45 | 0 | 150 | 4 | 100 | 180 | 0 | 0 | 840 | 0 | 4050.72 | 9728.05 | 92.73
11:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 14 | 0 | 56 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 306 | 0 | 0 | 0 | 26 | 250 | 0 | 0 | 27 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 30 | 0 | 2 | 1011 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 800 | 19 | 51 | 0 | 88 | 0 | 0 | 0 | 29 | 183 | 39 | 0 | 45 | 0 | 0 | 14 | 0 | 55 | 0 | 59 | 0 | 275 | 320 | 304 | 40 | 30 | 0 | 2 | 120 | 13 | 0 | 50 | 0 | 0 | 0 | 209 | 0 | 19 | 56 | 5 | 2 | 37.19 | 24 | 5668.19 | 919 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.16 | 0 | 0 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 45.25 | 140 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 3.67 | 8.5 | 210 | 71 | 0 | 23 | 0 | 0 | 0 | 1.9 | 134 | 0.55 | 0 | 150 | 4 | 100 | 180 | 0 | 0 | 810 | 0 | 4096.03 | 9764.22 | 92.72
12:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 18 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 255 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 30 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 30 | 0 | 2 | 993 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 780 | 20 | 51 | 0 | 133 | 0 | 0 | 0 | 29 | 183 | 42 | 1 | 40 | 5 | 5 | 17 | 0 | 59 | 0 | 64 | 0 | 285 | 392 | 365 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 0 | 0 | 0 | 209 | 0 | 19 | 59 | 5 | 2 | 40.73 | 24 | 5869.73 | 920 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.41 | 0 | 0 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 49.77 | 150 | 0 | 219 | 0 | 215 | 0 | 0 | 0 | 4.14 | 8.5 | 210 | 70 | 0 | 25 | 0 | 0 | 0 | 5 | 145 | 0.6 | 0 | 200 | 4 | 140 | 220 | 0 | 76 | 860 | 0 | 4509.42 | 10379.15 | 92.72
13:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 35 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 265 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 28 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 30 | 0 | 7 | 1012 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 730 | 19 | 51 | 0 | 173 | 0 | 0 | 0 | 29 | 183 | 44 | 16 | 40 | 17 | 27 | 14 | 0 | 58 | 0 | 58 | 0 | 300 | 320 | 383 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 0 | 0 | 0 | 206 | 0 | 19 | 59 | 5 | 2 | 37.55 | 24 | 5901.55 | 909 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.34 | 0 | 0 | 487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 47.62 | 181 | 0 | 215 | 0 | 211 | 0 | 0 | 0 | 4.03 | 8.5 | 210 | 69 | 0 | 25 | 0 | 0 | 0 | 5.1 | 138 | 0.56 | 0 | 250 | 4 | 140 | 220 | 0 | 96 | 960 | 0 | 4644.15 | 10545.7 | 92.72
14:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 36 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 248 | 0 | 0 | 0 | 23 | 250 | 0 | 0 | 24 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 30 | 0 | 3 | 957 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 730 | 17 | 51 | 0 | 177 | 0 | 0 | 0 | 29 | 182 | 46 | 16 | 40 | 17 | 27 | 14 | 0 | 66 | 0 | 52 | 0 | 295 | 320 | 384 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 83 | 0 | 0 | 0 | 206 | 0 | 19 | 59 | 5 | 2 | 32.19 | 23 | 5751.19 | 919 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.38 | 0 | 0 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 41.51 | 140 | 0 | 200 | 0 | 140 | 0 | 0 | 0 | 3.55 | 8.5 | 210 | 71 | 0 | 22 | 0 | 0 | 0 | 4.3 | 110 | 0.49 | 0 | 250 | 3 | 100 | 180 | 0 | 116 | 1100 | 0 | 4478.73 | 10229.92 | 92.72
15:00 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 36 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 300 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 18 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 0 | 2 | 955 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 730 | 13 | 51 | 0 | 177 | 0 | 0 | 0 | 29 | 182 | 46 | 0 | 40 | 17 | 27 | 17 | 0 | 58 | 0 | 35 | 0 | 290 | 320 | 384 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 83 | 0 | 0 | 0 | 207 | 0 | 19 | 58 | 5 | 1 | 23.14 | 22 | 5756.14 | 920 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.78 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 29.88 | 140 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 2.5 | 8.5 | 210 | 69 | 0 | 15 | 0 | 0 | 0 | 3.1 | 76 | 0.33 | 0 | 180 | 3 | 100 | 220 | 0 | 0 | 900 | 0 | 3996.09 | 9752.23 | 92.72
16:00 | 0 | 50 | 17 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 36 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 300 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 9 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 0 | 2 | 860 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 730 | 7 | 51 | 0 | 177 | 0 | 0 | 0 | 29 | 200 | 43 | 0 | 40 | 17 | 27 | 17 | 0 | 49 | 0 | 17 | 0 | 310 | 320 | 384 | 42 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 0 | 0 | 0 | 204 | 0 | 19 | 59 | 5 | 1 | 10.64 | 24 | 5640.64 | 919 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.11 | 0 | 0 | 519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 12.02 | 140 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 1.21 | 8.5 | 210 | 69 | 0 | 7 | 0 | 0 | 0 | 1.6 | 42 | 0.19 | 0 | 180 | 3 | 100 | 220 | 0 | 0 | 860 | 0 | 3934.63 | 9575.27 | 92.72
17:00 | 0 | 55 | 17 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 36 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 297 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 2 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 8 | 869 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 935 | 1 | 51 | 0 | 177 | 0 | 0 | 0 | 29 | 185 | 46 | 0 | 40 | 17 | 27 | 17 | 0 | 54 | 0 | 4 | 0 | 320 | 320 | 385 | 43 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 0 | 0 | 0 | 203 | 0 | 19 | 58 | 5 | 0 | 1.83 | 24 | 5843.83 | 920 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.52 | 0 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 2.86 | 140 | 0 | 160 | 0 | 140 | 0 | 0 | 0 | 0.26 | 8.5 | 210 | 69 | 0 | 2 | 0 | 0 | 0 | 0.3 | 9 | 0.05 | 0 | 250 | 4 | 100 | 220 | 0 | 0 | 860 | 0 | 3918.49 | 9762.32 | 92.71
18:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 36 | 0 | 70 | 48 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 309 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 0 | 0 | 16 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 12 | 1000 | 0 | 0 | 6 | 0 | 0 | 227 | 0 | 0 | 0 | 1107 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 200 | 45 | 14 | 45 | 17 | 44 | 17 | 0 | 58 | 0 | 0 | 0 | 310 | 320 | 384 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 25 | 0 | 0 | 204 | 0 | 19 | 58 | 5 | 0 | 0 | 24 | 6234 | 920 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 195 | 0 | 190 | 0 | 0 | 0 | 0 | 8.5 | 210 | 72 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 7 | 140 | 220 | 0 | 0 | 960 | 21 | 4351.5 | 10585.5 | 92.71
19:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 36 | 0 | 70 | 64 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 262 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 22 | 997 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1205 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 182 | 45 | 29 | 45 | 0 | 26 | 17 | 0 | 54 | 0 | 0 | 0 | 300 | 320 | 382 | 42 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 0 | 0 | 0 | 203 | 0 | 19 | 58 | 5 | 0 | 0 | 24 | 6298 | 919 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 197 | 0 | 190 | 0 | 0 | 0 | 0 | 8.5 | 210 | 72 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 180 | 0 | 0 | 1190 | 0 | 4658.5 | 10956.5 | 92.71
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 36 | 0 | 70 | 64 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 280 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 995 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1180 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 182 | 45 | 0 | 45 | 0 | 26 | 17 | 0 | 63 | 0 | 0 | 0 | 295 | 320 | 383 | 42 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 25 | 0 | 0 | 203 | 0 | 19 | 58 | 7 | 0 | 0 | 24 | 6267 | 920 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 193 | 0 | 190 | 0 | 0 | 0 | 0 | 8.5 | 210 | 72 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 180 | 0 | 0 | 1100 | 0 | 4560.5 | 10827.5
20:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 36 | 0 | 70 | 48 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 284 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 995 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 182 | 46 | 0 | 45 | 0 | 26 | 17 | 0 | 56 | 0 | 0 | 0 | 300 | 320 | 382 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 203 | 0 | 19 | 58 | 8 | 0 | 0 | 24 | 6152 | 920 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 193 | 0 | 190 | 0 | 0 | 0 | 0 | 8.5 | 210 | 72 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 180 | 0 | 0 | 1100 | 0 | 4559.5 | 10711.5 | 92.71
21:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 36 | 0 | 70 | 48 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 293 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 30 | 998 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 196 | 46 | 0 | 45 | 0 | 26 | 17 | 0 | 56 | 0 | 0 | 0 | 310 | 320 | 382 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 203 | 0 | 19 | 58 | 9 | 0 | 0 | 23 | 6009 | 920 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 193 | 0 | 190 | 0 | 0 | 0 | 0 | 8.5 | 210 | 73 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 5 | 140 | 180 | 0 | 0 | 1020 | 0 | 4445.5 | 10454.5 | 92.71
22:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 36 | 0 | 70 | 48 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 275 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 30 | 996 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 815 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 184 | 46 | 0 | 45 | 0 | 26 | 17 | 0 | 54 | 0 | 0 | 0 | 305 | 320 | 382 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 203 | 0 | 19 | 58 | 6 | 0 | 0 | 23 | 5902 | 919 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 193 | 0 | 188 | 0 | 0 | 0 | 0 | 8.5 | 210 | 72 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 140 | 180 | 0 | 0 | 900 | 0 | 4184.5 | 10086.5 | 92.71
23:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 17 | 0 | 70 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 275 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 33 | 995 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 47 | 0 | 45 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 290 | 320 | 382 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 204 | 0 | 19 | 58 | 6 | 0 | 0 | 24 | 5787 | 833 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 189 | 0 | 188 | 0 | 0 | 0 | 0 | 8.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 140 | 180 | 0 | 0 | 800 | 0 | 3821.5 | 9608.5 | 92.7
Total KWH | 0 | 979200 | 391680 | 0 | 0 | 0 | 0 | 0 | 8463600 | 0 | 0 | 0 | 435240 | 0 | 887616 | 505440 | 0 | 0 | 0 | 0 | 526320 | 0 | 7345000 | 6899665 | 0 | 0 | 0 | 595600 | 6062384 | 0 | 0 | 181174 | 0 | 365400 | 336960 | 0 | 0 | 0 | 0 | 0 | 0 | 335520 | 0 | 0 | 0 | 0 | 0 | 23019 | 741120 | 0 | 459840 | 21905454.55 | 0 | 0 | 30240 | 0 | 0 | 5260116 | 0 | 0 | 0 | 18905453 | 131760 | 832691 | 0 | 3680000 | 0 | 0 | 0 | 577440 | 4570000 | 982656 | 112320 | 1084170 | 135360 | 357840 | 365690 | 0 | 1242240 | 0 | 402291 | 0 | 7147000 | 7724600 | 8997000 | 617832 | 716000 | 0 | 54960 | 3688364 | 336192 | 0 | 1424640 | 133248 | 0 | 0 | 5217280 | 0 | 372000 | 1000800 | 211200 | 10150 | 235030 | 402480 | 134399275.55 | 20941090 | 6609888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523440 | 94545 | 0 | 12334181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 616440 | 0 | 299248 | 3933000 | 0 | 4343945 | 0 | 4253182 | 0 | 0 | 0 | 25320 | 184554 | 5086000 | 1645964 | 161506 | 154394 | 0 | 0 | 0 | 23939.52 | 847620 | 3604.5 | 0 | 4953000 | 133211 | 2896000 | 5014840 | 0 | 353320 | 20296727.27 | 51600 | 95780559.29 | 230179834.84

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 20-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 10379.15 | MW | 12:00 Hr. | Energy Generated |  |  | 230179.8348 |  | MWHr
Day Peak Demand |  |  | 10379.15 | MW | 12:00 Hr. | Energy Unserverd |  |  | 260 |  | MWHr
Evening Peak Generation |  |  | 10956.5 | MW | 19:00 Hr. | Energy Demand |  |  | 230439.8348 |  | MWHr
Evening Peak Demand |  |  | 10966.5 | MW | 19:00 Hr.
Minimum Generation of the Day |  |  | 7522.01 | MW | 05:00 Hr.
Maximum Generation of the Day |  |  | 10956.5 | MW | 19:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 30594.929 | 0 | 3199.176 | 0 | 0 | 181.174 | 0 | 0 | 33975.279 | Gas | 112044.468 | Gas | 398717972.56
Chattogram Zone |  |  | 5719.956 | 40810.9076 | 30.24 | 0 | 741.12 | 154.779 | 0 | 335.52 | 47792.5226 | Coal | 73240.4638 | Coal | 514671508.4111
Cumilla Zone |  |  | 12092.647 | 0 | 605.52 | 0 | 0 | 402.291 | 1242.24 | 0 | 14342.698 | HFO | 5823.322 | HFO | 112198521.8
Mymensingh Zone |  |  | 211.2 | 0 | 1775.28 | 0 | 0 | 245.18 | 0 | 0 | 2231.66 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 36057.116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36057.116 | Hydro | 741.12 | Hydro | 74112
Khulna Zone |  |  | 6609.888 | 94.545 | 0 | 0 | 0 | 523.44 | 20941.09 | 0 | 28168.963 | Solar | 3477.43 | Solar | 54001841.267
Barishal Zone |  |  | 8044.051 | 25603.0473 | 51.6 | 0 | 0 | 3.6045 | 0 | 0 | 33702.3028 | Import | 34517.511 | Import | 166448673.63
Rajshahi Zone |  |  | 12714.681 | 0 | 0 | 0 | 0 | 941.008 | 12334.181 | 0 | 25989.87 | Wind | 335.52 | Wind | 5234112
Rangpur Zone |  |  | 0 | 6731.964 | 161.506 | 0 | 0 | 1025.9535 | 0 | 0 | 7919.4235
Total |  |  | 112044.468 | 73240.4638 | 5823.322 | 0 | 741.12 | 3477.43 | 34517.511 | 335.52 | 230179.8348
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 398717972.56 |  | Hydro | 74112
|  |  | Coal | 514671508.4111 |  | Solar | 54001841.267
|  |  | HFO | 112198521.8 |  | Import | 166448673.63
|  |  | HSD | 0 |  | Wind | 5234112
|  |  |  | Total: | 1251346741.6681 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
| 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
| 4 | Barapukuria TPP Unit-2 |  |  | 85
| 5 | Khulna 330 MW CCPP GT |  |  | 220
| 6 | Khulna 330 MW CCPP ST |  |  | 110
| 7 | Siddhirgonj 210 MW TPP |  |  | 115
| 8 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 9 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1404 |  |  |  | Total | 435.09
|  |  | Total Unavailable Capacity |  |  |  | 1839.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 0 |  | 3997
|  |  | Chattogram |  | 0 |  | 1024
|  |  | Cumilla |  | 0 |  | 883
|  |  | Mymensingh |  | 10 |  | 923
|  |  | Sylhet |  | 0 |  | 383
|  |  | Khulna |  | 0 |  | 1208
|  |  | Barishal |  | 0 |  | 287
|  |  | Rajshahi |  | 0 |  | 1038
|  |  | Rangpur |  | 0 |  | 714
|  |  | Total |  | 10 |  | 10457
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:10 | 17:18 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Narshingdi 132/33kV end Due to
Annnul Maintenance
08:21 | 16:20 | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end Due to 132kV
Goalpara Line have been taken shutdown due to do their Annual Maintenance and from
Goalpara 132/33kV end Due to Annual maintenance
08:23 | 17:13 | Candpur (Desh)- Chandpur 132kV Ckt-1 Scheduled S/D from Chandpur 132/33kV end Due to
Annual maintenance
08:25 | 16:56 | Barishal(N)-Madaripur 132 kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to
Annual maintenance
08:26 | 08:38 | Tangail 132/33kV S/S Kaliakair-2 Tripped showing REL316*4 relays. | [7 empty] | 125.0MW load
interrup.
08:27 | 08:49 | Kaliakoir-Tangail 132kV Ckt-1 Tripped from Kaliakoir 400/230/132kV end showing 67
relays Due to Over current.
08:31 | 16:37 | Cumilla(S) 132/33kV S/S Tripura Ckt-2 Scheduled S/D Due to Annual Maintenance
08:36 | 16:55 | Barishal(N)-Madaripur 132 kV Ckt-2 Forced S/D from Barishal 230/132kV end Due to From
ALDC
08:58 | 12:39 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Scheduled S/D Due to Maintenance work
08:58 | 12:40 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Scheduled S/D Due to Maintenance work
09:01 | 17:36 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-02 Scheduled S/D Due to A/M
09:03 | 16:37 | Sirajganj-Ullahpara 132KV Ckt-1 Scheduled S/D from Sirajganj 132/33kV end Due to Annual
maintenance
09:04 | 13:49 | Jhenaidah 230/132kV S/S Transformer- 1 LT Scheduled S/D Due to Annual maintenance
09:05 | 13:41 | Jhenaidah 230/132kV S/S Transformer- 1 HT Scheduled S/D Due to Annual maintenance
09:06 | 20:18 | Rampura-Ullon-2 132kV Ckt-2 Forced S/D from Rampura 230/132kV end Due to Shutdown taken
by NLDC
09:17 | 18:56 | Kallyanpur-Lalbag 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to Disc
Cleaning at Tower 2,4,5,6
09:20 | 13:44 | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shahmirpur 132/33kV end Due to
Deadline checking.
09:22 |  | HVDC Bheramera- Rajshahi 230kV Ckt-2 Scheduled S/D from BIPTC end Due to Shutdown is
taken from Rajshahi end
09:25 | 15:33 | Haripur 230/132kV S/S Auto TR-2 LT Scheduled S/D Due to Annual Maintenance
09:26 | 15:33 | Haripur 230/132kV S/S Auto TR-2 HT Scheduled S/D Due to Annual Maintenance
09:30 |  | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to T-2 DS replacement
09:30 |  | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Ds replacement
09:31 |  | Tongi 230/132/33kV S/S T-03 HT Scheduled S/D Due to Annual maintenance
09:31 |  | Tongi 230/132/33kV S/S T-03 LT Scheduled S/D Due to Annual maintenance
09:32 | 15:33 | Ashuganj-Bhulta 400 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end.
09:58 | 11:54 | Mymensingh-Netrokona 132kV Ckt-2 Project Work S/D from Mymensingh 132/33kV end Due to | [7 empty] | 10.0MW load
|  | Shutdown taken by Mr Bapon sarker,SAE, CEEGSTL Project | [7 empty] | interrup.
Mymensingh 132/33kV
end
10:03 | 16:06 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Scheduled S/D Due to Works for Ruppur project.
10:22 | 16:51 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to
Annual Maintenance Work purposes and from Kishoreganj 132/33kV end Due to Work in
Mymensingh substation
10:45 | 10:51 | Mymensingh-Netrokona 132kV Ckt-1 Tripped from Mymensingh 132/33kV end showing 21 relays
Due to Tried due to Distance C ph,Z1
11:01 |  | Patuakhali 1320 MW (RNPL) unit-2 was sync.
| 11:08 | Bhandaria 132/33kV S/S Main Bus Bar is restored.
| 11:08 | Barishal-Bhandaria 132 kV Ckt-1 is restored.
| 11:09 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
| 11:09 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
| 11:09 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
| 11:10 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
11:12 |  | Baroirhat-Feni 132 kV Ckt-2 Scheduled S/D from Baroirhat 132/33kV end Due to Realy test
work
11:38 |  | Mymensingh-Netrokona 132kV Ckt-1 Tripped from Mymensingh 132/33kV end showing 21 relays
Due to Triped
11:57 |  | Sherpur 132/33kV S/S Transformer- 04 HT Forced S/D Due to Transporter differential relay
problem
11:57 |  | Sherpur 132/33kV S/S Transformer- 04 LT Forced S/D Due to Transporter differential relay
problem
12:00 |  | Day Peak Generation: 10376 MW.
12:48 | 15:23 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Scheduled S/D Due to Annual
Maintenance
12:50 | 15:22 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Scheduled S/D Due to Annual
Maintenance
14:26 |  | Rampura-Gulshan Ckt-2 was switched on.
| 14:26 | Gulsan-Rampura 132kV Ckt-2 is restored.
| 14:29 | Rampura 230/132kV S/S NLDC Trafo HT is restored.
| 14:29 | Rampura 230/132kV S/S Auto Transformer - 04 HT is restored.
| 14:29 | Rampura 230/132kV S/S Auto Transformer - 04 LT is restored.
14:51 |  | Patuakhali 1320 MW (RNPL) tripped due to boiler MFT trip.
15:14 |  | Adani U-1 GSUT was shut down.
| 17:18 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 is restored.
| 18:02 | Cantonment 132/33kV S/S Transformer-1 (T-1) HT is restored.
| 18:51 | Aminbazar-Airport(Old) 230kV Ckt-2 is restored.
19:00 |  | Evening Peak Gen. 10956 MW
19:29 |  | Adani U-1 GSUT was switched on.
| 20:28 | Kabirpur -Kodda 132kV Ckt-1 is restored.
20:42 | 21:20 | Kabirpur 132/33kV S/S XFR, T-I HT Forced S/D Due to High temperature maintenance work at | [7 empty] | 35.0MW load
|  | 33 kv kabirpur feeder 33KV BUS DS, shutdown taken by DPBS-1. | [7 empty] | interrup.
01:56 |  | Kabirpur 132/33kV S/S XFR, T-3 LT Tripped showing DIR Over current trip. relays Due to | [7 empty] | 30.0MW load
|  | 33kV CB tripped due to 33kV bus PT blast. | [7 empty] | interrup.
05:00 |  | Minimum Generation = 7,357MW
07:10 |  | Kabirpur -Kodda 132kV Ckt-1 Project Work S/D from Kabirpur 132/33kV end Due to Shutdown
taken by G2G project.
07:12 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to Maintenance work
07:13 |  | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D Due to Maintenance work
07:37 |  | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to
Insulator deep cleaning.
07:44 |  | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to 132kv CT change Work.
07:44 |  | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to 132kv CT change Work.
07:54 |  | Bhulta-Haripur 132 kV Ckt-1 Project Work S/D from Bhulta 132/33kV end Due to LILO Work at | [7 empty] | 25.0MW load
|  | Bhulta 400 KV Sub-Station | [7 empty] | interrup. Bhulta
132/33kV end
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 340 | 8463600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7345000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 262 | 6899665 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6062384 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 505440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 365400 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 336960 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 526320 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 595600 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 25 | 391680 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 70 | 887616 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 979200 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 181174 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 36 | 435240 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 1495 | 33975279
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 131760 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 30240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 741120 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 226 | 5260116 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | -
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 459840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23019 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1205 | 18905453 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 2 | 335520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 997 | 21905454.55 | Machine Problem
Chattogram Area Total |  |  |  |  | 4915.22 | 2482 | 47792522.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4570000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 45 | 982656 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 577440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 3680000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 832691 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 45 | 1084170 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 135360 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 54 | 1242240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 365690 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 26 | 357840 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 29 | 112320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 402291 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 675 | 14342698
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 5 | 211200 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1000800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 372000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 235030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 402480 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 106 | 2231660
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 716000 | Machine Problem
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3688364 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 42 | 617832 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 54960 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 0 | 133248 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1424640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 203 | 5217280 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 336192 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7147000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 382 | 8997000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7724600 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1540 | 36057116
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 919 | 20941090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 260 | 6609888 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 523440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 94545 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1179 | 28168963
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 353320 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 133211 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2896000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1190 | 20296727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 180 | 5014840 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 51600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 4953000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3604.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1824 | 33702302.77
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 189 | 3933000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 197 | 4343945 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 190 | 4253182 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | machine problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 8.5 | 184554 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | none
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 754 | 12334181 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 299248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 616440 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1338.5 | 25989870
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 72 | 1645964 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 5086000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 23939.52 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 161506 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 154394 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 847620 | -
Rangpur Area Total |  |  |  |  | 950 | 317 | 7919423.52
Eastern Grid Total |  |  |  |  | 16772.748 | 6298 | 134399275.55
Western Grid Total |  |  |  |  | 11614.5 | 4658.5 | 95780559.29
National Grid Total |  |  |  |  | 28387.248 | 10956.5 | 230179834.84
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9016.33 | 0 |  | 9016.33
1:00 | 8438.65 | 0 |  | 8438.65
2:00 | 8097.01 | 0 |  | 8097.01
3:00 | 7755.16 | 0 |  | 7755.16
4:00 | 7551.56 | 0 |  | 7551.56
5:00 | 7522.01 | 0 |  | 7522.01
6:00 | 7965.07 | 0 |  | 7965.07
7:00 | 8750.6 | 0 |  | 8750.6
8:00 | 9616.7 | 0 |  | 9616.7
9:00 | 9559.67 | 100 |  | 9663.67
10:00 | 9728.05 | 25 |  | 9754.05
11:00 | 9764.22 | 20 |  | 9785.22
12:00 | 10379.15 | 0 |  | 10379.15
13:00 | 10545.7 | 0 |  | 10545.7
14:00 | 10229.92 | 0 |  | 10229.92
15:00 | 9752.23 | 0 |  | 9752.23
16:00 | 9575.27 | 0 |  | 9575.27
17:00 | 9762.32 | 0 |  | 9762.32
18:00 | 10585.5 | 50 |  | 10637.5
19:00 | 10956.5 | 10 |  | 10966.5
19:30 | 10827.5 | 35 |  | 10864.5
20:00 | 10711.5 | 35 |  | 10748.5
21:00 | 10454.5 | 20 |  | 10475.5
22:00 | 10086.5 | 0 |  | 10086.5
23:00 | 9608.5 | 0 |  | 9608.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7200.42 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3247.3 | MW
i) Dhaka area |  |  | 3997.32 |  | MW | i) Khulna area |  |  |  | 1208 | MW
ii) Chattogram area |  |  | 1024.1 |  | MW | ii) Barishal area |  |  |  | 287.3 | MW
iii) Cumilla area |  |  | 883 |  | MW | iii) Rajshahi area |  |  |  | 1038 | MW
iv) Mymensingh area |  |  | 913 |  | MW | iv) Rangpur area |  |  |  | 714 | MW
v) Sylhet area |  |  | 383 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10447.72 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 00:00 | 67 | Jaldhaka | 58 | 18:00 | 133 | Purbachal | 15 | 18:30
2 | AKSML | 91 | 00:00 | 68 | Jamalpur | 99 | 08:00 | 134 | Purbasadipur | 97 | 18:30
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 109 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 71 | 13:00 | 70 | Jhenaidah | 96 | 08:00 | 136 | Rahim | 50 | 14:00
5 | Agrabad | 64 | 18:00 | 71 | Joydebpur | 126 | 18:00 | 137 | Rajbari | 56 | 18:30
6 | Amnura | 43 | 08:00 | 72 | Joypurhat | 40 | 08:00 | 138 | Rajendrapur | 102 | 13:00
7 | Ashuganj | 65 | 13:00 | 73 | Juldah | 10 | 11:00 | 139 | Rajshahi | 92 | 13:00
8 | BSRM | 185 | 04:00 | 74 | KSRM | 33 | 11:00 | 140 | Rajshahi-230 | 44 | 13:00
9 | Bagerhat | 61 | 18:30 | 75 | Kabirpur | 224 | 18:00 | 141 | Ramganj | 92 | 18:00
10 | Bajitpur | 0 | 02:00 | 76 | Kachua | 50 | 20:00 | 142 | Rampur | 25 | 18:00
11 | Bakulia | 64 | 13:00 | 77 | Kallyanpur | 72 | 13:00 | 143 | Rangamati | 12 | 18:00
12 | Banani | 40.2 | 13:00 | 78 | Kalurghat | 30 | 12:00 | 144 | Rangpur | 112 | 18:30
13 | Bangabhaban | 8 | 13:00 | 79 | Kamrangirchar | 56 | 12:00 | 145 | Ruppur | 4.6 | 16:00
14 | Barapukuria | 51 | 18:30 | 80 | Kaptai | N/A | N/A | 146 | SSM | 12 | 05:00
15 | Barguna | 14 | 19:30 | 81 | Kazla | 89 | 13:00 | 147 | Saidpur | 97 | 18:30
16 | Barishal | 69 | 13:00 | 82 | Keranigonj | 57 | 12:00 | 148 | Satkhira | 90 | 08:00
17 | Barishal-230 | 70 | 19:30 | 83 | Khagrachori | 24 | 18:30 | 149 | Satmasjid | 82 | 14:00
18 | Baroaulia | 66 | 10:00 | 84 | Khulna | 71 | 13:00 | 150 | Savar | 175 | 14:00
19 | Baroirhat | 55 | 18:30 | 85 | Khulshi | 138 | 10:00 | 151 | SevenRings | 17.83 | 17:00
20 | Bashundhara | 136 | 13:00 | 86 | Kishoreganj | 126 | 18:30 | 152 | ShahCement | 30 | 12:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kodda | 270 | 18:30 | 153 | Shahjadpur | 63 | 18:30
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 26 | 18:00 | 154 | Shahjibazar | 83 | 19:00
23 | Benapole | 54 | 08:00 | 89 | Kurigram | 46 | 08:00 | 155 | Shahmirpur | 39 | 00:00
24 | Bhaluka | 110 | 15:00 | 90 | Kushtia | 104 | 13:00 | 156 | Shariatpur | 52 | 20:00
25 | Bhandaria | 36 | 21:00 | 91 | Lalbag | 63 | 18:00 | 157 | Sherpur | 106 | 00:00
26 | Bhangura | 26 | 18:00 | 92 | Lalmonirhat | 47 | 18:30 | 158 | Shikalbaha | 20 | 12:00
27 | Bheramara(GK) | 40 | 18:30 | 93 | MI_Cement | 17 | 00:00 | 159 | Shitalakhya | 60.4 | 11:00
28 | Bhulta | 235 | 11:00 | 94 | Madanganj | 29 | 09:00 | 160 | Sholosohor | 31 | 12:00
29 | Bog-Sherpur | 54 | 08:00 | 95 | Madaripur | 67 | 21:00 | 161 | Shyampur | 122 | 01:00
30 | Bogura | 111 | 18:30 | 96 | Madartek | 58.42 | 13:00 | 162 | Siddhirganj | 96 | 09:00
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 37 | 18:00 | 163 | Sirajganj | 76 | 19:00
32 | Brahmanbaria | 102 | 20:00 | 98 | Magura | 46 | 18:00 | 164 | Sonargaon | 63 | 10:00
33 | Cantonment | 77 | 14:00 | 99 | Mahasthangarh | 48 | 18:30 | 165 | Sreemongol | 51 | 16:00
34 | Chandpur | 42 | 19:30 | 100 | Manikganj | 109 | 19:00 | 166 | Sreepur | 83 | 11:00
35 | Chandraghona | 26 | 18:00 | 101 | Maniknagar | 46 | 13:00 | 167 | Srinagar | 28.78 | 20:00
36 | Chapai | 61 | 13:00 | 102 | Matarbari | 34 | 19:00 | 168 | Sunamganj | 36 | 18:00
37 | Charsaidpur | 38 | 16:00 | 103 | Matuail | 49 | 12:00 | 169 | Sylhet | 28 | 21:00
38 | Chauddagram | 52 | 18:00 | 104 | Millgate | 65 | 12:00 | 170 | Sylhet-132 | 77 | 13:00
39 | Chhatak | 24 | 18:00 | 105 | Mirpur | 91 | 14:00 | 171 | TK | 21 | 18:00
40 | Chowmuhani | 136 | 18:00 | 106 | Mirsorai | 8 | 18:30 | 172 | Tangail | 148 | 18:00
41 | Chuadanga | 73 | 18:00 | 107 | Mirzapur | 42 | 11:00 | 173 | Thakurgaon | 75 | 18:30
42 | Coxsbazar | 100 | 07:00 | 108 | Mithapukur | 42 | 08:00 | 174 | Tongi | 96 | 08:00
43 | Cumilla(N) | 108 | 18:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 28 | 11:00
44 | Cumilla(S) | 131 | 14:00 | 110 | Mogbazar | 93.4 | 14:00 | 176 | Ullon | 33 | 21:00
45 | Daudkandi | 106 | 19:30 | 111 | Mongla | 33 | 06:00 | 177 | Uttara | 59 | 13:00
46 | Dhaka | 34 | 13:00 | 112 | Motijheel | 26 | 13:00 | 178 | UttaraNew | 33 | 14:00
47 | Dhamrai | 100 | 18:30 | 113 | Muktagacha | 25 | 07:00 | 179 | Zigatola | 53 | 13:00
48 | Dhanmondi | 95 | 13:00 | 114 | Munshiganj | 64 | 13:00
49 | Dohazari | 71 | 18:00 | 115 | Mymensingh | 168 | 13:00
50 | Faridpur | 108 | 20:00 | 116 | Naogaon | 94 | 13:00
51 | Fatullah | 81 | 12:00 | 117 | Narail | 41 | 18:30
52 | Fenchuganj | 28 | 18:00 | 118 | Narinda | 57 | 13:00
53 | Feni | 58 | 18:00 | 119 | Narshingdi | 148 | 19:00
54 | GPH | 85 | 12:00 | 120 | Natore | 108 | 18:30
55 | Ghatail | 32 | 07:00 | 121 | Nawabganj | 36.6 | 13:00
56 | Ghorashal | 8 | 01:00 | 122 | Netrakona | 137 | 07:00
57 | Ghorashal-230 | 57 | 18:30 | 123 | New | 70 | 12:00
58 | Goalpara | 26 | 13:00 | 124 | Niamatpur | 77 | 08:00
59 | Gollamari | 50 | 13:00 | 125 | Noapara | 34 | 19:00
60 | Gopalganj | 80 | 18:30 | 126 | PHP | 9 | 10:00
61 | Gulshan | 62 | 13:00 | 127 | Pabna | 65 | 18:30
62 | Halishahar | 42 | 15:00 | 128 | Palashbari | 83 | 18:30
63 | HaripurSBU | 183 | 11:00 | 129 | Panchagarh | 43 | 18:30
64 | Hasnabad | 64 | 13:00 | 130 | Patuakhali | 51.2 | 20:00
65 | Hathazari | 53 | 13:00 | 131 | Payra | 14 | 13:00
66 | Ishurdi | 58 | 18:30 | 132 | Postogola | 42 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## L-Curve
QF-LDC-11
Date | 20-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5213 | 3803.33 | 9016.33 | DAILY LOAD CURVE
00:30 | 5015 | 3712.49 | 8727.49
01:00 | 4817 | 3621.65 | 8438.65 | 20-01-2025
01:30 | 4793 | 3474.83 | 8267.83
02:00 | 4769 | 3328.01 | 8097.01
02:30 | 4704.5 | 3221.585 | 7926.085
03:00 | 4640 | 3115.16 | 7755.16
03:30 | 4620.5 | 3032.86 | 7653.36
04:00 | 4601 | 2950.56 | 7551.56
04:30 | 4583.5 | 2953.285 | 7536.785
05:00 | 4566 | 2956.01 | 7522.01
05:30 | 4682 | 3061.54 | 7743.54
06:00 | 4798 | 3167.07 | 7965.07
06:30 | 5070.86 | 3286.975 | 8357.835
07:00 | 5343.72 | 3406.88 | 8750.6
07:30 | 5469.765 | 3713.885 | 9183.65
08:00 | 5595.81 | 4020.89 | 9616.7
08:30 | 5549.675 | 4038.51 | 9588.185
09:00 | 5503.54 | 4056.13 | 9559.67
09:30 | 5590.435 | 4053.425 | 9643.86
10:00 | 5677.33 | 4050.72 | 9728.05
10:30 | 5672.76 | 4073.375 | 9746.135
11:00 | 5668.19 | 4096.03 | 9764.22
11:30 | 5768.96 | 4302.725 | 10071.685
12:00 | 5869.73 | 4509.42 | 10379.15
12:30 | 5885.64 | 4576.785 | 10462.425
13:00 | 5901.55 | 4644.15 | 10545.7
13:30 | 5826.37 | 4561.44 | 10387.81
14:00 | 5751.19 | 4478.73 | 10229.92
14:30 | 5753.665 | 4237.41 | 9991.075
15:00 | 5756.14 | 3996.09 | 9752.23
15:30 | 5698.39 | 3965.36 | 9663.75
16:00 | 5640.64 | 3934.63 | 9575.27
16:30 | 5742.235 | 3926.56 | 9668.795
17:00 | 5843.83 | 3918.49 | 9762.32
17:30 | 6038.915 | 4134.995 | 10173.91
18:00 | 6234 | 4351.5 | 10585.5
18:30 | 6266 | 4505 | 10771
19:00 | 6298 | 4658.5 | 10956.5
19:30 | 6267 | 4560.5 | 10827.5
20:00 | 6152 | 4559.5 | 10711.5
20:30 | 6080.5 | 4502.5 | 10583 |  | Executive Engineer
21:00 | 6009 | 4445.5 | 10454.5 |  | Network Operation Division
21:30 | 5955.5 | 4315 | 10270.5
22:00 | 5902 | 4184.5 | 10086.5
22:30 | 5844.5 | 4003 | 9847.5
23:00 | 5787 | 3821.5 | 9608.5

## En-Curve
QF-LDC-12
Date | 20-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2993 | 1530.5 | 917 | 0 | 54 | 412.83 | 30 | 2928 | 0 | 0 | 129 | 0 | 0 | 22 | 0 | DAILY ENERGY CURVE
00:30 | 3007.5 | 1475.5 | 917 | 0 | 50 | 412.99 | 30 | 2726.5 | 0 | 0 | 85 | 0 | 0 | 23 | 0 | 20-01-2025
01:00 | 3022 | 1420.5 | 917 | 0 | 46 | 413.15 | 30 | 2525 | 0 | 0 | 41 | 0 | 0 | 24 | 0
01:30 | 3017 | 1427.5 | 823.5 | 0 | 44 | 414.33 | 30 | 2455.5 | 0 | 0 | 29 | 0 | 0 | 27 | 0 |  | Total Energy | 230.1798 |  | MKWHr
02:00 | 3012 | 1434.5 | 730 | 0 | 42 | 415.51 | 30 | 2386 | 0 | 0 | 17 | 0 | 0 | 30 | 0 |  | Energy not Served | 0.26 |  | MKWHr
02:30 | 2870 | 1419.5 | 730 | 0 | 43 | 414.585 | 30 | 2378 | 0 | 0 | 8.5 | 0 | 0 | 32.5 | 0 |  | Energy Requirement | 230.4398 |  | MKWHr
03:00 | 2728 | 1404.5 | 730 | 0 | 44 | 413.66 | 30 | 2370 | 0 | 0 | 0 | 0 | 0 | 35 | 0
03:30 | 2650 | 1419 | 730 | 0 | 45 | 414.36 | 30 | 2327 | 0 | 0 | 0 | 0 | 0 | 38 | 0
04:00 | 2572 | 1433.5 | 730 | 0 | 46 | 415.06 | 30 | 2284 | 0 | 0 | 0 | 0 | 0 | 41 | 0
04:30 | 2572.5 | 1422 | 730 | 0 | 43 | 414.785 | 30 | 2283.5 | 0 | 0 | 0 | 0 | 0 | 41 | 0
05:00 | 2573 | 1410.5 | 730 | 0 | 40 | 414.51 | 30 | 2283 | 0 | 0 | 0 | 0 | 0 | 41 | 0
05:30 | 2715.5 | 1492 | 730 | 0 | 43 | 415.04 | 30 | 2285 | 0 | 0 | 0 | 0 | 0 | 33 | 0
06:00 | 2858 | 1573.5 | 730 | 0 | 46 | 415.57 | 30 | 2287 | 0 | 0 | 0 | 0 | 0 | 25 | 0
06:30 | 2911 | 1671 | 777 | 0 | 46 | 416.33 | 30 | 2413.5 | 4.505 | 8 | 50 | 0 | 0 | 30.5 | 0
07:00 | 2964 | 1768.5 | 824 | 0 | 46 | 417.09 | 30 | 2540 | 9.01 | 16 | 100 | 0 | 0 | 36 | 0
07:30 | 3009.5 | 1755.75 | 871.5 | 0 | 46 | 455.545 | 30 | 2758.5 | 63.855 | 42 | 120.5 | 0 | 0 | 30.5 | 0
08:00 | 3055 | 1743 | 919 | 0 | 46 | 494 | 30 | 2977 | 118.7 | 68 | 141 | 0 | 0 | 25 | 0
08:30 | 2918.5 | 1702.5 | 919 | 0 | 45 | 525.5 | 30 | 3039 | 188.685 | 98 | 104.5 | 0 | 0 | 17.5 | 50
09:00 | 2782 | 1662 | 919 | 0 | 44 | 557 | 30 | 3101 | 258.67 | 128 | 68 | 0 | 0 | 10 | 100
09:30 | 2781 | 1626 | 919 | 0 | 47 | 557.5 | 30 | 3092 | 342.86 | 128 | 113.5 | 0 | 0 | 7 | 62.5
10:00 | 2780 | 1590 | 919 | 0 | 50 | 558 | 30 | 3083 | 427.05 | 128 | 159 | 0 | 0 | 4 | 25
10:30 | 2778.5 | 1577.25 | 919 | 0 | 52.5 | 558.5 | 30 | 3067.5 | 474.885 | 120 | 164 | 0 | 0 | 4 | 22.5
11:00 | 2777 | 1564.5 | 919 | 0 | 55 | 559 | 30 | 3052 | 522.72 | 112 | 169 | 0 | 0 | 4 | 20
11:30 | 2933 | 1626.5 | 919.5 | 0 | 57 | 559 | 30 | 3120.5 | 545.685 | 112 | 166 | 0 | 0 | 2.5 | 10
12:00 | 3089 | 1688.5 | 920 | 0 | 59 | 559 | 30 | 3189 | 568.65 | 112 | 163 | 0 | 0 | 1 | 0
12:30 | 3104.5 | 1722 | 914.5 | 0 | 58.5 | 523 | 30 | 3258 | 559.925 | 102 | 188.5 | 0 | 0 | 1.5 | 0
13:00 | 3120 | 1755.5 | 909 | 0 | 58 | 487 | 30 | 3327 | 551.2 | 92 | 214 | 0 | 0 | 2 | 0
13:30 | 3019.5 | 1723.5 | 914 | 0 | 62 | 457 | 30 | 3380.5 | 506.31 | 80 | 214 | 0 | 0 | 1 | 0
14:00 | 2919 | 1691.5 | 919 | 0 | 66 | 427 | 30 | 3434 | 461.42 | 68 | 214 | 0 | 0 | 0 | 0
14:30 | 2901 | 1735.5 | 919.5 | 0 | 62 | 422 | 30 | 3239 | 397.575 | 75.5 | 205 | 0 | 0 | 4 | 0
15:00 | 2883 | 1779.5 | 920 | 0 | 58 | 417 | 30 | 3044 | 333.73 | 83 | 196 | 0 | 0 | 8 | 0
15:30 | 2889 | 1790 | 919.5 | 0 | 53.5 | 468 | 30 | 2976.5 | 249.25 | 83 | 197.5 | 0 | 0 | 7.5 | 0
16:00 | 2895 | 1800.5 | 919 | 0 | 49 | 519 | 30 | 2909 | 164.77 | 83 | 199 | 0 | 0 | 7 | 0
16:30 | 2887.5 | 1808 | 919.5 | 0 | 51.5 | 519.5 | 30 | 3051 | 101.295 | 93.5 | 202 | 0 | 0 | 5 | 0
17:00 | 2880 | 1815.5 | 920 | 0 | 54 | 520 | 30 | 3193 | 37.82 | 104 | 205 | 0 | 0 | 3 | 0
17:30 | 2962.5 | 1791.5 | 920 | 0 | 56 | 585 | 30 | 3410.5 | 18.91 | 123.5 | 274 | 0 | 0 | 2 | 25
18:00 | 3045 | 1767.5 | 920 | 0 | 58 | 650 | 30 | 3628 | 0 | 143 | 343 | 0 | 0 | 1 | 50
18:30 | 3024.5 | 1762 | 919.5 | 0 | 56 | 702 | 30 | 3804.5 | 0 | 151 | 320 | 0 | 0 | 1.5 | 30
19:00 | 3004 | 1756.5 | 919 | 0 | 54 | 754 | 30 | 3981 | 0 | 159 | 297 | 0 | 0 | 2 | 10
19:30 | 2982 | 1772.5 | 920 | 0 | 63 | 760 | 35 | 3864 | 0 | 159 | 268 | 0 | 0 | 4 | 35
20:00 | 2987 | 1753.5 | 920 | 0 | 56 | 760 | 35 | 3784 | 0 | 143 | 268 | 0 | 0 | 5 | 35
20:30 | 3020 | 1763.5 | 920 | 0 | 56 | 759.5 | 32.5 | 3617.5 | 0 | 143 | 267.5 | 0 | 0 | 3.5 | 27.5
21:00 | 3053 | 1773.5 | 920 | 0 | 56 | 759 | 30 | 3451 | 0 | 143 | 267 | 0 | 0 | 2 | 20
21:30 | 3053 | 1763 | 919.5 | 0 | 55 | 692 | 30 | 3347 | 0 | 143 | 267 | 0 | 0 | 1 | 10
22:00 | 3053 | 1752.5 | 919 | 0 | 54 | 625 | 30 | 3243 | 0 | 143 | 267 | 0 | 0 | 0 | 0
22:30 | 3037 | 1746.5 | 876 | 0 | 56 | 569 | 30 | 3185 | 0 | 117 | 227.5 | 0 | 0 | 3.5 | 0
23:00 | 3021 | 1740.5 | 833 | 0 | 58 | 513 | 30 | 3127 | 0 | 91 | 188 | 0 | 0 | 7 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 415 | 05:00 | 387 | 11:00 | Kaliakoir | 376 | 05:00 | 356 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 400 | 9:30 | 378 | 12:30 | Madunaghat | 409 | 05:00 | 393 | 19:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 408 | 04:00 | 380 | 13:00 | Meghnaghat | 411 | 05:00 | 386 | 13:00
| Bibiana | 395 | 05:00 | 384 | 12:00 | Payra | 418 | 05:00 | 406 | 13:00
| BIPTC | 406 | 02:00 | 391 | 12:00 | Rahanpur | 414 | 05:00 | 397 | 18:30
| Bogura | 414 | 05:00 | 393 | 18:30 | Rampal | 416 | 04:00 | 388 | 18:00
| Gopalganj | 418 | 05:00 | 393 | 13:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 237 | 05:00 | 219 | 13:00 | Haripur | 238 | 04:00 | 222 | 13:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 232 | 04:00 | 222 | 18:30 | Hasnabad | 232 | 00:00 | 220 | 13:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 236 | 04:00 | 221 | 11:00 | Hathazari | 233 | 05:00 | 226 | 18:00
| Ashuganj | 238 | 05:00 | 224 | 13:00 | Ishurdi | 244 | 03:00 | 230 | 13:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 05:00 | 224 | 13:00 | Jhenaidah | 243 | 05:00 | 224 | 13:00
| Baghabari | 240 | 00:00 | 230 | 12:00 | Kaliakoir | 236 | 03:00 | 223 | 12:00 | 230 kV MAX | 249 |  | 249 | 217
| Barapukuria | 224 | 00:00 | 217 | 18:30 | Keranigonj | 235 | 04:00 | 219 | 13:00 | 230 kV MIN | 217 |  | 245 | 219 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 224 | 00:00 | 217 | 18:30 | Khulna(S) | 243 | 05:00 | 224 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 247 | 03:00 | 236 | 13:00 | Madunaghat | 234 | 04:00 | 224 | 20:00 | 132 kV MAX | 143 |  | 143 | 112 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 242 | 04:00 | 227 | 13:00 | Madunaghat-400 | 234 | 03:00 | 224 | 13:00 | 132 kV MIN | 111 |  | 142 | 111 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 239 | 04:00 | 222 | 13:00 | Maniknagar | 236 | 04:00 | 221 | 13:00 | [35 empty] | 6:00
| Bibiana | 229 | 06:00 | 224 | 13:00 | Meghnaghat | 245 | 04:00 | 230 | 12:00 |  | 400 | [33 empty] | 392
| BIPTC | 243 | 03:00 | 227 | 13:00 | Meghnaghat-400 | 238 | 04:00 | 224 | 13:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 241 | 03:00 | 228 | 18:30 | Mirsorai | 233 | 04:00 | 222 | 13:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 239 | 00:00 | 227 | 18:30 | Rajshahi | 243 | 05:00 | 226 | 13:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 249 | 03:00 | 243 | 12:00 | Rampal | 240 | 01:00 | 222 | 12:00 |  | 132 |  |  | Ash 400-299274
| BSRM | 232 | 03:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 234 | 05:00 | 222 | 12:00 | Rampura | 238 | 05:00 | 221 | 13:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 248 | 05:00 | 233 | 13:00 | Shikalbaha | 232 | 03:00 | 222 | 18:00 |  | kaptai by call 399528
| Fenchuganj | 232 | 00:00 | 224 | 22:00 | Shyampur | 236 | 03:00 | 221 | 13:00
| Ghorashal | 232 | 17:00 | 230 | 00:00 | Siddhirganj | 235 | 00:00 | 224 | 13:00
| Ghorashal-230 | 236 | 05:00 | 222 | 13:00 | Sirajgonj | 248 | 05:00 | 238 | 13:00
| Gopalganj | 247 | 05:00 | 232 | 13:00 | Sreepur | 240 | 05:00 | 228 | 11:00
| GPH | 232 | 03:00 | 222 | 19:30 | Tongi | 233 | 04:00 | 218 | 12:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 136 | 03:00 | 125 | 13:00 | Kurigram | 131 | 05:00 | 119 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 138 | 04:00 | 126 | 13:00 | Kushtia | 141 | 01:00 | 132 | 12:00
| Agrabad | 134 | 04:00 | 126 | 12:00 | Lalbag | 137 | 05:00 | 126 | 13:00
| AKS | 130 | 00:00 | 126 | 12:00 | Lalmonirhat | 131 | 05:00 | 122 | 18:30
| Aminbazar | 137 | 04:00 | 126 | 11:00 | Madanganj | 135 | 04:00 | 127 | 12:00
| Amnura | 140 | 01:00 | 131 | 13:00 | Madaripur | 136 | 02:00 | 130 | 18:00
| Ashuganj | 138 | 00:00 | 135 | 12:00 | Madartek | 136 | 04:00 | 125 | 13:00
| Bagerhat | 138 | 00:00 | 124 | 13:00 | Madunaghat | 135 | 04:00 | 127 | 19:00
| Bajitpur | 135 | 04:00 | 126 | 17:00 | Magura | 141 | 02:00 | 128 | 13:00
| Bakulia | 133 | 05:00 | 127 | 12:00 | Mahasthangarh | 137 | 05:00 | 127 | 18:30
| Banani | 137 | 05:00 | 123 | 13:00 | Manikganj | 132 | 22:00 | 125 | 12:00
| Bangabhaban | 135 | 04:00 | 124 | 13:00 | Maniknagar | 134 | 01:00 | 124 | 13:00
| Barapukuria | 135 | 00:00 | 128 | 18:00 | Matarbari | 126 | 02:00 | 116 | 18:30
| Barguna | 137 | 04:00 | 132 | 19:00 | Matuail | 135 | 02:00 | 127 | 13:00
| Barishal | 137 | 03:00 | 129 | 13:00 | Millgate | 138 | 04:00 | 128 | 12:00
| Barishal-230 | 138 | 03:00 | 130 | 13:00 | Mirpur | 136 | 05:00 | 125 | 13:00
| Baroaulia | 132 | 03:00 | 127 | 13:00 | Mirzapur | 130 | 05:00 | 123 | 12:00
| Baroirhat | 131 | 01:00 | 124 | 13:00 | Mithapukur | 135 | 04:00 | 125 | 08:00
| Bashundhara | 138 | 04:00 | 123 | 13:00 | MI_Cement | 137 | 04:00 | 127 | 13:00
| BashundharaCement | 135 | 04:00 | 127 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 135 | 03:00 | 131 | 11:00 | Mogbazar | 138 | 03:00 | 125 | 13:00
| Benapole | 140 | 04:00 | 122 | 13:00 | Mongla | 137 | 01:00 | 122 | 13:00
| Bhaluka | 129 | 04:00 | 117 | 13:00 | Motijheel | 135 | 04:00 | 124 | 13:00
| Bhandaria | 135 | 06:00 | 126 | 13:00 | Muktagacha | 126 | 09:00 | 118 | 08:00
| Bhangura | 138 | 01:00 | 132 | 13:00 | Munshiganj | 135 | 04:00 | 126 | 13:00
| Bheramara | 141 | 05:00 | 134 | 13:00 | Mymensingh | 126 | 00:00 | 112 | 13:00
| Bheramara(GK) | 141 | 02:00 | 134 | 13:00 | Naogaon | 136 | 02:00 | 127 | 18:30
| Bhulta | 127 | 23:00 | 120 | 10:00 | Narail | 141 | 03:00 | 126 | 13:00
| Bog-Sherpur | 138 | 05:00 | 129 | 18:30 | Narinda | 134 | 01:00 | 124 | 13:00
| Bogura | 137 | 05:00 | 130 | 18:00 | Narshingdi | 132 | 23:00 | 122 | 11:00
| Bogura-230 | 138 | 03:00 | 130 | 18:30 | Natore | 139 | 02:00 | 131 | 13:00
| Brahmanbaria | 134 | 23:00 | 127 | 11:00 | Nawabganj | 137 | 04:00 | 127 | 12:00
| Cantonment | 138 | 05:00 | 127 | 13:00 | Netrakona | 128 | 06:00 | 111 | 13:00
| Chandpur | 129 | 05:00 | 123 | 11:00 | New | 137 | 03:00 | 126 | 12:00
| Chandraghona | 135 | 04:00 | 129 | 13:00 | Niamatpur | 139 | 03:00 | 134 | 08:00
| Chapai | 138 | 01:00 | 132 | 20:00 | Noapara | 139 | 03:00 | 128 | 12:00
| Charsaidpur | 136 | 01:00 | 126 | 13:00 | Pabna | 139 | 05:00 | 128 | 13:00
| Chauddagram | 133 | 03:00 | 124 | 12:00 | Palashbari | 134 | 04:00 | 122 | 18:30
| Chhatak | 134 | 02:00 | 131 | 11:00 | Panchagarh | 137 | 02:00 | 123 | 18:30
| Chowmuhani | 128 | 02:00 | 122 | 11:00 | Patuakhali | 137 | 03:00 | 131 | 19:00
| Chuadanga | 141 | 02:00 | 126 | 13:00 | Payra | 138 | 05:00 | 133 | 14:00
| Coxsbazar | 125 | 02:00 | 117 | 18:30 | PHP | 131 | 04:00 | 123 | 13:00
| Cumilla(N) | 136 | 03:00 | 128 | 12:00 | Postogola | 138 | 02:00 | 130 | 12:00
| Cumilla(S) | 134 | 04:00 | 124 | 11:00 | Purbachal | 138 | 04:00 | 124 | 13:00
| Daudkandi | 134 | 02:00 | 126 | 12:00 | Purbasadipur | 132 | 03:00 | 121 | 18:30
| Dhaka | 136 | 02:00 | 125 | 13:00 | Rahanpur | 140 | 00:00 | 135 | 18:30
| Dhamrai | 134 | 23:00 | 128 | 13:00 | Rahanpur-400 | 140 | 01:00 | 135 | 18:00
| Dhanmondi | 136.5 | 02:00 | 126 | 13:00 | Rahim | 134 | 05:00 | 126 | 13:00
| Dohazari | 131 | 03:00 | 123 | 19:00 | Rajbari | 137 | 04:00 | 128 | 13:00
| Faridpur | 137 | 02:00 | 130 | 12:00 | Rajendrapur | 133 | 05:00 | 124 | 15:00
| Fatullah | 138 | 04:00 | 129 | 12:00 | Rajshahi | 139 | 23:00 | 131 | 13:00
| Fenchuganj | 138 | 00:00 | 134 | 13:00 | Rajshahi-230 | 140 | 03:00 | 129 | 13:00
| Feni | 130 | 01:00 | 123 | 19:00 | Ramganj | 127 | 02:00 | 122 | 11:00
| Ghatail | 128 | 09:00 | 118 | 11:00 | Rampur | 134 | 03:00 | 125 | 12:00
| Ghorashal | 139 | 04:00 | 130 | 00:00 | Rampura | 137 | 05:00 | 125 | 13:00
| Goalpara | 140 | 05:00 | 127 | 13:00 | Rangamati | 134 | 02:00 | 127 | 18:00
| Gollamari | 140 | 05:00 | 130 | 13:00 | Rangpur | 134 | 06:00 | 119 | 18:30
| Gopalganj | 139 | 04:00 | 129 | 13:00 | Ruppur | 142 | 06:00 | 134 | 13:00
| Gopalganj-400 | 139 | 05:00 | 130 | 13:00 | Saidpur | 132 | 04:00 | 123 | 18:00
| Gulshan | 135 | 01:00 | 125 | 12:00 | Satkhira | 138 | 01:00 | 125 | 13:00
| Halishahar | 134 | 05:00 | 128 | 12:00 | Satmasjid | 137 | 03:00 | 125 | 13:00
| Haripur | 135 | 04:00 | 126 | 13:00 | Savar | 133 | 00:00 | 122 | 12:00
| HaripurSBU | 135 | 04:00 | 127 | 11:00 | SevenRings | 141 | 05:00 | 132 | 13:00
| Hasnabad | 139 | 03:00 | 128 | 2:00 | ShahCement | 136 | 01:00 | 126 | 13:00
| Hathazari | 136 | 05:00 | 131 | 18:30 | Shahjadpur | 142 | 02:00 | 135 | 12:00
| Ishurdi | 143 | 05:00 | 135 | 13:00 | Shahjibazar | 136 | 22:00 | 131 | 11:00
| Jaldhaka | 132 | 06:00 | 120 | 18:30 | Shahmirpur | 133 | 03:00 | 127 | 18:30
| Jamalpur | 126 | 00:00 | 112 | 06:00 | Shariatpur | 138 | 05:00 | 129 | 13:00
| Jashore | 140 | 03:00 | 125 | 13:00 | Sherpur | 132 | 09:00 | 112 | 06:00
| Jhenaidah | 142 | 04:00 | 127 | 13:00 | Shikalbaha | 124 | 03:00 | 116 | 13:00
| Jhenaidah-230 | 142 | 03:00 | 128 | 13:00 | Shikalbaha-230 | 134 | 03:00 | 127 | 19:00
| Joydebpur | 138 | 03:00 | 128 | 16:00 | Shitalakhya | 137 | 04:00 | 127 | 13:00
| Joypurhat | 137 | 02:00 | 128 | 08:00 | Sholosohor | 134 | 01:00 | 128 | 12:00
| Juldah | 133 | 01:00 | 126 | 18:30 | Shyampur | 137 | 05:00 | 133 | 18:00
| Kabirpur | 137 | 09:00 | 125 | 12:00 | Shyampur-230 | 138 | 04:00 | 128 | 13:00
| Kachua | 131 | 03:00 | 124 | 11:00 | Siddhirganj | 133 | 00:00 | 127 | 13:00
| Kaliakoir | 138 | 04:00 | 128 | 12:00 | Sirajganj | 138 | 00:00 | 130 | 18:30
| Kallyanpur | 137 | 02:00 | 128 | 12:00 | Sonargaon | 131 | 00:00 | 126 | 16:00
| Kalurghat | 133 | 04:00 | 128 | 19:00 | Sreemongol | 135 | 04:00 | 131 | 11:00
| Kamrangirchar | 136 | 01:00 | 127 | 13:00 | Sreepur | 131 | 05:00 | 122 | 13:00
| Kaptai | 138 | 3:00 | 133 | 21:00 | Srinagar | 138 | 04:00 | 127 | 13:00
| Kazla | 136 | 05:00 | 124 | 13:00 | SSM | 135 | 06:00 | 128 | 14:00
| Keranigonj | 137 | 05:00 | 121 | 18:00 | Sunamganj | 133 | 03:00 | 130 | 11:00
| Khagrachori | 135 | 04:00 | 127 | 13:00 | Sylhet | 135 | 02:00 | 132 | 13:00
| Khulna | 140 | 04:00 | 126 | 13:00 | Sylhet-132 | 134 | 00:00 | 132 | 13:00
| Khulna(S) | 141 | 03:00 | 129 | 13:00 | Tangail | 131 | 09:00 | 120 | 11:00
| Khulshi | 133 | 06:00 | 126 | 13:00 | Thakurgaon | 134 | 05:00 | 121 | 08:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 133 | 04:00 | 124 | 08:00 | TK | 134 | 04:00 | 129 | 12:00 |  |  | Nos | Nos | Nos
| Kodda | 133 | 07:00 | 123 | 12:00 | Tongi | 138 | 00:00 | 129 | 12:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 135 | 02:00 | 128 | 11:00 | Ullahpara | 140 | 03:00 | 132 | 13:00
| Kulaura | 138 | 07:00 | 134 | 18:00 | Ullon | 135 | 00:00 | 125 | 13:00
| UttaraNew | 136 | 01:00 | 123 | 12:00 | Uttara | 136 | 03:00 | 124 | 12:00
| Zigatola | 139 | 04:00 | 126 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.