## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-01-2025 | during | 22-01-2025 | during | 22-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 402 | 402 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 370 | 450 | 450 | 300 | 300 | Gas shortage
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 258 | 251 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 32 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 17 | 15 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 26 | 22 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 25 | 26 | 52.19 | 52.19 | 26 | 26 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 68 | 91 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 88 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 45 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 11 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 36 | 36 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6257.05 | 5842.27 | 1376 | 1833 | 4607.99 | 4585.99 | 2749.74 | 2727.74
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 228 | 161 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 72 | 72 | 72 | 72 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 15 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 1 | 0 | 3.9 | 0 | 3.9 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 25 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 850 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 1 | 10 | 5 | 26 | 5 | 26 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 997 | 370 | 1150 | 1150 | 1050 | 1050 | -
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2126 | 1864 | 4055.62 | 4070.72 | 3955.62 | 3970.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 182 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | schedule outage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 41 | 42 | 46.94 | 46.94 | 46.94 | 46.94 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 192 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 70 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 50 | 46 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 68 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 68 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 34 | 0 | 69 | 0 | 69 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 635 | 771 | 1677.97 | 1608.97 | 1545.14 | 1476.14
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 6 | 210 | 210 | 15 | 15 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 200 | 200 | 58 | 58 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 9 | 115 | 115 | 9 | 9 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 7.33 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 24 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 108.33 | 97 | 648.5 | 601.5 | 205.5 | 158.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 30 | 30 | 30 | 30 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 10 | 10 | 44 | 44 | 10 | 10 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 203 | 203 | 210 | 210 | 210 | 210 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 25 | 25 | 13 | 13 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 285 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 336 | 380 | 380 | 380 | 380 | FGMO Available, but GT Load set maximum 260MW
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 256 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1460 | 1477 | 1621.5 | 1621.5 | 1551.01 | 1551.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 918 | 920 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 307 | 254 | 410 | 410 | 310 | 310 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 37.73 | 0 | 67.5 | 0 | 67.5 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 220 | 220 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1262.73 | 1174 | 3456.5 | 3389 | 1672.52 | 1605.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 0 | 218.79 | 400 | 450 | 400 | 450 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 135 | 135 | 135 | 135 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 980 | 1200 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.25 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 1595.25 | 2146.79 | 2577.12 | 2626.12 | 2534 | 2583
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 153 | 171 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 193 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 186 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 2.14 | 0 | 4.55 | 0 | 4.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 645.53 | 760 | 1347.54 | 1347.54 | 800 | 800 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 24.51 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 35 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1231.18 | 1366.5 | 2772.54 | 2617.99 | 2154 | 1999.45
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 72 | 70 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 211 | 200 | 200 | 210 | 210 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.1 | 0 | 3.8 | 0 | 3.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 4 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 32 | 0 | 125 | 0 | 125 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 270.1 | 281 | 690.8 | 532 | 666.82 | 508.02
System Total |  |  |  |  | 29054.66 | 28387.248 | 10064.59 | 11010.29 | 22108.54 | 21653.79 | 17034.35 | 16579.6
Forecast Scenario (22-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9010 |  | 0 |  | 9010
|  |  |  | 1:00 | 8430 |  | 0 |  | 8430
|  |  |  | 2:00 | 8090 |  | 0 |  | 8090
|  |  |  | 3:00 | 7750 |  | 0 |  | 7750
|  |  |  | 4:00 | 7550 |  | 0 |  | 7550
|  |  |  | 5:00 | 7520 |  | 0 |  | 7520
|  |  |  | 6:00 | 7960 |  | 0 |  | 7960
|  |  |  | 7:00 | 8750 |  | 0 |  | 8750
|  |  |  | 8:00 | 9610 |  | 0 |  | 9610
|  |  |  | 9:00 | 9660 |  | 0 |  | 9660
|  |  |  | 10:00 | 9750 |  | 0 |  | 9750
|  |  |  | 11:00 | 9780 |  | 0 |  | 9780
|  |  |  | 12:00 | 10370 |  | 0 |  | 10370
|  |  |  | 13:00 | 10540 |  | 0 |  | 10540
|  |  |  | 14:00 | 10230 |  | 0 |  | 10230
|  |  |  | 15:00 | 9750 |  | 0 |  | 9750
|  |  |  | 16:00 | 9570 |  | 0 |  | 9570
|  |  |  | 17:00 | 9760 |  | 0 |  | 9760
|  |  |  | 18:00 | 10630 |  | 0 |  | 10630
|  |  |  | 18:30 | 10800 |  | 0 |  | 10800
|  |  |  | 19:00 | 10960 |  | 0 |  | 10960
|  |  |  | 19:30 | 10860 |  | 0 |  | 10860
|  |  |  | 20:00 | 10740 |  | 0 |  | 10740
|  |  |  | 21:00 | 10470 |  | 0 |  | 10470
|  |  |  | 22:00 | 10080 |  | 0 |  | 10080
|  |  |  | 23:00 | 9600 |  | 0 |  | 9600
Probable Maximum Temperature: |  |  | 25.70°C
Probable Maximum Demand at Day Peak: |  |  | 10370.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End): |  |  |  |  | 0
Probable Maximum Demand at Evening Peak: |  |  | 10960.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10960.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 226.56 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yesterday (21-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 24.60°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 832.72
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 21.2342 | Peak Hour Flow: |  | 920.00 MW at 19:00 hrs.
Energy Flow from West to East |  | 9415363.716 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 13.8298 | Peak Hour Flow: |  | 760.00 MW at 19:00 hrs.
Power Flow during Peak Demand |  | 496 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.1645 | Peak Hour Flow: |  | 46.00 MW at 19:00 hrs.
Maximum Power Flow |  | 886 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 36.2285 | Peak Hour Flow: |  | 1726.00 MW at 19:00 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-01-2025 | [28 empty] | Date: | 21-01-2025 | [28 empty] | Date: | 21-01-2025 | [28 empty] | Date: | 21-01-2025 | [28 empty] | Date: | 21-01-2025 | [19 empty] | Date: | 21-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [19 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 150.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 17 | 0 | 56 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 249 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 33 | 900 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 47 | 0 | 45 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 280 | 320 | 380 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 203 | 0 | 19 | 58 | 6 | 0 | 0 | 24 | 5511 | 920 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 182 | 0 | 188 | 0 | 0 | 0 | 0 | 8.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 180 | 0 | 0 | 700 | 0 | 3649.5 | 9160.5 | 92.7
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 258 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 35 | 810 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 610 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 29 | 182 | 47 | 0 | 45 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 275 | 320 | 369 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 30 | 0 | 0 | 204 | 0 | 9 | 24 | 11 | 0 | 0 | 16 | 4992 | 919 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 180 | 0 | 0 | 640 | 0 | 3420.5 | 8412.5 | 92.7
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 269 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 35 | 760 | 0 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 | 610 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 5 | 182 | 47 | 0 | 45 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 280 | 320 | 370 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 30 | 0 | 0 | 204 | 0 | 9 | 9 | 11 | 0 | 0 | 0 | 4901 | 813 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 180 | 0 | 0 | 560 | 0 | 3233.5 | 8134.5 | 92.7
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 261 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 35 | 764 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 600 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 5 | 182 | 5 | 0 | 45 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 275 | 320 | 370 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 20 | 0 | 0 | 203 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 4674 | 730 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 0 | 520 | 0 | 3043.5 | 7717.5 | 92.7
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 265 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 40 | 763 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 600 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 5 | 182 | 5 | 0 | 45 | 0 | 0 | 15 | 0 | 40 | 0 | 0 | 0 | 275 | 320 | 320 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 5 | 20 | 0 | 0 | 203 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 4570 | 730 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 0 | 500 | 0 | 2984.5 | 7554.5 | 92.7
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 274 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 40 | 762 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 600 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 5 | 182 | 5 | 0 | 45 | 0 | 0 | 15 | 0 | 40 | 0 | 0 | 0 | 305 | 300 | 310 | 10 | 30 | 0 | 2 | 140 | 13 | 0 | 5 | 20 | 0 | 0 | 203 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 4320 | 729 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 220 | 0 | 0 | 500 | 0 | 3037.5 | 7357.5 | 92.69
06:00 | 0 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 260 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 40 | 763 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 665 | 0 | 5 | 0 | 78 | 0 | 0 | 0 | 5 | 188 | 5 | 0 | 45 | 0 | 0 | 11 | 0 | 46 | 0 | 0 | 0 | 310 | 290 | 311 | 10 | 30 | 0 | 2 | 140 | 13 | 0 | 5 | 20 | 0 | 0 | 203 | 0 | 18 | 56 | 13 | 0 | 0 | 0 | 4648 | 730 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 220 | 0 | 0 | 530 | 0 | 3065.5 | 7713.5 | 92.69
07:00 | 0 | 22 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 313 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 1 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 39 | 905 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 690 | 1 | 32 | 0 | 125 | 0 | 0 | 0 | 6 | 210 | 44 | 0 | 45 | 0 | 0 | 10 | 0 | 48 | 0 | 2 | 0 | 300 | 284 | 367 | 10 | 30 | 0 | 2 | 140 | 13 | 0 | 50 | 20 | 0 | 0 | 203 | 0 | 18 | 56 | 13 | 0 | 0.3 | 6 | 5202.3 | 824 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.48 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0.04 | 0 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.01 | 0 | 200 | 6 | 140 | 220 | 0 | 0 | 650 | 0 | 3494.53 | 8696.83 | 92.69
08:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 24 | 0 | 42 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 420 | 273 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 5 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 0 | 11 | 995 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 808 | 6 | 51 | 0 | 184 | 0 | 0 | 0 | 25 | 182 | 41 | 0 | 45 | 0 | 0 | 11 | 0 | 44 | 0 | 16 | 0 | 295 | 266 | 368 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 203 | 0 | 19 | 56 | 10 | 0 | 4.11 | 18 | 5576.11 | 920 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 560.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8.26 | 149 | 0 | 156 | 0 | 175 | 0 | 0 | 0 | 0.89 | 0 | 166 | 71 | 0 | 1 | 0 | 0 | 0 | 0.4 | 14 | 0.11 | 0 | 250 | 5 | 140 | 220 | 0 | 0 | 820 | 0 | 3995.88 | 9571.99 | 92.69
09:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 36 | 0 | 68 | 16 | 0 | 0 | 0 | 45 | 17 | 0 | 370 | 258 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 11 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 35 | 0 | 2 | 997 | 0 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 | 850 | 12 | 51 | 0 | 192 | 0 | 0 | 0 | 29 | 182 | 41 | 0 | 45 | 0 | 0 | 11 | 0 | 50 | 0 | 34 | 0 | 300 | 256 | 368 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 203 | 0 | 19 | 58 | 5 | 1 | 7.33 | 18 | 5705.33 | 918 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.73 | 0 | 0 | 645.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 24.51 | 153 | 0 | 181 | 0 | 190 | 0 | 0 | 0 | 2.14 | 0 | 161 | 72 | 0 | 4 | 0 | 0 | 0 | 1.1 | 32 | 0.25 | 0 | 250 | 5 | 140 | 220 | 0 | 0 | 980 | 0 | 4359.26 | 10064.59 | 92.69
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 36 | 0 | 68 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 267 | 0 | 0 | 0 | 24 | 167 | 0 | 0 | 19 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 35 | 0 | 2 | 851 | 0 | 0 | 0 | 0 | 0 | 229 | 0 | 0 | 0 | 850 | 16 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 182 | 41 | 0 | 45 | 0 | 0 | 11 | 0 | 58 | 0 | 50 | 0 | 280 | 260 | 368 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 204 | 0 | 19 | 58 | 5 | 1 | 17.09 | 18 | 5671.09 | 920 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.33 | 0 | 0 | 654.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 37.41 | 172 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 3.13 | 0 | 210 | 72 | 0 | 7 | 0 | 0 | 0 | 1.9 | 50 | 0.39 | 0 | 200 | 5 | 100 | 180 | 0 | 0 | 860 | 0 | 4209.03 | 9880.12 | 92.69
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 36 | 0 | 68 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 305 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 22 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 35 | 0 | 2 | 850 | 0 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 850 | 19 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 201 | 36 | 0 | 45 | 0 | 0 | 11 | 0 | 52 | 0 | 58 | 0 | 290 | 300 | 370 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 205 | 0 | 19 | 58 | 5 | 2 | 33.59 | 18 | 5633.59 | 920 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.96 | 0 | 0 | 611.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 46.84 | 181 | 0 | 180 | 0 | 171 | 0 | 0 | 0 | 3.27 | 0 | 210 | 74 | 0 | 14 | 0 | 0 | 0 | 2 | 110 | 0.47 | 0 | 200 | 4 | 138 | 180 | 0 | 0 | 800 | 0 | 4282.2 | 9915.79 | 92.68
12:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 36 | 0 | 55 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 420 | 317 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 25 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 35 | 0 | 2 | 420 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 950 | 19 | 51 | 0 | 197 | 0 | 0 | 0 | 28 | 202 | 35 | 0 | 42 | 1 | 0 | 11 | 0 | 60 | 0 | 63 | 0 | 310 | 320 | 370 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 209 | 0 | 19 | 58 | 5 | 2 | 37.35 | 18 | 5524.35 | 919 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.31 | 0 | 0 | 621.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 53.02 | 182 | 0 | 203 | 0 | 194 | 0 | 0 | 0 | 4.15 | 2.5 | 210 | 71 | 0 | 21 | 0 | 0 | 0 | 4.7 | 126 | 0.52 | 0 | 261 | 4 | 136 | 220 | 0 | 0 | 840 | 3 | 4511.05 | 10035.4 | 92.68
13:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 14 | 36 | 0 | 48 | 16 | 0 | 4 | 17 | 72 | 25 | 0 | 370 | 240 | 0 | 0 | 17 | 22 | 21 | 0 | 0 | 23 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 6 | 407 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 1100 | 19 | 51 | 20 | 199 | 0 | 0 | 0 | 29 | 182 | 42 | 19 | 40 | 15 | 17 | 17 | 0 | 60 | 0 | 56 | 0 | 280 | 320 | 370 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 206 | 10 | 19 | 58 | 5 | 2 | 35.06 | 14 | 5610.06 | 920 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.58 | 0 | 0 | 743.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 78 | 0 | 50.69 | 181 | 0 | 209 | 0 | 210 | 0 | 0 | 0 | 4.46 | 2.5 | 210 | 70 | 34 | 21 | 10 | 0 | 0 | 4.5 | 119 | 0.5 | 0 | 307 | 5 | 100 | 220 | 0 | 0 | 1130 | 17 | 5000.66 | 10610.72 | 92.68
14:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 35 | 36 | 0 | 19 | 16 | 0 | 15 | 0 | 72 | 25 | 0 | 370 | 263 | 0 | 0 | 0 | 22 | 106 | 0 | 0 | 20 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 4 | 410 | 0 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 1100 | 16 | 51 | 20 | 199 | 0 | 0 | 0 | 29 | 183 | 44 | 34 | 40 | 17 | 17 | 17 | 0 | 58 | 0 | 44 | 0 | 300 | 320 | 312 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 207 | 0 | 19 | 58 | 5 | 1 | 28.89 | 12 | 5628.89 | 920 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.79 | 0 | 0 | 702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 42.76 | 176 | 0 | 206 | 0 | 204 | 0 | 0 | 0 | 3.77 | 2.5 | 210 | 70 | 0 | 18 | 0 | 0 | 0 | 3.8 | 99 | 0.44 | 0 | 250 | 4 | 100 | 180 | 0 | 0 | 1100 | 0 | 4626.06 | 10254.95 | 92.68
15:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 36 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 25 | 0 | 320 | 276 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 14 | 0 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 410 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 1005 | 12 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 41 | 25 | 40 | 0 | 0 | 17 | 0 | 50 | 0 | 35 | 0 | 275 | 320 | 289 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 207 | 0 | 9 | 58 | 5 | 1 | 19.89 | 12 | 5407.89 | 921 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.01 | 0 | 0 | 574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 21.43 | 174 | 0 | 150 | 0 | 197 | 0 | 0 | 0 | 2.32 | 2.5 | 210 | 70 | 0 | 12 | 0 | 0 | 0 | 2.7 | 70 | 0.32 | 0 | 200 | 4 | 100 | 180 | 0 | 22.78 | 1080 | 0 | 4292.06 | 9699.95 | 92.68
16:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 36 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 25 | 0 | 320 | 314 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 7 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 371 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 1005 | 7 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 216 | 40 | 16 | 40 | 0 | 0 | 17 | 0 | 52 | 0 | 17 | 0 | 305 | 320 | 362 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 30 | 0 | 0 | 207 | 0 | 9 | 58 | 5 | 0 | 10.15 | 8 | 5458.15 | 920 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.12 | 0 | 0 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 12.01 | 174 | 0 | 150 | 0 | 191 | 0 | 0 | 0 | 1.13 | 2.5 | 210 | 70 | 0 | 6 | 0 | 0 | 0 | 1.4 | 32 | 0.16 | 0 | 200 | 4 | 140 | 180 | 0 | 84.33 | 1040 | 0 | 4143.65 | 9601.8 | 92.68
17:00 | 0 | 80 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 1 | 36 | 0 | 33 | 16 | 0 | 0 | 1 | 35 | 25 | 0 | 320 | 279 | 0 | 0 | 12 | 22 | 335 | 0 | 0 | 2 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 1 | 3 | 0 | 40 | 0 | 7 | 371 | 9 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1005 | 1 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 184 | 40 | 16 | 50 | 12 | 5 | 17 | 0 | 46 | 0 | 3 | 0 | 305 | 320 | 333 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 205 | 0 | 19 | 57 | 5 | 0 | 2.07 | 24 | 5460.07 | 920 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.91 | 0 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 2.4 | 174 | 0 | 193 | 0 | 191 | 0 | 0 | 0 | 0.22 | 2.5 | 210 | 70 | 0 | 1 | 0 | 0 | 0 | 0.2 | 8 | 0.04 | 0 | 200 | 5 | 140 | 220 | 0 | 156.93 | 1000 | 2 | 4231.2 | 9691.27 | 92.67
18:00 | 0 | 100 | 22 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 27 | 36 | 0 | 45 | 32 | 0 | 10 | 17 | 108 | 25 | 5 | 370 | 267 | 0 | 0 | 17 | 22 | 335 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 18 | 0 | 0 | 0 | 13 | 0 | 3 | 0 | 12 | 12 | 0 | 40 | 12 | 5 | 370 | 17 | 0 | 12 | 0 | 11 | 161 | 0 | 0 | 0 | 1180 | 0 | 51 | 18 | 195 | 0 | 0 | 0 | 28 | 182 | 40 | 41 | 70 | 17 | 42 | 17 | 0 | 46 | 0 | 0 | 0 | 290 | 320 | 335 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 204 | 17 | 9 | 57 | 5 | 0 | 0 | 24 | 6038 | 920 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 9 | 0 | 0 | 0 | 171 | 0 | 193 | 0 | 189 | 0 | 0 | 0 | 0 | 2.5 | 210 | 70 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 6 | 140 | 220 | 0 | 184.19 | 1030 | 17 | 4582.69 | 10620.69 | 92.67
19:00 | 0 | 88 | 26 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 36 | 0 | 91 | 32 | 0 | 0 | 0 | 108 | 25 | 0 | 370 | 251 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 25 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 370 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 42 | 68 | 70 | 0 | 68 | 17 | 0 | 46 | 0 | 0 | 0 | 285 | 320 | 336 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 203 | 0 | 9 | 58 | 6 | 0 | 0 | 24 | 6042 | 920 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 193 | 0 | 186 | 0 | 0 | 0 | 0 | 5.5 | 211 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 218.79 | 1200 | 54 | 4968.29 | 11010.29 | 92.67
19:30 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 36 | 0 | 91 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 370 | 299 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 371 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 201 | 43 | 69 | 70 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 315 | 320 | 335 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 205 | 0 | 9 | 58 | 7 | 0 | 0 | 24 | 5950 | 920 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 191 | 0 | 183 | 0 | 0 | 0 | 0 | 5.5 | 211 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 220 | 1210 | 54 | 4917.5 | 10867.5
20:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 36 | 0 | 96 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 370 | 260 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 370 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 43 | 68 | 70 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 305 | 320 | 335 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 204 | 0 | 9 | 58 | 8 | 0 | 0 | 24 | 5899 | 919 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 189 | 0 | 183 | 0 | 0 | 0 | 0 | 5.5 | 210 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 219.48 | 1212 | 54 | 4911.98 | 10810.98 | 92.67
21:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 0 | 85 | 16 | 0 | 0 | 0 | 17 | 25 | 0 | 300 | 259 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 370 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 43 | 68 | 70 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 295 | 320 | 336 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 203 | 0 | 9 | 58 | 8 | 0 | 0 | 24 | 5738 | 919 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 188 | 0 | 180 | 0 | 0 | 0 | 0 | 5.5 | 210 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 219.32 | 1212 | 54 | 4906.82 | 10644.82 | 92.67
22:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 260 | 0 | 0 | 0 | 22 | 280 | 0 | 0 | 0 | 0 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 373 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1130 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 43 | 0 | 70 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 270 | 320 | 336 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 208 | 0 | 9 | 58 | 8 | 0 | 0 | 24 | 5424.5 | 920 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 681 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 188 | 0 | 175 | 0 | 0 | 0 | 0 | 5.5 | 210 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 140 | 220 | 0 | 220.02 | 1200 | 0 | 4707.52 | 10132.02 | 92.67
23:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 282 | 0 | 0 | 0 | 22 | 280 | 0 | 0 | 0 | 0 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 371 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 930 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 195 | 44 | 0 | 50 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 295 | 300 | 336 | 10 | 30 | 0 | 2 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 207 | 0 | 9 | 58 | 5 | 0 | 0 | 24 | 5219.5 | 920 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 188 | 0 | 172 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 140 | 220 | 0 | 219 | 1000 | 0 | 4348.5 | 9568 | 92.66
Total KWH | 0 | 1172160 | 428640 | 0 | 0 | 0 | 0 | 0 | 9302400 | 0 | 0 | 170640 | 625680 | 0 | 1025424 | 221280 | 0 | 49217 | 52644 | 744489 | 519480 | 11520 | 8331000 | 6669498 | 0 | 0 | 77467 | 555200 | 4467229 | 0 | 0 | 147858 | 0 | 376200 | 353880 | 0 | 0 | 79036 | 0 | 0 | 0 | 282240 | 0 | 14353 | 0 | 16320 | 14400 | 21238 | 827280 | 25090 | 458880 | 14509090.91 | 15055 | 0 | 75840 | 0 | 27599 | 4668127 | 0 | 0 | 0 | 21703634 | 126630 | 1028087 | 122109 | 3964364 | 0 | 0 | 0 | 549600 | 4558000 | 854064 | 379200 | 1168450 | 85440 | 177240 | 345410 | 0 | 1164480 | 0 | 380127 | 0 | 7132000 | 7379700 | 8608000 | 358200 | 716000 | 0 | 56976 | 3671427.2 | 339744 | 0 | 1532160 | 305856 | 0 | 0 | 4188320 | 48240 | 289200 | 1132800 | 165120 | 9400 | 197910 | 364320 | 129438663.11 | 21234181 | 6052032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476640 | 0 | 0 | 13829818 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 0 | 0 | 28066 | 496170 | 0 | 306748 | 4134427 | 0 | 4355255 | 0 | 4400182 | 0 | 0 | 0 | 25440 | 80640 | 5038000 | 1645963 | 90158 | 106145 | 17107 | 0 | 0 | 22849.56 | 649440 | 3208.5 | 0 | 5367000 | 142204 | 2957000 | 5138730 | 0 | 1665454 | 21764363.64 | 224400 | 100251621.83 | 229690284.94

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 21-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 10064.59 | MW | 09:00 Hr. | Energy Generated |  |  | 229690.2849 |  | MWHr
Day Peak Demand |  |  | 10090.59 | MW | 09:00 Hr. | Energy Unserverd |  |  | 404 |  | MWHr
Evening Peak Generation |  |  | 11010.29 | MW | 19:00 Hr. | Energy Demand |  |  | 230094.2849 |  | MWHr
Evening Peak Demand |  |  | 11067.29 | MW | 19:00 Hr.
Minimum Generation of the Day |  |  | 7357.5 | MW | 05:00 Hr.
Maximum Generation of the Day |  |  | 11010.29 | MW | 19:00 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 30574.887 | 0 | 4579.161 | 0 | 0 | 147.858 | 0 | 0 | 35301.906 | Gas | 109883.8422 | Gas | 392666145.844
Chattogram Zone |  |  | 5127.007 | 36212.7249 | 267.693 | 0 | 827.28 | 147.868 | 0 | 282.24 | 42864.8129 | Coal | 71693.5056 | Coal | 496001381.396
Cumilla Zone |  |  | 12467.975 | 0 | 763.989 | 0 | 0 | 380.127 | 1164.48 | 0 | 14776.571 | HFO | 7805.1341 | HFO | 146882354.7876
Mymensingh Zone |  |  | 165.12 | 0 | 1834.56 | 0 | 0 | 207.31 | 0 | 0 | 2206.99 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 34288.3832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34288.3832 | Hydro | 827.28 | Hydro | 82728
Khulna Zone |  |  | 6052.032 | 0 | 0 | 0 | 0 | 476.64 | 21234.181 | 0 | 27762.853 | Solar | 2969.8041 | Solar | 45601165.661
Barishal Zone |  |  | 8237.934 | 28796.8176 | 224.4 | 0 | 0 | 3.2085 | 0 | 0 | 37262.3601 | Import | 36228.479 | Import | 178505761.6
Rajshahi Zone |  |  | 12970.504 | 0 | 28.0661 | 0 | 0 | 828.358 | 13829.818 | 0 | 27656.7461 | Wind | 282.24 | Wind | 4402944
Rangpur Zone |  |  | 0 | 6683.963 | 107.265 | 0 | 0 | 778.4346 | 0 | 0 | 7569.6626
Total |  |  | 109883.8422 | 71693.5056 | 7805.1341 | 0 | 827.28 | 2969.8041 | 36228.479 | 282.24 | 229690.2849
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 392666145.844 |  | Hydro | 82728
|  |  | Coal | 496001381.396 |  | Solar | 45601165.661
|  |  | HFO | 146882354.7876 |  | Import | 178505761.6
|  |  | HSD | 0 |  | Wind | 4402944
|  |  |  | Total: | 1264142481.2886 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
| 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
| 4 | Barapukuria TPP Unit-2 |  |  | 85
| 5 | Khulna 330 MW CCPP ST |  |  | 110
| 6 | Siddhirgonj 210 MW TPP |  |  | 115
| 7 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1184 |  |  |  | Total | 435.09
|  |  | Total Unavailable Capacity |  |  |  | 1619.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 30 |  | 3968
|  |  | Chattogram |  | 0 |  | 1099
|  |  | Cumilla |  | 0 |  | 902
|  |  | Mymensingh |  | 25 |  | 951
|  |  | Sylhet |  | 0 |  | 374
|  |  | Khulna |  | 0 |  | 1196
|  |  | Barishal |  | 0 |  | 294
|  |  | Rajshahi |  | 0 |  | 1029
|  |  | Rangpur |  | 0 |  | 693
|  |  | Total |  | 55 |  | 10506
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:16 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
08:16 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
08:18 | 11:37 | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D Due to Maintenance Work
08:18 | 11:39 | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D Due to Maintenance Work
08:35 | 16:34 | Candpur (Desh)- Chandpur 132kV Ckt-1 Scheduled S/D from Chandpur 132/33kV end Due to
Annual Maintenance
08:35 | 13:44 | Chandraghona-Madunaghat 132 kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to
Disk Maintenance.
08:39 | 16:07 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-02 Scheduled S/D Due to Annual maintenance
08:41 | 13:13 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to Dead
line checking.
08:41 | 13:17 | Keraniganj-Sreenagar 132kV Ckt-1 Scheduled S/D from Srinagar 132/33kV end Due to
Keraniganj ckt-01 shutdown for dead line checking. and from Keranigonj 230/132/33kV end
Due to Dead line checking.
08:52 | 16:45 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D Due to Bay extension work by
IDRNPP Project.
08:56 | 17:17 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual maintenance dead line checking
09:00 |  | Minimum generation 10062MW
09:00 |  | Day peak Generation is 10062 MW
09:07 | 21:27 | Goalpara- Khulna (C) 132kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to Re
conductoring and from Khulna (C) end Due to Shut down by ALDC Khulna
09:08 | 21:27 | Goalpara- Khulna (C) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to Shutdown by
ALDC Khulna
09:09 | 16:39 | Baroaulia 132/33kV S/S T-1(405T) LT Scheduled S/D Due to Oil leakage maintenance work | [7 empty] | 10.0MW load
interrup.
09:10 | 16:37 | Baroaulia 132/33kV S/S T-1(405T) HT Scheduled S/D Due to Oil leakage maintenance work | [7 empty] | 10.0MW load
interrup.
09:10 | 14:09 | Khulna(S) 230/132kV S/S TR-3 LT Scheduled S/D Due to Yearly Maintenance Work.
09:11 | 14:07 | Khulna(S) 230/132kV S/S TR-3 HT Scheduled S/D Due to Yearly Maintenance Work.
09:11 | 15:45 | Cumilla(S) 132/33kV S/S Cumilla North-2 Scheduled S/D Due to A/M
09:22 | 11:13 | Ashuganj-Shahjibazar 132kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to
shutdown taken by ashugonj end
09:26 | 15:29 | Fenchuganj 230/132/33kV S/S TR-01 LT Scheduled S/D Due to Tan Delta Test
09:28 | 15:15 | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to Tan Delta Test
09:31 | 21:21 | Bhulta 400/230kV S/S 230kV Bus-02 Project Work S/D
09:47 | 13:56 | Fatullah 132/33kV S/S 132/33 kV GT-1 HT Scheduled S/D Due to Schedule Shutdown for
maintenance
10:08 | 21:28 | Goalpara- Khulna (C) 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to Re
conductoring
10:10 |  | Tongi 230/132/33kV S/S T-03 LT Scheduled S/D Due to Annual Maintenance Work
10:10 |  | Tongi 230/132/33kV S/S T-03 HT Scheduled S/D Due to Annual Maintenance Work
10:19 | 21:07 | Bhulta-Haripur 230 kV Ckt-1 Project Work S/D from Bhulta 400/230kV end. and from Haripur
230/132kV end Due to from nldc
10:19 | 21:07 | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to from nldc and
from Bhulta 400/230kVend.
10:27 | 16:01 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Kishoreganj 132/33kV end.
10:28 | 12:37 | Jhenaidah 230/132kV S/S Transformer- 2 LT Scheduled S/D Due to Annual maintenance
10:29 | 12:36 | Jhenaidah 230/132kV S/S Transformer- 2 HT Scheduled S/D Due to Annual maintenance
10:39 | 15:26 | Baghabari 230/132kV S/S Bus-1 Scheduled S/D Due to A/M
10:56 |  | Bogura 230/132kV S/S T-02 LT Scheduled S/D
10:56 |  | Bogura 230/132kV S/S T-02 HT Scheduled S/D
11:05 | 15:58 | Thakurgaon 132/33kV S/S T-2(412T) HT Scheduled S/D Due to টি-২ ট্রান্সফরমারের LT বুশিং
ক্লাম্প এলাইনমেন্ট পরিবর্তন।
11:05 | 16:01 | Thakurgaon 132/33kV S/S T-2(412T) LT Scheduled S/D Due to টি-২ ট্রান্সফরমারের LT বুশিং
ক্লাম্প এলাইনমেন্ট পরিবর্তন।
11:49 |  | Rangpur 132/33kV S/S T-1(414T) LT Project Work S/D Due to 132kv CB,CT,PT, Changes
11:50 |  | Rangpur 132/33kV S/S T-1(414T) HT Project Work S/D Due to 132kv CB,CT,PT, Changes
12:09 | 12:51 | Sonargaon 132/33kV S/S OPSL(IEL-2) Tripped showing Line distance protection relay.
(General trip) relays Due to Line trip.
12:12 | 12:12 | Kabirpur 132/33kV S/S XFR, T-3 LT Tripped showing Micom P127 relays. | [7 empty] | 30.0MW load
interrup.
| 12:12 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
13:10 | 20:16 | Kabirpur 132/33kV S/S XFR, T-3 HT Forced S/D Due to Maintenance by DPBS-1 | [7 empty] | 30.0MW load
interrup.
13:46 | 16:11 | Ramganj 132/33kV S/S Ramgonj- Desh Energy Ckt-01 Scheduled S/D Due to Annual maintenance
work
13:49 | 15:44 | Chandraghona-Madunaghat 132 kV Ckt-1 Forced S/D from Chandraghona 132/33kV end Due to
Disc insulator change and from Madunaghat 132/33kV end Due to Disk Maintenance
15:34 | 16:55 | Fenchuganj 230/132/33kV S/S TR-02 LT Scheduled S/D Due to Annual maintenance
15:39 | 16:40 | Fenchuganj 230/132/33kV S/S TR-02 HT Scheduled S/D Due to Annual maintenance
| 16:06 | HVDC Bheramera- Rajshahi 230kV Ckt-2 is restored.
16:20 |  | Ghatail 132/33kV S/S T-2 LT Forced S/D Due to Unusual noise coming from the PT in 33kV
Bus Section-2.
| 16:56 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) HT is restored.
| 16:58 | Bog-Sherpur 132/33kV S/S Transformer-2 (414T) LT is restored.
| 17:22 | Aminbazar-Kallyanpur 132kV Ckt-2 is restored.
19:00 |  | Evening Peak Generation: 11009 MW.
| 19:34 | Jamalpur 132/33kV S/S T-2 HT is restored.
| 19:34 | Jamalpur 132/33kV S/S T-2 LT is restored.
| 19:39 | Kabirpur -Kodda 132kV Ckt-1 is restored.
20:16 |  | Kabirpur 132/33kV S/S XFR, T-3 LT Tripped showing Micom P127 relays. | [7 empty] | 30.0MW load
interrup.
21:35 | 22:30 | Chowmuhani 132/33kV S/S TR2 Forced S/D Due to 33kv T2 Y Pase Red hot.
00:53 |  | Matarbari 2*600 MW (CPGCL) unit-1 was sync.
00:53 |  | Matarbari 2*600 MW (CPGCBL) Synchronized with remarks:- U1
01:58 |  | Patuakhali 1320 MW (RNPL) unit 2 tripped at 01:58 hours due to a decreasing in feed
water flow.
05:00 |  | Min. Gen. 7543 MW
07:10 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
07:11 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
07:30 |  | Chowmuhani-Ramganj 132 kV Ckt-1 Scheduled S/D from Ramganj 132/33kV end Due to Annual
Maintenance work (Schedule shutdown) and from Chowmuhani 132/33kV end Due to Annuel
Maintenance Works.
07:50 |  | Khulna (C) S/S North-WestCkt-1 Scheduled S/D Due to Due to North West End work,
permission by ALDC
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Under maintenance
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 402 | 9302400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 8331000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 251 | 6669498 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 49217 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 4467229 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 170640 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 32 | 221280 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 52644 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 77467 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 376200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 353880 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 519480 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 22 | 555200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 26 | 428640 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 91 | 1025424 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1172160 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 11520 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 744489 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 147858 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 36 | 625680 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 1833 | 35301906
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 126630 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 75840 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 827280 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 4668127 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 27599 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 14353 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 16320 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 458880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 21238 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 25090 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 14400 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 25 | 79036 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 15055 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 21703634 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 10 | 282240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 370 | 14509090.91 | Machine Problem
Chattogram Area Total |  |  |  |  | 4915.22 | 1864 | 42864812.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4558000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 42 | 854064 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 549600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 3964364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1028087 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 122109 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1168450 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 85440 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 46 | 1164480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 345410 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 68 | 177240 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 379200 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 380127 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 771 | 14776571
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 6 | 165120 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1132800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 289200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 197910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 364320 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 48240 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 97 | 2206990
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 716000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3671427.2 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 10 | 358200 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 56976 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 305856 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1532160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 203 | 4188320 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 339744 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7132000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 336 | 8608000 | FGMO not available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7379700 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1477 | 34288383.2
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 920 | 21234181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 254 | 6052032 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 476640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to CW Pond cleaning & Tx Radiator change.
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1174 | 27762853
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 218.79 | 1665454 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 142204 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2957000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 21764363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5138730 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 224400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5367000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3208.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2146.79 | 37262360.14
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 171 | 4134427 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 193 | 4355255 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 186 | 4400182 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 80640 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 28066 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 0.13 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25440 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 760 | 13829818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 306748 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 496170 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1366.5 | 27656746.13
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 70 | 1645963 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 211 | 5038000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 17107 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 22849.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 90158 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 106145 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 649440 | -
Rangpur Area Total |  |  |  |  | 950 | 281 | 7569662.56
Eastern Grid Total |  |  |  |  | 16772.748 | 6042 | 129438663.11
Western Grid Total |  |  |  |  | 11614.5 | 4968.29 | 100251621.83
National Grid Total |  |  |  |  | 28387.248 | 11010.29 | 229690284.94
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7238.99 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3212.9 | MW
i) Dhaka area |  |  | 3937.59 |  | MW | i) Khulna area |  |  |  | 1196 | MW
ii) Chattogram area |  |  | 1099.4 |  | MW | ii) Barishal area |  |  |  | 294.5 | MW
iii) Cumilla area |  |  | 902 |  | MW | iii) Rajshahi area |  |  |  | 1029.4 | MW
iv) Mymensingh area |  |  | 926 |  | MW | iv) Rangpur area |  |  |  | 693 | MW
v) Sylhet area |  |  | 374 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10451.89 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 01:00 | 67 | Jaldhaka | 55 | 18:00 | 133 | Purbachal | 14 | 13:00
2 | AKSML | 130.7 | 03:00 | 68 | Jamalpur | 95 | 07:00 | 134 | Purbasadipur | 100 | 13:00
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 107 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 71 | 13:00 | 70 | Jhenaidah | 98 | 08:00 | 136 | Rahim | 47 | 16:00
5 | Agrabad | 62 | 18:00 | 71 | Joydebpur | 127 | 18:00 | 137 | Rajbari | 56 | 18:30
6 | Amnura | 44 | 13:00 | 72 | Joypurhat | 41 | 20:00 | 138 | Rajendrapur | 98 | 13:00
7 | Ashuganj | 65 | 12:00 | 73 | Juldah | 10 | 00:00 | 139 | Rajshahi | 94 | 13:00
8 | BSRM | 184 | 19:30 | 74 | KSRM | 26 | 23:00 | 140 | Rajshahi-230 | 44 | 13:00
9 | Bagerhat | 62 | 18:30 | 75 | Kabirpur | 178 | 18:00 | 141 | Ramganj | 82 | 18:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 52 | 18:00 | 142 | Rampur | 25 | 18:00
11 | Bakulia | 66 | 18:00 | 77 | Kallyanpur | 72 | 13:00 | 143 | Rangamati | 12 | 18:00
12 | Banani | 37 | 14:00 | 78 | Kalurghat | 30 | 12:00 | 144 | Rangpur | 96 | 09:00
13 | Bangabhaban | 8 | 13:00 | 79 | Kamrangirchar | 55.7 | 12:00 | 145 | Ruppur | 4.6 | 16:00
14 | Barapukuria | 51 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 12 | 00:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 87 | 13:00 | 147 | Saidpur | 92 | 09:00
16 | Barishal | 80 | 13:00 | 82 | Keranigonj | 57 | 13:00 | 148 | Satkhira | 91 | 08:00
17 | Barishal-230 | 60 | 18:30 | 83 | Khagrachori | 26 | 18:00 | 149 | Satmasjid | 82 | 13:00
18 | Baroaulia | 52 | 06:00 | 84 | Khulna | 75 | 13:00 | 150 | Savar | 164 | 12:00
19 | Baroirhat | 54 | 18:00 | 85 | Khulshi | 145 | 18:30 | 151 | SevenRings | 19.26 | 21:00
20 | Bashundhara | 125 | 13:00 | 86 | Kishoreganj | 126 | 19:30 | 152 | ShahCement | 31 | 14:00
21 | BashundharaCement | 12 | 01:00 | 87 | Kodda | 277 | 15:00 | 153 | Shahjadpur | 62 | 19:30
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 27 | 18:30 | 154 | Shahjibazar | 80 | 18:30
23 | Benapole | 55 | 08:00 | 89 | Kurigram | 50 | 08:00 | 155 | Shahmirpur | 39 | 00:00
24 | Bhaluka | 112 | 18:00 | 90 | Kushtia | 110 | 18:30 | 156 | Shariatpur | 52 | 21:00
25 | Bhandaria | 34 | 21:00 | 91 | Lalbag | 58 | 10:00 | 157 | Sherpur | 108 | 00:00
26 | Bhangura | 25 | 13:00 | 92 | Lalmonirhat | 45 | 18:30 | 158 | Shikalbaha | 22 | 18:00
27 | Bheramara(GK) | 38 | 18:00 | 93 | MI_Cement | 17.2 | 20:00 | 159 | Shitalakhya | 60.6 | 12:00
28 | Bhulta | 226 | 00:00 | 94 | Madanganj | 23 | 01:00 | 160 | Sholosohor | 31 | 16:00
29 | Bog-Sherpur | 60 | 18:00 | 95 | Madaripur | 67 | 20:00 | 161 | Shyampur | 152 | 11:00
30 | Bogura | 109 | 18:30 | 96 | Madartek | 59.77 | 13:00 | 162 | Siddhirganj | 96 | 12:00
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 36 | 18:00 | 163 | Sirajganj | 82 | 18:30
32 | Brahmanbaria | 102 | 18:00 | 98 | Magura | 44 | 18:30 | 164 | Sonargaon | 74 | 18:30
33 | Cantonment | 76 | 13:00 | 99 | Mahasthangarh | 50 | 18:30 | 165 | Sreemongol | 50 | 18:00
34 | Chandpur | 42 | 18:00 | 100 | Manikganj | 117 | 18:30 | 166 | Sreepur | 81 | 12:00
35 | Chandraghona | 26 | 18:00 | 101 | Maniknagar | 44 | 13:00 | 167 | Srinagar | 29.73 | 13:00
36 | Chapai | 60 | 13:00 | 102 | Matarbari | 36 | 18:00 | 168 | Sunamganj | 38 | 19:00
37 | Charsaidpur | 41 | 15:00 | 103 | Matuail | 59 | 10:00 | 169 | Sylhet | 28 | 18:00
38 | Chauddagram | 51 | 18:00 | 104 | Millgate | 66 | 12:00 | 170 | Sylhet-132 | 77 | 14:00
39 | Chhatak | 22 | 18:00 | 105 | Mirpur | 91.5 | 18:30 | 171 | TK | 20.4 | 19:30
40 | Chowmuhani | 149 | 18:00 | 106 | Mirsorai | 8 | 18:00 | 172 | Tangail | 152 | 07:00
41 | Chuadanga | 76 | 13:00 | 107 | Mirzapur | 42 | 08:00 | 173 | Thakurgaon | 73 | 19:00
42 | Coxsbazar | 103 | 18:00 | 108 | Mithapukur | 58 | 18:00 | 174 | Tongi | 91 | 12:00
43 | Cumilla(N) | 122 | 18:30 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 21 | 19:30
44 | Cumilla(S) | 128 | 13:00 | 110 | Mogbazar | 91.5 | 13:00 | 176 | Ullon | 34 | 13:00
45 | Daudkandi | 102 | 20:00 | 111 | Mongla | 29 | 08:00 | 177 | Uttara | 64 | 13:00
46 | Dhaka | 32 | 12:00 | 112 | Motijheel | 26 | 13:00 | 178 | UttaraNew | 36 | 13:00
47 | Dhamrai | 104 | 18:00 | 113 | Muktagacha | 28 | 13:00 | 179 | Zigatola | 52 | 13:00
48 | Dhanmondi | 79 | 13:00 | 114 | Munshiganj | 70 | 21:00
49 | Dohazari | 69 | 18:30 | 115 | Mymensingh | 161 | 09:00
50 | Faridpur | 107 | 18:30 | 116 | Naogaon | 95 | 13:00
51 | Fatullah | 71 | 09:00 | 117 | Narail | 41 | 18:30
52 | Fenchuganj | 26 | 18:00 | 118 | Narinda | 57 | 13:00
53 | Feni | 58 | 18:00 | 119 | Narshingdi | 150 | 22:00
54 | GPH | 92 | 03:00 | 120 | Natore | 101 | 19:30
55 | Ghatail | 34 | 18:00 | 121 | Nawabganj | 36 | 13:00
56 | Ghorashal | 9 | 09:00 | 122 | Netrakona | 136 | 18:00
57 | Ghorashal-230 | 59 | 22:00 | 123 | New | 70 | 12:00
58 | Goalpara | 22 | 08:00 | 124 | Niamatpur | 79 | 09:00
59 | Gollamari | 60 | 13:00 | 125 | Noapara | 34 | 18:00
60 | Gopalganj | 78.8 | 18:30 | 126 | PHP | 9 | 12:00
61 | Gulshan | 66 | 13:00 | 127 | Pabna | 66 | 18:30
62 | Halishahar | 45 | 16:00 | 128 | Palashbari | 78 | 18:30
63 | HaripurSBU | 183 | 10:00 | 129 | Panchagarh | 39 | 18:00
64 | Hasnabad | 63 | 13:00 | 130 | Patuakhali | 54 | 20:00
65 | Hathazari | 55 | 13:00 | 131 | Payra | 14 | 13:00
66 | Ishurdi | 57 | 18:30 | 132 | Postogola | 43 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9160.5 | 0 |  | 9160.5
1:00 | 8412.5 | 0 |  | 8412.5
2:00 | 8134.5 | 0 |  | 8134.5
3:00 | 7717.5 | 0 |  | 7717.5
4:00 | 7554.5 | 0 |  | 7554.5
5:00 | 7357.5 | 0 |  | 7357.5
6:00 | 7713.5 | 0 |  | 7713.5
7:00 | 8696.83 | 0 |  | 8696.83
8:00 | 9571.99 | 20 |  | 9592.99
9:00 | 10064.59 | 25 |  | 10090.59
10:00 | 9880.12 | 0 |  | 9880.12
11:00 | 9915.79 | 0 |  | 9915.79
12:00 | 10035.4 | 0 |  | 10035.4
13:00 | 10610.72 | 0 |  | 10610.72
14:00 | 10254.95 | 25 |  | 10280.95
15:00 | 9699.95 | 30 |  | 9730.95
16:00 | 9601.8 | 30 |  | 9632.8
17:00 | 9691.27 | 30 |  | 9722.27
18:00 | 10620.69 | 45 |  | 10667.72
19:00 | 11010.29 | 55 |  | 11067.29
19:30 | 10867.5 | 60 |  | 10930.5
20:00 | 10810.98 | 54 |  | 10866.98
21:00 | 10644.82 | 30 |  | 10675.82
22:00 | 10132.02 | 30 |  | 10163.02
23:00 | 9568 | 30 |  | 9599
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5511 | 3649.5 | 9160.5 | DAILY LOAD CURVE
00:30 | 5251.5 | 3535 | 8786.5
01:00 | 4992 | 3420.5 | 8412.5 | 21-01-2025
01:30 | 4946.5 | 3327 | 8273.5
02:00 | 4901 | 3233.5 | 8134.5
02:30 | 4787.5 | 3138.5 | 7926
03:00 | 4674 | 3043.5 | 7717.5
03:30 | 4622 | 3014 | 7636
04:00 | 4570 | 2984.5 | 7554.5
04:30 | 4445 | 3011 | 7456
05:00 | 4320 | 3037.5 | 7357.5
05:30 | 4484 | 3051.5 | 7535.5
06:00 | 4648 | 3065.5 | 7713.5
06:30 | 4925.15 | 3280.015 | 8205.165
07:00 | 5202.3 | 3494.53 | 8696.83
07:30 | 5389.205 | 3745.205 | 9134.41
08:00 | 5576.11 | 3995.88 | 9571.99
08:30 | 5640.72 | 4177.57 | 9818.29
09:00 | 5705.33 | 4359.26 | 10064.59
09:30 | 5688.21 | 4284.145 | 9972.355
10:00 | 5671.09 | 4209.03 | 9880.12
10:30 | 5652.34 | 4245.615 | 9897.955
11:00 | 5633.59 | 4282.2 | 9915.79
11:30 | 5578.97 | 4396.625 | 9975.595
12:00 | 5524.35 | 4511.05 | 10035.4
12:30 | 5567.205 | 4755.855 | 10323.06
13:00 | 5610.06 | 5000.66 | 10610.72
13:30 | 5619.475 | 4813.36 | 10432.835
14:00 | 5628.89 | 4626.06 | 10254.95
14:30 | 5518.39 | 4459.06 | 9977.45
15:00 | 5407.89 | 4292.06 | 9699.95
15:30 | 5433.02 | 4217.855 | 9650.875
16:00 | 5458.15 | 4143.65 | 9601.8
16:30 | 5459.11 | 4187.425 | 9646.535
17:00 | 5460.07 | 4231.2 | 9691.27
17:30 | 5749.035 | 4406.945 | 10155.98
18:00 | 6038 | 4582.69 | 10620.69
18:30 | 6040 | 4775.49 | 10815.49
19:00 | 6042 | 4968.29 | 11010.29
19:30 | 5950 | 4917.5 | 10867.5
20:00 | 5899 | 4911.98 | 10810.98
20:30 | 5818.5 | 4909.4 | 10727.9 |  | Executive Engineer
21:00 | 5738 | 4906.82 | 10644.82 |  | Network Operation Division
21:30 | 5581.25 | 4807.17 | 10388.42
22:00 | 5424.5 | 4707.52 | 10132.02
22:30 | 5322 | 4528.01 | 9850.01
23:00 | 5219.5 | 4348.5 | 9568

## En-Curve
QF-LDC-12
Date | 21-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3010 | 1706.5 | 920 | 0 | 52 | 413 | 30 | 2782 | 0 | 58 | 174 | 0 | 0 | 15 | 0 | DAILY ENERGY CURVE
00:30 | 2945.5 | 1606.5 | 919.5 | 0 | 49 | 417 | 30 | 2637 | 0 | 37.5 | 128.5 | 0 | 0 | 16 | 0 | 21-01-2025
01:00 | 2881 | 1506.5 | 919 | 0 | 46 | 421 | 30 | 2492 | 0 | 17 | 83 | 0 | 0 | 17 | 0
01:30 | 2881 | 1502.5 | 866 | 0 | 45 | 421 | 30 | 2427 | 0 | 17 | 67.5 | 0 | 0 | 16.5 | 0 |  | Total Energy | 229.6903 |  | MKWHr
02:00 | 2881 | 1498.5 | 813 | 0 | 44 | 421 | 30 | 2362 | 0 | 17 | 52 | 0 | 0 | 16 | 0 |  | Energy not Served | 0.404 |  | MKWHr
02:30 | 2809.5 | 1443.5 | 771.5 | 0 | 43 | 425.5 | 30 | 2339 | 0 | 8.5 | 34.5 | 0 | 0 | 21 | 0 |  | Energy Requirement | 230.0943 |  | MKWHr
03:00 | 2738 | 1388.5 | 730 | 0 | 42 | 430 | 30 | 2316 | 0 | 0 | 17 | 0 | 0 | 26 | 0
03:30 | 2671.5 | 1392 | 730 | 0 | 41 | 430 | 30 | 2306 | 0 | 0 | 8.5 | 0 | 0 | 27 | 0
04:00 | 2605 | 1395.5 | 730 | 0 | 40 | 430 | 30 | 2296 | 0 | 0 | 0 | 0 | 0 | 28 | 0
04:30 | 2458.5 | 1445 | 729.5 | 0 | 40 | 427 | 30 | 2295.5 | 0 | 0 | 0 | 0 | 0 | 30.5 | 0
05:00 | 2312 | 1494.5 | 729 | 0 | 40 | 424 | 30 | 2295 | 0 | 0 | 0 | 0 | 0 | 33 | 0
05:30 | 2346 | 1549 | 729.5 | 0 | 43 | 424 | 30 | 2341.5 | 0 | 3.5 | 37 | 0 | 0 | 32 | 0
06:00 | 2380 | 1603.5 | 730 | 0 | 46 | 424 | 30 | 2388 | 0 | 7 | 74 | 0 | 0 | 31 | 0
06:30 | 2511.5 | 1681.75 | 777 | 0 | 47 | 467.5 | 30 | 2557 | 3.415 | 27 | 81 | 0 | 0 | 22 | 0
07:00 | 2643 | 1760 | 824 | 0 | 48 | 511 | 30 | 2726 | 6.83 | 47 | 88 | 0 | 0 | 13 | 0
07:30 | 2687.5 | 1801.5 | 872 | 0 | 46 | 535.61 | 30 | 2918 | 47.3 | 61 | 123.5 | 0 | 0 | 12 | 10
08:00 | 2732 | 1843 | 920 | 0 | 44 | 560.22 | 30 | 3110 | 87.77 | 75 | 159 | 0 | 0 | 11 | 20
08:30 | 2746.5 | 1814.5 | 919 | 0 | 47 | 602.875 | 32.5 | 3210 | 145.415 | 93 | 201.5 | 0 | 0 | 6 | 22.5
09:00 | 2761 | 1786 | 918 | 0 | 50 | 645.53 | 35 | 3310 | 203.06 | 111 | 244 | 0 | 0 | 1 | 25
09:30 | 2808 | 1707.5 | 919 | 0 | 54 | 650.2 | 35 | 3176.5 | 262.155 | 111 | 248.5 | 0 | 0 | 0.5 | 12.5
10:00 | 2855 | 1629 | 920 | 0 | 58 | 654.87 | 35 | 3043 | 321.25 | 111 | 253 | 0 | 0 | 0 | 0
10:30 | 2835 | 1652 | 920 | 0 | 55 | 633.265 | 35 | 3013.5 | 390.19 | 111 | 253 | 0 | 0 | 0 | 0
11:00 | 2815 | 1675 | 920 | 0 | 52 | 611.66 | 35 | 2984 | 459.13 | 111 | 253 | 0 | 0 | 0 | 0
11:30 | 2839 | 1794.25 | 919.5 | 0 | 56 | 616.755 | 35 | 2868 | 487.59 | 111 | 248.5 | 0 | 0 | 0 | 0
12:00 | 2863 | 1913.5 | 919 | 0 | 60 | 621.85 | 35 | 2752 | 516.05 | 111 | 244 | 0 | 0 | 0 | 0
12:30 | 2853 | 1819.5 | 919.5 | 0 | 60 | 682.64 | 37.5 | 2988 | 503.92 | 111 | 346.5 | 0 | 0 | 1.5 | 0
13:00 | 2843 | 1725.5 | 920 | 0 | 60 | 743.43 | 40 | 3224 | 491.79 | 111 | 449 | 0 | 0 | 3 | 0
13:30 | 2818 | 1725.5 | 920 | 0 | 59 | 722.715 | 40 | 3182 | 453.12 | 106.5 | 401.5 | 0 | 0 | 4.5 | 12.5
14:00 | 2793 | 1725.5 | 920 | 0 | 58 | 702 | 40 | 3140 | 414.45 | 102 | 354 | 0 | 0 | 6 | 25
14:30 | 2838.5 | 1690.5 | 920.5 | 0 | 54 | 638 | 40 | 3068.89 | 352.56 | 94 | 272.5 | 0 | 0 | 8 | 27.5
15:00 | 2884 | 1655.5 | 921 | 0 | 50 | 574 | 40 | 2997.78 | 290.67 | 86 | 191 | 0 | 0 | 10 | 30
15:30 | 2935.5 | 1691.5 | 920.5 | 0 | 51 | 526 | 40 | 2989.055 | 216.32 | 86 | 184.5 | 0 | 0 | 10.5 | 30
16:00 | 2987 | 1727.5 | 920 | 0 | 52 | 478 | 40 | 2980.33 | 141.97 | 86 | 178 | 0 | 0 | 11 | 30
16:30 | 2989 | 1755 | 920 | 0 | 49 | 471.5 | 40 | 2996.63 | 86.905 | 99 | 226 | 0 | 0 | 13.5 | 30
17:00 | 2991 | 1782.5 | 920 | 0 | 46 | 465 | 40 | 3012.93 | 31.84 | 112 | 274 | 0 | 0 | 16 | 30
17:30 | 3007.5 | 1792 | 920 | 0 | 46 | 517 | 40 | 3163.56 | 15.92 | 180 | 459.5 | 0 | 0 | 14.5 | 37.5
18:00 | 3024 | 1801.5 | 920 | 0 | 46 | 569 | 40 | 3314.19 | 0 | 248 | 645 | 0 | 0 | 13 | 45
18:30 | 3043 | 1799.5 | 920 | 0 | 46 | 664.5 | 40 | 3457.49 | 0 | 222.5 | 611 | 0 | 0 | 11.5 | 50
19:00 | 3062 | 1797.5 | 920 | 0 | 46 | 760 | 40 | 3600.79 | 0 | 197 | 577 | 0 | 0 | 10 | 55
19:30 | 3080 | 1862.5 | 920 | 0 | 48 | 752 | 40 | 3613 | 0 | 112 | 431 | 0 | 0 | 9 | 60
20:00 | 3058 | 1828.5 | 919 | 0 | 48 | 752 | 40 | 3611.48 | 0 | 112 | 435 | 0 | 0 | 7 | 54
20:30 | 3055.5 | 1794 | 919 | 0 | 46 | 751.5 | 40 | 3611.4 | 0 | 102 | 402.5 | 0 | 0 | 6 | 42
21:00 | 3053 | 1759.5 | 919 | 0 | 44 | 751 | 40 | 3611.32 | 0 | 92 | 370 | 0 | 0 | 5 | 30
21:30 | 3023.5 | 1750.25 | 919.5 | 0 | 43 | 716 | 37.5 | 3531.67 | 0 | 76 | 286 | 0 | 0 | 5 | 30
22:00 | 2994 | 1741 | 920 | 0 | 42 | 681 | 35 | 3452.02 | 0 | 60 | 202 | 0 | 0 | 5 | 30
22:30 | 2974.5 | 1762.5 | 920 | 0 | 47 | 606.5 | 35 | 3252.01 | 0 | 55.5 | 191 | 0 | 0 | 6 | 30
23:00 | 2955 | 1784 | 920 | 0 | 52 | 532 | 35 | 3052 | 0 | 51 | 180 | 0 | 0 | 7 | 30
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-20 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 415 | 04:00 | 380 | 22:00 | Kaliakoir | 376 | 05:00 | 356 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 400 | 9:30 | 378 | 12:30 | Madunaghat | 409 | 05:00 | 393 | 19:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 407 | 04:00 | 382 | 12:00 | Meghnaghat | 411 | 05:00 | 386 | 13:00
| Bibiana | 395 | 04:00 | 386 | 15:00 | Payra | 418 | 05:00 | 406 | 13:00
| BIPTC | 408 | 02:00 | 392 | 08:00 | Rahanpur | 414 | 05:00 | 397 | 18:30
| Bogura | 413 | 04:00 | 393 | 18:30 | Rampal | 416 | 04:00 | 388 | 18:00
| Gopalganj | 417 | 03:00 | 394 | 13:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 235 | 02:00 | 221 | 12:00 | Haripur | 234 | 06:00 | 223 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 234 | 04:00 | 222 | 12:00 | Hasnabad | 234 | 00:00 | 221 | 12:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 235 | 01:00 | 224 | 10:00 | Hathazari | 234 | 00:00 | 227 | 13:00
| Ashuganj | 238 | 00:00 | 225 | 12:00 | Ishurdi | 244 | 04:00 | 229 | 12:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 05:00 | 224 | 13:00 | Jhenaidah | 242 | 04:00 | 222 | 12:00
| Baghabari | 242 | 02:00 | 229 | 12:00 | Kaliakoir | 235 | 01:00 | 223 | 12:00 | 230 kV MAX | 249 |  | 249 | 215
| Barapukuria | 225 | 01:00 | 215 | 18:30 | Keranigonj | 234 | 02:00 | 220 | 12:00 | 230 kV MIN | 215 |  | 244 | 220 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 225 | 01:00 | 215 | 18:30 | Khulna(S) | 243 | 04:00 | 224 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 246 | 02:00 | 235 | 13:00 | Madunaghat | 232 | 00:00 | 225 | 12:00 | 132 kV MAX | 142 |  | 142 | 115 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 241 | 03:00 | 225 | 13:00 | Madunaghat-400 | 233 | 03:00 | 226 | 13:00 | 132 kV MIN | 108 |  | 142 | 108 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 237 | 02:00 | 222 | 12:00 | Maniknagar | 236 | 04:00 | 222 | 12:00 | [35 empty] | 6:00
| Bibiana | 230 | 00:00 | 222 | 12:00 | Meghnaghat | 240 | 00:00 | 227 | 17:00 |  | 400 | [33 empty] | 392
| BIPTC | 243 | 03:00 | 226 | 13:00 | Meghnaghat-400 | 237 | 01:00 | 224 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 240 | 05:00 | 228 | 18:30 | Mirsorai | 233 | 03:00 | 223 | 13:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 239 | 03:00 | 226 | 18:30 | Rajshahi | 243 | 04:00 | 224 | 13:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 249 | 02:00 | 243 | 13:00 | Rampal | 241 | 04:00 | 223 | 18:30 |  | 132 |  |  | Ash 400-299274
| BSRM | 234 | 05:00 | 222 | 19:30 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 234 | 05:00 | 220 | 12:00 | Rampura | 237 | 02:00 | 222 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 247 | 03:00 | 233 | 12:00 | Shikalbaha | 231 | 01:00 | 223 | 12:00 |  | kaptai by call 399528
| Fenchuganj | 231 | 00:00 | 226 | 16:00 | Shyampur | 236 | 04:00 | 221 | 12:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Siddhirganj | 238 | 01:00 | 224 | 12:00
| Ghorashal-230 | 235 | 02:00 | 223 | 12:00 | Sirajgonj | 247 | 03:00 | 236 | 12:00
| Gopalganj | 247 | 04:00 | 234 | 13:00 | Sreepur | 239 | 02:00 | 225 | 12:00
| GPH | 234 | 05:00 | 224 | 12:00 | Tongi | 234 | 05:00 | 220 | 12:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 136 | 01:00 | 126 | 12:00 | Kurigram | 131 | 02:00 | 115 | 18:30 |  | Gopalganj-230 | 599470
| Agargaon | 137 | 01:00 | 128 | 12:00 | Kushtia | 140 | 00:00 | 131 | 12:00
| Agrabad | 134 | 03:00 | 127 | 12:00 | Lalbag | 138 | 04:00 | 128 | 12:00
| AKS | 132 | 05:00 | 125 | 13:00 | Lalmonirhat | 131 | 03:00 | 121 | 18:30
| Aminbazar | 137 | 01:00 | 128 | 13:00 | Madanganj | 135 | 03:00 | 127 | 12:00
| Amnura | 140 | 02:00 | 130 | 12:00 | Madaripur | 138 | 06:00 | 130 | 12:00
| Ashuganj | 139 | 01:00 | 135 | 11:00 | Madartek | 136 | 05:00 | 127 | 11:00
| Bagerhat | 139 | 00:00 | 125 | 18:30 | Madunaghat | 134 | 00:00 | 129 | 13:00
| Bajitpur | 135 | 01:00 | 128 | 10:00 | Magura | 141 | 03:00 | 127 | 12:00
| Bakulia | 132 | 04:00 | 127 | 12:00 | Mahasthangarh | 137 | 04:00 | 125 | 18:30
| Banani | 136 | 00:00 | 125 | 12:00 | Manikganj | 131 | 00:00 | 124 | 16:00
| Bangabhaban | 134 | 00:00 | 125 | 13:00 | Maniknagar | 135 | 04:00 | 125 | 12:00
| Barapukuria | 135 | 01:00 | 126 | 18:30 | Matarbari | 128 | 04:00 | 118 | 19:00
| Barguna | 138 | 04:00 | 133 | 13:00 | Matuail | 134 | 00:00 | 128 | 13:00
| Barishal | 137 | 03:00 | 130 | 12:00 | Millgate | 138 | 01:00 | 127 | 12:00
| Barishal-230 | 136 | 00:00 | 130 | 12:00 | Mirpur | 136 | 02:00 | 126 | 12:00
| Baroaulia | 133 | 00:00 | 129 | 12:00 | Mirzapur | 131 | 00:00 | 124 | 15:00
| Baroirhat | 128 | 23:00 | 124 | 00:00 | Mithapukur | 134 | 05:00 | 122 | 18:30
| Bashundhara | 137 | 00:00 | 126 | 12:00 | MI_Cement | 136 | 02:00 | 128 | 12:00
| BashundharaCement | 135 | 03:00 | 127 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 135 | 03:00 | 132 | 11:00 | Mogbazar | 137 | 04:00 | 127 | 12:00
| Benapole | 138 | 03:00 | 123 | 12:00 | Mongla | 138 | 00:00 | 125 | 12:00
| Bhaluka | 129 | 03:00 | 117 | 12:00 | Motijheel | 134 | 00:00 | 125 | 13:00
| Bhandaria | 135 | 02:00 | 127 | 13:00 | Muktagacha | 127 | 04:00 | 117 | 18:00
| Bhangura | 138 | 01:00 | 131 | 12:00 | Munshiganj | 135 | 04:00 | 127 | 12:00
| Bheramara | 140 | 00:00 | 133 | 12:00 | Mymensingh | 127 | 06:00 | 113 | 12:00
| Bheramara(GK) | 141 | 03:00 | 133 | 14:00 | Naogaon | 136 | 03:00 | 126 | 18:30
| Bhulta | 128 | 00:00 | 115 | 11:00 | Narail | 141 | 03:00 | 126 | 12:00
| Bog-Sherpur | 138 | 03:00 | 128 | 18:30 | Narinda | 135 | 04:00 | 125 | 12:00
| Bogura | 138 | 04:00 | 130 | 18:00 | Narshingdi | 133 | 00:00 | 116 | 18:00
| Bogura-230 | 139 | 05:00 | 128 | 18:30 | Natore | 138 | 00:00 | 131 | 08:00
| Brahmanbaria | 136 | 00:00 | 125 | 13:00 | Nawabganj | 137 | 01:00 | 127 | 12:00
| Cantonment | 138 | 04:00 | 128 | 12:00 | Netrakona | 128 | 04:00 | 112 | 11:00
| Chandpur | 130 | 18:00 | 122 | 12:00 | New | 137 | 00:00 | 128 | 12:00
| Chandraghona | 136 | 05:00 | 130 | 11:00 | Niamatpur | 139 | 00:00 | 133 | 08:00
| Chapai | 138 | 02:00 | 132 | 08:00 | Noapara | 140 | 02:00 | 126 | 12:00
| Charsaidpur | 135 | 01:00 | 128 | 12:00 | Pabna | 138 | 03:00 | 126 | 18:30
| Chauddagram | 132 | 01:00 | 122 | 12:00 | Palashbari | 132 | 03:00 | 120 | 18:30
| Chhatak | 134 | 03:00 | 130 | 18:00 | Panchagarh | 136 | 04:00 | 117 | 18:30
| Chowmuhani | 128 | 05:00 | 120 | 12:00 | Patuakhali | 136 | 00:00 | 133 | 11:00
| Chuadanga | 140 | 03:00 | 123 | 12:00 | Payra | 138 | 04:00 | 134 | 12:00
| Coxsbazar | 125 | 00:00 | 119 | 12:00 | PHP | 131 | 02:00 | 122 | 12:00
| Cumilla(N) | 136 | 02:00 | 127 | 12:00 | Postogola | 138 | 00:00 | 130 | 12:00
| Cumilla(S) | 135 | 02:00 | 125 | 12:00 | Purbachal | 136 | 01:00 | 125 | 12:00
| Daudkandi | 134 | 04:00 | 119 | 12:00 | Purbasadipur | 130 | 04:00 | 118 | 18:30
| Dhaka | 136 | 00:00 | 126 | 12:00 | Rahanpur | 140 | 00:00 | 134 | 08:00
| Dhamrai | 136 | 03:00 | 126 | 12:00 | Rahanpur-400 | 140 | 00:00 | 135 | 08:00
| Dhanmondi | 136 | 02:00 | 128 | 12:00 | Rahim | 134 | 04:00 | 127 | 12:00
| Dohazari | 131 | 04:00 | 125 | 12:00 | Rajbari | 137 | 02:00 | 128 | 13:00
| Faridpur | 137 | 02:00 | 130 | 12:00 | Rajendrapur | 134 | 01:00 | 126 | 13:00
| Fatullah | 137 | 01:00 | 129 | 12:00 | Rajshahi | 139 | 00:00 | 131 | 12:00
| Fenchuganj | 139 | 00:00 | 134 | 13:00 | Rajshahi-230 | 140 | 01:00 | 128 | 12:00
| Feni | 132 | 05:00 | 124 | 12:00 | Ramganj | 130 | 03:00 | 120 | 12:00
| Ghatail | 127 | 00:00 | 118 | 07:00 | Rampur | 133 | 02:00 | 127 | 12:00
| Ghorashal | 139 | 03:00 | 136 | 11:00 | Rampura | 136 | 04:00 | 126 | 12:00
| Goalpara | 139 | 00:00 | 127 | 14:00 | Rangamati | 135 | 03:00 | 129 | 11:00
| Gollamari | 141 | 00:00 | 128 | 12:00 | Rangpur | 133 | 04:00 | 118 | 18:30
| Gopalganj | 139 | 04:00 | 128 | 13:00 | Ruppur | 141 | 00:00 | 134 | 12:00
| Gopalganj-400 | 139 | 03:00 | 130 | 13:00 | Saidpur | 133 | 02:00 | 122 | 08:00
| Gulshan | 134 | 00:00 | 125 | 12:00 | Satkhira | 139 | 00:00 | 124 | 13:00
| Halishahar | 134 | 01:00 | 128 | 13:00 | Satmasjid | 137 | 01:00 | 127 | 13:00
| Haripur | 133 | 04:00 | 127 | 12:00 | Savar | 135 | 00:00 | 124 | 11:00
| HaripurSBU | 133 | 04:00 | 127 | 12:00 | SevenRings | 141 | 00:00 | 134 | 12:00
| Hasnabad | 138 | 04:00 | 131 | 11:00 | ShahCement | 135 | 01:00 | 128 | 12:00
| Hathazari | 135 | 00:00 | 132 | 13:00 | Shahjadpur | 142 | 00:00 | 134 | 12:00
| Ishurdi | 142 | 00:00 | 134 | 12:00 | Shahjibazar | 138 | 00:00 | 129 | 19:30
| Jaldhaka | 130 | 03:00 | 116 | 18:30 | Shahmirpur | 132 | 00:00 | 127 | 12:00
| Jamalpur | 128 | 06:00 | 115 | 17:00 | Shariatpur | 138 | 04:00 | 128 | 13:00
| Jashore | 139 | 00:00 | 124 | 13:00 | Sherpur | 126 | 06:00 | 108 | 02:00
| Jhenaidah | 141 | 00:00 | 128 | 12:00 | Shikalbaha | 123 | 01:00 | 117 | 12:00
| Jhenaidah-230 | 142 | 04:00 | 128 | 12:00 | Shikalbaha-230 | 134 | 02:00 | 128 | 12:00
| Joydebpur | 137 | 00:00 | 130 | 12:00 | Shitalakhya | 136 | 02:00 | 128 | 12:00
| Joypurhat | 136 | 02:00 | 126 | 18:30 | Sholosohor | 134 | 03:00 | 129 | 11:00
| Juldah | 132 | 00:00 | 126 | 12:00 | Shyampur | 134 | 00:00 | 128 | 13:00
| Kabirpur | 137 | 01:00 | 126 | 16:00 | Shyampur-230 | 137 | 04:00 | 128 | 12:00
| Kachua | 132 | 05:00 | 122 | 12:00 | Siddhirganj | 135 | 00:00 | 128 | 12:00
| Kaliakoir | 137 | 06:00 | 129 | 12:00 | Sirajganj | 140 | 01:00 | 127 | 18:30
| Kallyanpur | 137 | 04:00 | 129 | 12:00 | Sonargaon | 131 | 01:00 | 113 | 12:00
| Kalurghat | 136 | 04:00 | 129 | 12:00 | Sreemongol | 136 | 00:00 | 131 | 12:00
| Kamrangirchar | 136 | 00:00 | 127 | 12:00 | Sreepur | 130 | 00:00 | 121 | 12:00
| Kaptai | N/A | N/A | N/A | N/A | Srinagar | 137 | 01:00 | 127 | 12:00
| Kazla | 135 | 02:00 | 125 | 13:00 | SSM | 138 | 01:00 | 131 | 00:00
| Keranigonj | 137 | 04:00 | 128 | 12:00 | Sunamganj | 133 | 03:00 | 129 | 12:00
| Khagrachori | 134 | 00:00 | 128 | 11:00 | Sylhet | 135 | 00:00 | 132 | 13:00
| Khulna | 140 | 03:00 | 126 | 12:00 | Sylhet-132 | 134 | 00:00 | 132 | 15:00
| Khulna(S) | 141 | 03:00 | 128 | 12:00 | Tangail | 128 | 00:00 | 120 | 15:00
| Khulshi | 132 | 05:00 | 127 | 11:00 | Thakurgaon | 133 | 03:00 | 114 | 18:30 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 132 | 02:00 | 123 | 08:00 | TK | 134 | 06:00 | 129 | 11:00 |  |  | Nos | Nos | Nos
| Kodda | 135 | 00:00 | 124 | 15:00 | Tongi | 138 | 04:00 | 130 | 12:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 135 | 01:00 | 129 | 11:00 | Ullahpara | 139 | 00:00 | 132 | 08:00
| Kulaura | 138 | 00:00 | 134 | 12:00 | Ullon | 135 | 00:00 | 126 | 12:00
[6 empty] | Uttara | 136 | 03:00 | 124 | 12:00
[6 empty] | UttaraNew | 136 | 01:00 | 123 | 12:00
[6 empty] | Zigatola | 139 | 04:00 | 126 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.