## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-01-2025 | during | 23-01-2025 | during | 23-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 401 | 401 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 420 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 316 | 298 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 335 | 335 | 335 | 250 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 19 | 19 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 21 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 25 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 150 | 43 | 130 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 88 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 36 | 0 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0.01 | 0.01 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0.01 | 0.01 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6257.05 | 5842.27 | 1539 | 1837 | 4605.99 | 4585.99 | 2738.93 | 2803.93
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 0 | 0 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 162 | 161 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 72 | 72 | 72 | 72 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 21 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.67 | 0 | 3.67 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | Liquid fuel shortage
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 980 | 1050 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 16 | 26 | 5 | 13 | 5 | 13 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 950 | 950 | 1150 | 1150 | 1050 | 1050 | -
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2174 | 2248 | 3989.39 | 3992.72 | 3849.39 | 3852.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 215 | 198 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 41 | 44 | 46.94 | 46.94 | 46.94 | 46.94 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 26 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 197 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 50 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 60 | 62 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 11 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 27 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 16 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 59 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 711 | 685 | 1668.97 | 1608.97 | 1556.14 | 1496.14
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 6 | 210 | 210 | 15 | 15 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 58 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 35.1 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 112.1 | 73 | 645.4 | 601.5 | 450.4 | 406.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 10 | 43 | 0 | 0 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | -
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 40 | 40 | 44 | 44 | 44 | 44 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 30 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 161 | 159 | 0 | 0 | 210 | 210 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 25 | 25 | 13 | 13 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 374 | 354 | 380 | 380 | 372 | 372 | FGMO Available, but GT Load set maximum 260MW
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1468 | 1522 | 1381.5 | 1381.5 | 1547.01 | 1547.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 920 | 904 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 293 | 284 | 410 | 410 | 310 | 310 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | S/D due to changing of ST Power Tx Radiators
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1295 | 1188 | 3472 | 3394 | 1688.02 | 1610.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 0 | 0 | 0 | 0 | 165 | 165 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 6 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 135 | 135 | 140 | 140 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1030 | 1192 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 164 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.53 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 1558.53 | 1865 | 2177.12 | 2176.12 | 2304 | 2303
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 166 | 161 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 193 | 171 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 187 | 173 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 0.56 | 0 | 4.55 | 0 | 4.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 609 | 756.49 | 1347.54 | 1347.54 | 749 | 749 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 9.7 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 40 | 0 | 85 | 0 | 85 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1207.76 | 1314.99 | 2684.54 | 2544.99 | 2066 | 1926.45
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 70 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 211 | 210 | 210 | 210 | 210 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2 | 0 | 3.8 | 0 | 3.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 24 | 0 | 100 | 0 | 100 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 313 | 281 | 655.8 | 542 | 641.82 | 508.02
System Total |  |  |  |  | 29054.66 | 28387.248 | 10378.39 | 11013.99 | 21280.71 | 20827.79 | 16841.71 | 16453.79
Forecast Scenario (23-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9060 |  | 0 |  | 9060
|  |  |  | 1:00 | 8560 |  | 0 |  | 8560
|  |  |  | 2:00 | 8060 |  | 0 |  | 8060
|  |  |  | 3:00 | 7750 |  | 0 |  | 7750
|  |  |  | 4:00 | 7570 |  | 0 |  | 7570
|  |  |  | 5:00 | 7520 |  | 0 |  | 7520
|  |  |  | 6:00 | 7920 |  | 0 |  | 7920
|  |  |  | 7:00 | 8700 |  | 0 |  | 8700
|  |  |  | 8:00 | 9540 |  | 0 |  | 9540
|  |  |  | 9:00 | 10020 |  | 0 |  | 10020
|  |  |  | 10:00 | 9790 |  | 0 |  | 9790
|  |  |  | 11:00 | 9890 |  | 0 |  | 9890
|  |  |  | 12:00 | 10340 |  | 0 |  | 10340
|  |  |  | 13:00 | 10660 |  | 0 |  | 10660
|  |  |  | 14:00 | 10330 |  | 0 |  | 10330
|  |  |  | 15:00 | 10000 |  | 0 |  | 10000
|  |  |  | 16:00 | 9600 |  | 0 |  | 9600
|  |  |  | 17:00 | 9740 |  | 0 |  | 9740
|  |  |  | 18:00 | 10790 |  | 0 |  | 10790
|  |  |  | 18:30 | 10850 |  | 0 |  | 10850
|  |  |  | 19:00 | 10940 |  | 0 |  | 10940
|  |  |  | 19:30 | 10880 |  | 0 |  | 10880
|  |  |  | 20:00 | 10820 |  | 0 |  | 10820
|  |  |  | 21:00 | 10510 |  | 0 |  | 10510
|  |  |  | 22:00 | 10130 |  | 0 |  | 10130
|  |  |  | 23:00 | 9480 |  | 0 |  | 9480
Probable Maximum Temperature: |  |  | 25.20°C
Probable Maximum Demand at Day Peak: |  |  | 10340.00 MW |  | Total Load Shed forecast at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 10940.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10940.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 227.72 MKWHr.
Yesterday (22-01-2025) Scenario
Maximum Temperature: |  |  |  |  | 25.30°C |  | Total Gas Supplied(MMCFD): |  |  |  |  | 813.48
E-W Interconnector Scenario |  |  |  |  | Import Scenario
Energy Flow from East to West |  | 0 |  |  | Import through HVDC Cross-Border Interconnector: |  |  |  |  | MKWHr: | 20.7447 | Peak Hour Flow: |  | 904.00 MW at 19:30 hrs.
Energy Flow from West to East |  | 8226036.439 |  |  | Import through Adani Cross-Border Interconnector: |  |  |  |  | MKWHr: | 13.7073 | Peak Hour Flow: |  | 756.49 MW at 19:30 hrs.
Power Flow during Peak Demand |  | 436 |  |  | Import through Cumilla Cross-Border Interconnector: |  |  |  |  | MKWHr: | 1.2902 | Peak Hour Flow: |  | 62.00 MW at 19:30 hrs.
Maximum Power Flow |  | 606 |  |  | Total Import through Cross-Border Interconnector: |  |  |  |  | MKWHr: | 35.7422 | Peak Hour Flow: |  | 1722.49 MW at 19:30 hrs.
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-01-2025 | [28 empty] | Date: | 22-01-2025 | [28 empty] | Date: | 22-01-2025 | [28 empty] | Date: | 22-01-2025 | [28 empty] | Date: | 22-01-2025 | [19 empty] | Date: | 22-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [19 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 150.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 287 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 0 | 0 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 373 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 820 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 192 | 44 | 0 | 50 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 300 | 300 | 303 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 82 | 30 | 0 | 0 | 207 | 0 | 9 | 58 | 10 | 0 | 0 | 24 | 5001.5 | 920 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 188 | 0 | 172 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 7 | 140 | 220 | 0 | 219 | 900 | 0 | 4077.5 | 9079 | 92.66
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 289 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 0 | 0 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 384 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 635 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 44 | 0 | 50 | 0 | 0 | 16 | 0 | 46 | 0 | 0 | 0 | 295 | 280 | 300 | 10 | 30 | 0 | 2 | 120 | 8 | 0 | 82 | 30 | 0 | 0 | 204 | 0 | 9 | 35 | 9 | 0 | 0 | 24 | 4717.5 | 920 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 165 | 0 | 150 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 220 | 0 | 212 | 700 | 0 | 3779.5 | 8497 | 92.66
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 324 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 0 | 0 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 500 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 108 | 0 | 0 | 0 | 29 | 220 | 44 | 0 | 50 | 0 | 0 | 16 | 0 | 46 | 0 | 0 | 0 | 305 | 255 | 331 | 10 | 30 | 0 | 2 | 120 | 8 | 0 | 82 | 30 | 0 | 0 | 204 | 0 | 9 | 9 | 10 | 0 | 0 | 0 | 4667.5 | 800 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 220 | 0 | 0 | 600 | 0 | 3246.5 | 7914 | 92.66
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 310 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 0 | 0 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 496 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 600 | 0 | 5 | 0 | 108 | 0 | 0 | 0 | 27 | 194 | 44 | 0 | 50 | 0 | 0 | 16 | 0 | 40 | 0 | 0 | 0 | 310 | 255 | 308 | 36 | 30 | 0 | 2 | 163 | 13 | 0 | 10 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 4564.5 | 729 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 220 | 0 | 0 | 600 | 0 | 3177.5 | 7742 | 92.66
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 287 | 0 | 0 | 0 | 26 | 240 | 0 | 0 | 0 | 0 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 589 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 600 | 0 | 5 | 0 | 108 | 0 | 0 | 0 | 12 | 181 | 44 | 0 | 70 | 0 | 0 | 16 | 0 | 46 | 0 | 0 | 0 | 305 | 270 | 300 | 39 | 30 | 0 | 2 | 120 | 13 | 0 | 10 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 4504.5 | 729 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 0 | 600 | 0 | 3089.5 | 7594 | 92.65
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 300 | 0 | 0 | 0 | 26 | 240 | 0 | 0 | 0 | 0 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 840 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 600 | 0 | 5 | 0 | 108 | 0 | 0 | 0 | 5 | 160 | 10 | 0 | 70 | 0 | 0 | 11 | 0 | 46 | 0 | 0 | 0 | 265 | 276 | 305 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 10 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 4591.5 | 730 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 2.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 0 | 500 | 0 | 2951.5 | 7543 | 92.65
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 321 | 0 | 0 | 0 | 28 | 240 | 0 | 0 | 0 | 0 | 21 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 925 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 600 | 0 | 5 | 0 | 108 | 0 | 0 | 0 | 5 | 200 | 10 | 0 | 50 | 0 | 0 | 11 | 0 | 48 | 0 | 0 | 0 | 250 | 276 | 350 | 10 | 30 | 0 | 2 | 120 | 13 | 0 | 10 | 0 | 0 | 0 | 202 | 0 | 0 | 2 | 13 | 0 | 0 | 0 | 4760 | 729 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 0 | 500 | 0 | 2971.5 | 7731.5 | 92.65
07:00 | 0 | 45 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 36 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 315 | 0 | 0 | 0 | 28 | 240 | 0 | 0 | 0 | 0 | 21 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 27 | 950 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 683 | 1 | 20 | 0 | 195 | 0 | 0 | 0 | 8 | 202 | 38 | 0 | 70 | 0 | 0 | 11 | 0 | 44 | 0 | 2 | 0 | 325 | 270 | 363 | 20 | 30 | 0 | 2 | 120 | 13 | 0 | 50 | 0 | 0 | 0 | 202 | 0 | 9 | 56 | 13 | 0 | 0.41 | 0 | 5323.41 | 824 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.13 | 152 | 0 | 140 | 0 | 162 | 0 | 0 | 0 | 0.01 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 150 | 6 | 80 | 220 | 0 | 0 | 560 | 0 | 3303.85 | 8627.26 | 92.65
08:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 36 | 0 | 39 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 310 | 0 | 0 | 0 | 28 | 280 | 0 | 0 | 2 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 6 | 950 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 757 | 6 | 51 | 0 | 195 | 0 | 0 | 0 | 24 | 193 | 41 | 0 | 50 | 0 | 0 | 11 | 0 | 42 | 0 | 13 | 0 | 320 | 250 | 352 | 36 | 30 | 0 | 2 | 163 | 13 | 0 | 80 | 0 | 0 | 0 | 161 | 0 | 9 | 56 | 5 | 0 | 5.25 | 13 | 5571.25 | 920 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 1.9 | 144 | 0 | 154 | 0 | 161 | 0 | 0 | 0 | 0.22 | 2.5 | 210 | 70 | 0 | 1 | 0 | 0 | 0 | 0.2 | 6 | 0.1 | 0 | 299 | 4 | 140 | 220 | 0 | 0 | 830 | 0 | 3926.92 | 9498.17 | 92.65
09:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 0 | 50 | 16 | 0 | 0 | 0 | 17 | 17 | 0 | 300 | 298 | 0 | 0 | 0 | 25 | 280 | 0 | 0 | 6 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 950 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 900 | 12 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 184 | 41 | 0 | 50 | 0 | 0 | 11 | 0 | 46 | 0 | 29 | 0 | 310 | 240 | 324 | 39 | 30 | 0 | 2 | 120 | 13 | 0 | 83 | 0 | 0 | 0 | 161 | 0 | 9 | 56 | 5 | 0 | 12.1 | 24 | 5695.1 | 920 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 6.94 | 126 | 0 | 145 | 0 | 150 | 0 | 0 | 0 | 0.52 | 2.5 | 211 | 70 | 0 | 2 | 0 | 0 | 0 | 0.4 | 11 | 0.23 | 0 | 307 | 3 | 100 | 180 | 0 | 0 | 1170 | 0 | 4328.59 | 10023.69 | 92.64
10:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 0 | 50 | 0 | 0 | 0 | 0 | 35 | 25 | 0 | 300 | 290 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 18 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 950 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 900 | 16 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 180 | 41 | 0 | 50 | 0 | 0 | 16 | 0 | 56 | 0 | 44 | 0 | 280 | 240 | 325 | 37 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 161 | 0 | 9 | 57 | 5 | 0 | 25.1 | 24 | 5709.1 | 920 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 10.15 | 130 | 0 | 129 | 0 | 151 | 0 | 0 | 0 | 0.63 | 2.5 | 210 | 72 | 0 | 4 | 0 | 0 | 0 | 1.1 | 19 | 0.36 | 0 | 200 | 4 | 100 | 180 | 0 | 0 | 1100 | 0 | 4162.74 | 9871.84 | 92.64
11:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 0 | 58 | 0 | 0 | 0 | 0 | 35 | 25 | 0 | 300 | 267 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 21 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 2 | 950 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 900 | 19 | 51 | 0 | 200 | 0 | 0 | 0 | 28 | 181 | 38 | 0 | 50 | 0 | 0 | 17 | 0 | 58 | 0 | 55 | 0 | 290 | 300 | 325 | 40 | 30 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 161 | 0 | 9 | 58 | 5 | 0 | 34.48 | 17 | 5785.48 | 919 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 9.35 | 149 | 0 | 166 | 0 | 165 | 0 | 0 | 0 | 0.57 | 2.5 | 210 | 72 | 0 | 5 | 0 | 0 | 0 | 1.3 | 22 | 0.48 | 0 | 200 | 3 | 100 | 180 | 0 | 0 | 1080 | 0 | 4237.2 | 10022.68 | 92.64
12:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 0 | 43 | 0 | 0 | 0 | 0 | 35 | 25 | 0 | 300 | 316 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 2 | 950 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 980 | 20 | 51 | 0 | 197 | 0 | 0 | 0 | 26 | 215 | 41 | 0 | 45 | 0 | 0 | 17 | 0 | 60 | 0 | 59 | 0 | 300 | 320 | 374 | 40 | 10 | 0 | 2 | 163 | 13 | 0 | 85 | 0 | 0 | 0 | 161 | 0 | 9 | 57 | 5 | 0 | 35.1 | 6 | 6004.1 | 920 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 9.7 | 166 | 0 | 193 | 0 | 187 | 0 | 0 | 0 | 0.56 | 2.5 | 210 | 70 | 0 | 7 | 0 | 0 | 0 | 2 | 24 | 0.53 | 0 | 164 | 4 | 140 | 220 | 0 | 0 | 1030 | 0 | 4374.29 | 10378.39 | 92.64
13:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 36 | 0 | 32 | 0 | 0 | 0 | 0 | 72 | 25 | 0 | 300 | 234 | 0 | 0 | 10 | 20 | 250 | 0 | 0 | 0 | 0 | 19 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 8 | 900 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1020 | 19 | 51 | 0 | 199 | 0 | 0 | 0 | 28 | 182 | 43 | 13 | 46 | 5 | 9 | 17 | 0 | 64 | 0 | 54 | 0 | 290 | 320 | 324 | 40 | 17 | 0 | 2 | 163 | 13 | 0 | 85 | 0 | 0 | 0 | 161 | 0 | 9 | 58 | 5 | 0 | 32.79 | 6 | 5922.79 | 920 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 12.09 | 172 | 0 | 180 | 0 | 193 | 0 | 0 | 0 | 0.61 | 2.5 | 210 | 70 | 0 | 8 | 0 | 0 | 0 | 3.4 | 50 | 0.52 | 0 | 307 | 4 | 140 | 220 | 0 | 0 | 1130 | 0 | 4716.12 | 10638.91 | 92.63
14:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 25 | 0 | 300 | 278 | 0 | 0 | 17 | 16 | 250 | 0 | 0 | 0 | 0 | 19 | 15 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 6 | 904 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 900 | 17 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 183 | 43 | 20 | 45 | 0 | 9 | 17 | 0 | 58 | 0 | 45 | 0 | 290 | 320 | 344 | 40 | 17 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 159 | 0 | 9 | 58 | 5 | 0 | 28.47 | 6 | 5740.47 | 920 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 634.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 9.55 | 171 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 0.57 | 2.5 | 210 | 70 | 0 | 7 | 0 | 0 | 0 | 3.3 | 33 | 0.43 | 0 | 250 | 3 | 100 | 180 | 0 | 0 | 1150 | 0 | 4467.94 | 10208.41 | 92.63
15:00 | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 25 | 0 | 300 | 282 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 804 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 850 | 13 | 51 | 0 | 158 | 0 | 0 | 0 | 29 | 190 | 42 | 16 | 45 | 0 | 9 | 17 | 0 | 66 | 0 | 32 | 0 | 280 | 320 | 342 | 40 | 20 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 159 | 0 | 9 | 58 | 5 | 0 | 18.59 | 6 | 5435.59 | 920 | 273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 610.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 8.54 | 130 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0.55 | 2.5 | 210 | 68 | 0 | 5 | 0 | 0 | 0 | 2.1 | 29 | 0.33 | 0 | 190 | 3 | 100 | 180 | 0 | 0 | 1100 | 0 | 4198.08 | 9633.67 | 92.63
16:00 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 72 | 25 | 0 | 300 | 277 | 0 | 0 | 0 | 21 | 250 | 0 | 0 | 7 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 802 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 850 | 7 | 51 | 0 | 158 | 0 | 0 | 0 | 29 | 187 | 44 | 16 | 45 | 0 | 9 | 10 | 0 | 58 | 0 | 15 | 0 | 305 | 320 | 321 | 43 | 41 | 0 | 2 | 120 | 13 | 0 | 85 | 0 | 0 | 0 | 158 | 0 | 9 | 58 | 5 | 0 | 9.93 | 6 | 5498.93 | 912 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 531.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 4.5 | 130 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0.32 | 2.5 | 210 | 68 | 0 | 3 | 0 | 0 | 0 | 1.2 | 16 | 0.17 | 0 | 150 | 3 | 100 | 180 | 0 | 0 | 1050 | 0 | 3957 | 9455.93 | 92.63
17:00 | 0 | 90 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 36 | 25 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 280 | 0 | 0 | 0 | 21 | 250 | 0 | 0 | 2 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 800 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 950 | 1 | 51 | 0 | 158 | 0 | 0 | 0 | 29 | 183 | 44 | 17 | 50 | 0 | 9 | 17 | 0 | 58 | 0 | 3 | 0 | 320 | 320 | 322 | 43 | 43 | 0 | 2 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 158 | 0 | 9 | 58 | 5 | 0 | 2.27 | 6 | 5713.27 | 911 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 519.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1.45 | 135 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 0.09 | 2.5 | 210 | 68 | 0 | 1 | 0 | 0 | 0 | 0.3 | 3 | 0.05 | 0 | 200 | 4 | 140 | 180 | 0 | 42.28 | 1000 | 2 | 3980.5 | 9693.77 | 92.62
18:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 38 | 0 | 0 | 91 | 45 | 0 | 0 | 0 | 54 | 25 | 0 | 420 | 294 | 0 | 0 | 17 | 21 | 335 | 0 | 0 | 0 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 11 | 950 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 190 | 44 | 51 | 50 | 0 | 27 | 11 | 0 | 66 | 0 | 0 | 0 | 285 | 320 | 332 | 43 | 43 | 0 | 2 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 9 | 58 | 5 | 0 | 0 | 6 | 6455 | 912 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562.93 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 156 | 0 | 180 | 0 | 0 | 0 | 0 | 2.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 5 | 140 | 220 | 0 | 112.21 | 1020 | 17 | 4317.64 | 10772.64 | 92.62
19:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 124 | 48 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 295 | 0 | 0 | 0 | 21 | 335 | 0 | 0 | 0 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 20 | 950 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 196 | 44 | 35 | 50 | 0 | 27 | 11 | 0 | 60 | 0 | 0 | 0 | 295 | 320 | 339 | 43 | 43 | 0 | 2 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 9 | 58 | 5 | 0 | 0 | 0 | 6321 | 904 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.93 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 169 | 0 | 175 | 0 | 0 | 0 | 0 | 2.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 0 | 1190 | 0 | 4644.43 | 10965.43 | 92.62
19:30 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 130 | 48 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 298 | 0 | 0 | 0 | 21 | 335 | 0 | 0 | 0 | 12 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 950 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 198 | 44 | 16 | 50 | 0 | 27 | 11 | 0 | 62 | 0 | 0 | 0 | 315 | 320 | 354 | 40 | 43 | 0 | 2 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 9 | 58 | 6 | 0 | 0 | 0 | 6365 | 904 | 284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.49 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 171 | 0 | 173 | 0 | 0 | 0 | 0 | 2.5 | 211 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 140 | 220 | 0 | 0 | 1192 | 0 | 4648.99 | 11013.99
20:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 130 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 420 | 261 | 0 | 0 | 0 | 21 | 335 | 0 | 0 | 0 | 17 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 23 | 950 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 44 | 0 | 50 | 0 | 27 | 11 | 0 | 60 | 0 | 0 | 0 | 300 | 320 | 323 | 43 | 43 | 0 | 2 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 9 | 58 | 5 | 0 | 0 | 0 | 6244 | 903 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 172 | 0 | 173 | 0 | 0 | 0 | 0 | 2.5 | 211 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 0 | 1192 | 0 | 4591.84 | 10835.84 | 92.62
21:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 117 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 310 | 256 | 0 | 0 | 0 | 21 | 335 | 0 | 0 | 0 | 35 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 948 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 44 | 0 | 50 | 0 | 27 | 11 | 0 | 58 | 0 | 0 | 0 | 295 | 320 | 323 | 43 | 43 | 0 | 2 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 160 | 0 | 14 | 58 | 6 | 0 | 0 | 0 | 6117 | 904 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 170 | 0 | 171 | 0 | 0 | 0 | 0 | 2.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 0 | 1200 | 0 | 4602.5 | 10719.5 | 92.61
22:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 100 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 310 | 293 | 0 | 0 | 0 | 21 | 250 | 0 | 0 | 0 | 35 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 910 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 44 | 0 | 50 | 0 | 9 | 17 | 0 | 58 | 0 | 0 | 0 | 280 | 320 | 287 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 160 | 0 | 9 | 58 | 5 | 0 | 0 | 0 | 5706 | 903 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 169 | 0 | 169 | 0 | 0 | 0 | 0 | 2.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 100 | 180 | 0 | 0 | 1050 | 0 | 4168.5 | 9874.5 | 92.61
23:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 55 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 270 | 0 | 0 | 0 | 21 | 250 | 0 | 0 | 0 | 35 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 908 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 180 | 38 | 0 | 50 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 285 | 280 | 292 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 9 | 58 | 5 | 0 | 0 | 0 | 5519.5 | 903 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 166 | 0 | 160 | 0 | 0 | 0 | 0 | 2.5 | 158 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 180 | 0 | 0 | 980 | 0 | 4012.5 | 9532 | 92.61
Total KWH | 0 | 1180800 | 445920 | 0 | 0 | 0 | 0 | 0 | 9284400 | 0 | 0 | 120600 | 496440 | 0 | 1115712 | 247680 | 0 | 0 | 0 | 444960 | 502920 | 0 | 7818000 | 6948509 | 0 | 0 | 69089 | 522400 | 6503357 | 0 | 0 | 67281 | 112800 | 451200 | 338040 | 0 | 0 | 48927 | 0 | 0 | 0 | 413760 | 0 | 0 | 0 | 0 | 0 | 18602 | 899520 | 0 | 389760 | 20021818.18 | 0 | 0 | 0 | 0 | 0 | 3813762 | 0 | 0 | 0 | 20165452 | 130815 | 1051167 | 0 | 4165091 | 0 | 0 | 0 | 600960 | 4603000 | 955512 | 190080 | 1230960 | 13440 | 194040 | 334520 | 0 | 1290240 | 0 | 352527 | 0 | 7202500 | 6948700 | 8142000 | 827136 | 760000 | 0 | 51792 | 3562282 | 340992 | 0 | 1704000 | 653952 | 0 | 0 | 4627440 | 0 | 196800 | 1072800 | 154560 | 2250 | 204940 | 170400 | 134176605.18 | 20744727 | 6532416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 496800 | 0 | 0 | 13707273 | 0 | 0 | 0 | 0 | 0 | 0 | 111120 | 0 | 0 | 0 | 322690 | 0 | 75000 | 3807782 | 0 | 3942109 | 0 | 3996536 | 0 | 0 | 0 | 4800 | 67014 | 5064000 | 1676072 | 0 | 42912 | 0 | 0 | 0 | 15330.12 | 208080 | 3181.5 | 0 | 5149000 | 133913 | 2682000 | 5048620 | 0 | 589090 | 23329454.55 | 31200 | 97781120.17 | 231957725.35

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
| Date : | 22-01-2025
Power Supply Scenario
Day Peak Generation |  |  | 10378.39 | MW | 12:00 Hr. | Energy Generated |  |  | 231957.7253 |  | MWHr
Day Peak Demand |  |  | 10422.39 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1461 |  | MWHr
Evening Peak Generation |  |  | 11013.99 | MW | 19:30 Hr. | Energy Demand |  |  | 233418.7253 |  | MWHr
Evening Peak Demand |  |  | 11100.99 | MW | 19:30 Hr.
Minimum Generation of the Day |  |  | 7543 | MW | 05:00 Hr.
Maximum Generation of the Day |  |  | 11013.99 | MW | 19:30 Hr.
Zone-wise Generation Summary (MWHr.)
|  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
Dhaka Zone |  |  | 32368.826 | 0 | 4234.001 | 0 | 0 | 67.281 | 0 | 0 | 36670.108 | Gas | 110699.302 | Gas | 397656735.03
Chattogram Zone |  |  | 4203.522 | 40187.2702 | 48.927 | 0 | 899.52 | 149.417 | 0 | 413.76 | 45902.4162 | Coal | 75994.8867 | Coal | 531909829.9239
Cumilla Zone |  |  | 12941.21 | 0 | 397.56 | 0 | 0 | 352.527 | 1290.24 | 0 | 14981.537 | HFO | 6262.808 | HFO | 117267514.5
Mymensingh Zone |  |  | 154.56 | 0 | 1440 | 0 | 0 | 207.19 | 0 | 0 | 1801.75 | HSD | 0 | HSD | 0
Sylhet Zone |  |  | 34820.794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34820.794 | Hydro | 899.52 | Hydro | 89952
Khulna Zone |  |  | 6532.416 | 0 | 0 | 0 | 0 | 496.8 | 20744.727 | 0 | 27773.943 | Solar | 1945.2086 | Solar | 29663690.127
Barishal Zone |  |  | 7864.533 | 29067.5445 | 31.2 | 0 | 0 | 3.1815 | 0 | 0 | 36966.459 | Import | 35742.24 | Import | 177404436.81
Rajshahi Zone |  |  | 11813.441 | 0 | 111.12 | 0 | 0 | 402.49 | 13707.273 | 0 | 26034.324 | Wind | 413.76 | Wind | 6454656
Rangpur Zone |  |  | 0 | 6740.072 | 0 | 0 | 0 | 266.3221 | 0 | 0 | 7006.3941
Total |  |  | 110699.302 | 75994.8867 | 6262.808 | 0 | 899.52 | 1945.2086 | 35742.24 | 413.76 | 231957.7253
Production Cost (Tk.)
|  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  | Gas | 397656735.03 |  | Hydro | 89952
|  |  | Coal | 531909829.9239 |  | Solar | 29663690.127
|  |  | HFO | 117267514.5 |  | Import | 177404436.81
|  |  | HSD | 0 |  | Wind | 6454656
|  |  |  | Total: | 1260446814.3909 |  | Tk.
Status of unavailable Power Plant
| Planned S/D |  |  |  |  | Forced S/D
| Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
| 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
| 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
| 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
| 4 | Barapukuria TPP Unit-2 |  |  | 85
| 5 | Khulna 330 MW CCPP ST |  |  | 110
| 6 | Siddhirgonj 210 MW TPP |  |  | 115
| 7 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
| 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
|  |  |  | Total | 1184 |  |  |  | Total | 435.09
|  |  | Total Unavailable Capacity |  |  |  | 1619.09
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  | Zone |  | Load-Shed |  | Demand
|  |  | Dhaka |  | 18 |  | 3944
|  |  | Chattogram |  | 0 |  | 1126
|  |  | Cumilla |  | 0 |  | 884
|  |  | Mymensingh |  | 65 |  | 958
|  |  | Sylhet |  | 0 |  | 377
|  |  | Khulna |  | 0 |  | 1186
|  |  | Barishal |  | 0 |  | 296
|  |  | Rajshahi |  | 0 |  | 1059
|  |  | Rangpur |  | 0 |  | 674
|  |  | Total |  | 83 |  | 10504
Event Summary
Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
08:03 | 15:05 | Ramganj 132/33kV S/S 132 Kv Bus- A Scheduled S/D Due to Annual Maintenance work
08:13 | 15:43 | Keraniganj-Sreenagar 132kV Ckt-1 Scheduled S/D from Srinagar 132/33kV end Due to Deadline
checking purpose. and from Keranigonj 230/132/33kV end Due to Dead line Checking from
Sree Nagar End
08:20 | 17:45 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to 33 kV side
maintenance
08:21 | 17:45 | Bog-Sherpur 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to 33 kV side
maintenance
08:23 | 15:35 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-02 Scheduled S/D Due to Annual maintenance
08:23 | 15:18 | Sholosohor 132/33kV S/S Sholoshahar-Khulshi Ckt-1 Scheduled S/D Due to Scheduled line
check by khulshi S/S.
08:27 |  | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to OLTC maintenance
08:28 | 15:54 | Magura 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Annual Maintenance
08:29 | 15:53 | Magura 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Annual Maintenance
08:39 | 18:26 | Ashuganj-Bhulta 400 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end.
08:44 | 17:50 | Sirajganj-Sreepur 230 kV Ckt-1 Scheduled S/D from Sirajgonj 230 end Due to Annual
Maintenance
08:54 | 17:35 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Forced S/D from Siddhirganj 132/33kV end | [7 empty] | 16.0MW load
|  | Due to S/D Taken by NLDC. | [7 empty] | interrup.
Siddhirganj
132/33kV end
09:05 | 17:52 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 Scheduled S/D
09:05 | 19:27 | Baghabari-Ruppur 230 KV CKT-1 S/D [Annual Maintenance]
09:06 | 18:04 | Fatullah-Madanganj 132 kV Ckt-2 Scheduled S/D from Fatullah 132/33kV end Due to
Maintenance Work
09:08 | 18:05 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Scheduled S/D
09:10 | 17:15 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end.
09:14 | 17:39 | Haripur 230/132kV S/S Auto TR-3 LT Scheduled S/D Due to Annual maintenence
09:14 | 17:39 | Haripur 230/132kV S/S Auto TR-3 HT Scheduled S/D Due to Annual maintenance
09:14 | 17:31 | Mymensingh-Netrokona 132kV Ckt-2 Project Work S/D from Netrakona 132/33kV end. and from
Mymensingh 132/33kVend.
09:14 | 17:31 | Mymensingh-Netrokona 132kV Ckt-2 Project Work S/D from Netrakona 132/33kV end. and from
Mymensingh 132/33kVend.
09:14 | 17:31 | Mymensingh-Netrokona 132kV Ckt-2 Project Work S/D from Netrakona 132/33kV end. and from
Mymensingh 132/33kVend.
09:18 | 16:20 | Hathazari-Raozan 230kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end.
09:19 | 16:20 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Scheduled S/D Due to Annual maintenance
09:19 | 16:26 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Scheduled S/D Due to Annual maintenance
09:23 | 17:42 | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to Dhaka pbs-1 33 kv underground | [7 empty] | 50.0MW load
|  | cable work. | [7 empty] | interrup.
09:24 | 17:40 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to Dhaka pbs-1 33 kv underground | [7 empty] | 40.0MW load
|  | cable work. | [7 empty] | interrup.
09:29 | 11:43 | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to Dhaka pbs-1 underground cable | [7 empty] | 40.0MW load
|  | work. | [7 empty] | interrup.
09:30 | 11:43 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to Dhaka pbs-1 underground cable | [7 empty] | 40.0MW load
|  | work. | [7 empty] | interrup.
09:43 | 16:56 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Kishoreganj 132/33kV end. and from
Mymensingh 132/33kVend.
09:45 | 17:37 | Aminbazar 400/230/132kV S/S 400/132kV Interim Transformer LT Scheduled S/D
10:03 | 16:16 | Goalpara- Khulna (C) 132kV Ckt-1 Project Work S/D from Goalpara 132/33kV end Due to opgw
work and from Khulna (C) end Due to shutdown taken by SPMD
10:09 | 18:55 | Rangpur 132/33kV S/S Rangpur-GTPS Scheduled S/D Due to Project work
10:12 | 17:32 | Aminbazar 400/230/132kV S/S 400/132kV Interim Transformer HT Scheduled S/D Due to None
10:14 | 18:34 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to For tan delta test
10:15 | 18:34 | Fenchuganj 230/132/33kV S/S AT-02 HT Scheduled S/D Due to For tan delta test
10:22 | 13:32 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Scheduled S/D Due to T-4 Transformer
Shutdown under Ten-delta Test
10:23 | 13:28 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Scheduled S/D Due to T-4 Transformer
Shutdown under Ten-delta Test
11:53 | 14:41 | Joypurhat 132/33kV S/S Transformer T-2 (417 T) LT Scheduled S/D Due to 417T T-2
Transformer Shutdown under Ten-delta Test
11:54 | 14:36 | Joypurhat 132/33kV S/S Transformer T-2 (417 T) HT Scheduled S/D Due to 417T T-2
Transformer Shutdown under Ten-delta Test
| 12:01 | Khulna (C) S/S North-WestCkt-1 is restored.
12:06 | 15:54 | Khulna (C) S/S North- West Ckt-2 Scheduled S/D Due to taken by NWPGCL due to annual
maintenance
12:28 | 16:00 | Baghabari 230/132kV S/S Bus-2 Scheduled S/D Due to Annual Maintenance
13:24 | 16:02 | Aminbazar 400/230/132kV S/S ATR-01 LT Tripped showing 86 Master relay relays Due to Non
directional earth fault
13:24 | 14:56 | Aminbazar 400/230/132kV S/S ATR-01 HT Tripped showing 86 relays Due to Non directional
earth fault
13:36 | 16:50 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) LT Scheduled S/D Due to 427T T-3
Transformer Shutdown under Ten-delta Test
13:37 | 16:43 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) HT Scheduled S/D Due to 427T T-3
Transformer Shutdown under Ten-delta Test
14:37 | 17:27 | Sreepur 230/132/33kV S/S 230 kV BUS-2 Forced S/D Due to Polythene and thread removing.
14:42 | 17:30 | Joypurhat 132/33kV S/S Transformer T-1 (407 T) LT Scheduled S/D Due to 407T T-1
Transformer Shutdown under Ten-delta Test
14:44 | 17:28 | Joypurhat 132/33kV S/S Transformer T-1 (407 T) HT Scheduled S/D Due to 407T T-1
Transformer Shutdown under Ten-delta Test
15:08 | 18:40 | Ramganj 132/33kV S/S 132 Kv Bus-B Scheduled S/D Due to Annual Maintenance work
15:19 | 17:08 | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to Dhaka pbs-1 33 kv underground | [7 empty] | 40.0MW load
|  | cable work. | [7 empty] | interrup.
15:19 | 17:08 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to Dhaka pbs-1 33 kv underground | [7 empty] | 40.0MW load
|  | cable work. | [7 empty] | interrup.
| 18:26 | Ashuganj-Bhulta 400 kV Ckt-2 is restored.
| 18:40 | Chowmuhani-Ramganj 132 kV Ckt-1 is restored.
| 18:45 | Kabirpur -Kodda 132kV Ckt-1 is restored.
19:30 |  | Peak generation 11013 MW
20:12 | 21:31 | Kabirpur -Kodda 132kV Ckt-2 Forced S/D from Kabirpur 132/33kV end Due to High
temperature maintenance work.
21:00 |  | Baghabari-Ruppur 230 KV CKT-1 syn from Ruppur end.
21:32 | 22:49 | Mymensingh RPCL-Tangail 132kV Ckt-1 Forced S/D from Ghatail 132/33kV end Due to As per | [7 empty] | 5.0MW load
|  | direction of NLDC due to Red hot at Tangail Grid S/S. | [7 empty] | interrup. Ghatail
132/33kV end
21:37 | 22:50 | Mymensingh RPCL-Tangail 132kV Ckt-2 Forced S/D from Ghatail 132/33kV end Due to As per
direction of NLDC due to Red hot at Tangail Grid S/S.
21:53 | 22:44 | Chowmuhani-Ramganj 132 kV Ckt-1 Forced S/D from Chowmuhani 132/33kV end Due to A mad
clambing a 132kv Mizdee tower and from Ramganj 132/33kV end Due to a mentally disabled
person climbing on transmission tower
| 21:58 | Bhulta-Haripur 132 kV Ckt-1 is restored.
23:12 | 23:45 | Bhulta-Haripur 132 kV Ckt-1 Forced S/D from Haripur 230/132kV end Due to Flashing at
Bhulta end.
01:00 |  | Sirajgonj 225MW CCPP Unit-2 ST Shutdown with remarks:- Plant has been given shutdown as
per NLDC demand. Shutdown command executed @23:59hr on 22.01.2025 by Mr. Rayhan,
Assistant Engineer, NLDC.
01:00 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
01:09 |  | Sirajgonj 225MW CCPP Unit-2 GT Shutdown with remarks:- Plant has been given shutdown as
per NLDC demand. Shutdown command executed @23:59hr on 22.01.2025 by Mr. Rayhan,
Assistant Engineer, NLDC.
01:09 |  | Sirajgonj Gas 225 MW Unit-2 was shutdown in order to provide gas for the DCT of Bheramara
410 MW CCPP.
01:09 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- GT
01:10 |  | Chowmuhani 132/33kV S/S TR1 Tripped showing Overcurrent E/F relay. relays Due to 33 KV | [7 empty] | 10.0MW load
|  | Station transformer lope cut out three phases. | [7 empty] | interrup.
04:15 |  | Aminbazar-Meghnaghat 400kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing 1002B
CB pole discrepency operated relays Due to 1002B CB pole discrepency operated
04:15 |  | Aminbazar 400/230/132kV S/S ATR-01 LT Tripped showing 86-1 &86-2 master relay operated
relays Due to 86-1 &86-2 master relay operated
04:15 |  | Aminbazar 400/230/132kV S/S ATR-01 HT Tripped showing 86-1 &86-2 master relay operated
relays Due to 86-1 &86-2 master relay operated
05:00 |  | Minimum Generation: 7313 MW.
07:14 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
07:14 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
07:21 |  | Sylhet CCPP 225 MW was shutdown to change air filter. | [7 empty] | 150MW generation
interrup.
07:38 |  | Haripur-Narsingdi 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end.
07:51 |  | Chowmuhani-Ramganj 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 401 | 9284400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 7818000 | Gas shortage
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 298 | 6948509 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | -
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6503357 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 120600 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 247680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 69089 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 451200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 338040 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 502920 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 21 | 522400 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 25 | 445920 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 150 | 130 | 1115712 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1180800 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 444960 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 67281 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 0 | 496440 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 12 | 112800 | -
Dhaka Area Total |  |  |  |  | 5842.27 | 1837 | 36670108
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130815 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 899520 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3813762 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 389760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 18602 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 48927 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1050 | 20165452 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 26 | 413760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 950 | 20021818.18 | -
Chattogram Area Total |  |  |  |  | 4915.22 | 2248 | 45902416.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 198 | 4603000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | schedule outage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 44 | 955512 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 600960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 4165091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1051167 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1230960 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 13440 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 62 | 1290240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 11 | 334520 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 194040 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 190080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 352527 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 685 | 14981537
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 6 | 154560 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 2250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1072800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 196800 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 204940 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 170400 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 73 | 1801750
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 43 | 760000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3562282 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 40 | 827136 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 51792 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 653952 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1704000 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 159 | 4627440 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 340992 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7202500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 354 | 8142000 | FGMO Available, but GT Load set maximum 260MW
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 6948700 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1522 | 34820794
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 904 | 20744727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 284 | 6532416 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 496800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1188 | 27773943
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 589090 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 6 | 133913 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2682000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1192 | 23329454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5048620 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 31200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5149000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3181.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1865 | 36966459.05
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 161 | 3807782 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 171 | 3942109 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 173 | 3996536 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 67014 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 111120 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 4800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 756.49 | 13707273 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 75000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 322690 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1314.99 | 26034324
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 70 | 1676072 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 211 | 5064000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 15330.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 42912 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 208080 | -
Rangpur Area Total |  |  |  |  | 950 | 281 | 7006394.12
Eastern Grid Total |  |  |  |  | 16772.748 | 6365 | 134176605.18
Western Grid Total |  |  |  |  | 11614.5 | 4648.99 | 97781120.17
National Grid Total |  |  |  |  | 28387.248 | 11013.99 | 231957725.35
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-01-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7205.75 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3214.2 | MW
i) Dhaka area |  |  | 3926.05 |  | MW | i) Khulna area |  |  |  | 1185.5 | MW
ii) Chattogram area |  |  | 1125.7 |  | MW | ii) Barishal area |  |  |  | 295.7 | MW
iii) Cumilla area |  |  | 884 |  | MW | iii) Rajshahi area |  |  |  | 1059 | MW
iv) Mymensingh area |  |  | 893 |  | MW | iv) Rangpur area |  |  |  | 674 | MW
v) Sylhet area |  |  | 377 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10419.95 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 55 | 18:00 | 133 | Purbachal | 14 | 13:00
2 | AKSML | 101.6 | 07:00 | 68 | Jamalpur | 92 | 07:00 | 134 | Purbasadipur | 108 | 18:30
3 | Aftabnagar | 24 | 12:00 | 69 | Jashore | 112 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 76 | 13:00 | 70 | Jhenaidah | 95 | 18:30 | 136 | Rahim | 45 | 18:00
5 | Agrabad | 64 | 18:00 | 71 | Joydebpur | 129 | 12:00 | 137 | Rajbari | 54 | 19:00
6 | Amnura | 44 | 20:00 | 72 | Joypurhat | 44 | 18:30 | 138 | Rajendrapur | 100 | 10:00
7 | Ashuganj | 61 | 20:00 | 73 | Juldah | 12 | 10:00 | 139 | Rajshahi | 88 | 13:00
8 | BSRM | 194 | 22:00 | 74 | KSRM | 40 | 15:00 | 140 | Rajshahi-230 | 56 | 13:00
9 | Bagerhat | 61 | 18:30 | 75 | Kabirpur | 188 | 19:30 | 141 | Ramganj | 90 | 18:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 50 | 20:00 | 142 | Rampur | 24 | 13:00
11 | Bakulia | 66 | 18:00 | 77 | Kallyanpur | 63 | 12:00 | 143 | Rangamati | 12 | 18:00
12 | Banani | 38.4 | 13:00 | 78 | Kalurghat | 30 | 13:00 | 144 | Rangpur | 96 | 18:00
13 | Bangabhaban | 8 | 10:00 | 79 | Kamrangirchar | 54.8 | 13:00 | 145 | Ruppur | 4.6 | 09:00
14 | Barapukuria | 53 | 18:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 14 | 03:00
15 | Barguna | 14 | 19:30 | 81 | Kazla | 90 | 13:00 | 147 | Saidpur | 99 | 18:00
16 | Barishal | 80 | 13:00 | 82 | Keranigonj | 58 | 13:00 | 148 | Satkhira | 91 | 18:30
17 | Barishal-230 | 60 | 19:30 | 83 | Khagrachori | 24 | 18:30 | 149 | Satmasjid | 82 | 14:00
18 | Baroaulia | 64 | 11:00 | 84 | Khulna | 70 | 18:30 | 150 | Savar | 158 | 12:00
19 | Baroirhat | 54 | 18:30 | 85 | Khulshi | 128 | 00:00 | 151 | SevenRings | 19.68 | 00:00
20 | Bashundhara | 119 | 13:00 | 86 | Kishoreganj | 128 | 20:00 | 152 | ShahCement | 22 | 13:00
21 | BashundharaCement | 12 | 00:00 | 87 | Kodda | 280 | 15:00 | 153 | Shahjadpur | 62 | 18:30
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 27 | 18:00 | 154 | Shahjibazar | 84 | 21:00
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 51 | 08:00 | 155 | Shahmirpur | 42 | 00:00
24 | Bhaluka | 112 | 08:00 | 90 | Kushtia | 93 | 18:30 | 156 | Shariatpur | 52 | 20:00
25 | Bhandaria | 34 | 21:00 | 91 | Lalbag | 59 | 18:30 | 157 | Sherpur | 104 | 00:00
26 | Bhangura | 26 | 18:00 | 92 | Lalmonirhat | 46 | 08:00 | 158 | Shikalbaha | 21 | 17:00
27 | Bheramara(GK) | 41 | 18:30 | 93 | MI_Cement | 17.7 | 12:00 | 159 | Shitalakhya | 63 | 13:00
28 | Bhulta | 212 | 23:00 | 94 | Madanganj | 25 | 13:00 | 160 | Sholosohor | 31 | 16:00
29 | Bog-Sherpur | 60 | 08:00 | 95 | Madaripur | 66 | 20:00 | 161 | Shyampur | 158 | 10:00
30 | Bogura | 176 | 02:00 | 96 | Madartek | 57.8 | 13:00 | 162 | Siddhirganj | 102 | 12:00
31 | Borhanuddin | 54 | 22:00 | 97 | Madunaghat | 37 | 18:00 | 163 | Sirajganj | 82 | 19:00
32 | Brahmanbaria | 102 | 19:00 | 98 | Magura | 44 | 18:30 | 164 | Sonargaon | 82 | 19:30
33 | Cantonment | 80 | 13:00 | 99 | Mahasthangarh | 50 | 19:30 | 165 | Sreemongol | 49 | 18:00
34 | Chandpur | 41 | 21:00 | 100 | Manikganj | 120 | 18:30 | 166 | Sreepur | 81 | 12:00
35 | Chandraghona | 25 | 18:30 | 101 | Maniknagar | 50 | 13:00 | 167 | Srinagar | 30.28 | 13:00
36 | Chapai | 58 | 08:00 | 102 | Matarbari | 35 | 18:00 | 168 | Sunamganj | 38 | 18:30
37 | Charsaidpur | 43 | 11:00 | 103 | Matuail | 58 | 12:00 | 169 | Sylhet | 28 | 18:00
38 | Chauddagram | 46 | 12:00 | 104 | Millgate | 66 | 09:00 | 170 | Sylhet-132 | 72 | 18:00
39 | Chhatak | 23 | 18:30 | 105 | Mirpur | 95 | 18:30 | 171 | TK | 20.5 | 18:00
40 | Chowmuhani | 135 | 18:00 | 106 | Mirsorai | 8 | 01:00 | 172 | Tangail | 140 | 18:30
41 | Chuadanga | 73 | 13:00 | 107 | Mirzapur | 48 | 18:30 | 173 | Thakurgaon | 73 | 18:30
42 | Coxsbazar | 105 | 18:30 | 108 | Mithapukur | 61 | 18:30 | 174 | Tongi | 94 | 11:00
43 | Cumilla(N) | 109 | 18:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 22 | 18:00
44 | Cumilla(S) | 128 | 13:00 | 110 | Mogbazar | 96.1 | 13:00 | 176 | Ullon | 34 | 13:00
45 | Daudkandi | 94 | 20:00 | 111 | Mongla | 35 | 08:00 | 177 | Uttara | 54 | 14:00
46 | Dhaka | 30 | 12:00 | 112 | Motijheel | 26 | 13:00 | 178 | UttaraNew | 36 | 09:00
47 | Dhamrai | 104 | 12:00 | 113 | Muktagacha | 26 | 18:00 | 179 | Zigatola | 54 | 13:00
48 | Dhanmondi | 95.3 | 13:00 | 114 | Munshiganj | 68 | 21:00
49 | Dohazari | 70 | 18:00 | 115 | Mymensingh | 178 | 18:00
50 | Faridpur | 109 | 19:30 | 116 | Naogaon | 97 | 13:00
51 | Fatullah | 68 | 17:00 | 117 | Narail | 42 | 18:30
52 | Fenchuganj | 24 | 19:30 | 118 | Narinda | 59 | 13:00
53 | Feni | 64 | 18:00 | 119 | Narshingdi | 153 | 19:30
54 | GPH | 88 | 04:00 | 120 | Natore | 108 | 18:30
55 | Ghatail | 32 | 08:00 | 121 | Nawabganj | 35.2 | 21:00
56 | Ghorashal | 8 | 00:00 | 122 | Netrakona | 131 | 07:00
57 | Ghorashal-230 | 76 | 19:00 | 123 | New | 70.5 | 12:00
58 | Goalpara | 36 | 17:00 | 124 | Niamatpur | 79 | 08:00
59 | Gollamari | 56 | 13:00 | 125 | Noapara | 35 | 18:30
60 | Gopalganj | 78 | 18:30 | 126 | PHP | 10 | 13:00
61 | Gulshan | 68 | 13:00 | 127 | Pabna | 66 | 18:30
62 | Halishahar | 45 | 10:00 | 128 | Palashbari | 76 | 18:00
63 | HaripurSBU | 153 | 01:00 | 129 | Panchagarh | 40 | 19:00
64 | Hasnabad | 62 | 12:00 | 130 | Patuakhali | 53.7 | 20:00
65 | Hathazari | 51 | 18:30 | 131 | Payra | 14 | 13:00
66 | Ishurdi | 56 | 18:30 | 132 | Postogola | 42 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9079 | 30 |  | 9110
1:00 | 8497 | 30 |  | 8528
2:00 | 7914 | 30 |  | 7945
3:00 | 7742 | 30 |  | 7773
4:00 | 7594 | 30 |  | 7625
5:00 | 7543 | 30 |  | 7574
6:00 | 7731.5 | 30 |  | 7762.5
7:00 | 8627.26 | 30 |  | 8658.26
8:00 | 9498.17 | 52 |  | 9552.17
9:00 | 10023.69 | 52 |  | 10077.69
10:00 | 9871.84 | 38 |  | 9911.84
11:00 | 10022.68 | 38 |  | 10062.68
12:00 | 10378.39 | 42 |  | 10422.39
13:00 | 10638.91 | 61 |  | 10702.91
14:00 | 10208.41 | 67 |  | 10278.41
15:00 | 9633.67 | 66 |  | 9702.67
16:00 | 9455.93 | 64 |  | 9522.93
17:00 | 9693.77 | 56 |  | 9752.77
18:00 | 10772.64 | 95 |  | 10871.64
19:00 | 10965.43 | 101 |  | 11071.43
19:30 | 11013.99 | 83 |  | 11100.99
20:00 | 10835.84 | 81 |  | 10920.84
21:00 | 10719.5 | 58 |  | 10780.5
22:00 | 9874.5 | 250 |  | 10135.5
23:00 | 9532 | 100 |  | 9636
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5001.5 | 4077.5 | 9079 | DAILY LOAD CURVE
00:30 | 4859.5 | 3928.5 | 8788
01:00 | 4717.5 | 3779.5 | 8497 | 22-01-2025
01:30 | 4692.5 | 3513 | 8205.5
02:00 | 4667.5 | 3246.5 | 7914
02:30 | 4616 | 3212 | 7828
03:00 | 4564.5 | 3177.5 | 7742
03:30 | 4534.5 | 3133.5 | 7668
04:00 | 4504.5 | 3089.5 | 7594
04:30 | 4548 | 3020.5 | 7568.5
05:00 | 4591.5 | 2951.5 | 7543
05:30 | 4675.75 | 2961.5 | 7637.25
06:00 | 4760 | 2971.5 | 7731.5
06:30 | 5041.705 | 3137.675 | 8179.38
07:00 | 5323.41 | 3303.85 | 8627.26
07:30 | 5447.33 | 3615.385 | 9062.715
08:00 | 5571.25 | 3926.92 | 9498.17
08:30 | 5633.175 | 4127.755 | 9760.93
09:00 | 5695.1 | 4328.59 | 10023.69
09:30 | 5702.1 | 4245.665 | 9947.765
10:00 | 5709.1 | 4162.74 | 9871.84
10:30 | 5747.29 | 4199.97 | 9947.26
11:00 | 5785.48 | 4237.2 | 10022.68
11:30 | 5894.79 | 4305.745 | 10200.535
12:00 | 6004.1 | 4374.29 | 10378.39
12:30 | 5963.445 | 4545.205 | 10508.65
13:00 | 5922.79 | 4716.12 | 10638.91
13:30 | 5831.63 | 4592.03 | 10423.66
14:00 | 5740.47 | 4467.94 | 10208.41
14:30 | 5588.03 | 4333.01 | 9921.04
15:00 | 5435.59 | 4198.08 | 9633.67
15:30 | 5467.26 | 4077.54 | 9544.8
16:00 | 5498.93 | 3957 | 9455.93
16:30 | 5606.1 | 3968.75 | 9574.85
17:00 | 5713.27 | 3980.5 | 9693.77
17:30 | 6084.135 | 4149.07 | 10233.205
18:00 | 6455 | 4317.64 | 10772.64
18:30 | 6388 | 4481.035 | 10869.035
19:00 | 6321 | 4644.43 | 10965.43
19:30 | 6365 | 4648.99 | 11013.99
20:00 | 6244 | 4591.84 | 10835.84
20:30 | 6180.5 | 4597.17 | 10777.67 |  | Executive Engineer
21:00 | 6117 | 4602.5 | 10719.5 |  | Network Operation Division
21:30 | 5911.5 | 4385.5 | 10297
22:00 | 5706 | 4168.5 | 9874.5
22:30 | 5612.75 | 4090.5 | 9703.25
23:00 | 5519.5 | 4012.5 | 9532

## En-Curve
QF-LDC-12
Date | 22-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2924 | 1742 | 920 | 0 | 52 | 426 | 35 | 2779 | 0 | 34 | 155 | 0 | 0 | 12 | 30 | DAILY ENERGY CURVE
00:30 | 2881.5 | 1737.5 | 920 | 0 | 49 | 423 | 35 | 2571 | 0 | 25.5 | 129.5 | 0 | 0 | 16 | 30 | 22-01-2025
01:00 | 2839 | 1733 | 920 | 0 | 46 | 420 | 35 | 2363 | 0 | 17 | 104 | 0 | 0 | 20 | 30
01:30 | 2776.5 | 1709.5 | 860 | 0 | 46 | 420 | 35 | 2247.5 | 0 | 8.5 | 79 | 0 | 0 | 23.5 | 30 |  | Total Energy | 231.9577 |  | MKWHr
02:00 | 2714 | 1686 | 800 | 0 | 46 | 420 | 35 | 2132 | 0 | 0 | 54 | 0 | 0 | 27 | 30 |  | Energy not Served | 1.461 |  | MKWHr
02:30 | 2681 | 1683.5 | 764.5 | 0 | 43 | 421.5 | 35 | 2130 | 0 | 0 | 45 | 0 | 0 | 24.5 | 30 |  | Energy Requirement | 233.4187 |  | MKWHr
03:00 | 2648 | 1681 | 729 | 0 | 40 | 423 | 35 | 2128 | 0 | 0 | 36 | 0 | 0 | 22 | 30
03:30 | 2614.5 | 1595.5 | 729 | 0 | 43 | 421.5 | 35 | 2174.5 | 0 | 0 | 36 | 0 | 0 | 19 | 30
04:00 | 2581 | 1510 | 729 | 0 | 46 | 420 | 35 | 2221 | 0 | 0 | 36 | 0 | 0 | 16 | 30
04:30 | 2511 | 1476 | 729.5 | 0 | 46 | 420 | 35 | 2297 | 0 | 0 | 36 | 0 | 0 | 18 | 30
05:00 | 2441 | 1442 | 730 | 0 | 46 | 420 | 35 | 2373 | 0 | 0 | 36 | 0 | 0 | 20 | 30
05:30 | 2489 | 1447.75 | 729.5 | 0 | 47 | 421 | 35 | 2415 | 0 | 0 | 37 | 0 | 0 | 16 | 30
06:00 | 2537 | 1453.5 | 729 | 0 | 48 | 422 | 35 | 2457 | 0 | 0 | 38 | 0 | 0 | 12 | 30
06:30 | 2661 | 1584.5 | 776.5 | 0 | 46 | 422.5 | 35 | 2541 | 2.88 | 26.5 | 72.5 | 0 | 0 | 11 | 30
07:00 | 2785 | 1715.5 | 824 | 0 | 44 | 423 | 35 | 2625 | 5.76 | 53 | 107 | 0 | 0 | 10 | 30
07:30 | 2802 | 1766.5 | 872 | 0 | 43 | 426 | 35 | 2870.5 | 33.715 | 72 | 130 | 0 | 0 | 12 | 41
08:00 | 2819 | 1817.5 | 920 | 0 | 42 | 429 | 35 | 3116 | 61.67 | 91 | 153 | 0 | 0 | 14 | 52
08:30 | 2762.5 | 1766.5 | 920 | 0 | 44 | 500 | 37.5 | 3362 | 92.93 | 91 | 172.5 | 0 | 0 | 12 | 52
09:00 | 2706 | 1715.5 | 920 | 0 | 46 | 571 | 40 | 3608 | 124.19 | 91 | 192 | 0 | 0 | 10 | 52
09:30 | 2670 | 1695 | 920 | 0 | 51 | 589.5 | 40 | 3520 | 168.265 | 83 | 201.5 | 0 | 0 | 9.5 | 45
10:00 | 2634 | 1674.5 | 920 | 0 | 56 | 608 | 40 | 3432 | 212.34 | 75 | 211 | 0 | 0 | 9 | 38
10:30 | 2683.5 | 1679 | 919.5 | 0 | 57 | 608 | 40 | 3422 | 239.26 | 75 | 212 | 0 | 0 | 12 | 38
11:00 | 2733 | 1683.5 | 919 | 0 | 58 | 608 | 40 | 3412 | 266.18 | 75 | 213 | 0 | 0 | 15 | 38
11:30 | 2848 | 1752.5 | 919.5 | 0 | 59 | 608.5 | 40 | 3408 | 275.035 | 75 | 199.5 | 0 | 0 | 15.5 | 40
12:00 | 2963 | 1821.5 | 920 | 0 | 60 | 609 | 40 | 3404 | 283.89 | 75 | 186 | 0 | 0 | 16 | 42
12:30 | 2922 | 1778.5 | 920 | 0 | 62 | 633.5 | 40 | 3520.5 | 308.65 | 75 | 234 | 0 | 0 | 14.5 | 51.5
13:00 | 2881 | 1735.5 | 920 | 0 | 64 | 658 | 40 | 3637 | 333.41 | 75 | 282 | 0 | 0 | 13 | 61
13:30 | 2830.5 | 1713 | 920 | 0 | 61 | 646.295 | 40 | 3560.5 | 311.865 | 75 | 251 | 0 | 0 | 14.5 | 64
14:00 | 2780 | 1690.5 | 920 | 0 | 58 | 634.59 | 40 | 3484 | 290.32 | 75 | 220 | 0 | 0 | 16 | 67
14:30 | 2742 | 1649.5 | 920 | 0 | 62 | 622.325 | 40 | 3353 | 251.215 | 75 | 192.5 | 0 | 0 | 13.5 | 66.5
15:00 | 2704 | 1608.5 | 920 | 0 | 66 | 610.06 | 40 | 3222 | 212.11 | 75 | 165 | 0 | 0 | 11 | 66
15:30 | 2706.5 | 1634.5 | 916 | 0 | 62 | 570.685 | 40 | 3176 | 163.615 | 80 | 183.5 | 0 | 0 | 12 | 65
16:00 | 2709 | 1660.5 | 912 | 0 | 58 | 531.31 | 40 | 3130 | 115.12 | 85 | 202 | 0 | 0 | 13 | 64
16:30 | 2749 | 1696 | 911.5 | 0 | 58 | 525.57 | 40 | 3200.14 | 71.14 | 112.5 | 196.5 | 0 | 0 | 14.5 | 60
17:00 | 2789 | 1731.5 | 911 | 0 | 58 | 519.83 | 40 | 3270.28 | 27.16 | 140 | 191 | 0 | 0 | 16 | 56
17:30 | 2888.5 | 1819.5 | 911.5 | 0 | 62 | 541.38 | 40 | 3474.745 | 13.58 | 183 | 279.5 | 0 | 0 | 19.5 | 75.5
18:00 | 2988 | 1907.5 | 912 | 0 | 66 | 562.93 | 40 | 3679.21 | 0 | 226 | 368 | 0 | 0 | 23 | 95
18:30 | 3000.5 | 1919.5 | 908 | 0 | 63 | 658.93 | 40 | 3728.105 | 0 | 218.5 | 310.5 | 0 | 0 | 22 | 98
19:00 | 3013 | 1931.5 | 904 | 0 | 60 | 754.93 | 40 | 3777 | 0 | 211 | 253 | 0 | 0 | 21 | 101
19:30 | 3030 | 1951.5 | 904 | 0 | 62 | 756.49 | 40 | 3780 | 0 | 224 | 240 | 0 | 0 | 26 | 83
20:00 | 2981 | 1908.5 | 903 | 0 | 60 | 756.34 | 40 | 3775 | 0 | 162 | 224 | 0 | 0 | 26 | 81
20:30 | 2979 | 1849 | 903.5 | 0 | 59 | 757.17 | 37.5 | 3780 | 0 | 171 | 220 | 0 | 0 | 21.5 | 69.5
21:00 | 2977 | 1789.5 | 904 | 0 | 58 | 758 | 35 | 3785 | 0 | 180 | 216 | 0 | 0 | 17 | 58
21:30 | 2894 | 1763.5 | 903.5 | 0 | 58 | 712.5 | 35 | 3537.5 | 0 | 180 | 196 | 0 | 0 | 17 | 154
22:00 | 2811 | 1737.5 | 903 | 0 | 58 | 667 | 35 | 3290 | 0 | 180 | 176 | 0 | 0 | 17 | 250
22:30 | 2775.5 | 1725.25 | 903 | 0 | 58 | 663.5 | 35 | 3228.5 | 0 | 145 | 149 | 0 | 0 | 20.5 | 175
23:00 | 2740 | 1713 | 903 | 0 | 58 | 660 | 35 | 3167 | 0 | 110 | 122 | 0 | 0 | 24 | 100
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 416 | 04:00 | 387 | 13:00 | Kaliakoir | 378 | 05:00 | 355 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 411 | 4:00 | 376 | 12:00 | Madunaghat | 409 | 04:00 | 339 | 09:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 409 | 05:00 | 377 | 12:00 | Meghnaghat | 405 | 05:00 | 386 | 12:00
| Bibiana | 395 | 23:00 | 384 | 12:00 | Payra | 418 | 03:00 | 403 | 19:00
| BIPTC | 408 | 02:00 | 392 | 10:00 | Rahanpur | 415 | 04:00 | 398 | 12:00
| Bogura | 414 | 04:00 | 393 | 13:00 | Rampal | 417 | 04:00 | 383 | 13:00
| Gopalganj | 419 | 05:00 | 388 | 13:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 237 | 04:00 | 219 | 12:00 | Haripur | 234 | 08:00 | 226 | 18:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 234 | 01:00 | 220 | 12:00 | Hasnabad | 232 | 00:00 | 218 | 14:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 234 | 03:00 | 220 | 11:00 | Hathazari | 234 | 01:00 | 225 | 12:00
| Ashuganj | 239 | 05:00 | 223 | 13:00 | Ishurdi | 245 | 04:00 | 228 | 12:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 239 | 05:00 | 223 | 13:00 | Jhenaidah | 242 | 04:00 | 221 | 13:00
| Baghabari | 243 | 03:00 | 229 | 12:00 | Kaliakoir | 237 | 04:00 | 219 | 12:00 | 230 kV MAX | 248 |  | 248 | 216
| Barapukuria | 226 | 02:00 | 216 | 18:30 | Keranigonj | 236 | 04:00 | 219 | 12:00 | 230 kV MIN | 216 |  | 245 | 218 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 226 | 02:00 | 216 | 18:30 | Khulna(S) | 243 | 04:00 | 222 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 247 | 04:00 | 233 | 13:00 | Madunaghat | 234 | 01:00 | 224 | 12:00 | 132 kV MAX | 143 |  | 143 | 112 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 243 | 05:00 | 224 | 13:00 | Madunaghat-400 | 234 | 03:00 | 223 | 13:00 | 132 kV MIN | 107 |  | 142 | 107 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 239 | 05:00 | 220 | 12:00 | Maniknagar | 235 | 03:00 | 220 | 12:00 | [35 empty] | 6:00
| Bibiana | 228 | 00:00 | 222 | 12:00 | Meghnaghat | 245 | 04:00 | 228 | 12:00 |  | 400 | [33 empty] | 392
| BIPTC | 244 | 04:00 | 225 | 13:00 | Meghnaghat-400 | 239 | 05:00 | 224 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 240 | 05:00 | 228 | 12:00 | Mirsorai | 233 | 03:00 | 219 | 13:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 240 | 05:00 | 227 | 13:00 | Rajshahi | 244 | 05:00 | 224 | 12:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 248 | 01:00 | 241 | 12:00 | Rampal | 241 | 04:00 | 220 | 13:00 |  | 132 |  |  | Ash 400-299274
| BSRM | 233 | 03:00 | 219 | 13:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 235 | 04:00 | 220 | 12:00 | Rampura | 239 | 04:00 | 221 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 248 | 04:00 | 232 | 13:00 | Shikalbaha | 232 | 03:00 | 221 | 12:00 |  | kaptai by call 399528
| Fenchuganj | 233 | 23:00 | 220 | 14:00 | Shyampur | 237 | 04:00 | 220 | 12:00
| Ghorashal | 240 | 01:00 | 230 | 00:00 | Siddhirganj | 238 | 06:00 | 222 | 12:00
| Ghorashal-230 | 237 | 04:00 | 220 | 13:00 | Sirajgonj | 247 | 03:00 | 237 | 12:00
| Gopalganj | 247 | 04:00 | 230 | 13:00 | Sreepur | 239 | 01:00 | 225 | 13:00
| GPH | 233 | 03:00 | 221 | 12:00 | Tongi | 238 | 03:00 | 217 | 11:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 136 | 01:00 | 125 | 12:00 | Kurigram | 131 | 05:00 | 117 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 138 | 04:00 | 127 | 12:00 | Kushtia | 141 | 06:00 | 132 | 11:00
| Agrabad | 133 | 00:00 | 126 | 18:00 | Lalbag | 139 | 04:00 | 127 | 12:00
| AKS | 130 | 00:00 | 125 | 12:00 | Lalmonirhat | 127 | 01:00 | 118 | 08:00
| Aminbazar | 137 | 03:00 | 125 | 12:00 | Madanganj | 135 | 06:00 | 126 | 12:00
| Amnura | 140 | 02:00 | 130 | 12:00 | Madaripur | 137 | 05:00 | 130 | 12:00
| Ashuganj | 141 | 02:00 | 135 | 12:00 | Madartek | 136 | 04:00 | 126 | 12:00
| Bagerhat | 138 | 01:00 | 124 | 12:00 | Madunaghat | 135 | 03:00 | 128 | 12:00
| Bajitpur | 134 | 04:00 | 128 | 12:00 | Magura | 142 | 04:00 | 127 | 13:00
| Bakulia | 134 | 03:00 | 126 | 12:00 | Mahasthangarh | 137 | 04:00 | 126 | 13:00
| Banani | 137 | 04:00 | 125 | 12:00 | Manikganj | 132 | 01:00 | 122 | 12:00
| Bangabhaban | 137 | 04:00 | 125 | 12:00 | Maniknagar | 134 | 00:00 | 125 | 12:00
| Barapukuria | 136 | 02:00 | 127 | 12:00 | Matarbari | 126 | 02:00 | 116 | 18:00
| Barguna | 137 | 04:00 | 132 | 13:00 | Matuail | 137 | 04:00 | 127 | 12:00
| Barishal | 136 | 03:00 | 128 | 13:00 | Millgate | 139 | 04:00 | 125 | 12:00
| Barishal-230 | 138 | 03:00 | 130 | 12:00 | Mirpur | 136 | 02:00 | 122 | 12:00
| Baroaulia | 132 | 00:00 | 126 | 13:00 | Mirzapur | 137 | 22:00 | 122 | 12:00
| Baroirhat | 132 | 01:00 | 121 | 13:00 | Mithapukur | 135 | 03:00 | 124 | 08:00
| Bashundhara | 138 | 04:00 | 124 | 13:00 | MI_Cement | 137 | 04:00 | 127 | 12:00
| BashundharaCement | 135 | 06:00 | 127 | 13:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 136 | 05:00 | 131 | 12:00 | Mogbazar | 137 | 04:00 | 125 | 12:00
| Benapole | 141 | 04:00 | 122 | 13:00 | Mongla | 137 | 02:00 | 124 | 13:00
| Bhaluka | 129 | 04:00 | 116 | 12:00 | Motijheel | 137 | 04:00 | 125 | 12:00
| Bhandaria | 134 | 06:00 | 126 | 13:00 | Muktagacha | 129 | 23:00 | 116 | 08:00
| Bhangura | 138 | 00:00 | 130 | 12:00 | Munshiganj | 135 | 03:00 | 126 | 12:00
| Bheramara | 141 | 03:00 | 133 | 12:00 | Mymensingh | 128 | 04:00 | 112 | 12:00
| Bheramara(GK) | 140 | 02:00 | 133 | 12:00 | Naogaon | 137 | 05:00 | 125 | 12:00
| Bhulta | 127 | 23:00 | 114 | 19:00 | Narail | 140 | 05:00 | 126 | 13:00
| Bog-Sherpur | 138 | 04:00 | 128 | 12:00 | Narinda | 134 | 00:00 | 125 | 12:00
| Bogura | 137 | 03:00 | 129 | 09:00 | Narshingdi | 131 | 22:00 | 115 | 12:00
| Bogura-230 | 139 | 04:00 | 129 | 09:00 | Natore | 140 | 03:00 | 129 | 13:00
| Brahmanbaria | 132 | 01:00 | 122 | 12:00 | Nawabganj | 139 | 05:00 | 128 | 12:00
| Cantonment | 138 | 04:00 | 127 | 12:00 | Netrakona | 127 | 01:00 | 107 | 12:00
| Chandpur | 129 | 06:00 | 119 | 12:00 | New | 139 | 03:00 | 124 | 12:00
| Chandraghona | 136 | 03:00 | 128 | 12:00 | Niamatpur | 139 | 05:00 | 133 | 08:00
| Chapai | 137 | 02:00 | 131 | 13:00 | Noapara | 140 | 02:00 | 125 | 13:00
| Charsaidpur | 136 | 03:00 | 127 | 12:00 | Pabna | 138 | 03:00 | 125 | 12:00
| Chauddagram | 133 | 04:00 | 122 | 12:00 | Palashbari | 134 | 04:00 | 122 | 08:00
| Chhatak | 134 | 00:00 | 129 | 14:00 | Panchagarh | 137 | 04:00 | 121 | 09:00
| Chowmuhani | 125 | 00:00 | 118 | 12:00 | Patuakhali | 136 | 17:00 | 131 | 07:00
| Chuadanga | 139 | 03:00 | 127 | 12:00 | Payra | 138 | 04:00 | 132 | 19:00
| Coxsbazar | 126 | 02:00 | 116 | 18:00 | PHP | 132 | 05:00 | 121 | 12:00
| Cumilla(N) | 139 | 18:00 | 128 | 12:00 | Postogola | 139 | 05:00 | 129 | 12:00
| Cumilla(S) | 133 | 04:00 | 124 | 12:00 | Purbachal | 138 | 04:00 | 125 | 12:00
| Daudkandi | 133 | 03:00 | 124 | 12:00 | Purbasadipur | 132 | 02:00 | 118 | 08:00
| Dhaka | 137 | 04:00 | 126 | 12:00 | Rahanpur | 141 | 03:00 | 134 | 12:00
| Dhamrai | 134 | 00:00 | 125 | 12:00 | Rahanpur-400 | 141 | 03:00 | 134 | 12:00
| Dhanmondi | 137 | 04:00 | 126 | 12:00 | Rahim | 136 | 04:00 | 126 | 12:00
| Dohazari | 132 | 03:00 | 124 | 12:00 | Rajbari | 137 | 04:00 | 127 | 13:00
| Faridpur | 137 | 03:00 | 129 | 19:00 | Rajendrapur | 134 | 05:00 | 123 | 13:00
| Fatullah | 139 | 05:00 | 128 | 13:00 | Rajshahi | 141 | 05:00 | 130 | 12:00
| Fenchuganj | 138 | 08:00 | 134 | 12:00 | Rajshahi-230 | 140 | 04:00 | 126 | 13:00
| Feni | 130 | 06:00 | 121 | 12:00 | Ramganj | 127 | 04:00 | 117 | 14:00
| Ghatail | 126 | 09:00 | 117 | 08:00 | Rampur | 134 | 05:00 | 126 | 13:00
| Ghorashal | 140 | 01:00 | 135 | 14:00 | Rampura | 137 | 04:00 | 125 | 12:00
| Goalpara | 142 | 04:00 | 128 | 12:00 | Rangamati | 135 | 04:00 | 127 | 12:00
| Gollamari | 141 | 04:00 | 128 | 13:00 | Rangpur | 132 | 03:00 | 120 | 18:00
| Gopalganj | 139 | 04:00 | 127 | 13:00 | Ruppur | 142 | 05:00 | 134 | 12:00
| Gopalganj-400 | 139 | 05:00 | 129 | 13:00 | Saidpur | 135 | 04:00 | 120 | 18:00
| Gulshan | 135 | 05:00 | 126 | 12:00 | Satkhira | 140 | 05:00 | 124 | 13:00
| Halishahar | 132 | 07:00 | 127 | 12:00 | Satmasjid | 136 | 01:00 | 125 | 13:00
| Haripur | 136 | 04:00 | 129 | 11:00 | Savar | 135 | 01:00 | 120 | 12:00
| HaripurSBU | 136 | 04:00 | 127 | 12:00 | SevenRings | 141 | 05:00 | 131 | 13:00
| Hasnabad | 138 | 00:00 | 124 | 11:00 | ShahCement | 136 | 03:00 | 127 | 12:00
| Hathazari | 134 | 00:00 | 129 | 12:00 | Shahjadpur | 142 | 03:00 | 135 | 08:00
| Ishurdi | 143 | 03:00 | 134 | 12:00 | Shahjibazar | 135 | 01:00 | 128 | 13:00
| Jaldhaka | 133 | 05:00 | 118 | 09:00 | Shahmirpur | 132 | 00:00 | 127 | 12:00
| Jamalpur | 128 | 23:00 | 112 | 06:00 | Shariatpur | 139 | 04:00 | 129 | 12:00
| Jashore | 140 | 05:00 | 124 | 13:00 | Sherpur | 127 | 23:00 | 110 | 06:00
| Jhenaidah | 140 | 01:00 | 128 | 13:00 | Shikalbaha | 123 | 01:00 | 117 | 12:00
| Jhenaidah-230 | 142 | 04:00 | 129 | 13:00 | Shikalbaha-230 | 135 | 04:00 | 127 | 12:00
| Joydebpur | 137 | 03:00 | 127 | 12:00 | Shitalakhya | 137 | 04:00 | 127 | 12:00
| Joypurhat | 135 | 01:00 | 124 | 13:00 | Sholosohor | 135 | 04:00 | 128 | 12:00
| Juldah | 133 | 03:00 | 126 | 12:00 | Shyampur | 135 | 01:00 | 127 | 12:00
| Kabirpur | 139 | 06:00 | 121 | 12:00 | Shyampur-230 | 138 | 04:00 | 128 | 12:00
| Kachua | 132 | 05:00 | 121 | 14:00 | Siddhirganj | 136 | 04:00 | 127 | 12:00
| Kaliakoir | 138 | 03:00 | 126 | 12:00 | Sirajganj | 139 | 03:00 | 128 | 12:00
| Kallyanpur | 136 | 04:00 | 124 | 12:00 | Sonargaon | 135 | 05:00 | 124 | 12:00
| Kalurghat | 134 | 00:00 | 128 | 12:00 | Sreemongol | 135 | 01:00 | 130 | 12:00
| Kamrangirchar | 137 | 07:00 | 123 | 13:00 | Sreepur | 134 | 01:00 | 121 | 16:00
| Kaptai | 136 | 5:00 | 127 | 12:00 | Srinagar | 138 | 06:00 | 127 | 12:00
| Kazla | 137 | 05:00 | 124 | 13:00 | SSM | 138 | 01:00 | 130 | 13:00
| Keranigonj | 139 | 04:00 | 127 | 12:00 | Sunamganj | 133 | 02:00 | 129 | 12:00
| Khagrachori | 135 | 03:00 | 126 | 13:00 | Sylhet | 135 | 01:00 | 131 | 12:00
| Khulna | 138 | 02:00 | 126 | 13:00 | Sylhet-132 | 134 | 01:00 | 131 | 12:00
| Khulna(S) | 141 | 04:00 | 126 | 13:00 |  | 127 | 00:00 | 120 | 12:00
| Khulshi | 132 | 01:00 | 125 | 12:00 | Thakurgaon | 135 | 05:00 | 118 | 09:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 131 | 00:00 | 124 | 08:00 | TK | 133 | 01:00 | 127 | 12:00 |  |  | Nos | Nos | Nos
| Kodda | 134 | 05:00 | 123 | 12:00 | Tongi | 139 | 04:00 | 129 | 11:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 135 | 02:00 | 127 | 13:00 | Ullahpara | 137 | 00:00 | 129 | 12:00
| Kulaura | 137 | 00:00 | 133 | 13:00 | Ullon | 136 | 04:00 | 126 | 12:00
[6 empty] | Uttara | 137 | 04:00 | 126 | 16:00
[6 empty] | UttaraNew | 137 | 03:00 | 123 | 12:00
[6 empty] | Zigatola | 139 | 04:00 | 127 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.