## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-01-2025 | [28 empty] | Date: | 23-01-2025 | [28 empty] | Date: | 23-01-2025 | [28 empty] | Date: | 23-01-2025 | [28 empty] | Date: | 23-01-2025 | [19 empty] | Date: | 23-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [19 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 256 | 0 | 0 | 0 | 21 | 250 | 0 | 0 | 0 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 908 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 755 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 37 | 0 | 45 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 275 | 250 | 292 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 9 | 58 | 5 | 0 | 0 | 0 | 5255 | 904 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 130 | 0 | 154 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 180 | 0 | 0 | 900 | 0 | 3828.5 | 9083.5 | 92.61
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 277 | 0 | 0 | 0 | 24 | 250 | 0 | 0 | 0 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 828 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 670 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 37 | 0 | 45 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 275 | 220 | 288 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 9 | 58 | 8 | 0 | 0 | 0 | 5061 | 903 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 102 | 0 | 151 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 0 | 700 | 0 | 3399.5 | 8460.5 | 92.6
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 292 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 15.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 745 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 605 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 188 | 37 | 0 | 50 | 0 | 0 | 15 | 0 | 44 | 0 | 0 | 0 | 280 | 200 | 288 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 9 | 19 | 10 | 0 | 0 | 0 | 4814.5 | 718 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 0 | 600 | 0 | 3021.5 | 7836 | 92.6
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 270 | 0 | 0 | 0 | 10 | 250 | 0 | 0 | 0 | 0 | 14.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 740 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 605 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 37 | 0 | 50 | 0 | 0 | 15 | 0 | 44 | 0 | 0 | 0 | 285 | 192 | 290 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 159 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 4765.5 | 717 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 2.5 | 209 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 0 | 540 | 0 | 2968.5 | 7734 | 92.6
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 264 | 0 | 0 | 0 | 12 | 250 | 0 | 0 | 0 | 0 | 14.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 743 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 605 | 0 | 5 | 0 | 88 | 0 | 0 | 0 | 29 | 181 | 37 | 0 | 70 | 0 | 0 | 11 | 0 | 42 | 0 | 0 | 0 | 280 | 187 | 290 | 10 | 43 | 0 | 2 | 120 | 13 | 0 | 10 | 30 | 0 | 0 | 156 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 4441.5 | 717 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 0 | 510 | 0 | 2943.5 | 7385 | 92.6
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 270 | 0 | 0 | 0 | 12 | 250 | 0 | 0 | 0 | 0 | 14.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 743 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 605 | 0 | 5 | 0 | 88 | 0 | 0 | 0 | 5 | 181 | 37 | 0 | 70 | 0 | 0 | 11 | 0 | 40 | 0 | 0 | 0 | 280 | 177 | 287 | 10 | 0 | 0 | 2 | 120 | 13 | 0 | 10 | 30 | 0 | 0 | 156 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 4378.5 | 717 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 2.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 0 | 500 | 0 | 2935.5 | 7314 | 92.59
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 314 | 0 | 0 | 0 | 12 | 250 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 800 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 660 | 0 | 13 | 0 | 127 | 0 | 0 | 0 | 12 | 200 | 37 | 0 | 70 | 0 | 0 | 11 | 0 | 42 | 0 | 0 | 0 | 310 | 177 | 335 | 38 | 0 | 0 | 2 | 120 | 13 | 0 | 50 | 30 | 0 | 0 | 158 | 0 | 9 | 24 | 13 | 0 | 0 | 0 | 4783 | 717 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 2.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 100 | 180 | 0 | 0 | 560 | 0 | 3058.5 | 7841.5 | 92.59
07:00 | 0 | 20 | 18 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 22 | 4 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 317 | 0 | 0 | 0 | 14 | 250 | 0 | 0 | 0 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 22 | 904 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 740 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 207 | 37 | 0 | 50 | 0 | 0 | 11 | 0 | 40 | 0 | 2 | 0 | 315 | 177 | 340 | 38 | 0 | 0 | 2 | 163 | 13 | 0 | 80 | 30 | 0 | 0 | 50 | 0 | 9 | 56 | 13 | 0 | 0.32 | 0 | 5171.32 | 809 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 2.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 135 | 220 | 0 | 0 | 640 | 0 | 3422 | 8593.32 | 92.59
08:00 | 0 | 40 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 316 | 0 | 0 | 0 | 25 | 335 | 0 | 0 | 0 | 0 | 22 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 11 | 950 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 820 | 2 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 204 | 37 | 0 | 50 | 0 | 0 | 11 | 0 | 42 | 0 | 11 | 0 | 335 | 177 | 357 | 43 | 0 | 0 | 0 | 163 | 13 | 0 | 80 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 5 | 0 | 3.48 | 0 | 5470.48 | 904 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.49 | 0 | 0 | 562.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0.75 | 123 | 0 | 0 | 0 | 129 | 0 | 0 | 0 | 0.07 | 2.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0.4 | 8 | 0.03 | 0 | 307 | 5 | 140 | 220 | 0 | 0 | 910 | 0 | 3971.21 | 9441.69 | 92.59
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 89 | 32 | 0 | 0 | 0 | 70 | 17 | 0 | 310 | 283 | 0 | 0 | 0 | 24 | 300 | 0 | 0 | 5 | 0 | 20 | 15 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 952 | 0 | 0 | 7 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 11 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 192 | 37 | 8 | 50 | 0 | 0 | 15 | 0 | 50 | 0 | 22 | 0 | 310 | 177 | 310 | 43 | 0 | 0 | 0 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 5 | 0 | 8.7 | 0 | 5676.7 | 904 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.83 | 0 | 0 | 746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 1.87 | 125 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0.18 | 2.5 | 210 | 68 | 0 | 1 | 0 | 0 | 0 | 0.2 | 25 | 0.09 | 0 | 307 | 5 | 140 | 220 | 0 | 0 | 1140 | 11 | 4434.67 | 10111.37 | 92.58
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 107 | 32 | 0 | 0 | 0 | 72 | 17 | 0 | 310 | 261 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 8 | 0 | 20 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 950 | 0 | 0 | 18 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 16 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 182 | 41 | 50 | 50 | 0 | 21 | 15 | 0 | 56 | 0 | 51 | 0 | 280 | 178 | 291 | 43 | 0 | 0 | 0 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 5 | 0 | 22.03 | 0 | 5741.03 | 904 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.28 | 0 | 0 | 752.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 9.97 | 125 | 0 | 0 | 0 | 127 | 0 | 0 | 0 | 0.86 | 2.5 | 210 | 71 | 0 | 3 | 0 | 0 | 0 | 0.8 | 44 | 0.16 | 0 | 250 | 4 | 100 | 180 | 0 | 0 | 1170 | 35 | 4408.58 | 10149.61 | 92.58
11:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 113 | 32 | 0 | 0 | 0 | 72 | 17 | 0 | 310 | 289 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 8 | 0 | 20 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 2 | 900 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 950 | 19 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 184 | 41 | 50 | 50 | 0 | 26 | 15 | 0 | 58 | 0 | 61 | 0 | 295 | 177 | 309 | 43 | 0 | 0 | 0 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 5 | 0 | 36.71 | 1 | 5760.71 | 900 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.2 | 0 | 0 | 760.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 10.23 | 125 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 0.77 | 2.5 | 210 | 71 | 0 | 5 | 0 | 0 | 0 | 0.7 | 18 | 0.28 | 0 | 277 | 4 | 140 | 220 | 0 | 0 | 1170 | 35 | 4560.76 | 10321.47 | 92.58
12:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17 | 0 | 0 | 113 | 32 | 0 | 0 | 0 | 72 | 17 | 0 | 310 | 280 | 0 | 0 | 17 | 24 | 280 | 0 | 0 | 11 | 0 | 0 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 2 | 950 | 0 | 0 | 19 | 0 | 5 | 161 | 0 | 0 | 0 | 950 | 20 | 51 | 15 | 199 | 0 | 0 | 0 | 29 | 180 | 41 | 50 | 50 | 10 | 26 | 5 | 0 | 62 | 0 | 59 | 0 | 275 | 177 | 327 | 43 | 0 | 0 | 0 | 130 | 13 | 0 | 83 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 5 | 1 | 40.66 | 6 | 5837.66 | 899 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.26 | 0 | 0 | 753.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 10.2 | 125 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 1.01 | 2.5 | 210 | 72 | 0 | 7 | 0 | 0 | 0 | 0.7 | 23 | 0.54 | 0 | 307 | 4 | 138 | 220 | 0 | 0 | 1180 | 35 | 4705.43 | 10543.09 | 92.58
13:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 35 | 0 | 0 | 113 | 32 | 0 | 0 | 0 | 108 | 17 | 0 | 310 | 249 | 0 | 0 | 17 | 24 | 280 | 0 | 0 | 26 | 0 | 19 | 9 | 0 | 0 | 35 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 10 | 950 | 0 | 0 | 19 | 0 | 17 | 161 | 0 | 0 | 0 | 1050 | 19 | 51 | 20 | 199 | 0 | 0 | 0 | 29 | 182 | 41 | 57 | 45 | 17 | 26 | 15 | 0 | 62 | 0 | 60 | 0 | 305 | 221 | 367 | 43 | 0 | 0 | 0 | 163 | 13 | 0 | 83 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 5 | 1 | 39.77 | 6 | 6183.77 | 898 | 430 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.74 | 0 | 0 | 754.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 23.59 | 125 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 1.36 | 2.5 | 210 | 71 | 0 | 5 | 0 | 0 | 0 | 0.8 | 34 | 0.52 | 0 | 303 | 5 | 100 | 180 | 0 | 0 | 1190 | 35 | 4652.7 | 10836.47 | 92.57
14:00 | 0 | 34 | 30 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 35 | 0 | 0 | 70 | 32 | 0 | 0 | 0 | 108 | 25 | 0 | 310 | 275 | 0 | 0 | 17 | 24 | 280 | 0 | 0 | 21 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 7 | 903 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1050 | 16 | 51 | 20 | 128 | 0 | 0 | 0 | 29 | 182 | 38 | 88 | 45 | 17 | 26 | 17 | 0 | 68 | 0 | 50 | 0 | 310 | 260 | 311 | 40 | 0 | 0 | 0 | 120 | 13 | 0 | 83 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 5 | 1 | 32.89 | 6 | 5923.89 | 898 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.09 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 32.27 | 125 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 1.75 | 2.5 | 210 | 72 | 0 | 6 | 0 | 0 | 0 | 0.6 | 38 | 0.45 | 0 | 250 | 3 | 100 | 180 | 0 | 0 | 1100 | 0 | 4368.66 | 10292.55 | 92.57
15:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17 | 10 | 0 | 70 | 16 | 0 | 0 | 0 | 108 | 25 | 0 | 310 | 286 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 16 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 901 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 995 | 12 | 51 | 10 | 128 | 0 | 0 | 0 | 29 | 190 | 41 | 53 | 45 | 17 | 9 | 17 | 0 | 56 | 0 | 36 | 0 | 290 | 260 | 345 | 40 | 0 | 0 | 0 | 120 | 13 | 0 | 83 | 30 | 0 | 18 | 0 | 0 | 9 | 58 | 5 | 1 | 22.66 | 6 | 5752.66 | 900 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.04 | 0 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 34.49 | 126 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 2.99 | 2.5 | 210 | 70 | 0 | 5 | 0 | 0 | 0 | 0.5 | 39 | 0.31 | 0 | 250 | 3 | 100 | 180 | 0 | 0 | 1040 | 0 | 4276.83 | 10029.49 | 92.57
16:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 37 | 0 | 70 | 16 | 0 | 0 | 0 | 108 | 25 | 0 | 300 | 226 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 8 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 804 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 950 | 7 | 51 | 10 | 128 | 0 | 0 | 0 | 29 | 182 | 41 | 34 | 50 | 0 | 9 | 17 | 0 | 60 | 0 | 20 | 0 | 295 | 260 | 333 | 43 | 0 | 0 | 0 | 120 | 0 | 0 | 83 | 30 | 0 | 18 | 20 | 0 | 9 | 58 | 5 | 1 | 11.97 | 6 | 5562.97 | 899 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.53 | 0 | 0 | 665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 16.42 | 126 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 1.81 | 2.5 | 210 | 71 | 0 | 2 | 0 | 0 | 0 | 0.1 | 11 | 0.16 | 0 | 250 | 3 | 100 | 180 | 0 | 0 | 1000 | 0 | 4141.52 | 9704.49 | 92.56
17:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 43 | 28 | 0 | 70 | 16 | 0 | 0 | 0 | 108 | 25 | 0 | 300 | 224 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 2 | 45 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 7 | 804 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 860 | 1 | 51 | 16 | 194 | 0 | 0 | 0 | 6 | 182 | 41 | 34 | 50 | 0 | 9 | 17 | 0 | 58 | 0 | 4 | 0 | 295 | 246 | 333 | 43 | 0 | 0 | 0 | 120 | 11 | 0 | 83 | 30 | 0 | 8 | 135 | 0 | 9 | 68 | 5 | 0 | 2.71 | 6 | 5670.71 | 899 | 429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.54 | 0 | 0 | 669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 3.78 | 126 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 0.32 | 2.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.41 | 0 | 250 | 4 | 100 | 180 | 0 | 0 | 1000 | 0 | 4084.55 | 9755.26 | 92.56
18:00 | 0 | 56 | 25 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 54 | 37 | 0 | 78 | 64 | 0 | 25 | 17 | 162 | 25 | 0 | 300 | 223 | 0 | 0 | 35 | 0 | 335 | 0 | 0 | 0 | 52 | 19 | 15 | 0 | 0 | 18 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 12 | 0 | 40 | 16 | 13 | 902 | 17 | 0 | 19 | 0 | 16 | 160 | 0 | 0 | 0 | 890 | 0 | 51 | 66 | 195 | 0 | 0 | 0 | 9 | 181 | 41 | 58 | 50 | 31 | 51 | 17 | 0 | 66 | 0 | 0 | 49 | 260 | 230 | 302 | 10 | 20 | 0 | 0 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 135 | 9 | 9 | 58 | 5 | 0 | 0 | 6 | 6200 | 898 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 2.5 | 210 | 71 | 55 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 100 | 180 | 0 | 0 | 1020 | 14 | 4314.5 | 10514.5 | 92.56
19:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 35 | 37 | 0 | 90 | 64 | 0 | 15 | 0 | 54 | 25 | 0 | 300 | 223 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 45 | 19.5 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 903 | 0 | 0 | 33 | 0 | 0 | 161 | 0 | 0 | 0 | 930 | 0 | 51 | 100 | 195 | 0 | 0 | 0 | 27 | 181 | 41 | 102 | 50 | 34 | 27 | 17 | 0 | 58 | 0 | 0 | 48 | 275 | 230 | 290 | 10 | 30 | 0 | 0 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 130 | 17 | 9 | 58 | 5 | 0 | 0 | 0 | 6139.5 | 899 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 5.5 | 209 | 71 | 91 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 100 | 220 | 0 | 0 | 1200 | 17 | 4607.5 | 10747 | 92.55
19:30 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 37 | 0 | 106 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 290 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 25 | 19.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 945 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 930 | 0 | 51 | 15 | 195 | 0 | 0 | 0 | 29 | 181 | 41 | 50 | 50 | 0 | 27 | 17 | 0 | 52 | 0 | 0 | 48 | 305 | 230 | 344 | 10 | 30 | 0 | 0 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 130 | 0 | 9 | 58 | 5 | 0 | 0 | 0 | 6034.5 | 899 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 5.5 | 210 | 71 | 91 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 0 | 1200 | 0 | 4663.5 | 10698
20:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 37 | 0 | 108 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 274 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 17 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 945 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1063 | 0 | 51 | 10 | 195 | 0 | 0 | 0 | 29 | 181 | 41 | 50 | 50 | 0 | 27 | 17 | 0 | 56 | 0 | 0 | 0 | 295 | 230 | 335 | 10 | 30 | 0 | 0 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 130 | 0 | 9 | 58 | 9 | 0 | 0 | 0 | 6080 | 899 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 0 | 1202 | 0 | 4640.5 | 10720.5 | 92.55
21:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 37 | 0 | 112 | 32 | 0 | 0 | 0 | 0 | 25 | 7 | 350 | 315 | 0 | 0 | 0 | 14 | 335 | 0 | 0 | 0 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 940 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 196 | 41 | 0 | 50 | 0 | 0 | 17 | 0 | 56 | 0 | 0 | 0 | 310 | 220 | 346 | 10 | 30 | 0 | 0 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 130 | 0 | 9 | 58 | 9 | 0 | 0 | 0 | 6017 | 898 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 0 | 1202 | 0 | 4485.04 | 10502.04 | 92.54
22:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 37 | 0 | 100 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 280 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 0 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 26 | 940 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 970 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 41 | 0 | 50 | 0 | 0 | 17 | 0 | 56 | 0 | 0 | 0 | 300 | 200 | 335 | 10 | 30 | 0 | 0 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 130 | 0 | 9 | 58 | 6 | 0 | 0 | 0 | 5802.5 | 897 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 24 | 0 | 191 | 0 | 0 | 0 | 0 | 5.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 140 | 220 | 0 | 0 | 1100 | 0 | 4331.28 | 10133.78 | 92.54
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 37 | 0 | 95 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 281 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 0 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 940 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 41 | 0 | 45 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 285 | 192 | 336 | 10 | 30 | 0 | 0 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 134 | 0 | 9 | 58 | 6 | 0 | 0 | 0 | 5557.5 | 899 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 663.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 22 | 0 | 174 | 0 | 0 | 0 | 0 | 5.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 100 | 180 | 0 | 0 | 1070 | 0 | 4110.88 | 9668.38 | 92.53
Total KWH | 0 | 864960 | 375840 | 0 | 0 | 0 | 0 | 0 | 9259200 | 0 | 0 | 285840 | 327960 | 0 | 1633680 | 536640 | 0 | 64237 | 30822 | 1075680 | 502560 | 12480 | 7627000 | 6720349 | 0 | 0 | 120753 | 432100 | 7084212 | 0 | 0 | 102349 | 145200 | 411000 | 333720 | 0 | 0 | 223309 | 0 | 0 | 0 | 501600 | 0 | 0 | 0 | 0 | 13440 | 21000 | 900420 | 39309 | 416640 | 21141818.18 | 15055 | 0 | 231840 | 0 | 81127 | 3794029 | 0 | 0 | 0 | 20645452 | 122985 | 1135528 | 362981 | 4148364 | 0 | 0 | 0 | 612000 | 4570000 | 948312 | 707520 | 1226830 | 180960 | 322560 | 365780 | 0 | 1271040 | 0 | 384518 | 96272 | 7160000 | 4963000 | 8084000 | 740592 | 376000 | 0 | 17136 | 3556636.4 | 327312 | 0 | 1781760 | 720192 | 0 | 90000 | 1676420 | 35640 | 205200 | 1152000 | 161280 | 5700 | 224340 | 44640 | 133749119.58 | 20858181 | 8567424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352080 | 0 | 0 | 15234545 | 0 | 0 | 0 | 0 | 0 | 0 | 132192 | 0 | 0 | 0 | 397070 | 0 | 143252 | 3086182 | 0 | 151300 | 0 | 3785173 | 0 | 0 | 0 | 11820 | 83016 | 5109000 | 1655999 | 231011 | 33691 | 140755 | 0 | 0 | 4692.48 | 232560 | 2652 | 0 | 5935000 | 141703 | 2725000 | 4950270 | 0 | 0 | 23346909.09 | 178800 | 97490277.57 | 231239397.15

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-01-2025 | during | 24-01-2025 | during | 24-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.3 | 97.3 | 0.01 | 0.01 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 360 | 400 | 400.37 | 400.37 | 400 | 400 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 310 | 300 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 280 | 223 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 0 | 19.5 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 15 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 17 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 24 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 25 | 8 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 90 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 70 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 11 | 0 | 22 | 0 | 22 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 37 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0.01 | 0.01 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0.01 | 0.01 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6257.05 | 5841.27 | 1643 | 1759.5 | 4599.99 | 4585.99 | 2713.56 | 2699.56
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 161 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 5 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 16 | 20 | 32 | 20 | 32 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.6 | 0 | 3.6 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 950 | 930 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 16 | 31 | 23 | 13 | 23 | 13 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 950 | 903 | 1150 | 1150 | 1150 | 1150 | -
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2202 | 2149 | 4018.32 | 3996.72 | 4018.32 | 3996.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 180 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 41 | 41 | 46.94 | 46.94 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 27 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 199 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 15 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 48 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 10 | 34 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 62 | 58 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 27 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 50 | 102 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 59 | 0 | 62 | 0 | 62 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 777 | 931 | 1670.97 | 1608.97 | 1532.2 | 1470.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[8 empty] | during | 0 | during | 0 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 5 | 210 | 210 | 15 | 15 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.3 | 0 | 1.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 200 | 200 | 58 | 58 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 9 | 9 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 40.66 | 0 | 38.5 | 0 | 38.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 22 | 22 | Unable to dispatch due to fuel shortages.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 119.66 | 89 | 641.3 | 601.5 | 198.3 | 158.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 0 | 30 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 120 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 43 | 10 | 44 | 44 | 10 | 10 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 2.5 | 2.5 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 130 | 135 | 135 | 135 | 135 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 0 | 20 | 20 | 0.01 | 0.01 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 25 | 25 | 13 | 13 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 275 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 327 | 290 | 380 | 380 | 352 | 352 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 177 | 230 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1096 | 1211 | 1516.5 | 1516.5 | 1416.01 | 1416.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 899 | 899 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 432 | 250 | 410 | 410 | 310 | 310 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 74.26 | 0 | 50 | 0 | 50 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | S/D due to changing of ST Power Tx Radiators
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1405.26 | 1149 | 3444 | 3394 | 1450.02 | 1400.02
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 138 | 100 | 135 | 135 | 135 | 135 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1180 | 1200 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.54 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1884.54 | 1851 | 2177.12 | 2176.12 | 2174 | 2173
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 125 | 149 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 125 | 204 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 0 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 8.25 | 8.25 | 5 | 5 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 1.01 | 0 | 2.5 | 0 | 2.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 753.22 | 757 | 1347.54 | 1347.54 | 749 | 749 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 10.2 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 86 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1102.93 | 1166.5 | 2694.49 | 2546.99 | 2092.7 | 1945.2
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 72 | 71 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 209 | 210 | 210 | 210 | 210 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.7 | 0 | 2.8 | 0 | 2.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 91 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 23 | 0 | 70 | 0 | 70 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 312.7 | 441 | 614.8 | 542 | 600.82 | 508.02
System Total |  |  |  |  | 27734.66 | 27066.248 | 10543.09 | 10747 | 21377.49 | 20968.79 | 16195.93 | 15767.23
Forecast Scenario (24-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9000 |  | 0 |  | 9000
|  |  |  | 1:00 | 8440 |  | 0 |  | 8440
|  |  |  | 2:00 | 8110 |  | 0 |  | 8110
|  |  |  | 3:00 | 7860 |  | 0 |  | 7860
|  |  |  | 4:00 | 7620 |  | 0 |  | 7620
|  |  |  | 5:00 | 7470 |  | 0 |  | 7470
|  |  |  | 6:00 | 7740 |  | 0 |  | 7740
|  |  |  | 7:00 | 7880 |  | 0 |  | 7880
|  |  |  | 8:00 | 8470 |  | 0 |  | 8470
|  |  |  | 9:00 | 8790 |  | 0 |  | 8790
|  |  |  | 10:00 | 8590 |  | 0 |  | 8590
|  |  |  | 11:00 | 8750 |  | 0 |  | 8750
|  |  |  | 12:00 | 9460 |  | 0 |  | 9460
|  |  |  | 13:00 | 10190 |  | 0 |  | 10190
|  |  |  | 14:00 | 8660 |  | 0 |  | 8660
|  |  |  | 15:00 | 7990 |  | 0 |  | 7990
|  |  |  | 16:00 | 7530 |  | 0 |  | 7530
|  |  |  | 17:00 | 7820 |  | 0 |  | 7820
|  |  |  | 18:00 | 9420 |  | 0 |  | 9420
|  |  |  | 18:30 | 9490 |  | 0 |  | 9490
|  |  |  | 19:00 | 9580 |  | 0 |  | 9580
|  |  |  | 19:30 | 9600 |  | 0 |  | 9600
|  |  |  | 20:00 | 9550 |  | 0 |  | 9550
|  |  |  | 21:00 | 9560 |  | 0 |  | 9560
|  |  |  | 22:00 | 9240 |  | 0 |  | 9240
|  |  |  | 23:00 | 8810 |  | 0 |  | 8810
Probable Maximum Temperature: |  |  | 23.0°C
Probable Maximum Demand at Day Peak: |  |  | 9460.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 9600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 9600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 206.53 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:20 hrs on 24-01-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division
Formulas:
Effective Available Gen. on = [Forecasted Available Gen. on]

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-01-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10543.09 | MW | 12:00 Hr. | Energy Generated |  |  | 231.2394 |  | MKWHr.
| Day Peak Demand |  |  | 10543.09 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.805 |  | MKWHr.
| Evening Peak Generation |  |  | 10747 | MW | 19:00 Hr. | Energy Demand |  |  | 232.0444 |  | MKWHr.
| Evening Peak Demand |  |  | 10891 | MW | 19:00 Hr. | Maximum Temperature |  |  | 23 |  | °C
| Minimum Generation of the Day |  |  | 7314 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 790.44 |  | MMCFD
| Maximum Generation of the Day |  |  | 10836.47 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.7375 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.3701 | 0 | 5.4741 | 0 | 0 | 0.10235 | 0 | 0 | 37.9466 | Gas | 102.732 | Gas | 368972946.368
| Chattogram Zone |  |  | 4.2107 | 41.7873 | 0.60408 | 0 | 0.90042 | 0.14399 | 0 | 0.5016 | 48.148 | Coal | 77.8342 | Coal | 548310181.0781
| Cumilla Zone |  |  | 13.0068 | 0 | 1.6703 | 0 | 0 | 0.38452 | 1.271 | 0 | 16.3327 | HFO | 9.8687 | HFO | 181187293.43
| Mymensingh Zone |  |  | 0.16128 | 0 | 1.4375 | 0 | 0 | 0.23004 | 0 | 0 | 1.8288 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.493 | Hydro | 0.90042 | Hydro | 90042
| Khulna Zone |  |  | 8.5674 | 0 | 0 | 0 | 0 | 0.35208 | 20.8582 | 0 | 29.7777 | Solar | 2.0387 | Solar | 30550939.328
| Barishal Zone |  |  | 7.817 | 29.2819 | 0.1788 | 0 | 0 | 0.002652 | 0 | 0 | 37.2803 | Import | 37.3638 | Import | 189789354.61
| Rajshahi Zone |  |  | 7.1057 | 0 | 0.13219 | 0 | 0 | 0.55214 | 15.2345 | 0 | 23.0246 | Wind | 0.5016 | Wind | 7824960
| Rangpur Zone |  |  | 0 | 6.765 | 0.37177 | 0 | 0 | 0.27094 | 0 | 0 | 7.4077
| Total |  |  | 102.732 | 77.8342 | 9.8687 | 0 | 0.90042 | 2.0387 | 37.3638 | 0.5016 | 231.2394
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 368972946.368 |  | Hydro | 90042
|  |  |  | Coal | 548310181.0781 |  | Solar | 30550939.328
|  |  |  | HFO | 181187293.43 |  | Import | 189789354.61
|  |  |  | HSD | 0 |  | Wind | 7824960
[5 empty] | Total: | 132,67,25,716 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West |  |  |  | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.8582 | Peak Hr Flow | 899.00 MW at 19:00 hrs.
Energy Flow from West to East |  |  |  | 8117254.625 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.2345 | Peak Hr Flow | 757.00 MW at 19:00 hrs.
Power Flow during Peak Demand |  |  |  | 430 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.271 | Peak Hr Flow | 58.00 MW at 19:00 hrs.
Maximum Power Flow |  |  |  | 657 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.3638 | Peak Hr Flow | 1714.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 90 |  | 3938
|  |  |  | Chattogram |  | 0 |  | 1118
|  |  |  | Cumilla |  | 0 |  | 838
|  |  |  | Mymensingh |  | 48 |  | 947
|  |  |  | Sylhet |  | 0 |  | 377
|  |  |  | Khulna |  | 0 |  | 1214
|  |  |  | Barishal |  | 0 |  | 288
|  |  |  | Rajshahi |  | 0 |  | 1030
|  |  |  | Rangpur |  | 0 |  | 719
|  |  |  | Total |  | 138 |  | 10469
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Rupganj 33 MW PP(Summit) |  |  | 33
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 5 | Khulna 330 MW CCPP ST |  |  | 110
|  | 6 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 7 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1184 |  |  |  | Total | 468.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1652.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:07 | 18:26 | Magura 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Annual Maintenance
| 08:15 | 17:14 | Bheramara(GK) 132/33kV S/S TR-4 LT Scheduled S/D Due to For painting work.
| 08:16 | 17:12 | Bheramara(GK) 132/33kV S/S TR-4 HT Scheduled S/D Due to For painting work.
| 08:19 | 15:09 | Rajshahi 230/132/33kV S/S 230 Kv BIPTC Ckt-02 Scheduled S/D Due to বার্ষিক সংরক্ষণ কাজ।
| 08:24 | 17:02 | Goalpara 132/33kV S/S Goalpara-NWPGCL Project Work S/D Due to shut down taken by NWPGCL
| 08:29 | 13:23 | Rampura 230/132kV S/S Auto Transformer - 02 LT Scheduled S/D
| 08:30 |  | Rampura 230/132kV S/S Auto Transformer - 02 HT Scheduled S/D
| 08:36 | 17:22 | Aminbazar-Manikgonj PP 132kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end.
| 08:37 | 11:27 | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Hot Spot Maintenance
| 08:37 | 11:28 | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Hot Spot Maintenance
| 08:45 | 15:32 | Khulshi-Madunaghat 132kV Ckt-2 Scheduled S/D from Khulshi 132/33kV end Due to Annual
maintenance(Dead line checking) work.
| 08:45 | 16:56 | Sirajganj-Sreepur 230 kV Ckt-1 Scheduled S/D from Sirajgonj 230 end Due to Annual
Maintenance
| 08:51 | 15:09 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Scheduled S/D from BIPTC end.
| 08:56 | 16:49 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Scheduled S/D Due to From other end.
| 08:57 | 15:54 | Chattak-Sunamganj 132 kV Ckt-1 Scheduled S/D from Sunamganj 132/33kV end Due to Dead line
Checking of CKT-1
| 08:58 | 15:50 | Chhatak 132/33kV S/S Sunamganj 1 Scheduled S/D Due to Dead Line checking Of
Chhatak-Sunamganj Ckt-1.
| 09:04 | 16:57 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-1 Scheduled S/D
| 09:20 | 16:15 | Hathazari-Raozan 230kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end.
| 09:21 | 20:12 | Ashuganj-Bhulta 400 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end.
| 09:25 | 19:23 | Haripur-Madanganj 132kV Ckt-1 Scheduled S/D from Madanganj 132/33kV end. and from
Haripur 230/132kV end Due to From other end.
| 09:30 |  | Rangpur 132/33kV S/S Rangpur-GTPS Scheduled S/D Due to Project work
| 09:47 | 17:30 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT Project Work S/D Due to Project work.
| 09:47 | 17:30 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT Project Work S/D Due to Project work.
| 09:50 | 16:32 | Kishoreganj-Mymensingh 132kV Ckt-1 Scheduled S/D from Kishoreganj 132/33kV end Due to
Work by Mymensingh substation
| 09:51 |  | Bhulta-Rampura 230 kV Ckt-1 Scheduled S/D from Rampura 230/132kV end. and from Bhulta
400/230kVend.
| 10:04 | 16:06 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT Scheduled S/D Due to Maintenance work.
| 10:04 | 16:06 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT Scheduled S/D Due to Maintenance work.
| 10:27 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:-
| 11:51 | 14:35 | Narshingdi 132/33kV S/S 132 kV Main Bus-1 Scheduled S/D Due to Purpose of Haripur Bus
DS-1,R-Phase (I Clamp) Maintenance Work.
| 12:00 |  | Day Peak generation = 10,543MW
| 12:37 | 16:13 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Forced S/D from Gopalganj 132/33kV end Due to Due to
R Phase ammeter burned
| 13:00 | 16:12 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Forced S/D from Gopalganj 400/132kV end Due to
Maintenance at Gopalganj 132 kv S/S
| 13:04 | 14:48 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Forced S/D from Jhenaidah 230/132kV end Due to
Maintenance work at HVDC end
| 13:06 | 14:12 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to High temperature of 33 kv feeder | [7 empty] | 38.0MW load
|  |  | EPZ & Nayerhat wile done by DPBS-1 | [7 empty] | interrup.
| 13:28 | 14:48 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Forced S/D from BIPTC end Due to As Emergency for
CVT oil leakage rectification
|  | 15:40 | Ghatail 132/33kV S/S T-2 LT is restored.
| 15:54 | 16:10 | Madanganj 132/33kV S/S GT-2 HT Tripped showing Back up protection relay relays Due to Due | [7 empty] | 12.0MW load
|  |  | to Shah Cement feeder fault ( O/C Relay R & Y phase) | [7 empty] | interrup.
| 15:54 | 16:12 | Madanganj 132/33kV S/S GT-2 LT Tripped showing Phase Instantaneous Fault relays Due to | [7 empty] | 12.0MW load
|  |  | Due to Shah Cement feeder fault ( O/C Relay R & Y phase) | [7 empty] | interrup.
| 16:40 | 19:13 | Haripur-Meghnaghat 230kV Ckt-1 Forced S/D from Haripur 230/132kV end Due to High
tempareture maintanence at several points. and from Meghnaghat 230/132kV end Due to
Maintenance work
|  | 16:43 | Aminbazar-Meghnaghat 400kV Ckt-2 is restored.
|  | 17:06 | Chowmuhani-Ramganj 132 kV Ckt-1 is restored.
| 17:20 | 19:55 | Bhulta-Haripur 132 kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Ordered by
NLDC.
|  | 17:54 | Bogura 230/132kV S/S T-02 HT is restored.
|  | 17:54 | Bogura 230/132kV S/S T-02 LT is restored.
|  | 18:24 | KSRM 132/33kV S/S Transformer-01 HT is restored.
| 19:32 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:-
|  | 20:12 | Ashuganj-Bhulta 400 kV Ckt-2 is restored.
| 21:32 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 21:32 |  | Sirajgonj 225MW CCPP Unit-2 GT Synchronized with remarks:- None
|  | 21:49 | Haripur-Narsingdi 132kV Ckt-1 is restored.
| 01:09 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- ST
| 01:09 |  | Sirajgonj 225MW CCPP Unit-2 ST Synchronized with remarks:- None
| 01:35 |  | Matarbari 2*600 MW (CPGCL) unit-2 was shutdown due to boiler maintenance.
| 02:39 |  | Amnura 132/33kV S/S T-1 (406T) LT Tripped showing Over current relays. | [7 empty] | 10.0MW load
interrup.
| 02:39 |  | Amnura 132/33kV S/S Auxiliary-1 HT Tripped showing Over current relays.
| 02:39 | 05:06 | Amnura 132/33kV S/S T-2 (416T) LT Tripped showing Over current relays Due to 33kV bus PT | [7 empty] | 10.0MW load
|  |  | blast B-Phase | [7 empty] | interrup.
| 03:46 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
| 03:53 |  | Sirajgonj Unit-1 was forced shutdown due to dp high.
| 03:53 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- GT
| 05:00 |  | Minimum Generation is 7222 MW
| 06:02 |  | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Tripped showing REF, Differential Protection
Operated, Lockout Relay Operated. relays Due to 33KV Under ground Cable Brust( R-Phase)
| 06:02 |  | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Tripped showing None relays Due to 33KV Under
ground Cable Brust
| 06:46 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to 33 KV Outgonig under ground Cable
heatshink damage
| 06:53 |  | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to 33 KV Outgonig under ground Cable
heatshink damage
| 07:14 |  | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT Project Work S/D Due to Pile work
| 07:14 | 07:14 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 LT Project Work S/D Due to Pile work for
project
| 07:15 |  | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT Project Work S/D Due to Pile work
| 07:24 |  | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to Projcet Work(T-2 D/S change)
| 07:24 |  | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to Projcet Work(T-2 D/S change)
| 07:32 |  | Aminbazar-Meghnaghat 400kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing
Distance relay relays Due to Trip due to distance relay B to G
| 07:34 |  | Jamalpur United (20MW)-Jamalpur 132kV Ckt-1 Scheduled S/D from Jamalpur 132/33kV end Due
to Projcet Work(T-2 D/S change)
| 07:42 |  | Jamalpur 132/33kV S/S Bus-A Project Work S/D Due to T-2 B-Bus D/s Change Work
| 07:50 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
| 07:51 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 400 | 9259200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7627000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 223 | 6720349 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 64237 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7084212 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 285840 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 536640 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 30822 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 120753 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19.5 | 411000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 333720 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 502560 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 24 | 432100 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 8 | 375840 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 90 | 1633680 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 864960 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 12480 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 1075680 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 102349 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 37 | 327960 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 45 | 145200 | -
Dhaka Area Total |  |  |  |  | 5841.27 | 1759.5 | 37946582
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 122985 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 231840 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 900420 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3794029 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 81127 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 16 | 416640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 21000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 39309 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 13440 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 223309 | Liquid fuel shortage
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 15055 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 930 | 20645452 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 31 | 501600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 903 | 21141818.18 | -
Chattogram Area Total |  |  |  |  | 4915.22 | 2149 | 48148024.18
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4570000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 41 | 948312 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 27 | 612000 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4148364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1135528 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 362981 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 48 | 96272 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1226830 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 180960 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 58 | 1271040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 365780 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 322560 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 102 | 707520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 384518 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 931 | 16332665
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 5 | 161280 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1152000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 205200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 224340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 44640 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 35640 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 89 | 1828800
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 30 | 376000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3556636.4 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | -
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 10 | 740592 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 17136 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 720192 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1781760 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 130 | 1676420 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 90000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 327312 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7160000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 290 | 8084000 | FGMO Available, but GT Load set maximum 260MW
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 230 | 4963000 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1211 | 29493048.4
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 899 | 20858181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 250 | 8567424 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 352080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to changing of ST Power Tx Radiators
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1149 | 29777685
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 141703 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 100 | 2725000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 23346909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 4950270 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 178800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5935000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2652 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1851 | 37280334.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 149 | 3086182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 151300 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 204 | 3785173 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 83016 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 132192 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 11820 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 757 | 15234545 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 143252 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 397070 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1166.5 | 23024550
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 71 | 1655999 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 209 | 5109000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 140755 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 4692.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 91 | 231011 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 33691 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 232560 | -
Rangpur Area Total |  |  |  |  | 950 | 441 | 7407708.48
Eastern Grid Total |  |  |  |  | 16771.748 | 6139.5 | 133749119.58
Western Grid Total |  |  |  |  | 10294.5 | 4607.5 | 97490277.57
National Grid Total |  |  |  |  | 27066.248 | 10747 | 231239397.15
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7079.86 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3250.4 | MW
i) Dhaka area |  |  | 3848.36 |  | MW | i) Khulna area |  |  |  | 1214 | MW
ii) Chattogram area |  |  | 1117.5 |  | MW | ii) Barishal area |  |  |  | 287.6 | MW
iii) Cumilla area |  |  | 838 |  | MW | iii) Rajshahi area |  |  |  | 1029.8 | MW
iv) Mymensingh area |  |  | 899 |  | MW | iv) Rangpur area |  |  |  | 719 | MW
v) Sylhet area |  |  | 377 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10330.26 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 59 | 18:00 | 133 | Purbachal | 14 | 13:00
2 | AKSML | 102 | 09:00 | 68 | Jamalpur | 102 | 19:30 | 134 | Purbasadipur | 100 | 13:00
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 106 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 73 | 13:00 | 70 | Jhenaidah | 95 | 18:30 | 136 | Rahim | 43 | 11:00
5 | Agrabad | 50 | 18:00 | 71 | Joydebpur | 129 | 18:00 | 137 | Rajbari | 56 | 18:30
6 | Amnura | 45 | 18:30 | 72 | Joypurhat | 43 | 18:00 | 138 | Rajendrapur | 100 | 09:00
7 | Ashuganj | 63 | 13:00 | 73 | Juldah | 12 | 12:00 | 139 | Rajshahi | 91 | 13:00
8 | BSRM | 193 | 18:30 | 74 | KSRM | 29 | 14:00 | 140 | Rajshahi-230 | 44 | 12:00
9 | Bagerhat | 62 | 18:30 | 75 | Kabirpur | 192 | 09:00 | 141 | Ramganj | 76 | 18:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 50 | 19:00 | 142 | Rampur | 25 | 18:00
11 | Bakulia | 66 | 18:00 | 77 | Kallyanpur | 63 | 16:00 | 143 | Rangamati | 12 | 18:00
12 | Banani | 46 | 12:00 | 78 | Kalurghat | 28 | 16:00 | 144 | Rangpur | 97 | 13:00
13 | Bangabhaban | 7 | 10:00 | 79 | Kamrangirchar | 53.9 | 13:00 | 145 | Ruppur | 4.2 | 15:00
14 | Barapukuria | 56 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 13 | 00:00
15 | Barguna | 14 | 19:30 | 81 | Kazla | 81 | 16:00 | 147 | Saidpur | 96 | 10:00
16 | Barishal | 78 | 13:00 | 82 | Keranigonj | 60 | 13:00 | 148 | Satkhira | 94 | 18:30
17 | Barishal-230 | 60 | 18:30 | 83 | Khagrachori | 24 | 18:00 | 149 | Satmasjid | 79 | 13:00
18 | Baroaulia | 63 | 11:00 | 84 | Khulna | 73 | 13:00 | 150 | Savar | 182 | 18:00
19 | Baroirhat | 55 | 18:00 | 85 | Khulshi | 148 | 18:30 | 151 | SevenRings | 18.37 | 03:00
20 | Bashundhara | 123 | 14:00 | 86 | Kishoreganj | 126 | 19:30 | 152 | ShahCement | 30 | 17:00
21 | BashundharaCement | 12 | 11:00 | 87 | Kodda | 264 | 16:00 | 153 | Shahjadpur | 57 | 12:00
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 27 | 19:30 | 154 | Shahjibazar | 87 | 18:30
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 54 | 08:00 | 155 | Shahmirpur | 44 | 16:00
24 | Bhaluka | 110 | 09:00 | 90 | Kushtia | 110 | 18:30 | 156 | Shariatpur | 52 | 20:00
25 | Bhandaria | 35.5 | 21:00 | 91 | Lalbag | 57 | 19:00 | 157 | Sherpur | 110 | 23:00
26 | Bhangura | 27 | 18:30 | 92 | Lalmonirhat | 46 | 08:00 | 158 | Shikalbaha | 18 | 12:00
27 | Bheramara(GK) | 40 | 18:30 | 93 | MI_Cement | 18 | 11:00 | 159 | Shitalakhya | 63.9 | 12:00
28 | Bhulta | 224 | 16:00 | 94 | Madanganj | 22 | 13:00 | 160 | Sholosohor | 33 | 15:00
29 | Bog-Sherpur | 62 | 09:00 | 95 | Madaripur | 65 | 20:00 | 161 | Shyampur | 168 | 11:00
30 | Bogura | 106 | 18:30 | 96 | Madartek | 58.06 | 13:00 | 162 | Siddhirganj | 97 | 13:00
31 | Borhanuddin | 54 | 22:00 | 97 | Madunaghat | 36 | 13:00 | 163 | Sirajganj | 76 | 19:00
32 | Brahmanbaria | 100 | 21:00 | 98 | Magura | 44 | 18:30 | 164 | Sonargaon | 93 | 12:00
33 | Cantonment | 74 | 13:00 | 99 | Mahasthangarh | 50 | 19:30 | 165 | Sreemongol | 49 | 18:00
34 | Chandpur | 42 | 18:00 | 100 | Manikganj | 109 | 18:30 | 166 | Sreepur | 80 | 11:00
35 | Chandraghona | 26 | 18:00 | 101 | Maniknagar | 50 | 13:00 | 167 | Srinagar | 29.4 | 20:00
36 | Chapai | 63 | 12:00 | 102 | Matarbari | 34 | 18:00 | 168 | Sunamganj | 38 | 18:00
37 | Charsaidpur | 43 | 13:00 | 103 | Matuail | 61 | 12:00 | 169 | Sylhet | 30 | 18:00
38 | Chauddagram | 45 | 13:00 | 104 | Millgate | 57 | 18:00 | 170 | Sylhet-132 | 71 | 16:00
39 | Chhatak | 23 | 18:00 | 105 | Mirpur | 95 | 13:00 | 171 | TK | 21 | 18:00
40 | Chowmuhani | 160 | 18:30 | 106 | Mirsorai | 9 | 19:30 | 172 | Tangail | 140 | 19:30
41 | Chuadanga | 74 | 18:30 | 107 | Mirzapur | 40 | 18:00 | 173 | Thakurgaon | 76 | 18:30
42 | Coxsbazar | 107 | 18:00 | 108 | Mithapukur | 63 | 18:00 | 174 | Tongi | 105 | 11:00
43 | Cumilla(N) | 101 | 11:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 21 | 15:00
44 | Cumilla(S) | 129 | 14:00 | 110 | Mogbazar | 94.6 | 15:00 | 176 | Ullon | 34 | 13:00
45 | Daudkandi | 90 | 20:00 | 111 | Mongla | 35 | 10:00 | 177 | Uttara | 62 | 13:00
46 | Dhaka | 28 | 12:00 | 112 | Motijheel | 25 | 13:00 | 178 | UttaraNew | 36 | 12:00
47 | Dhamrai | 108 | 11:00 | 113 | Muktagacha | 26 | 18:00 | 179 | Zigatola | 50 | 14:00
48 | Dhanmondi | 88 | 13:00 | 114 | Munshiganj | 64 | 21:00
49 | Dohazari | 73 | 18:30 | 115 | Mymensingh | 165 | 13:00
50 | Faridpur | 110 | 18:30 | 116 | Naogaon | 103 | 13:00
51 | Fatullah | 71 | 10:00 | 117 | Narail | 41 | 18:30
52 | Fenchuganj | 25 | 18:00 | 118 | Narinda | 58.5 | 13:00
53 | Feni | 64 | 18:00 | 119 | Narshingdi | 148 | 21:00
54 | GPH | 93 | 15:00 | 120 | Natore | 105 | 18:30
55 | Ghatail | 32 | 07:00 | 121 | Nawabganj | 35.2 | 13:00
56 | Ghorashal | 9 | 08:00 | 122 | Netrakona | 131 | 08:00
57 | Ghorashal-230 | 70 | 09:00 | 123 | New | 71 | 12:00
58 | Goalpara | 26 | 13:00 | 124 | Niamatpur | 76 | 09:00
59 | Gollamari | 48 | 13:00 | 125 | Noapara | 36 | 18:30
60 | Gopalganj | 79 | 18:30 | 126 | PHP | 9 | 18:00
61 | Gulshan | 70 | 14:00 | 127 | Pabna | 66 | 18:30
62 | Halishahar | 45 | 11:00 | 128 | Palashbari | 82 | 18:30
63 | HaripurSBU | 180 | 12:00 | 129 | Panchagarh | 42 | 18:30
64 | Hasnabad | 62 | 11:00 | 130 | Patuakhali | 57.6 | 21:00
65 | Hathazari | 52 | 13:00 | 131 | Payra | 14 | 18:00
66 | Ishurdi | 58 | 18:30 | 132 | Postogola | 41 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9083.5 | 0 |  | 9083.5
1:00 | 8460.5 | 0 |  | 8460.5
2:00 | 7836 | 0 |  | 7836
3:00 | 7734 | 0 |  | 7734
4:00 | 7385 | 0 |  | 7385
5:00 | 7314 | 0 |  | 7314
6:00 | 7841.5 | 0 |  | 7841.5
7:00 | 8593.32 | 0 |  | 8593.32
8:00 | 9441.69 | 78 |  | 9523.2
9:00 | 10111.37 | 88 |  | 10203.33
10:00 | 10149.61 | 61 |  | 10213.36
11:00 | 10321.47 | 0 |  | 10321.47
12:00 | 10543.09 | 0 |  | 10543.09
13:00 | 10836.47 | 36 |  | 10874.09
14:00 | 10292.55 | 30 |  | 10323.9
15:00 | 10029.49 | 0 |  | 10029.49
16:00 | 9704.49 | 0 |  | 9704.49
17:00 | 9755.26 | 98 |  | 9857.67
18:00 | 10514.5 | 96 |  | 10614.82
19:00 | 10747 | 138 |  | 10891
19:30 | 10698 | 108 |  | 10811
20:00 | 10720.5 | 143 |  | 10869.5
21:00 | 10502.04 | 37 |  | 10541.04
22:00 | 10133.78 | 0 |  | 10133.78
23:00 | 9668.38 | 0 |  | 9668.38
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5255 | 3828.5 | 9083.5 | DAILY GENERATION CURVE
00:30 | 5158 | 3614 | 8772
01:00 | 5061 | 3399.5 | 8460.5 | 23-01-2025
01:30 | 4937.75 | 3210.5 | 8148.25
02:00 | 4814.5 | 3021.5 | 7836
02:30 | 4790 | 2995 | 7785
03:00 | 4765.5 | 2968.5 | 7734
03:30 | 4603.5 | 2956 | 7559.5
04:00 | 4441.5 | 2943.5 | 7385
04:30 | 4410 | 2939.5 | 7349.5
05:00 | 4378.5 | 2935.5 | 7314
05:30 | 4580.75 | 2997 | 7577.75
06:00 | 4783 | 3058.5 | 7841.5
06:30 | 4977.16 | 3240.25 | 8217.41
07:00 | 5171.32 | 3422 | 8593.32
07:30 | 5320.9 | 3696.605 | 9017.505
08:00 | 5470.48 | 3971.21 | 9441.69
08:30 | 5573.59 | 4202.94 | 9776.53
09:00 | 5676.7 | 4434.67 | 10111.37
09:30 | 5708.865 | 4421.625 | 10130.49
10:00 | 5741.03 | 4408.58 | 10149.61
10:30 | 5750.87 | 4484.67 | 10235.54
11:00 | 5760.71 | 4560.76 | 10321.47
11:30 | 5799.185 | 4633.095 | 10432.28
12:00 | 5837.66 | 4705.43 | 10543.09
12:30 | 6010.715 | 4679.065 | 10689.78
13:00 | 6183.77 | 4652.7 | 10836.47
13:30 | 6053.83 | 4510.68 | 10564.51
14:00 | 5923.89 | 4368.66 | 10292.55
14:30 | 5838.275 | 4322.745 | 10161.02
15:00 | 5752.66 | 4276.83 | 10029.49
15:30 | 5657.815 | 4209.175 | 9866.99
16:00 | 5562.97 | 4141.52 | 9704.49
16:30 | 5616.84 | 4113.035 | 9729.875
17:00 | 5670.71 | 4084.55 | 9755.26
17:30 | 5935.355 | 4199.525 | 10134.88
18:00 | 6200 | 4314.5 | 10514.5
18:30 | 6169.75 | 4461 | 10630.75
19:00 | 6139.5 | 4607.5 | 10747
19:30 | 6034.5 | 4663.5 | 10698
20:00 | 6080 | 4640.5 | 10720.5
20:30 | 6048.5 | 4562.77 | 10611.27 |  | Executive Engineer
21:00 | 6017 | 4485.04 | 10502.04 |  | Network Operation Division
21:30 | 5909.75 | 4408.16 | 10317.91
22:00 | 5802.5 | 4331.28 | 10133.78
22:30 | 5680 | 4221.08 | 9901.08
23:00 | 5557.5 | 4110.88 | 9668.38

## En-Curve
QF-LDC-12
Date | 23-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2638 | 1688.5 | 904 | 0 | 52 | 569 | 35 | 3045 | 0 | 17 | 118 | 0 | 0 | 17 | 0 | DAILY ENERGY CURVE
00:30 | 2607 | 1700 | 903.5 | 0 | 50 | 495.5 | 35 | 2837.5 | 0 | 17 | 109 | 0 | 0 | 17.5 | 0 | 23-01-2025
01:00 | 2576 | 1711.5 | 903 | 0 | 48 | 422 | 35 | 2630 | 0 | 17 | 100 | 0 | 0 | 18 | 0
01:30 | 2529 | 1707.25 | 810.5 | 0 | 46 | 419.5 | 35 | 2506 | 0 | 8.5 | 64 | 0 | 0 | 22.5 | 0 | Energy Generated | 231.2394 |  | MKWHr
02:00 | 2482 | 1703 | 718 | 0 | 44 | 417 | 35 | 2382 | 0 | 0 | 28 | 0 | 0 | 27 | 0 | Energy not Served | 0.805 |  | MKWHr
02:30 | 2481 | 1699 | 717.5 | 0 | 44 | 417.5 | 35 | 2349 | 0 | 0 | 14 | 0 | 0 | 28 | 0 | Total Energy Requirement | 232.0444 |  | MKWHr
03:00 | 2480 | 1695 | 717 | 0 | 44 | 418 | 35 | 2316 | 0 | 0 | 0 | 0 | 0 | 29 | 0
03:30 | 2463 | 1556.5 | 717 | 0 | 43 | 418.5 | 35 | 2303 | 0 | 0 | 0 | 0 | 0 | 23.5 | 0
04:00 | 2446 | 1418 | 717 | 0 | 42 | 419 | 35 | 2290 | 0 | 0 | 0 | 0 | 0 | 18 | 0
04:30 | 2418 | 1409.5 | 717 | 0 | 41 | 419 | 35 | 2285.5 | 0 | 0 | 0 | 0 | 0 | 24.5 | 0
05:00 | 2390 | 1401 | 717 | 0 | 40 | 419 | 35 | 2281 | 0 | 0 | 0 | 0 | 0 | 31 | 0
05:30 | 2431 | 1498.75 | 717 | 0 | 41 | 419 | 35 | 2392 | 0 | 0 | 16.5 | 0 | 0 | 27.5 | 0
06:00 | 2472 | 1596.5 | 717 | 0 | 42 | 419 | 35 | 2503 | 0 | 0 | 33 | 0 | 0 | 24 | 0
06:30 | 2448 | 1718 | 763 | 0 | 41 | 448.5 | 35 | 2659 | 1.41 | 21 | 60 | 0 | 0 | 22.5 | 0
07:00 | 2424 | 1839.5 | 809 | 0 | 40 | 478 | 35 | 2815 | 2.82 | 42 | 87 | 0 | 0 | 21 | 0
07:30 | 2460.5 | 1851.5 | 856.5 | 0 | 41 | 520.485 | 35 | 3041.5 | 18.52 | 69.5 | 101 | 0 | 0 | 22 | 39
08:00 | 2497 | 1863.5 | 904 | 0 | 42 | 562.97 | 35 | 3268 | 34.22 | 97 | 115 | 0 | 0 | 23 | 78
08:30 | 2456.5 | 1833 | 904 | 0 | 46 | 654.485 | 37.5 | 3472.5 | 64.545 | 103 | 187.5 | 0 | 0 | 17.5 | 83
09:00 | 2416 | 1802.5 | 904 | 0 | 50 | 746 | 40 | 3677 | 94.87 | 109 | 260 | 0 | 0 | 12 | 88
09:30 | 2367 | 1757 | 904 | 0 | 53 | 749.005 | 40 | 3664 | 144.985 | 109 | 332.5 | 0 | 0 | 10 | 74.5
10:00 | 2318 | 1711.5 | 904 | 0 | 56 | 752.01 | 40 | 3651 | 195.1 | 109 | 405 | 0 | 0 | 8 | 61
10:30 | 2363 | 1753 | 902 | 0 | 57 | 756.045 | 40 | 3614.5 | 211.995 | 118 | 411.5 | 0 | 0 | 8.5 | 30.5
11:00 | 2408 | 1794.5 | 900 | 0 | 58 | 760.08 | 40 | 3578 | 228.89 | 127 | 418 | 0 | 0 | 9 | 0
11:30 | 2428.5 | 1748.5 | 899.5 | 0 | 60 | 756.65 | 40 | 3623.5 | 283.63 | 127 | 452.5 | 0 | 0 | 12.5 | 0
12:00 | 2449 | 1702.5 | 899 | 0 | 62 | 753.22 | 40 | 3669 | 338.37 | 127 | 487 | 0 | 0 | 16 | 0
12:30 | 2470 | 1714.5 | 898.5 | 0 | 62 | 753.705 | 40 | 3721.5 | 355.575 | 127 | 529.5 | 0 | 0 | 17.5 | 18
13:00 | 2491 | 1726.5 | 898 | 0 | 62 | 754.19 | 40 | 3774 | 372.78 | 127 | 572 | 0 | 0 | 19 | 36
13:30 | 2479.5 | 1689.5 | 898 | 0 | 65 | 707.095 | 40 | 3679.5 | 355.915 | 111.5 | 522.5 | 0 | 0 | 16 | 33
14:00 | 2468 | 1652.5 | 898 | 0 | 68 | 660 | 40 | 3585 | 339.05 | 96 | 473 | 0 | 0 | 13 | 30
14:30 | 2491 | 1645.5 | 899 | 0 | 62 | 664 | 40 | 3525.5 | 301.52 | 90 | 429.5 | 0 | 0 | 13 | 15
15:00 | 2514 | 1638.5 | 900 | 0 | 56 | 668 | 40 | 3466 | 263.99 | 84 | 386 | 0 | 0 | 13 | 0
15:30 | 2549 | 1601 | 899.5 | 0 | 58 | 666.5 | 40 | 3375.5 | 197.99 | 84 | 381.5 | 0 | 0 | 14 | 0
16:00 | 2584 | 1563.5 | 899 | 0 | 60 | 665 | 40 | 3285 | 131.99 | 84 | 377 | 0 | 0 | 15 | 0
16:30 | 2645 | 1587.5 | 899 | 0 | 59 | 667 | 40 | 3239.5 | 81.375 | 102 | 393.5 | 0 | 0 | 16 | 49
17:00 | 2706 | 1611.5 | 899 | 0 | 58 | 669 | 40 | 3194 | 30.76 | 120 | 410 | 0 | 0 | 17 | 98
17:30 | 2638 | 1576.5 | 898.5 | 0 | 62 | 708.5 | 40 | 3297 | 15.38 | 204 | 676.5 | 0 | 0 | 18.5 | 97
18:00 | 2570 | 1541.5 | 898 | 0 | 66 | 748 | 40 | 3400 | 0 | 288 | 943 | 0 | 0 | 20 | 96
18:30 | 2578 | 1593.75 | 898.5 | 0 | 62 | 752.5 | 40 | 3510 | 0 | 287 | 883.5 | 0 | 0 | 25.5 | 117
19:00 | 2586 | 1646 | 899 | 0 | 58 | 757 | 40 | 3620 | 0 | 286 | 824 | 0 | 0 | 31 | 138
19:30 | 2767 | 1847 | 899 | 0 | 52 | 757 | 40 | 3663 | 0 | 214 | 425 | 0 | 0 | 34 | 108
20:00 | 2773 | 1825.5 | 899 | 0 | 56 | 758 | 40 | 3797 | 0 | 158 | 386 | 0 | 0 | 28 | 143
20:30 | 2765 | 1848 | 898.5 | 0 | 56 | 757.77 | 40 | 3788 | 0 | 124 | 304.5 | 0 | 0 | 29.5 | 90
21:00 | 2757 | 1870.5 | 898 | 0 | 56 | 757.54 | 40 | 3779 | 0 | 90 | 223 | 0 | 0 | 31 | 37
21:30 | 2735.5 | 1853.25 | 897.5 | 0 | 56 | 757.66 | 37.5 | 3659.5 | 0 | 78 | 213.5 | 0 | 0 | 29.5 | 18.5
22:00 | 2714 | 1836 | 897 | 0 | 56 | 757.78 | 35 | 3540 | 0 | 66 | 204 | 0 | 0 | 28 | 0
22:30 | 2679.5 | 1789.5 | 898 | 0 | 55 | 710.58 | 35 | 3441.5 | 0 | 66 | 201.5 | 0 | 0 | 24.5 | 0
23:00 | 2645 | 1743 | 899 | 0 | 54 | 663.38 | 35 | 3343 | 0 | 66 | 199 | 0 | 0 | 21 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 23-01-2025 | 0 | [6 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 417 | 04:00 | 390 | 12:00 | Kaliakoir | 376 | 02:00 | 366 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 410 | 5:00 | 380 | 13:00 | Madunaghat | 409 | 04:00 | 395 | 13:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 411 | 03:00 | 382 | 12:00 | Meghnaghat | 410 | 03:00 | 380 | 10:00
| Bibiana | 396 | 03:00 | 388 | 22:00 | Payra | 419 | 05:00 | 406 | 08:00
| BIPTC | 407 | 02:00 | 394 | 08:00 | Rahanpur | 415 | 04:00 | 393 | 09:00
| Bogura | 414 | 03:00 | 389 | 09:00 | Rampal | 417 | 05:00 | 388 | 12:00
| Gopalganj | 417 | 04:00 | 394 | 12:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 237 | 03:00 | 222 | 12:00 | Haripur | 235 | 04:00 | 224 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 236 | 01:00 | 223 | 12:00 | Hasnabad | 235 | 22:00 | 223 | 11:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 234 | 00:00 | 223 | 13:00 | Hathazari | 233 | 00:00 | 225 | 14:00
| Ashuganj | 237 | 01:00 | 226 | 13:00 | Ishurdi | 245 | 03:00 | 231 | 09:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 5:00 | 224 | 12:00 | Jhenaidah | 243 | 05:00 | 222 | 13:00
| Baghabari | 242 | 01:00 | 227 | 12:00 | Kaliakoir | 237 | 05:00 | 222 | 12:00 | 230 kV MAX | 249 |  | 249 | 215
| Barapukuria | 225 | 02:00 | 215 | 08:00 | Keranigonj | 236 | 03:00 | 221 | 12:00 | 230 kV MIN | 215 |  | 245 | 221 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 227 | 3:00 | 216 | 19:00 | Khulna(S) | 244 | 04:00 | 225 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 247 | 03:00 | 235 | 12:00 | Madunaghat | 233 | 02:00 | 225 | 12:00 | 132 kV MAX | 143 |  | 143 | 112 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 242 | 03:00 | 227 | 09:00 | Madunaghat-400 | 234 | 04:00 | 226 | 12:00 | 132 kV MIN | 109 |  | 141 | 109 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 240 | 03:00 | 223 | 12:00 | Maniknagar | 238 | 05:00 | 223 | 12:00 | [35 empty] | 6:00
| Bibiana | 229 | 00:00 | 224 | 11:00 | Meghnaghat | 244 | 04:00 | 230 | 11:00 |  | 400 | [33 empty] | 392
| BIPTC | 245 | 04:00 | 228 | 09:00 | Meghnaghat-400 | 238 | 03:00 | 226 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 241 | 03:00 | 225 | 09:00 | Mirsorai | 235 | 04:00 | 222 | 21:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 240 | 03:00 | 224 | 09:00 | Rajshahi | 243 | 04:00 | 224 | 13:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 249 | 03:00 | 243 | 08:00 | Rampal | 241 | 02:00 | 222 | 12:00 |  | 132 |  |  | Ash 400-299274
| BSRM | 235 | 04:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 233 | 05:00 | 223 | 12:00 | Rampura | 239 | 03:00 | 223 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 247 | 03:00 | 232 | 12:00 | Shikalbaha | 234 | 05:00 | 223 | 13:00 |  | kaptai by call 399528
| Fenchuganj | 234 | 17:00 | 227 | 11:00 | Shyampur | 237 | 03:00 | 221 | 12:00
| Ghorashal | 240 | 04:00 | 230 | 00:00 | Siddhirganj | 238 | 04:00 | 226 | 12:00
| Ghorashal-230 | 237 | 03:00 | 223 | 11:00 | Sirajgonj | 245 | 00:00 | 232 | 16:00
| Gopalganj | 248 | 04:00 | 233 | 13:00 | Sreepur | 241 | 03:00 | 223 | 11:00
| GPH | 235 | 04:00 | 222 | 12:00 | Tongi | 232 | 04:00 | 220 | 12:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 137 | 02:00 | 127 | 12:00 | Kurigram | 132 | 04:00 | 118 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 138 | 03:00 | 128 | 12:00 | Kushtia | 140 | 00:00 | 131 | 09:00
| Agrabad | 134 | 04:00 | 127 | 12:00 | Lalbag | 139 | 03:00 | 127 | 12:00
| AKS | 132 | 05:00 | 126 | 12:00 | Lalmonirhat | 128 | 05:00 | 118 | 08:00
| Aminbazar | 135 | 00:00 | 128 | 11:00 | Madanganj | 137 | 18:00 | 127 | 12:00
| Amnura | 140 | 05:00 | 129 | 08:00 | Madaripur | 135 | 00:00 | 130 | 12:00
| Ashuganj | 141 | 01:00 | 135 | 15:00 | Madartek | 137 | 04:00 | 127 | 12:00
| Bagerhat | 136 | 01:00 | 126 | 09:00 | Madunaghat | 134 | 02:00 | 129 | 13:00
| Bajitpur | 136 | 03:00 | 128 | 11:00 | Magura | 141 | 03:00 | 129 | 12:00
| Bakulia | 134 | 03:00 | 128 | 12:00 | Mahasthangarh | 137 | 04:00 | 125 | 08:00
| Banani | 137 | 02:00 | 127 | 12:00 | Manikganj | 132 | 09:00 | 128 | 00:00
| Bangabhaban | 136 | 03:00 | 126 | 12:00 | Maniknagar | 135 | 04:00 | 126 | 13:00
| Barapukuria | 136 | 18:30 | 126 | 08:00 | Matarbari | 125 | 02:00 | 118 | 18:30
| Barguna | 138 | 03:00 | 132 | 21:00 | Matuail | 136 | 04:00 | 128 | 12:00
| Barishal | 137 | 03:00 | 129 | 12:00 | Millgate | 138 | 03:00 | 128 | 10:00
| Barishal-230 | 138 | 02:00 | 130 | 12:00 | Mirpur | 135 | 01:00 | 127 | 12:00
| Baroaulia | 134 | 02:00 | 129 | 14:00 | Mirzapur | 130 | 00:00 | 125 | 07:00
| Baroirhat | 131 | 18:30 | 124 | 13:00 | Mithapukur | 135 | 04:00 | 132 | 18:00
| Bashundhara | 138 | 00:00 | 127 | 14:00 | MI_Cement | 137 | 02:00 | 128 | 12:00
| BashundharaCement | 137 | 18:00 | 127 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 135 | 03:00 | 131 | 11:00 | Mogbazar | 137 | 04:00 | 127 | 13:00
| Benapole | 139 | 02:00 | 124 | 09:00 | Mongla | 136 | 02:00 | 126 | 09:00
| Bhaluka | 129 | 03:00 | 117 | 11:00 | Motijheel | 136 | 03:00 | 126 | 12:00
| Bhandaria | 134 | 04:00 | 127 | 12:00 | Muktagacha | 126 | 10:00 | 115 | 12:00
| Bhangura | 140 | 02:00 | 129 | 09:00 | Munshiganj | 137 | 18:00 | 127 | 12:00
| Bheramara | 141 | 03:00 | 131 | 09:00 | Mymensingh | 126 | 00:00 | 112 | 12:00
| Bheramara(GK) | 141 | 03:00 | 132 | 08:00 | Naogaon | 136 | 03:00 | 124 | 13:00
| Bhulta | 130 | 03:00 | 115 | 19:30 | Narail | 140 | 04:00 | 127 | 13:00
| Bog-Sherpur | 138 | 03:00 | 126 | 09:00 | Narinda | 135 | 4:00 | 126 | 13:00
| Bogura | 138 | 03:00 | 127 | 09:00 | Narshingdi | 132 | 04:00 | 118 | 19:30
| Bogura-230 | 139 | 14:00 | 127 | 09:00 | Natore | 139 | 03:00 | 127 | 08:00
| Brahmanbaria | 133 | 02:00 | 126 | 15:00 | Nawabganj | 138 | 01:00 | 129 | 12:00
| Cantonment | 138 | 03:00 | 128 | 12:00 | Netrakona | 126 | 00:00 | 109 | 12:00
| Chandpur | 137 | 18:00 | 122 | 21:00 | New | 138 | 04:00 | 128 | 12:00
| Chandraghona | 135 | 02:00 | 129 | 13:00 | Niamatpur | 139 | 01:00 | 132 | 10:00
| Chapai | 138 | 03:00 | 130 | 13:00 | Noapara | 140 | 03:00 | 128 | 09:00
| Charsaidpur | 138 | 18:00 | 128 | 11:00 | Pabna | 139 | 04:00 | 125 | 09:00
| Chauddagram | 133 | 03:00 | 124 | 12:00 | Palashbari | 134 | 04:00 | 119 | 08:00
| Chhatak | 134 | 01:00 | 129 | 16:00 | Panchagarh | 138 | 18:30 | 119 | 08:00
| Chowmuhani | 130 | 18:00 | 121 | 21:00 | Patuakhali | 137 | 03:00 | 132 | 14:00
| Chuadanga | 140 | 02:00 | 127 | 17:00 | Payra | 138 | 02:00 | 133 | 08:00
| Coxsbazar | 124 | 05:00 | 118 | 18:00 | PHP | 132 | 03:00 | 124 | 13:00
| Cumilla(N) | 135 | 05:00 | 129 | 12:00 | Postogola | 138 | 01:00 | 131 | 11:00
| Cumilla(S) | 136 | 04:00 | 132 | 14:00 | Purbachal | 137 | 03:00 | 127 | 12:00
| Daudkandi | 134 | 05:00 | 124 | 17:00 | Purbasadipur | 133 | 18:30 | 118 | 09:00
| Dhaka | 137 | 04:00 | 126 | 12:00 | Rahanpur | 140 | 01:00 | 136 | 12:00
| Dhamrai | 136 | 03:00 | 127 | 14:00 | Rahanpur-400 | 141 | 02:00 | 133 | 09:00
| Dhanmondi | 138 | 05:00 | 127 | 13:00 | Rahim | 135 | 04:00 | 127 | 12:00
| Dohazari | 128 | 00:00 | 125 | 11:00 | Rajbari | 137 | 03:00 | 128 | 12:00
| Faridpur | 137 | 03:00 | 130 | 17:00 | Rajendrapur | 135 | 18:00 | 126 | 11:00
| Fatullah | 138 | 03:00 | 129 | 11:00 | Rajshahi | 141 | 04:00 | 130 | 09:00
| Fenchuganj | 139 | 05:00 | 135 | 11:00 | Rajshahi-230 | 141 | 03:00 | 125 | 13:00
| Feni | 130 | 04:00 | 122 | 21:00 | Ramganj | 132 | 18:00 | 119 | 09:00
| Ghatail | 127 | 10:00 | 118 | 19:30 | Rampur | 135 | 04:00 | 127 | 11:00
| Ghorashal | 140 | 00:00 | 134 | 10:00 | Rampura | 137 | 03:00 | 127 | 12:00
| Goalpara | 143 | 04:00 | 128 | 09:00 | Rangamati | 134 | 01:00 | 128 | 12:00
| Gollamari | 141 | 04:00 | 129 | 12:00 | Rangpur | 133 | 04:00 | 119 | 08:00
| Gopalganj | 139 | 03:00 | 128 | 13:00 | Ruppur | 140 | 00:00 | 130 | 09:00
| Gopalganj-400 | 139 | 03:00 | 131 | 11:00 | Saidpur | 134 | 05:00 | 120 | 08:00
| Gulshan | 135 | 01:00 | 127 | 12:00 | Satkhira | 140 | 04:00 | 126 | 08:00
| Halishahar | 133 | 18:30 | 128 | 13:00 | Satmasjid | 138 | 03:00 | 128 | 12:00
| Haripur | 134 | 00:00 | 127 | 12:00 | Savar | 136 | 02:00 | 127 | 12:00
| HaripurSBU | 134 | 00:00 | 128 | 11:00 | SevenRings | 141 | 03:00 | 134 | 11:00
| Hasnabad | 139 | 01:00 | 132 | 13:00 | ShahCement | 138 | 18:00 | 128 | 11:00
| Hathazari | 135 | 04:00 | 130 | 10:00 | Shahjadpur | 140 | 00:00 | 132 | 12:00
| Ishurdi | 143 | 04:00 | 130 | 09:00 | Shahjibazar | 135 | 01:00 | 131 | 11:00
| Jaldhaka | 132 | 19:00 | 117 | 08:00 | Shahmirpur | 132 | 00:00 | 127 | 12:00
| Jamalpur | 126 | 10:00 | 112 | 05:00 | Shariatpur | 139 | 04:00 | 129 | 12:00
| Jashore | 139 | 02:00 | 125 | 13:00 | Sherpur | 123 | 10:00 | 111 | 05:00
| Jhenaidah | 140 | 00:00 | 134 | 02:00 | Shikalbaha | 124 | 04:00 | 117 | 12:00
| Jhenaidah-230 | 143 | 04:00 | 130 | 09:00 | Shikalbaha-230 | 135 | 01:00 | 128 | 13:00
| Joydebpur | 139 | 18:00 | 130 | 10:00 | Shitalakhya | 137 | 02:00 | 128 | 12:00
| Joypurhat | 136 | 01:00 | 124 | 08:00 | Sholosohor | 135 | 03:00 | 128 | 12:00
| Juldah | 133 | 03:00 | 128 | 12:00 | Shyampur | 136 | 03:00 | 129 | 12:00
| Kabirpur | 136 | 01:00 | 125 | 12:00 | Shyampur-230 | 139 | 03:00 | 128 | 12:00
| Kachua | 134 | 18:00 | 125 | 21:00 | Siddhirganj | 135 | 04:00 | 128 | 12:00
| Kaliakoir | 138 | 05:00 | 127 | 17:00 | Sirajganj | 139 | 04:00 | 126 | 09:00
| Kallyanpur | 135 | 00:00 | 127 | 12:00 | Sonargaon | 136 | 02:00 | 119 | 17:00
| Kalurghat | 136 | 05:00 | 129 | 12:00 | Sreemongol | 136 | 02:00 | 131 | 11:00
| Kamrangirchar | 137 | 01:00 | 125 | 12:00 | Sreepur | 131 | 03:00 | 120 | 11:00
| Kaptai | N/A | N/A | N/A | N/A | Srinagar | 138 | 01:00 | 129 | 12:00
| Kazla | 136 | 03:00 | 125 | 13:00 | SSM | 136 | 01:00 | 131 | 09:00
| Keranigonj | 139 | 05:00 | 128 | 11:00 | Sunamganj | 133 | 01:00 | 127 | 13:00
| Khagrachori | 135 | 03:00 | 128 | 12:00 | Sylhet | 135 | 00:00 | 131 | 13:00
| Khulna | 139 | 04:00 | 127 | 13:00 | Sylhet-132 | 135 | 03:00 | 131 | 13:00
| Khulna(S) | 142 | 04:00 | 130 | 09:00 | Tangail | 127 | 10:00 | 120 | 19:30
| Khulshi | 132 | 01:00 | 127 | 11:00 | Thakurgaon | 137 | 18:30 | 116 | 08:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 132 | 00:00 | 125 | 08:00 | TK | 133 | 04:00 | 129 | 12:00 |  |  | Nos | Nos | Nos
| Kodda | 135 | 10:00 | 127 | 16:00 | Tongi | 138 | 02:00 | 130 | 12:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 134 | 01:00 | 128 | 12:00 | Ullahpara | 139 | 00:00 | 128 | 09:00
| Kulaura | 138 | 05:00 | 134 | 13:00 | Ullon | 136 | 02:00 | 128 | 11:00
[6 empty] | Uttara | 137 | 04:00 | 126 | 16:00
[6 empty] | UttaraNew | 137 | 03:00 | 123 | 12:00
[6 empty] | Zigatola | 139 | 04:00 | 127 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.