## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-01-2025 | during | 25-01-2025 | during | 25-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 2 | 3 | 97.3 | 97.3 | 5 | 5 | Demand "0" due to gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 323 | 412 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 310 | 350 | 450 | 450 | 310 | 310 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 263 | 249 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 260 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 64 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 16 | 15 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 7 | 15 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 22 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 15 | 32 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 12 | 0 | 52.19 | 52.19 | 34 | 34 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 51 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 0 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 14 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 17 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 0 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.27 | 1342 | 1518 | 4602.99 | 4585.99 | 2663.23 | 2646.23
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 20 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 162 | 161 | 160 | 160 | 160 | 160 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 29 | 29 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 50 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.85 | 0 | 3.85 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1105 | 920 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 9 | 44 | 23 | 14 | 23 | 14 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 577 | 576 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1946 | 1770 | 3425.57 | 3410.72 | 3367.57 | 3352.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 193 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 41 | 37 | 46.94 | 46.94 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 25 | 25 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 199 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 64 | 58 | 90 | 90 | 90 | 90 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 3 | 0 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 61 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 685 | 627 | 1673.97 | 1608.97 | 1555.2 | 1490.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-01-2025 | during | 25-01-2025 | during | 25-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 7 | 16 | 210 | 210 | 15 | 15 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.3 | 0 | 1.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 19 | 200 | 200 | 9 | 9 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 58 | 115 | 115 | 58 | 58 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.2 | 0 | 40.4 | 0 | 40.4 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | Ready to Dispatch as per NLDC Demand.
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 111.2 | 93 | 643.2 | 601.5 | 200.2 | 158.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 43 | 43 | 43 | 43 | 43 | 43 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 35 | 37 | 44 | 44 | 35 | 35 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 2.5 | 2.5 | 0 | 0 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 135 | 0 | 135 | 135 | 135 | 135 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 13 | 25 | 25 | 13 | 13 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 45 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 288 | 368 | 380 | 380 | 352 | 352 | FGMO Available, but GT Load set maximum 260MW
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 275 | 236 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1112 | 1232 | 1559.5 | 1559.5 | 1484.01 | 1484.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 913 | 912 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 300 | 350 | 410 | 410 | 340 | 340 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 72.13 | 0 | 73 | 0 | 73 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 220 | 220 | 0 | 0 | S/D due to changing of ST Power Tx Radiators
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1285.13 | 1262 | 3462 | 3389 | 1498.02 | 1425.02
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 136 | 140 | 135 | 135 | 140 | 140 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1160 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 293 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.52 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2265.1 | 1753.52 | 1834 | 2177.12 | 2176.12 | 2179 | 2178
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 58 | 214 | 214 | 150 | 150 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 123 | 196 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 187 | 142 | 220 | 220 | 170 | 170 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 0 | 0 | 0 | 120 | 0 | 0 | Partial Shutdown due to maintenance
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 1.42 | 0 | 4.1 | 0 | 4.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 714.67 | 717 | 1347.54 | 1347.54 | 717 | 717 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 41.13 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 83 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1152.72 | 1115.5 | 2694.09 | 2664.99 | 1949.55 | 1800.45
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 73 | 73 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 210 | 210 | 210 | 210 | 210 | 210 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.1 | 0 | 1.4 | 0 | 1.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 8 | 0 | 8 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 20 | 0 | 76 | 0 | 76 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 310.1 | 283 | 607.4 | 542 | 593.41 | 508.01
System Total |  |  |  |  | 27884.66 | 27066.248 | 9697.67 | 9734.5 | 20845.84 | 20538.79 | 15490.19 | 15043.14
Forecast Scenario (25-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 8360 |  | 191 |  | 8560
|  |  |  | 1:00 | 8050 |  | 191 |  | 8250
|  |  |  | 2:00 | 7410 |  | 191 |  | 7610
|  |  |  | 3:00 | 7220 |  | 191 |  | 7420
|  |  |  | 4:00 | 6990 |  | 191 |  | 7190
|  |  |  | 5:00 | 6990 |  | 191 |  | 7190
|  |  |  | 6:00 | 7440 |  | 191 |  | 7640
|  |  |  | 7:00 | 8180 |  | 191 |  | 8380
|  |  |  | 8:00 | 8890 |  | 191 |  | 9090
|  |  |  | 9:00 | 9120 |  | 191 |  | 9320
|  |  |  | 10:00 | 9140 |  | 191 |  | 9340
|  |  |  | 11:00 | 9090 |  | 191 |  | 9290
|  |  |  | 12:00 | 9770 |  | 191 |  | 9970
|  |  |  | 13:00 | 10140 |  | 191 |  | 10340
|  |  |  | 14:00 | 9680 |  | 191 |  | 9880
|  |  |  | 15:00 | 9180 |  | 191 |  | 9380
|  |  |  | 16:00 | 8910 |  | 191 |  | 9110
|  |  |  | 17:00 | 9390 |  | 191 |  | 9590
|  |  |  | 18:00 | 10500 |  | 191 |  | 10700
|  |  |  | 18:30 | 10550 |  | 191 |  | 10750
|  |  |  | 19:00 | 10800 |  | 191 |  | 11000
|  |  |  | 19:30 | 10720 |  | 191 |  | 10920
|  |  |  | 20:00 | 10620 |  | 191 |  | 10820
|  |  |  | 21:00 | 10420 |  | 191 |  | 10620
|  |  |  | 22:00 | 9970 |  | 191 |  | 10170
|  |  |  | 23:00 | 9510 |  | 191 |  | 9710
Probable Maximum Temperature: |  |  | 25.00°C
Probable Maximum Demand at Day Peak: |  |  | 9970.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 215.77 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:30 hrs on 25-01-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-01-2025 | [28 empty] | Date: | 24-01-2025 | [28 empty] | Date: | 24-01-2025 | [28 empty] | Date: | 24-01-2025 | [28 empty] | Date: | 24-01-2025 | [19 empty] | Date: | 24-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [19 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 77 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 288 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 762 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 805 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 41 | 0 | 40 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 285 | 192 | 336 | 10 | 30 | 0 | 0 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 134 | 0 | 9 | 58 | 6 | 0 | 0 | 0 | 5303 | 898 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 573.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 21 | 0 | 154 | 0 | 0 | 0 | 0 | 5.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 100 | 180 | 0 | 0 | 1000 | 0 | 3916.93 | 9219.93 | 92.53
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 274 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 704 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 720 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 180 | 41 | 0 | 40 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 275 | 190 | 336 | 10 | 30 | 0 | 0 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 134 | 0 | 9 | 37 | 10 | 0 | 0 | 0 | 5021 | 898 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 32 | 0 | 145 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 7 | 100 | 180 | 0 | 0 | 800 | 0 | 3443.45 | 8464.45 | 92.52
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 273 | 0 | 0 | 0 | 24 | 335 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 577 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 41 | 0 | 50 | 0 | 0 | 15 | 0 | 44 | 0 | 0 | 0 | 295 | 190 | 334 | 10 | 30 | 0 | 0 | 120 | 13 | 0 | 83 | 30 | 0 | 0 | 134 | 0 | 9 | 28 | 10 | 0 | 0 | 0 | 4738 | 747 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 76 | 0 | 141 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 7 | 100 | 180 | 0 | 0 | 750 | 0 | 3291.32 | 8029.32 | 92.52
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 269 | 0 | 0 | 0 | 26 | 300 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 450 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 181 | 41 | 0 | 70 | 0 | 0 | 15 | 0 | 42 | 0 | 0 | 0 | 290 | 186 | 336 | 10 | 30 | 0 | 0 | 120 | 13 | 0 | 42 | 29 | 0 | 0 | 134 | 0 | 9 | 19 | 10 | 0 | 0 | 0 | 4527 | 724 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 126 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 6 | 100 | 180 | 0 | 0 | 600 | 0 | 3164 | 7691 | 92.51
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 310 | 291 | 0 | 0 | 0 | 26 | 300 | 0 | 0 | 0 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 375 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 29 | 190 | 41 | 0 | 70 | 0 | 0 | 15 | 0 | 48 | 0 | 0 | 0 | 310 | 181 | 284 | 10 | 30 | 0 | 0 | 163 | 13 | 0 | 5 | 28 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4405 | 725 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 180 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 6 | 140 | 180 | 0 | 0 | 600 | 0 | 3052.35 | 7457.35 | 92.51
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 274 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 10 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 378 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 605 | 0 | 51 | 0 | 158 | 0 | 0 | 0 | 29 | 181 | 41 | 0 | 70 | 0 | 0 | 15 | 0 | 50 | 0 | 0 | 0 | 290 | 181 | 289 | 10 | 30 | 0 | 0 | 163 | 13 | 0 | 5 | 28 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4261 | 724 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 418.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 180 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 6 | 140 | 180 | 0 | 0 | 600 | 0 | 2961.17 | 7222.17 | 92.5
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 295 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 380 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 158 | 0 | 0 | 0 | 29 | 204 | 41 | 0 | 70 | 0 | 0 | 10 | 0 | 50 | 0 | 0 | 0 | 300 | 181 | 337 | 10 | 30 | 0 | 0 | 163 | 13 | 0 | 5 | 30 | 0 | 0 | 134 | 0 | 9 | 22 | 10 | 0 | 0 | 0 | 4341 | 725 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 180 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 6 | 140 | 180 | 0 | 0 | 600 | 0 | 2955.41 | 7296.41 | 92.5
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 304 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 375 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 600 | 1 | 51 | 0 | 158 | 0 | 0 | 0 | 29 | 196 | 41 | 0 | 70 | 0 | 0 | 10 | 0 | 40 | 0 | 1 | 0 | 290 | 181 | 375 | 10 | 30 | 0 | 0 | 163 | 13 | 0 | 5 | 30 | 0 | 0 | 135 | 0 | 12 | 35 | 10 | 0 | 0 | 0 | 4404 | 724 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 414.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 180 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 140 | 6 | 140 | 220 | 0 | 0 | 600 | 0 | 2991.38 | 7395.38 | 92.49
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 278 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 2 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 1 | 35 | 0 | 30 | 575 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 600 | 6 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 181 | 41 | 0 | 70 | 0 | 0 | 6 | 0 | 42 | 0 | 5 | 0 | 320 | 181 | 332 | 10 | 30 | 0 | 0 | 163 | 13 | 0 | 72 | 30 | 0 | 0 | 135 | 0 | 37 | 28 | 10 | 0 | 7.69 | 0 | 4729.69 | 818 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 411.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 3.48 | 0 | 0 | 122 | 0 | 125 | 0 | 0 | 0 | 0.2 | 0 | 202 | 70 | 0 | 0 | 0 | 0 | 0 | 0.1 | 5 | 0.06 | 0 | 200 | 5 | 135 | 220 | 0 | 0 | 680 | 0 | 3358.72 | 8088.41 | 92.49
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 8.5 | 0 | 310 | 301 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 5 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 31 | 577 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 700 | 12 | 51 | 0 | 197 | 0 | 0 | 0 | 28 | 204 | 41 | 0 | 50 | 0 | 0 | 0 | 0 | 44 | 0 | 14 | 0 | 320 | 181 | 333 | 10 | 30 | 0 | 0 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 135 | 0 | 57 | 9 | 10 | 0 | 15.89 | 0 | 4890.39 | 819 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.47 | 0 | 0 | 513.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 9.44 | 0 | 0 | 120 | 0 | 125 | 0 | 0 | 0 | 0.79 | 2.5 | 210 | 70 | 0 | 1 | 0 | 0 | 0 | 0.5 | 12 | 0.22 | 0 | 250 | 4 | 140 | 220 | 0 | 0 | 870 | 0 | 3760.82 | 8651.21 | 92.48
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 14.5 | 0 | 310 | 293 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 28 | 576 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 800 | 17 | 43 | 0 | 199 | 0 | 0 | 0 | 22 | 198 | 41 | 0 | 50 | 0 | 0 | 6 | 0 | 48 | 0 | 43 | 0 | 315 | 222 | 345 | 10 | 15 | 0 | 0 | 163 | 13 | 0 | 83 | 30 | 0 | 0 | 135 | 0 | 57 | 9 | 8 | 0 | 26.88 | 0 | 5034.38 | 819 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.75 | 0 | 0 | 513.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 21.11 | 0 | 0 | 116 | 0 | 125 | 0 | 0 | 0 | 1.76 | 2.5 | 210 | 71 | 0 | 2 | 0 | 0 | 0 | 1 | 16 | 0.36 | 0 | 250 | 4 | 140 | 220 | 0 | 0 | 1000 | 0 | 3944.61 | 8978.99 | 92.48
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 22 | 0 | 310 | 281 | 0 | 0 | 0 | 15 | 270 | 0 | 0 | 11 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 28 | 576 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 940 | 18 | 43 | 0 | 199 | 0 | 0 | 0 | 22 | 181 | 41 | 0 | 45 | 0 | 0 | 11 | 0 | 64 | 0 | 56 | 0 | 95 | 270 | 335 | 33 | 17 | 0 | 0 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 135 | 0 | 58 | 9 | 7 | 1 | 26.35 | 0 | 5036.35 | 818 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.15 | 0 | 0 | 610.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 39.88 | 0 | 0 | 117 | 0 | 153 | 0 | 0 | 0 | 3.17 | 2.5 | 210 | 71 | 0 | 3 | 0 | 0 | 0 | 1.2 | 24 | 0.5 | 0 | 250 | 4 | 136 | 180 | 0 | 0 | 1020 | 0 | 4123.16 | 9159.51 | 92.47
12:00 | 0 | 17 | 12 | 0 | 0 | 0 | 0 | 2 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 14 | 22 | 0 | 310 | 263 | 0 | 0 | 0 | 15 | 260 | 0 | 0 | 17 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 29 | 577 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 1105 | 20 | 43 | 0 | 199 | 0 | 0 | 0 | 25 | 193 | 41 | 0 | 45 | 0 | 3 | 11 | 0 | 64 | 0 | 61 | 0 | 45 | 275 | 288 | 35 | 43 | 0 | 0 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 135 | 0 | 58 | 9 | 7 | 1 | 36.2 | 0 | 5196.2 | 913 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.13 | 0 | 0 | 714.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 41.13 | 0 | 0 | 123 | 0 | 187 | 0 | 0 | 0 | 1.42 | 2.5 | 210 | 73 | 0 | 6 | 0 | 0 | 0 | 1.1 | 20 | 0.52 | 0 | 293 | 4 | 136 | 220 | 0 | 0 | 1100 | 0 | 4501.47 | 9697.67 | 92.47
13:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 35 | 0 | 0 | 310 | 290 | 0 | 0 | 0 | 28 | 300 | 0 | 0 | 26 | 0 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 31 | 577 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1220 | 19 | 43 | 0 | 199 | 0 | 0 | 0 | 25 | 185 | 40 | 23 | 45 | 0 | 25 | 11 | 0 | 76 | 0 | 58 | 0 | 235 | 285 | 332 | 10 | 43 | 0 | 0 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 135 | 0 | 58 | 9 | 7 | 2 | 25.49 | 0 | 5703.49 | 913 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.07 | 0 | 0 | 753.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 45.93 | 0 | 0 | 131 | 0 | 188 | 0 | 0 | 0 | 4.1 | 2.5 | 210 | 73 | 35 | 4 | 0 | 0 | 0 | 0.3 | 16 | 0.47 | 0 | 307 | 5 | 136 | 220 | 0 | 0 | 1140 | 0 | 4691.78 | 10395.27 | 92.46
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 318 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 278 | 0 | 0 | 0 | 32 | 260 | 0 | 0 | 21 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 31 | 575 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 910 | 16 | 43 | 0 | 158 | 0 | 0 | 0 | 25 | 140 | 40 | 0 | 45 | 0 | 0 | 11 | 0 | 70 | 0 | 50 | 0 | 290 | 320 | 291 | 10 | 42 | 0 | 0 | 120 | 13 | 0 | 85 | 30 | 0 | 0 | 135 | 0 | 58 | 9 | 8 | 0 | 23.66 | 0 | 5053.66 | 912 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.64 | 0 | 0 | 552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 38.51 | 0 | 0 | 141 | 0 | 190 | 0 | 0 | 0 | 3.42 | 2.5 | 210 | 73 | 0 | 1 | 0 | 0 | 0 | 0.7 | 29 | 0.36 | 0 | 178 | 3 | 80 | 180 | 0 | 0 | 800 | 0 | 3776.13 | 8829.79 | 92.46
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 310 | 266 | 0 | 0 | 0 | 32 | 260 | 0 | 0 | 14 | 0 | 17.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 31 | 452 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 800 | 12 | 43 | 0 | 158 | 0 | 0 | 0 | 25 | 140 | 41 | 0 | 45 | 0 | 0 | 11 | 0 | 46 | 0 | 36 | 0 | 305 | 320 | 329 | 10 | 42 | 0 | 0 | 120 | 13 | 0 | 10 | 30 | 0 | 0 | 132 | 0 | 58 | 9 | 9 | 1 | 19.99 | 0 | 4712.49 | 803 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.24 | 0 | 0 | 464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 27.15 | 0 | 0 | 163 | 0 | 212 | 0 | 0 | 0 | 1.59 | 2.5 | 180 | 73 | 0 | 3 | 0 | 0 | 0 | 0.3 | 31 | 0.27 | 0 | 150 | 3 | 80 | 180 | 0 | 0 | 790 | 0 | 3508.05 | 8220.54 | 92.45
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 310 | 308 | 0 | 0 | 0 | 30 | 260 | 0 | 0 | 8 | 0 | 17.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 28 | 407 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 800 | 6 | 43 | 0 | 108 | 0 | 0 | 0 | 25 | 208 | 10 | 0 | 45 | 0 | 0 | 0 | 0 | 50 | 0 | 20 | 0 | 300 | 320 | 300 | 10 | 41 | 0 | 0 | 120 | 13 | 0 | 11 | 30 | 0 | 0 | 0 | 0 | 58 | 9 | 16 | 0 | 9.89 | 0 | 4474.39 | 724 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.52 | 0 | 0 | 466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 13.02 | 0 | 0 | 199 | 0 | 130 | 0 | 0 | 0 | 1.22 | 2.5 | 210 | 74 | 0 | 1 | 0 | 0 | 0 | 0.2 | 15 | 0.14 | 0 | 150 | 3 | 80 | 180 | 0 | 0 | 720 | 0 | 3315.6 | 7789.99 | 92.45
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 310 | 276 | 0 | 0 | 0 | 30 | 260 | 0 | 0 | 2 | 0 | 14.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 28 | 409 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 2 | 43 | 0 | 108 | 0 | 0 | 0 | 24 | 183 | 10 | 0 | 45 | 0 | 0 | 0 | 0 | 54 | 0 | 4 | 0 | 305 | 300 | 290 | 10 | 42 | 0 | 0 | 120 | 13 | 0 | 11 | 30 | 0 | 0 | 0 | 0 | 58 | 9 | 16 | 0 | 2.16 | 0 | 4560.66 | 912 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.81 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 2.49 | 31 | 0 | 206 | 0 | 130 | 0 | 0 | 0 | 0.22 | 2.5 | 210 | 72 | 0 | 1 | 0 | 0 | 0 | 0 | 3 | 0.1 | 0 | 150 | 4 | 80 | 180 | 0 | 0 | 770 | 0 | 3567.12 | 8127.78 | 92.44
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 20 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 310 | 277 | 0 | 0 | 0 | 30 | 260 | 0 | 0 | 0 | 25 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 576 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 192 | 0 | 0 | 0 | 25 | 182 | 40 | 0 | 70 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 285 | 290 | 353 | 33 | 43 | 0 | 0 | 120 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 58 | 9 | 16 | 0 | 0 | 0 | 5147 | 912 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 202 | 0 | 130 | 0 | 0 | 0 | 0 | 2.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 6 | 80 | 220 | 0 | 0 | 890 | 0 | 4078.5 | 9225.5 | 92.44
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 412 | 0 | 0 | 0 | 0 | 0 | 51 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 249 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 576 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 920 | 0 | 43 | 0 | 195 | 0 | 0 | 0 | 25 | 182 | 37 | 0 | 70 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 300 | 236 | 368 | 37 | 43 | 0 | 0 | 120 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 58 | 19 | 16 | 0 | 0 | 0 | 5240 | 912 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 196 | 0 | 142 | 0 | 0 | 0 | 0 | 2.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 0 | 1160 | 0 | 4494.5 | 9734.5 | 92.43
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 400 | 0 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 299 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 577 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 900 | 0 | 43 | 0 | 195 | 0 | 0 | 0 | 25 | 202 | 37 | 0 | 70 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 320 | 220 | 369 | 37 | 43 | 0 | 0 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 58 | 19 | 19 | 0 | 0 | 0 | 5272 | 912 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 193 | 0 | 218 | 0 | 0 | 0 | 0 | 2.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 7 | 140 | 220 | 0 | 0 | 1200 | 0 | 4385.5 | 9657.5
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 402 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 291 | 0 | 0 | 0 | 32 | 335 | 0 | 0 | 0 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 577 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 902 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 25 | 193 | 37 | 0 | 50 | 0 | 0 | 11 | 0 | 54 | 0 | 0 | 0 | 305 | 210 | 380 | 37 | 43 | 0 | 0 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 58 | 19 | 20 | 0 | 0 | 0 | 5230 | 912 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 193 | 0 | 220 | 0 | 0 | 0 | 0 | 2.5 | 210 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 7 | 140 | 220 | 0 | 0 | 1190 | 0 | 4383.5 | 9613.5 | 92.43
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 284 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 577 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 25 | 183 | 40 | 0 | 50 | 0 | 0 | 11 | 0 | 52 | 0 | 0 | 0 | 315 | 200 | 380 | 40 | 43 | 0 | 0 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 59 | 19 | 21 | 0 | 0 | 0 | 5208 | 913 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 190 | 0 | 220 | 0 | 0 | 0 | 0 | 2.5 | 210 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 7 | 140 | 220 | 0 | 0 | 1150 | 0 | 4384.5 | 9592.5 | 92.42
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 400 | 267 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 28 | 578 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 25 | 183 | 40 | 0 | 70 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 285 | 185 | 380 | 43 | 43 | 0 | 0 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 58 | 19 | 20 | 0 | 0 | 0 | 5064 | 913 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 190 | 0 | 220 | 0 | 0 | 0 | 0 | 2.5 | 210 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 7 | 140 | 220 | 0 | 0 | 1060 | 0 | 4289.5 | 9353.5 | 92.42
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 350 | 276 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 12.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29 | 575 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 25 | 182 | 40 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 300 | 175 | 380 | 43 | 43 | 0 | 0 | 163 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 45 | 19 | 19 | 0 | 0 | 0 | 4978.5 | 913 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 171 | 0 | 207 | 0 | 0 | 0 | 0 | 2.5 | 210 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 7 | 140 | 220 | 0 | 0 | 950 | 0 | 4007.5 | 8986 | 92.41
Total KWH | 0 | 55680 | 43200 | 0 | 0 | 0 | 0 | 40772.28 | 8643600 | 0 | 0 | 0 | 15480 | 0 | 209664 | 414720 | 0 | 0 | 0 | 44640 | 318600 | 0 | 7885000 | 6852160 | 0 | 0 | 0 | 480200 | 7307312 | 0 | 0 | 115660 | 30000 | 327600 | 229680 | 0 | 0 | 0 | 0 | 0 | 0 | 695520 | 0 | 0 | 0 | 0 | 0 | 24359 | 903060 | 0 | 699840 | 12618181.82 | 0 | 0 | 0 | 0 | 0 | 3851210 | 0 | 0 | 0 | 19183634 | 129870 | 1157511 | 0 | 4399273 | 0 | 0 | 0 | 631200 | 4512000 | 912024 | 34560 | 1311570 | 0 | 38640 | 251120 | 0 | 1229760 | 0 | 355245 | 0 | 6791070 | 5458000 | 8553000 | 537408 | 823000 | 0 | 864 | 3654491 | 352944 | 0 | 1371840 | 709152 | 0 | 0 | 2130540 | 0 | 967200 | 388800 | 266880 | 4900 | 193060 | 0 | 118155695.1 | 20168727 | 7719552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 434160 | 0 | 0 | 12717577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 449660 | 0 | 244496 | 1141636 | 0 | 3708227 | 0 | 4078182 | 0 | 0 | 0 | 16320 | 51282 | 4943000 | 1726254 | 31759 | 23073 | 0 | 0 | 0 | 6188.04 | 182880 | 0 | 0 | 4843000 | 135226 | 2848000 | 5036570 | 0 | 0 | 21714909.09 | 0 | 92220678.13 | 210376373.23

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-01-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9697.67 | MW | 12:00 Hr. | Energy Generated |  |  | 210.3764 |  | MKWHr.
| Day Peak Demand |  |  | 9697.67 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.203 |  | MKWHr.
| Evening Peak Generation |  |  | 9734.5 | MW | 19:00 Hr. | Energy Demand |  |  | 210.5794 |  | MKWHr.
| Evening Peak Demand |  |  | 9734.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 23.7 |  | °C
| Minimum Generation of the Day |  |  | 7222.17 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 784.12 |  | MMCFD
| Maximum Generation of the Day |  |  | 10395.27 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.2158 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.0849 | 0 | 0.81338 | 0 | 0 | 0.11566 | 0 | 0 | 33.014 | Gas | 105.1785 | Gas | 380085205.698
| Chattogram Zone |  |  | 4.5511 | 31.8018 | 0 | 0 | 0.90306 | 0.15423 | 0 | 0.69552 | 38.1057 | Coal | 65.029 | Coal | 462254838.8533
| Cumilla Zone |  |  | 13.1747 | 0 | 0.0732 | 0 | 0 | 0.35524 | 1.2298 | 0 | 14.8329 | HFO | 2.2743 | HFO | 44438904.5
| Mymensingh Zone |  |  | 0.26688 | 0 | 1.356 | 0 | 0 | 0.19796 | 0 | 0 | 1.8208 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.3823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.3823 | Hydro | 0.90306 | Hydro | 90306
| Khulna Zone |  |  | 7.7196 | 0 | 0 | 0 | 0 | 0.43416 | 20.1687 | 0 | 28.3224 | Solar | 2.1799 | Solar | 32215074.434
| Barishal Zone |  |  | 8.0198 | 26.5579 | 0 | 0 | 0 | 0 | 0 | 0 | 34.5777 | Import | 34.1161 | Import | 167355296.33
| Rajshahi Zone |  |  | 8.9793 | 0 | 0 | 0 | 0 | 0.71048 | 12.7176 | 0 | 22.4074 | Wind | 0.69552 | Wind | 10850112
| Rangpur Zone |  |  | 0 | 6.6693 | 0.031759 | 0 | 0 | 0.21214 | 0 | 0 | 6.9132
| Total |  |  | 105.1785 | 65.029 | 2.2743 | 0 | 0.90306 | 2.1799 | 34.1161 | 0.69552 | 210.3764
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 380085205.698 |  | Hydro | 90306
|  |  |  | Coal | 462254838.8533 |  | Solar | 32215074.434
|  |  |  | HFO | 44438904.5 |  | Import | 167355296.33
|  |  |  | HSD | 0 |  | Wind | 10850112
[5 empty] | Total: | 109,72,89,737 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West |  |  |  | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.1687 | Peak Hr Flow | 912.00 MW at 19:00 hrs.
Energy Flow from West to East |  |  |  | 7172818.247 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 12.7176 | Peak Hr Flow | 717.00 MW at 19:00 hrs.
Power Flow during Peak Demand |  |  |  | 434 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.2298 | Peak Hr Flow | 58.00 MW at 19:00 hrs.
Maximum Power Flow |  |  |  | 598 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 34.1161 | Peak Hr Flow | 1687.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3104
|  |  |  | Chattogram |  | 0 |  | 1030
|  |  |  | Cumilla |  | 0 |  | 831
|  |  |  | Mymensingh |  | 0 |  | 921
|  |  |  | Sylhet |  | 0 |  | 353
|  |  |  | Khulna |  | 0 |  | 1104
|  |  |  | Barishal |  | 0 |  | 271
|  |  |  | Rajshahi |  | 0 |  | 963
|  |  |  | Rangpur |  | 0 |  | 670
|  |  |  | Total |  | 0 |  | 9247
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
|  | 9 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1404 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1839.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:17 |  | KSRM 132/33kV S/S Transformer-02 HT Scheduled S/D Due to Transformer 02(Two) OLTC
Maintenance.
| 08:18 | 11:48 | Rampura 230/132kV S/S 230kV Busbar-1 Project Work S/D Due to 230kV Bhulta ckt-1 Jackbus
replace
| 08:20 | 17:13 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT Scheduled S/D Due to Changing the
flexible conduit of the Transformer's mechanical protective devices.
| 08:20 | 17:12 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT Scheduled S/D Due to Changing the
flexible conduit of the Transformer's mechanical protective devices.
| 08:21 |  | Kamrangirchar-Keraniganj 132kV Ckt Scheduled S/D from Keranigonj 230/132/33kV end Due to
Annual maientenance and dead line check.
| 08:29 | 12:08 | Kodda 132/33kV S/S Summit 149 MW PS Scheduled S/D
| 08:34 |  | Baghabari-Ruppur 230 KV CKT-2 S/D [Annual Maintenance]
| 08:38 | 16:30 | Bhulta-Haripur 230 kV Ckt-2 Project Work S/D from Haripur 230/132kV end. and from Bhulta
400/230kVend.
| 08:45 | 14:59 | BSRM-GPH 230 kV Ckt-2 Scheduled S/D from GPH 230/33kV end Due to Annual Maintenance
| 08:45 | 15:00 | BSRM-GPH 230 kV Ckt-1 Scheduled S/D from BSRM 230/33kV end Due to GpH S/S Maintenance
|  | 09:10 | Jamalpur 132/33kV S/S Bus-A is restored.
| 09:20 |  | Jamalpur 132/33kV S/S Bus-B Project Work S/D Due to T-2 B-Bus D/s Change Work
| 09:46 |  | Kabirpur -Kodda 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Kabirpur 230
kv GIS S/S work.
| 10:00 |  | Summit Bibiyana-2 ST tripped at 10:00 hours.
| 10:16 | 17:24 | Siddhirganj 132/33kV S/S T-2 LT Scheduled S/D Due to Maintenance work by DPDC
| 10:17 | 17:21 | Siddhirganj 132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenance by DPDC
| 10:27 |  | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Kabirpur
230 KV GIS S/ S work. and from Tongi 230/132/33kV end Due to Kabirpur side work.
|  | 11:18 | Jamalpur 132/33kV S/S T-2 HT is restored.
|  | 11:18 | Jamalpur 132/33kV S/S T-2 LT is restored.
| 11:53 |  | Summit Bibiyana-2 ST was sync. at 11:53 hours.
| 12:00 |  | Day Peak Gen. 9697 MW
|  | 12:20 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-1 is restored.
| 15:48 |  | Sylhet CCPP 225 MW tripped at 15:48 hours due to tripping of Governing Valve.
| 16:04 |  | Sirajganj Unit-1 GT was sync. at 16:04 hours.
| 16:04 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
|  | 17:03 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT is restored.
|  | 17:03 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT is restored.
| 17:19 |  | Baghabari-Ruppur 230 KV CKT-2 syn.
|  | 18:04 | Aminbazar 400/230/132kV S/S ATR-01 HT is restored.
|  | 18:30 | Aminbazar 400/230/132kV S/S ATR-01 LT is restored.
|  | 18:58 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt is restored.
| 19:00 |  | Evening Peak Generation = 9,734MW
| 19:28 |  | Sirajganj Unit-1 ST as sync. at 19:28.
| 19:28 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
|  | 21:09 | Rangpur 132/33kV S/S Rangpur-GTPS is restored.
| 21:21 | 21:54 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to pbs 33kv pran feeder maintenance | [7 empty] | 40.0MW load
|  |  | work | [7 empty] | interrup.
| 21:22 | 21:53 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to pbs 33kv pran feeder maintenance | [7 empty] | 40.0MW load
|  |  | work | [7 empty] | interrup.
| 06:15 |  | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D
| 06:15 |  | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D
| 06:35 |  | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to
Annual maintenance ( Insulator Disc Replacement)
| 06:46 |  | Mongla 132/33kV S/S 100MW ERBL Solar PS Project Work S/D Due to G2G Proect work | [7 empty] | 21.0MW load
interrup.
| 06:52 |  | Mongla 132/33kV S/S 33 KV Bus Project Work S/D Due to G2G Proect work | [7 empty] | 21.0MW load
interrup.
| 06:52 |  | Mongla 132/33kV S/S T-2 LT Project Work S/D Due to G2G Proect work | [7 empty] | 21.0MW load
interrup.
| 06:54 |  | Bagerhat-Mongla 132 kV Ckt-2 Project Work S/D from Mongla 132/33kV end Due to G2G Proect | [7 empty] | 21.0MW load
|  |  | work and from Bagerhat 132/33kV end Due to Same as ckt-1 | [7 empty] | interrup. Mongla
132/33kV end
| 06:54 |  | Mongla 132/33kV S/S T-2 HT Project Work S/D Due to G2G Proect work | [7 empty] | 21.0MW load
interrup.
| 06:54 |  | Mongla 132/33kV S/S Main Bus Project Work S/D Due to G2G Proect work | [7 empty] | 21.0MW load
interrup.
| 06:55 |  | Bagerhat-Mongla 132 kV Ckt-1 Project Work S/D from Mongla 132/33kV end Due to G2G Proect | [7 empty] | 21.0MW load
|  |  | work and from Bagerhat 132/33kV end Due to Mongla Will change Tr HT Loop conductor | [7 empty] | interrup. Mongla
132/33kV end
| 07:19 |  | Khulshi 132/33kV S/S 415T (T2) HT Scheduled S/D Due to Annual maintenance
| 07:28 |  | Meghnaghat-Shyampur 230kV Ckt-1 Scheduled S/D from Shyampur 230/132kV end Due to Disk
cleaning
| 07:37 |  | Chowmuhani-Ramganj 132 kV Ckt-2 Scheduled S/D from Chowmuhani 132/33kV end Due to Yearly
Maintenance of GCB-852B and Associated Equipment's and from Ramganj 132/33kV end Due to
Annual Maintenance
| 07:47 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D Due to NPBS Bus maintenance | [7 empty] | 10.0MW load
|  |  | work | [7 empty] | interrup.
| 07:48 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to NPBS Bus maintenance | [7 empty] | 10.0MW load
|  |  | work. | [7 empty] | interrup.
| 07:53 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
| 07:53 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to 33kV Bus Section-1 & 2 | [7 empty] | 30.0MW load
|  |  | maintenance by wzpdcl, faridpur. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 3 | 40772.28 | Demand "0" due to gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 412 | 8643600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 7885000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 249 | 6852160 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7307312 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 414720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 327600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 229680 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 318600 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32 | 480200 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 0 | 43200 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 51 | 209664 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 55680 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 44640 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 115660 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 0 | 15480 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 15 | 30000 | -
Dhaka Area Total |  |  |  |  | 5841.27 | 1518 | 33013968.28
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 129870 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 903060 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3851210 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 29 | 699840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 24359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 920 | 19183634 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 44 | 695520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 576 | 12618181.82 | -
Chattogram Area Total |  |  |  |  | 4915.22 | 1770 | 38105674.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4512000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 37 | 912024 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 25 | 631200 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4399273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 1157511 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1311570 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 58 | 1229760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 251120 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 0 | 38640 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 34560 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 355245 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 627 | 14832903
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 16 | 266880 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 4900 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 19 | 388800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 58 | 967200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 193060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Unable to dispatch due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 93 | 1820840
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 43 | 823000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3654491 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 37 | 537408 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 864 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 709152 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1371840 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 2130540 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 13 | 352944 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 6791070 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 8553000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 236 | 5458000 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1232 | 30382309
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 912 | 20168727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 350 | 7719552 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 434160 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to changing of ST Power Tx Radiators
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1262 | 28322439
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 135226 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2848000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1160 | 21714909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5036570 | -
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 4843000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2265.1 | 1834 | 34577705.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 58 | 1141636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 196 | 3708227 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 142 | 4078182 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 0 | 0 | Scheduled Outage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 51282 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 16320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 717 | 12717577 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 244496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 449660 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1115.5 | 22407380
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 73 | 1726254 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 4943000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 6188.04 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 31759 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 23073 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 182880 | -
Rangpur Area Total |  |  |  |  | 950 | 283 | 6913154.04
Eastern Grid Total |  |  |  |  | 16771.748 | 5240 | 118155695.1
Western Grid Total |  |  |  |  | 10294.5 | 4494.5 | 92220678.13
National Grid Total |  |  |  |  | 27066.248 | 9734.5 | 210376373.23
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6239.05 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3007.5 | MW
i) Dhaka area |  |  | 3104.05 |  | MW | i) Khulna area |  |  |  | 1103.9 | MW
ii) Chattogram area |  |  | 1030 |  | MW | ii) Barishal area |  |  |  | 271 | MW
iii) Cumilla area |  |  | 831 |  | MW | iii) Rajshahi area |  |  |  | 962.6 | MW
iv) Mymensingh area |  |  | 921 |  | MW | iv) Rangpur area |  |  |  | 670 | MW
v) Sylhet area |  |  | 353 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9246.55 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 56 | 18:30 | 133 | Purbachal | 15 | 13:00
2 | AKSML | 117 | 06:00 | 68 | Jamalpur | 100 | 18:30 | 134 | Purbasadipur | 110 | 12:00
3 | Aftabnagar | 26 | 12:00 | 69 | Jashore | 104 | 12:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 74 | 13:00 | 70 | Jhenaidah | 93 | 13:00 | 136 | Rahim | 35 | 02:00
5 | Agrabad | 42 | 19:00 | 71 | Joydebpur | 119 | 12:00 | 137 | Rajbari | 50 | 18:30
6 | Amnura | 44 | 18:30 | 72 | Joypurhat | 42 | 20:00 | 138 | Rajendrapur | 84 | 13:00
7 | Ashuganj | 56 | 00:00 | 73 | Juldah | 10 | 00:00 | 139 | Rajshahi | 87 | 13:00
8 | BSRM | 199 | 18:30 | 74 | KSRM | 29 | 06:00 | 140 | Rajshahi-230 | 51 | 13:00
9 | Bagerhat | 62 | 18:30 | 75 | Kabirpur | 143 | 00:00 | 141 | Ramganj | 108 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 53 | 13:00 | 142 | Rampur | 24 | 12:00
11 | Bakulia | 58 | 13:00 | 77 | Kallyanpur | 66 | 12:00 | 143 | Rangamati | 12 | 18:00
12 | Banani | 23.6 | 13:00 | 78 | Kalurghat | 18 | 12:00 | 144 | Rangpur | 111 | 13:00
13 | Bangabhaban | 3 | 11:00 | 79 | Kamrangirchar | 45.2 | 13:00 | 145 | Ruppur | 3.6 | 10:00
14 | Barapukuria | 53 | 12:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 11 | 03:00
15 | Barguna | 14 | 21:00 | 81 | Kazla | 73 | 13:00 | 147 | Saidpur | 87 | 11:00
16 | Barishal | 80 | 13:00 | 82 | Keranigonj | 42 | 00:00 | 148 | Satkhira | 91 | 08:00
17 | Barishal-230 | 64 | 13:00 | 83 | Khagrachori | 24 | 13:00 | 149 | Satmasjid | 84 | 13:00
18 | Baroaulia | 54 | 11:00 | 84 | Khulna | 60 | 13:00 | 150 | Savar | 116 | 10:00
19 | Baroirhat | 57 | 13:00 | 85 | Khulshi | 143 | 18:00 | 151 | SevenRings | 14.99 | 00:00
20 | Bashundhara | 124 | 12:00 | 86 | Kishoreganj | 124 | 13:00 | 152 | ShahCement | 29 | 00:00
21 | BashundharaCement | 12 | 00:00 | 87 | Kodda | 200 | 00:00 | 153 | Shahjadpur | 47 | 18:30
22 | Beanibazar | 42 | 13:00 | 88 | Kulaura | 28 | 13:00 | 154 | Shahjibazar | 85 | 18:30
23 | Benapole | 46 | 08:00 | 89 | Kurigram | 50 | 08:00 | 155 | Shahmirpur | 31 | 17:00
24 | Bhaluka | 96 | 09:00 | 90 | Kushtia | 104 | 13:00 | 156 | Shariatpur | 57 | 13:00
25 | Bhandaria | 34 | 21:00 | 91 | Lalbag | 51 | 00:00 | 157 | Sherpur | 122 | 18:30
26 | Bhangura | 28 | 13:00 | 92 | Lalmonirhat | 44 | 18:00 | 158 | Shikalbaha | 20 | 23:00
27 | Bheramara(GK) | 36 | 19:30 | 93 | MI_Cement | 12 | 04:00 | 159 | Shitalakhya | 42.7 | 13:00
28 | Bhulta | 218 | 00:00 | 94 | Madanganj | 16 | 13:00 | 160 | Sholosohor | 22 | 00:00
29 | Bog-Sherpur | 58 | 18:30 | 95 | Madaripur | 64 | 21:00 | 161 | Shyampur | 140 | 11:00
30 | Bogura | 87 | 18:30 | 96 | Madartek | 66.66 | 13:00 | 162 | Siddhirganj | 66 | 00:00
31 | Borhanuddin | 52 | 13:00 | 97 | Madunaghat | 32 | 12:00 | 163 | Sirajganj | 62 | 19:00
32 | Brahmanbaria | 115 | 13:00 | 98 | Magura | 41 | 13:00 | 164 | Sonargaon | 74 | 00:00
33 | Cantonment | 80 | 13:00 | 99 | Mahasthangarh | 52 | 18:30 | 165 | Sreemongol | 43 | 18:00
34 | Chandpur | 44 | 13:00 | 100 | Manikganj | 99 | 21:00 | 166 | Sreepur | 62 | 00:00
35 | Chandraghona | 24 | 18:30 | 101 | Maniknagar | 46 | 13:00 | 167 | Srinagar | 32.2 | 13:00
36 | Chapai | 76 | 12:00 | 102 | Matarbari | 34 | 18:00 | 168 | Sunamganj | 38 | 19:00
37 | Charsaidpur | 42 | 01:00 | 103 | Matuail | 46 | 00:00 | 169 | Sylhet | 28 | 13:00
38 | Chauddagram | 56 | 13:00 | 104 | Millgate | 93 | 13:00 | 170 | Sylhet-132 | 72 | 13:00
39 | Chhatak | 22 | 11:00 | 105 | Mirpur | 92 | 13:00 | 171 | TK | 20 | 18:00
40 | Chowmuhani | 132 | 13:00 | 106 | Mirsorai | 7 | 00:00 | 172 | Tangail | 144 | 18:30
41 | Chuadanga | 75 | 13:00 | 107 | Mirzapur | 44 | 07:00 | 173 | Thakurgaon | 73 | 18:30
42 | Coxsbazar | 104 | 13:00 | 108 | Mithapukur | 60 | 18:00 | 174 | Tongi | 81 | 12:00
43 | Cumilla(N) | 117 | 17:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 22 | 18:30
44 | Cumilla(S) | 133 | 13:00 | 110 | Mogbazar | 84.5 | 14:00 | 176 | Ullon | 41 | 13:00
45 | Daudkandi | 78 | 19:30 | 111 | Mongla | 31 | 00:00 | 177 | Uttara | 57 | 12:00
46 | Dhaka | 14 | 11:00 | 112 | Motijheel | 24 | 13:00 | 178 | UttaraNew | 37 | 12:00
47 | Dhamrai | 86 | 10:00 | 113 | Muktagacha | 30 | 13:00 | 179 | Zigatola | 58 | 13:00
48 | Dhanmondi | 80 | 13:00 | 114 | Munshiganj | 70 | 13:00
49 | Dohazari | 69 | 18:30 | 115 | Mymensingh | 191 | 13:00
50 | Faridpur | 93 | 18:30 | 116 | Naogaon | 100 | 09:00
51 | Fatullah | 52 | 00:00 | 117 | Narail | 38 | 13:00
52 | Fenchuganj | 24 | 13:00 | 118 | Narinda | 44 | 13:00
53 | Feni | 63 | 13:00 | 119 | Narshingdi | 142 | 20:00
54 | GPH | 104 | 12:00 | 120 | Natore | 97 | 10:00
55 | Ghatail | 32 | 08:00 | 121 | Nawabganj | 43 | 13:00
56 | Ghorashal | 7 | 00:00 | 122 | Netrakona | 132 | 18:00
57 | Ghorashal-230 | 57 | 13:00 | 123 | New | 49 | 00:00
58 | Goalpara | 28 | 13:00 | 124 | Niamatpur | 75 | 13:00
59 | Gollamari | 60 | 13:00 | 125 | Noapara | 27 | 20:00
60 | Gopalganj | 76 | 18:30 | 126 | PHP | 8 | 01:00
61 | Gulshan | 56 | 12:00 | 127 | Pabna | 55 | 18:30
62 | Halishahar | 32 | 15:00 | 128 | Palashbari | 71 | 18:00
63 | HaripurSBU | 167 | 00:00 | 129 | Panchagarh | 40 | 18:00
64 | Hasnabad | 67 | 12:00 | 130 | Patuakhali | 53.5 | 20:00
65 | Hathazari | 50 | 12:00 | 131 | Payra | 14 | 00:00
66 | Ishurdi | 54 | 19:00 | 132 | Postogola | 34 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9219.93 | 0 |  | 9219.93
1:00 | 8464.45 | 0 |  | 8464.45
2:00 | 8029.32 | 0 |  | 8029.32
3:00 | 7691 | 0 |  | 7691
4:00 | 7457.35 | 0 |  | 7457.35
5:00 | 7222.17 | 0 |  | 7222.17
6:00 | 7296.41 | 0 |  | 7296.41
7:00 | 7395.38 | 0 |  | 7395.38
8:00 | 8088.41 | 60 |  | 8151.41
9:00 | 8651.21 | 60 |  | 8714.21
10:00 | 8978.99 | 53 |  | 9034.38
11:00 | 9159.51 | 30 |  | 9190.51
12:00 | 9697.67 | 0 |  | 9697.67
13:00 | 10395.27 | 0 |  | 10395.27
14:00 | 8829.79 | 0 |  | 8829.79
15:00 | 8220.54 | 0 |  | 8220.54
16:00 | 7789.99 | 0 |  | 7789.99
17:00 | 8127.78 | 0 |  | 8127.78
18:00 | 9225.5 | 0 |  | 9225.5
19:00 | 9734.5 | 0 |  | 9734.5
19:30 | 9657.5 | 0 |  | 9657.5
20:00 | 9613.5 | 0 |  | 9613.5
21:00 | 9592.5 | 0 |  | 9592.5
22:00 | 9353.5 | 0 |  | 9353.5
23:00 | 8986 | 0 |  | 8986
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5303 | 3916.93 | 9219.93 | DAILY GENERATION CURVE
00:30 | 5162 | 3680.19 | 8842.19
01:00 | 5021 | 3443.45 | 8464.45 | 24-01-2025
01:30 | 4879.5 | 3367.385 | 8246.885
02:00 | 4738 | 3291.32 | 8029.32
02:30 | 4632.5 | 3227.66 | 7860.16
03:00 | 4527 | 3164 | 7691
03:30 | 4466 | 3108.175 | 7574.175
04:00 | 4405 | 3052.35 | 7457.35
04:30 | 4333 | 3006.76 | 7339.76
05:00 | 4261 | 2961.17 | 7222.17
05:30 | 4301 | 2958.29 | 7259.29
06:00 | 4341 | 2955.41 | 7296.41
06:30 | 4372.5 | 2973.395 | 7345.895
07:00 | 4404 | 2991.38 | 7395.38
07:30 | 4566.845 | 3175.05 | 7741.895
08:00 | 4729.69 | 3358.72 | 8088.41
08:30 | 4810.04 | 3559.77 | 8369.81
09:00 | 4890.39 | 3760.82 | 8651.21
09:30 | 4962.385 | 3852.715 | 8815.1
10:00 | 5034.38 | 3944.61 | 8978.99
10:30 | 5035.365 | 4033.885 | 9069.25
11:00 | 5036.35 | 4123.16 | 9159.51
11:30 | 5116.275 | 4312.315 | 9428.59
12:00 | 5196.2 | 4501.47 | 9697.67
12:30 | 5449.845 | 4596.625 | 10046.47
13:00 | 5703.49 | 4691.78 | 10395.27
13:30 | 5378.575 | 4233.955 | 9612.53
14:00 | 5053.66 | 3776.13 | 8829.79
14:30 | 4883.075 | 3642.09 | 8525.165
15:00 | 4712.49 | 3508.05 | 8220.54
15:30 | 4593.44 | 3411.825 | 8005.265
16:00 | 4474.39 | 3315.6 | 7789.99
16:30 | 4517.525 | 3441.36 | 7958.885
17:00 | 4560.66 | 3567.12 | 8127.78
17:30 | 4853.83 | 3822.81 | 8676.64
18:00 | 5147 | 4078.5 | 9225.5
18:30 | 5193.5 | 4286.5 | 9480
19:00 | 5240 | 4494.5 | 9734.5
19:30 | 5272 | 4385.5 | 9657.5
20:00 | 5230 | 4383.5 | 9613.5
20:30 | 5219 | 4384 | 9603 |  | Executive Engineer
21:00 | 5208 | 4384.5 | 9592.5 |  | Network Operation Division
21:30 | 5136 | 4337 | 9473
22:00 | 5064 | 4289.5 | 9353.5
22:30 | 5021.25 | 4148.5 | 9169.75
23:00 | 4978.5 | 4007.5 | 8986

## En-Curve
QF-LDC-12
Date | 24-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2608 | 1737.5 | 898 | 0 | 50 | 573.43 | 35 | 3099 | 0 | 33 | 161 | 0 | 0 | 25 | 0 | DAILY ENERGY CURVE
00:30 | 2608.5 | 1704 | 898 | 0 | 51 | 493.19 | 35 | 2872.5 | 0 | 16.5 | 126.5 | 0 | 0 | 37 | 0 | 24-01-2025
01:00 | 2609 | 1670.5 | 898 | 0 | 52 | 412.95 | 35 | 2646 | 0 | 0 | 92 | 0 | 0 | 49 | 0
01:30 | 2636 | 1679 | 822.5 | 0 | 48 | 414.885 | 35 | 2497.5 | 0 | 0 | 64.5 | 0 | 0 | 49.5 | 0 | Energy Generated | 210.3764 |  | MKWHr
02:00 | 2663 | 1687.5 | 747 | 0 | 44 | 416.82 | 35 | 2349 | 0 | 0 | 37 | 0 | 0 | 50 | 0 | Energy not Served | 0.203 |  | MKWHr
02:30 | 2676.5 | 1661.75 | 735.5 | 0 | 43 | 417.41 | 35 | 2211 | 0 | 0 | 32.5 | 0 | 0 | 47.5 | 0 | Total Energy Requirement | 210.5794 |  | MKWHr
03:00 | 2690 | 1636 | 724 | 0 | 42 | 418 | 35 | 2073 | 0 | 0 | 28 | 0 | 0 | 45 | 0
03:30 | 2615 | 1660 | 724.5 | 0 | 45 | 418.675 | 35 | 2020.5 | 0 | 0 | 14 | 0 | 0 | 41.5 | 0
04:00 | 2540 | 1684 | 725 | 0 | 48 | 419.35 | 35 | 1968 | 0 | 0 | 0 | 0 | 0 | 38 | 0
04:30 | 2474.5 | 1621.5 | 724.5 | 0 | 49 | 418.76 | 35 | 1971.5 | 0 | 0 | 0 | 0 | 0 | 45 | 0
05:00 | 2409 | 1559 | 724 | 0 | 50 | 418.17 | 35 | 1975 | 0 | 0 | 0 | 0 | 0 | 52 | 0
05:30 | 2431.5 | 1566 | 724.5 | 0 | 50 | 417.79 | 35 | 1973.5 | 0 | 0 | 15.5 | 0 | 0 | 45.5 | 0
06:00 | 2454 | 1573 | 725 | 0 | 50 | 417.41 | 35 | 1972 | 0 | 0 | 31 | 0 | 0 | 39 | 0
06:30 | 2484 | 1591.5 | 724.5 | 0 | 45 | 415.89 | 35 | 1968.5 | 1.505 | 0 | 39 | 0 | 0 | 41 | 0
07:00 | 2514 | 1610 | 724 | 0 | 40 | 414.37 | 35 | 1965 | 3.01 | 0 | 47 | 0 | 0 | 43 | 0
07:30 | 2528 | 1664 | 771 | 0 | 41 | 413.125 | 35 | 2146 | 27.27 | 24 | 56 | 0 | 0 | 36.5 | 30
08:00 | 2542 | 1718 | 818 | 0 | 42 | 411.88 | 35 | 2327 | 51.53 | 48 | 65 | 0 | 0 | 30 | 60
08:30 | 2546 | 1738.5 | 818.5 | 0 | 43 | 462.89 | 37.5 | 2502 | 88.42 | 48 | 65.5 | 0 | 0 | 19.5 | 60
09:00 | 2550 | 1759 | 819 | 0 | 44 | 513.9 | 40 | 2677 | 125.31 | 48 | 66 | 0 | 0 | 9 | 60
09:30 | 2567.5 | 1742.5 | 819 | 0 | 46 | 513.515 | 40 | 2792 | 173.585 | 48 | 66 | 0 | 0 | 7 | 56.5
10:00 | 2585 | 1726 | 819 | 0 | 48 | 513.13 | 40 | 2907 | 221.86 | 48 | 66 | 0 | 0 | 5 | 53
10:30 | 2585 | 1623.75 | 818.5 | 0 | 56 | 561.945 | 40 | 2987 | 268.555 | 56 | 66.5 | 0 | 0 | 6 | 41.5
11:00 | 2585 | 1521.5 | 818 | 0 | 64 | 610.76 | 40 | 3067 | 315.25 | 64 | 67 | 0 | 0 | 7 | 30
11:30 | 2566.5 | 1515.5 | 865.5 | 0 | 64 | 662.715 | 40 | 3212.5 | 339.875 | 78.5 | 75.5 | 0 | 0 | 8 | 15
12:00 | 2548 | 1509.5 | 913 | 0 | 64 | 714.67 | 40 | 3358 | 364.5 | 93 | 84 | 0 | 0 | 9 | 0
12:30 | 2636.5 | 1604.5 | 913 | 0 | 70 | 734.04 | 40 | 3442.5 | 360.43 | 99.5 | 134.5 | 0 | 0 | 11.5 | 0
13:00 | 2725 | 1699.5 | 913 | 0 | 76 | 753.41 | 40 | 3527 | 356.36 | 106 | 185 | 0 | 0 | 14 | 0
13:30 | 2588 | 1658.5 | 912.5 | 0 | 73 | 652.705 | 40 | 3136.5 | 337.325 | 61.5 | 128.5 | 0 | 0 | 24 | 0
14:00 | 2451 | 1617.5 | 912 | 0 | 70 | 552 | 40 | 2746 | 318.29 | 17 | 72 | 0 | 0 | 34 | 0
14:30 | 2484 | 1594.75 | 857.5 | 0 | 58 | 508 | 40 | 2595.5 | 280.415 | 8.5 | 69.5 | 0 | 0 | 29 | 0
15:00 | 2517 | 1572 | 803 | 0 | 46 | 464 | 40 | 2445 | 242.54 | 0 | 67 | 0 | 0 | 24 | 0
15:30 | 2460 | 1558 | 763.5 | 0 | 48 | 465 | 40 | 2403 | 182.265 | 0 | 67 | 0 | 0 | 18.5 | 0
16:00 | 2403 | 1544 | 724 | 0 | 50 | 466 | 40 | 2361 | 121.99 | 0 | 67 | 0 | 0 | 13 | 0
16:30 | 2420 | 1529 | 818 | 0 | 52 | 458 | 40 | 2486 | 75.885 | 0 | 67 | 0 | 0 | 13 | 0
17:00 | 2437 | 1514 | 912 | 0 | 54 | 450 | 40 | 2611 | 29.78 | 0 | 67 | 0 | 0 | 13 | 0
17:30 | 2520 | 1625.75 | 912 | 0 | 56 | 553 | 40 | 2830.5 | 14.89 | 28.5 | 77 | 0 | 0 | 19 | 0
18:00 | 2603 | 1737.5 | 912 | 0 | 58 | 656 | 40 | 3050 | 0 | 57 | 87 | 0 | 0 | 25 | 0
18:30 | 2689.5 | 1760 | 912 | 0 | 58 | 686.5 | 40 | 3148 | 0 | 44 | 107.5 | 0 | 0 | 34.5 | 0
19:00 | 2776 | 1782.5 | 912 | 0 | 58 | 717 | 40 | 3246 | 0 | 31 | 128 | 0 | 0 | 44 | 0
19:30 | 2846 | 1896.5 | 912 | 0 | 52 | 561 | 40 | 3200 | 0 | 16 | 95 | 0 | 0 | 39 | 0
20:00 | 2829 | 1876.5 | 912 | 0 | 54 | 561 | 40 | 3192 | 0 | 16 | 100 | 0 | 0 | 33 | 0
20:30 | 2841.5 | 1893 | 912.5 | 0 | 53 | 560.5 | 37.5 | 3170.5 | 0 | 8 | 97.5 | 0 | 0 | 29 | 0
21:00 | 2854 | 1909.5 | 913 | 0 | 52 | 560 | 35 | 3149 | 0 | 0 | 95 | 0 | 0 | 25 | 0
21:30 | 2854 | 1889.5 | 913 | 0 | 52 | 560.5 | 35 | 3053.5 | 0 | 0 | 86 | 0 | 0 | 29.5 | 0
22:00 | 2854 | 1869.5 | 913 | 0 | 52 | 561 | 35 | 2958 | 0 | 0 | 77 | 0 | 0 | 34 | 0
22:30 | 2823.5 | 1857.25 | 913 | 0 | 50 | 518.5 | 35 | 2872 | 0 | 0 | 70.5 | 0 | 0 | 30 | 0
23:00 | 2793 | 1845 | 913 | 0 | 48 | 476 | 35 | 2786 | 0 | 0 | 64 | 0 | 0 | 26 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 24-01-2025 | 0 | [6 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 415 | 05:00 | 396 | 12:00 | Kaliakoir | 380 | 06:00 | 370 | 13:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 415 | 5:00 | 339 | 6:00 | Madunaghat | 411 | 04:00 | 397 | 13:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 413 | 05:00 | 394 | 09:00 | Meghnaghat | 413 | 05:00 | 393 | 13:00
| Bibiana | 396 | 00:00 | 390 | 13:00 | Payra | 418 | 03:00 | 407 | 13:00
| BIPTC | 408 | 03:00 | 391 | 12:00 | Rahanpur | 415 | 03:00 | 399 | 12:00
| Bogura | 415 | 03:00 | 396 | 12:00 | Rampal | 417 | 05:00 | 392 | 13:00
| Gopalganj | 417 | 05:00 | 399 | 12:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 238 | 05:00 | 225 | 13:00 | Haripur | 240 | 05:00 | 229 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 234 | 04:00 | 224 | 13:00 | Hasnabad | 239 | 17:00 | 227 | 13:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 239 | 05:00 | 228 | 12:00 | Hathazari | 233 | 06:00 | 226 | 12:00
| Ashuganj | 240 | 04:00 | 229 | 13:00 | Ishurdi | 245 | 05:00 | 232 | 13:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 240 | 04:00 | 229 | 13:00 | Jhenaidah | 242 | 04:00 | 226 | 13:00
| Baghabari | 242 | 05:00 | 232 | 12:00 | Kaliakoir | 238 | 06:00 | 228 | 12:00 | 230 kV MAX | 249 |  | 249 | 218
| Barapukuria | 226 | 01:00 | 218 | 12:00 | Keranigonj | 237 | 05:00 | 224 | 13:00 | 230 kV MIN | 218 |  | 245 | 223 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 226 | 01:00 | 218 | 12:00 | Khulna(S) | 243 | 03:00 | 227 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 246 | 02:00 | 236 | 13:00 | Madunaghat | 237 | 04:00 | 227 | 12:00 | 132 kV MAX | 159 |  | 143 | 115 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 243 | 05:00 | 229 | 13:00 | Madunaghat-400 | 235 | 04:00 | 225 | 13:00 | 132 kV MIN | 112 |  | 159 | 112 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 240 | 05:00 | 229 | 13:00 | Maniknagar | 239 | 06:00 | 229 | 12:00 | [35 empty] | 6:00
| Bibiana | 230 | 00:00 | 226 | 12:00 | Meghnaghat | 243 | 04:00 | 234 | 11:00 |  | 400 | [33 empty] | 392
| BIPTC | 244 | 03:00 | 230 | 13:00 | Meghnaghat-400 | 240 | 05:00 | 230 | 13:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 242 | 05:00 | 230 | 12:00 | Mirsorai | 234 | 03:00 | 223 | 13:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 240 | 03:00 | 229 | 12:00 | Rajshahi | 242 | 03:00 | 229 | 13:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 249 | 04:00 | 243 | 12:00 | Rampal | 241 | 04:00 | 224 | 13:00 |  | 132 |  |  | Ash 400-299274
| BSRM | 235 | 08:00 | 223 | 12:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 237 | 05:00 | 226 | 13:00 | Rampura | 240 | 05:00 | 227 | 13:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 248 | 04:00 | 234 | 13:00 | Shikalbaha | 234 | 05:00 | 225 | 13:00 |  | kaptai by call 399528
| Fenchuganj | 234 | 06:00 | 222 | 13:00 | Shyampur | 238 | 05:00 | 228 | 13:00
| Ghorashal | 245 | 02:00 | 238 | 00:00 | Siddhirganj | 239 | 06:00 | 236 | 00:00
| Ghorashal-230 | 237 | 03:00 | 226 | 13:00 | Sirajgonj | 248 | 05:00 | 238 | 13:00
| Gopalganj | 248 | 05:00 | 236 | 12:00 | Sreepur | 240 | 03:00 | 234 | 09:00
| GPH | 234 | 05:00 | 223 | 13:00 | Tongi | 236 | 23:00 | 228 | 12:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 139 | 05:00 | 130 | 11:00 | Kurigram | 134 | 03:00 | 122 | 09:00 |  | Gopalganj-230 | 599470
| Agargaon | 138 | 04:00 | 130 | 13:00 | Kushtia | 141 | 02:00 | 134 | 13:00
| Agrabad | 134 | 01:00 | 127 | 13:00 | Lalbag | 139 | 03:00 | 132 | 12:00
| AKS | 132 | 02:00 | 127 | 12:00 | Lalmonirhat | 159 | 07:00 | 123 | 09:00
| Aminbazar | 137 | 05:00 | 131 | 10:00 | Madanganj | 137 | 03:00 | 132 | 11:00
| Amnura | 140 | 04:00 | 129 | 12:00 | Madaripur | 136 | 04:00 | 132 | 14:00
| Ashuganj | 142 | 07:00 | 137 | 13:00 | Madartek | 137 | 03:00 | 130 | 13:00
| Bagerhat | 140 | 05:00 | 131 | 12:00 | Madunaghat | 136 | 05:00 | 131 | 11:00
| Bajitpur | 137 | 05:00 | 130 | 12:00 | Magura | 142 | 04:00 | 131 | 13:00
| Bakulia | 134 | 04:00 | 128 | 13:00 | Mahasthangarh | 138 | 05:00 | 129 | 09:00
| Banani | 138 | 02:00 | 131 | 12:00 | Manikganj | 133 | 19:00 | 129 | 17:00
| Bangabhaban | 137 | 01:00 | 127 | 12:00 | Maniknagar | 138 | 06:00 | 126 | 13:00
| Barapukuria | 136 | 01:00 | 129 | 08:00 | Matarbari | 126 | 06:00 | 118 | 13:00
| Barguna | 137 | 05:00 | 133 | 12:00 | Matuail | 137.4 | 06:00 | 132 | 12:00
| Barishal | 137 | 06:00 | 130 | 13:00 | Millgate | 140 | 05:00 | 133 | 11:00
| Barishal-230 | 137 | 02:00 | 130 | 13:00 | Mirpur | 137 | 05:00 | 128 | 13:00
| Baroaulia | 134 | 07:00 | 131 | 09:00 | Mirzapur | 131 | 06:00 | 127 | 07:00
| Baroirhat | 133 | 07:00 | 124 | 13:00 | Mithapukur | 136 | 03:00 | 134 | 01:00
| Bashundhara | 140 | 06:00 | 130 | 12:00 | MI_Cement | 139 | 05:00 | 132 | 13:00
| BashundharaCement | 137 | 03:00 | 132 | 11:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 136 | 03:00 | 132 | 13:00 | Mogbazar | 141 | 06:00 | 132 | 12:00
| Benapole | 140 | 04:00 | 125 | 13:00 | Mongla | 138 | 05:00 | 131 | 12:00
| Bhaluka | 130 | 04:00 | 118 | 13:00 | Motijheel | 137 | 05:00 | 127 | 12:00
| Bhandaria | 134 | 02:00 | 128 | 21:00 | Muktagacha | 128 | 06:00 | 118 | 07:00
| Bhangura | 141 | 03:00 | 133 | 12:00 | Munshiganj | 137 | 05:00 | 131 | 13:00
| Bheramara | 141 | 05:00 | 135 | 13:00 | Mymensingh | 128 | 23:00 | 113 | 13:00
| Bheramara(GK) | 141 | 02:00 | 136 | 12:00 | Naogaon | 138 | 05:00 | 128 | 09:00
| Bhulta | 132 | 05:00 | 129 | 00:00 | Narail | 141 | 02:00 | 129 | 13:00
| Bog-Sherpur | 139 | 05:00 | 131 | 09:00 | Narinda | 138 | 06:00 | 126 | 13:00
| Bogura | 138 | 04:00 | 131 | 09:00 | Narshingdi | 136 | 04:00 | 123 | 18:30
| Bogura-230 | 139 | 05:00 | 131 | 12:00 | Natore | 140 | 03:00 | 132 | 13:00
| Brahmanbaria | 134 | 02:00 | 128 | 13:00 | Nawabganj | 140 | 05:00 | 132 | 13:00
| Cantonment | 139 | 05:00 | 130 | 13:00 | Netrakona | 129 | 03:00 | 120 | 09:00
| Chandpur | 129 | 05:00 | 122 | 13:00 | New | 140 | 06:00 | 134 | 11:00
| Chandraghona | 136 | 05:00 | 130 | 12:00 | Niamatpur | 140 | 23:00 | 133 | 12:00
| Chapai | 138 | 01:00 | 131 | 12:00 | Noapara | 140 | 01:00 | 129 | 13:00
| Charsaidpur | 138 | 05:00 | 132 | 12:00 | Pabna | 139 | 05:00 | 130 | 13:00
| Chauddagram | 134 | 04:00 | 125 | 13:00 | Palashbari | 134 | 01:00 | 124 | 12:00
| Chhatak | 135 | 05:00 | 130 | 19:30 | Panchagarh | 138 | 03:00 | 121 | 12:00
| Chowmuhani | 130 | 04:00 | 120 | 13:00 | Patuakhali | 136 | 23:00 | 132 | 12:00
| Chuadanga | 141 | 03:00 | 129 | 13:00 | Payra | 138 | 03:00 | 133 | 13:00
| Coxsbazar | 127 | 05:00 | 118 | 13:00 | PHP | 133 | 05:00 | 123 | 13:00
| Cumilla(N) | 138 | 06:00 | 130 | 13:00 | Postogola | 141 | 05:00 | 135 | 12:00
| Cumilla(S) | 136 | 08:00 | 128 | 11:00 | Purbachal | 139 | 04:00 | 130 | 13:00
| Daudkandi | 135 | 03:00 | 129 | 13:00 | Purbasadipur | 134 | 05:00 | 120 | 09:00
| Dhaka | 138 | 04:00 | 132 | 12:00 | Rahanpur | 141 | 23:00 | 136 | 09:00
| Dhamrai | 136 | 02:00 | 130 | 09:00 | Rahanpur-400 | 141 | 03:00 | 134 | 01:00
| Dhanmondi | 138 | 05:00 | 132 | 13:00 | Rahim | 136 | 05:00 | 131 | 12:00
| Dohazari | 132 | 03:00 | 126 | 12:00 | Rajbari | 137 | 02:00 | 129 | 13:00
| Faridpur | 138 | 05:00 | 130 | 13:00 | Rajendrapur | 140 | 07:00 | 129 | 11:00
| Fatullah | 139 | 05:00 | 133 | 12:00 | Rajshahi | 140 | 02:00 | 134 | 12:00
| Fenchuganj | 140 | 06:00 | 136 | 13:00 | Rajshahi-230 | 139 | 03:00 | 127 | 12:00
| Feni | 132 | 05:00 | 125 | 13:00 | Ramganj | 128 | 04:00 | 121 | 13:00
| Ghatail | 128 | 16:00 | 118 | 07:00 | Rampur | 134 | 04:00 | 128 | 13:00
| Ghorashal | 143 | 02:00 | 136 | 13:00 | Rampura | 138 | 04:00 | 130 | 13:00
| Goalpara | 140 | 01:00 | 131 | 13:00 | Rangamati | 135 | 04:00 | 129 | 13:00
| Gollamari | 141 | 05:00 | 131 | 13:00 | Rangpur | 134 | 02:00 | 122 | 12:00
| Gopalganj | 139 | 03:00 | 130 | 13:00 | Ruppur | 142 | 04:00 | 137 | 09:00
| Gopalganj-400 | 139 | 03:00 | 132 | 12:00 | Saidpur | 136 | 06:00 | 123 | 09:00
| Gulshan | 138 | 05:00 | 129 | 13:00 | Satkhira | 140 | 05:00 | 127 | 13:00
| Halishahar | 134 | 04:00 | 129 | 13:00 | Satmasjid | 137 | 03:00 | 129 | 13:00
| Haripur | 137 | 05:00 | 132 | 12:00 | Savar | 135 | 02:00 | 129 | 12:00
| HaripurSBU | 137 | 05:00 | 132 | 00:00 | SevenRings | 143 | 03:00 | 136 | 13:00
| Hasnabad | 140 | 23:00 | 135 | 12:00 | ShahCement | 138 | 05:00 | 132 | 12:00
| Hathazari | 136 | 04:00 | 132 | 12:00 | Shahjadpur | 143 | 03:00 | 136 | 12:00
| Ishurdi | 143 | 05:00 | 137 | 13:00 | Shahjibazar | 137 | 03:00 | 131 | 13:00
| Jaldhaka | 135 | 05:00 | 119 | 12:00 | Shahmirpur | 133 | 04:00 | 130 | 11:00
| Jamalpur | 129 | 23:00 | 115 | 12:00 | Shariatpur | 139 | 04:00 | 129 | 13:00
| Jashore | 141 | 04:00 | 129 | 12:00 | Sherpur | 124 | 14:00 | 112 | 07:00
| Jhenaidah | 141 | 05:00 | 132 | 13:00 | Shikalbaha | 124 | 03:00 | 118 | 12:00
| Jhenaidah-230 | 142 | 04:00 | 131 | 13:00 | Shikalbaha-230 | 136 | 05:00 | 129 | 12:00
| Joydebpur | 142 | 02:00 | 134 | 19:30 | Shitalakhya | 139 | 05:00 | 132 | 13:00
| Joypurhat | 138 | 03:00 | 129 | 09:00 | Sholosohor | 135 | 03:00 | 129 | 12:00
| Juldah | 134 | 07:00 | 128 | 13:00 | Shyampur | 137 | 22:00 | 133 | 00:00
| Kabirpur | 136 | 02:00 | 130 | 12:00 | Shyampur-230 | 139 | 05:00 | 133 | 12:00
| Kachua | 132 | 05:00 | 125 | 13:00 | Siddhirganj | 138 | 05:00 | 133 | 12:00
| Kaliakoir | 139 | 06:00 | 132 | 12:00 | Sirajganj | 139 | 04:00 | 133 | 08:00
| Kallyanpur | 138 | 05:00 | 128 | 13:00 | Sonargaon | 137 | 06:00 | 131 | 00:00
| Kalurghat | 135 | 05:00 | 129 | 13:00 | Sreemongol | 137 | 07:00 | 131 | 14:00
| Kamrangirchar | 140 | 04:00 | 127 | 13:00 | Sreepur | 130 | 03:00 | 127 | 09:00
| Kaptai | 138 | 6:00 | 133 | 1:00 | Srinagar | 140 | 05:00 | 132 | 12:00
| Kazla | 138 | 07:00 | 128 | 12:00 | SSM | 139 | 03:00 | 136 | 00:00
| Keranigonj | 138 | 03:00 | 131 | 13:00 | Sunamganj | 134 | 01:00 | 130 | 13:00
| Khagrachori | 134 | 02:00 | 127 | 12:00 | Sylhet | 137 | 03:00 | 132 | 13:00
| Khulna | 139 | 00:00 | 130 | 13:00 | Sylhet-132 | 136 | 04:00 | 133 | 11:00
| Khulna(S) | 141 | 01:00 | 131 | 13:00 | Tangail | 130 | 14:00 | 122 | 07:00
| Khulshi | 134 | 05:00 | 126 | 13:00 | Thakurgaon | 135 | 05:00 | 119 | 09:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 132 | 22:00 | 122 | 13:00 | TK | 135 | 04:00 | 130 | 13:00 |  |  | Nos | Nos | Nos
| Kodda | 138 | 06:00 | 129 | 17:00 | Tongi | 140 | 23:00 | 135 | 12:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 136 | 07:00 | 129 | 11:00 | Ullahpara | 139 | 15:00 | 134 | 12:00
| Kulaura | 138 | 07:00 | 135 | 13:00 | Ullon | 138 | 03:00 | 130 | 13:00
[6 empty] | Uttara | 137 | 04:00 | 128 | 13:00
[6 empty] | UttaraNew | 137 | 03:00 | 128 | 12:00
[6 empty] | Zigatola | 141 | 07:00 | 127 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.