## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-01-2025 | [28 empty] | Date: | 26-01-2025 | [28 empty] | Date: | 26-01-2025 | [28 empty] | Date: | 26-01-2025 | [28 empty] | Date: | 26-01-2025 | [19 empty] | Date: | 26-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [19 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 300 | 285 | 0 | 0 | 0 | 26 | 280 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 503 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 987 | 0 | 51 | 0 | 189 | 0 | 0 | 0 | 26 | 183 | 38 | 0 | 45 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 290 | 280 | 336 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 79 | 0 | 0 | 0 | 24 | 5074 | 917 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 140 | 0 | 140 | 0 | 229 | 0 | 0 | 2.5 | 154 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 180 | 0 | 0 | 900 | 0 | 3979.92 | 9053.92 | 92.31
01:00 | 0 | 17 | 13 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 268 | 0 | 0 | 0 | 26 | 280 | 0 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 406 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 854 | 0 | 51 | 0 | 108 | 0 | 0 | 0 | 25 | 182 | 38 | 0 | 45 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 280 | 280 | 297 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 24 | 4666 | 920 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 515.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 140 | 0 | 140 | 0 | 230 | 0 | 0 | 2.5 | 156 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 180 | 0 | 0 | 800 | 0 | 3802.87 | 8468.87 | 92.31
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 286 | 0 | 0 | 0 | 26 | 280 | 0 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 406 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 756 | 0 | 51 | 0 | 108 | 0 | 0 | 0 | 26 | 188 | 38 | 0 | 45 | 0 | 0 | 17 | 0 | 44 | 0 | 0 | 0 | 295 | 250 | 287 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 0 | 24 | 4499 | 808 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 486.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 140 | 0 | 140 | 0 | 229 | 0 | 0 | 2.5 | 156 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 0 | 800 | 0 | 3580.63 | 8079.63 | 92.3
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 314 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 270 | 0 | 0 | 0 | 26 | 280 | 0 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 408 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 758 | 0 | 51 | 0 | 76 | 0 | 0 | 0 | 26 | 200 | 38 | 0 | 50 | 0 | 0 | 15 | 0 | 42 | 0 | 0 | 0 | 300 | 250 | 287 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 0 | 24 | 4437 | 730 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 140 | 0 | 140 | 0 | 230 | 0 | 0 | 2.5 | 153 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 0 | 600 | 0 | 3286.17 | 7723.17 | 92.3
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 302 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 275 | 0 | 0 | 0 | 28 | 280 | 0 | 0 | 0 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 407 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 760 | 0 | 5 | 0 | 76 | 0 | 0 | 0 | 25 | 183 | 34 | 0 | 50 | 0 | 0 | 15 | 0 | 40 | 0 | 0 | 0 | 295 | 250 | 287 | 37 | 43 | 0 | 2 | 120 | 13 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 0 | 24 | 4323 | 730 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 140 | 0 | 140 | 0 | 229 | 0 | 0 | 2.5 | 151 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 0 | 600 | 0 | 3283.59 | 7606.59 | 92.3
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 273 | 0 | 0 | 0 | 28 | 280 | 0 | 0 | 0 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 408 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 704 | 0 | 5 | 0 | 76 | 0 | 0 | 0 | 5 | 182 | 34 | 0 | 50 | 0 | 0 | 15 | 0 | 40 | 0 | 0 | 0 | 290 | 260 | 287 | 40 | 43 | 0 | 2 | 120 | 13 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 7 | 0 | 0 | 0 | 4181 | 729 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 453.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 140 | 0 | 140 | 0 | 229 | 0 | 0 | 2.5 | 152 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 0 | 600 | 0 | 3267.22 | 7448.22 | 92.29
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 287 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 407 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 700 | 0 | 5 | 0 | 125 | 0 | 0 | 0 | 5 | 192 | 31 | 0 | 50 | 0 | 0 | 15 | 0 | 42 | 0 | 0 | 0 | 310 | 261 | 370 | 43 | 42 | 0 | 2 | 163 | 13 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 2 | 38 | 7 | 0 | 0 | 0 | 4446 | 730 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 140 | 0 | 140 | 0 | 228 | 0 | 0 | 2.5 | 150 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 140 | 220 | 0 | 0 | 630 | 0 | 3413.26 | 7859.26 | 92.29
07:00 | 0 | 20 | 13 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 14 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 318 | 0 | 0 | 0 | 28 | 280 | 0 | 0 | 1 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 501 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 876 | 1 | 5 | 0 | 143 | 0 | 0 | 0 | 13 | 220 | 31 | 0 | 50 | 0 | 0 | 17 | 0 | 42 | 0 | 2 | 0 | 310 | 231 | 370 | 43 | 42 | 0 | 2 | 163 | 13 | 0 | 66 | 30 | 0 | 0 | 0 | 0 | 9 | 47 | 7 | 0 | 0.78 | 17 | 4922.78 | 824 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.45 | 0 | 0 | 484.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.68 | 123 | 0 | 140 | 0 | 140 | 0 | 228 | 0 | 0.06 | 2.5 | 147 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 246 | 6 | 140 | 220 | 0 | 0 | 840 | 0 | 3828.76 | 8751.54 | 92.29
08:00 | 0 | 33 | 26 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 3 | 0 | 0 | 43 | 32 | 0 | 0 | 0 | 17 | 22 | 0 | 300 | 274 | 0 | 0 | 0 | 26 | 280 | 0 | 0 | 6 | 0 | 0 | 20 | 0 | 0 | 8 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 7 | 576 | 0 | 0 | 3 | 0 | 0 | 160 | 0 | 0 | 0 | 1077 | 5 | 43 | 0 | 195 | 0 | 0 | 0 | 24 | 186 | 31 | 2 | 50 | 0 | 3 | 17 | 0 | 42 | 0 | 18 | 0 | 300 | 200 | 370 | 43 | 42 | 0 | 2 | 163 | 13 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 5 | 0 | 8.08 | 24 | 5309.08 | 920 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.51 | 0 | 0 | 696.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8.46 | 129 | 0 | 155 | 0 | 148 | 0 | 230 | 0 | 0.78 | 2.5 | 127 | 72 | 0 | 3 | 0 | 0 | 0 | 0.6 | 18 | 0.11 | 0 | 250 | 4 | 140 | 220 | 0 | 29.52 | 1040 | 10 | 4450.54 | 9759.62 | 92.28
09:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 70 | 16 | 0 | 0 | 0 | 54 | 22 | 0 | 300 | 267 | 0 | 0 | 0 | 25 | 280 | 0 | 0 | 15 | 0 | 19.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 5 | 576 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1224 | 11 | 51 | 0 | 195 | 0 | 0 | 0 | 25 | 183 | 36 | 16 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 40 | 0 | 280 | 200 | 370 | 43 | 43 | 0 | 2 | 120 | 13 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 5 | 1 | 20.06 | 24 | 5526.56 | 919 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.44 | 0 | 0 | 708.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 23.36 | 128 | 0 | 156 | 0 | 149 | 0 | 325 | 0 | 1.97 | 2.5 | 151 | 71 | 0 | 11 | 0 | 0 | 0 | 2.1 | 51 | 0.25 | 0 | 307 | 4 | 100 | 220 | 0 | 65.13 | 1070 | 0 | 4750.41 | 10276.97 | 92.28
10:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 0 | 5 | 0 | 75 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 260 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 23 | 0 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 5 | 506 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1098 | 15 | 51 | 0 | 200 | 0 | 0 | 0 | 26 | 183 | 31 | 16 | 50 | 0 | 0 | 17 | 0 | 54 | 0 | 55 | 0 | 280 | 300 | 337 | 43 | 42 | 0 | 2 | 120 | 13 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 4 | 1 | 31.3 | 24 | 5444.3 | 919 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.63 | 0 | 0 | 640.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 36.98 | 133 | 0 | 143 | 0 | 164 | 0 | 313 | 0 | 3.16 | 2.5 | 120 | 71 | 0 | 19 | 0 | 0 | 0 | 3.4 | 103 | 0.4 | 0 | 250 | 3 | 100 | 180 | 0 | 76.17 | 1000 | 0 | 4608.18 | 10052.48 | 92.28
11:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 352 | 0 | 0 | 0 | 17 | 0 | 79 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 291 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 26 | 0 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 4 | 503 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1100 | 19 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 193 | 32 | 16 | 45 | 0 | 0 | 17 | 0 | 56 | 0 | 65 | 0 | 290 | 320 | 345 | 37 | 42 | 0 | 2 | 120 | 13 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 2 | 37.12 | 24 | 5556.12 | 920 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.99 | 0 | 0 | 557.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 46.04 | 148 | 0 | 120 | 0 | 163 | 0 | 381 | 0 | 3.93 | 2.5 | 120 | 70 | 0 | 23 | 0 | 0 | 0 | 4.4 | 141 | 0.51 | 0 | 200 | 3 | 100 | 180 | 0 | 77.02 | 900 | 0 | 4509.58 | 10065.7 | 92.28
12:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 352 | 0 | 0 | 0 | 17 | 0 | 79 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 241 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 28 | 0 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 5 | 576 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1194 | 19 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 36 | 16 | 45 | 0 | 0 | 17 | 0 | 62 | 0 | 69 | 0 | 300 | 320 | 336 | 37 | 43 | 0 | 2 | 163 | 13 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 2 | 40.02 | 24 | 5717.02 | 920 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.26 | 0 | 0 | 648.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 47.87 | 144 | 0 | 0 | 0 | 157 | 0 | 414 | 0 | 3.46 | 2.5 | 150 | 70 | 0 | 25 | 0 | 0 | 0 | 4.9 | 153 | 0.57 | 0 | 298 | 3 | 136 | 220 | 0 | 84.08 | 1000 | 0 | 4823.24 | 10540.26 | 92.28
13:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 352 | 0 | 0 | 0 | 17 | 0 | 60 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 258 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 26 | 0 | 19 | 20 | 0 | 0 | 12 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 13 | 575 | 0 | 0 | 12 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 19 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 35 | 41 | 45 | 0 | 15 | 17 | 0 | 62 | 0 | 66 | 0 | 270 | 320 | 337 | 35 | 42 | 0 | 2 | 120 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 13 | 58 | 0 | 2 | 35.24 | 24 | 5737.24 | 920 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.5 | 0 | 0 | 659.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 34.48 | 168 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 3.68 | 2.5 | 150 | 69 | 0 | 25 | 0 | 0 | 0 | 4.9 | 148 | 0.53 | 0 | 307 | 4 | 140 | 180 | 0 | 76.64 | 1200 | 0 | 4990.27 | 10727.51 | 92.27
14:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 352 | 0 | 0 | 0 | 17 | 0 | 52 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 270 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 21 | 0 | 19 | 20 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 8 | 577 | 0 | 0 | 18 | 0 | 0 | 161 | 0 | 0 | 0 | 1100 | 16 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 182 | 37 | 16 | 45 | 0 | 9 | 17 | 0 | 66 | 0 | 57 | 0 | 285 | 320 | 337 | 38 | 42 | 0 | 2 | 120 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 13 | 58 | 0 | 1 | 25.43 | 24 | 5587.43 | 920 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.2 | 0 | 0 | 638.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 34.91 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 3.28 | 2.5 | 150 | 69 | 0 | 21 | 0 | 0 | 0 | 4.2 | 129 | 0.51 | 0 | 250 | 4 | 140 | 180 | 0 | 74.29 | 1020 | 0 | 4615.15 | 10202.58 | 92.27
15:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 352 | 0 | 0 | 0 | 17 | 0 | 52 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 242 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 17 | 0 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 3 | 575 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1073 | 13 | 51 | 0 | 197 | 0 | 0 | 0 | 26 | 182 | 37 | 16 | 40 | 0 | 9 | 17 | 0 | 58 | 0 | 36 | 0 | 295 | 320 | 337 | 39 | 42 | 0 | 2 | 120 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 15 | 58 | 0 | 1 | 24.61 | 24 | 5481.61 | 923 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.96 | 0 | 0 | 508.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 18.24 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 2.29 | 2.5 | 152 | 69 | 0 | 15 | 0 | 0 | 0 | 2.9 | 93 | 0.37 | 0 | 242 | 3 | 138 | 220 | 0 | 83 | 980 | 0 | 4376.95 | 9858.56 | 92.27
16:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 352 | 0 | 0 | 0 | 17 | 0 | 52 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 300 | 262 | 0 | 0 | 0 | 24 | 280 | 0 | 0 | 7 | 0 | 18.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 576 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1000 | 8 | 51 | 0 | 197 | 0 | 0 | 0 | 26 | 182 | 37 | 16 | 40 | 0 | 9 | 17 | 0 | 56 | 0 | 19 | 0 | 295 | 320 | 337 | 39 | 42 | 0 | 2 | 120 | 16 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 16 | 58 | 0 | 0 | 10.75 | 24 | 5383.25 | 922 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.92 | 0 | 0 | 416.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 13.51 | 130 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 1.26 | 2.5 | 153 | 69 | 0 | 8 | 0 | 0 | 0 | 1.4 | 47 | 0.19 | 0 | 200 | 4 | 135 | 220 | 0 | 83 | 900 | 0 | 4042.86 | 9426.11 | 92.26
17:00 | 0 | 60 | 26 | 0 | 0 | 0 | 0 | 3 | 352 | 0 | 0 | 17 | 17 | 0 | 62 | 16 | 0 | 0 | 0 | 72 | 25 | 0 | 300 | 290 | 0 | 0 | 6 | 15 | 280 | 0 | 0 | 2 | 0 | 18.5 | 20 | 0 | 0 | 2 | 15 | 0 | 0 | 12 | 0 | 0 | 0 | 4 | 2 | 0 | 40 | 0 | 6 | 576 | 17 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1045 | 2 | 51 | 2 | 197 | 0 | 0 | 0 | 26 | 193 | 40 | 18 | 40 | 0 | 10 | 17 | 0 | 56 | 0 | 4 | 0 | 300 | 320 | 348 | 42 | 42 | 0 | 2 | 120 | 8 | 0 | 79 | 30 | 0 | 0 | 0 | 2 | 11 | 58 | 0 | 0 | 2.54 | 24 | 5525.04 | 923 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2 | 0 | 0 | 417.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 2.99 | 130 | 0 | 0 | 0 | 130 | 0 | 252 | 0 | 0.28 | 2.5 | 152 | 69 | 0 | 2 | 0 | 0 | 0 | 0.2 | 11 | 0.05 | 0 | 250 | 4 | 137 | 220 | 0 | 85 | 920 | 10 | 3864.83 | 9389.87 | 92.26
18:00 | 0 | 80 | 26 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 54 | 17 | 0 | 105 | 32 | 0 | 22 | 17 | 108 | 25 | 0 | 300 | 268 | 0 | 0 | 17 | 15 | 240 | 0 | 0 | 0 | 8 | 18 | 14 | 0 | 0 | 31 | 15 | 4 | 0 | 12 | 9 | 33 | 0 | 12 | 12 | 0 | 40 | 15 | 13 | 575 | 17 | 0 | 19 | 0 | 15 | 161 | 0 | 0 | 0 | 1160 | 0 | 51 | 24 | 184 | 0 | 0 | 0 | 26 | 183 | 40 | 48 | 40 | 25 | 34 | 17 | 0 | 63 | 0 | 0 | 35 | 290 | 320 | 337 | 43 | 42 | 0 | 2 | 120 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 17 | 17 | 58 | 0 | 0 | 0 | 24 | 6078 | 923 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609.96 | 0 | 0 | 17 | 0 | 0 | 0 | 68 | 0 | 0 | 8 | 0 | 16 | 0 | 135 | 0 | 0 | 0 | 135 | 0 | 414 | 0 | 0 | 2.5 | 154 | 68 | 30 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 5 | 80 | 180 | 0 | 84 | 1080 | 100 | 4575.46 | 10653.46 | 92.26
19:00 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 54 | 17 | 0 | 115 | 48 | 0 | 0 | 0 | 72 | 25 | 0 | 380 | 259 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 17 | 18 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 14 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21 | 575 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 195 | 0 | 0 | 0 | 26 | 183 | 39 | 50 | 50 | 34 | 9 | 17 | 0 | 56 | 0 | 0 | 0 | 270 | 320 | 337 | 43 | 42 | 0 | 2 | 163 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 0 | 0 | 24 | 6084 | 923 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 152 | 0 | 414 | 0 | 0 | 2.5 | 154 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 83 | 1244 | 54 | 4811.5 | 10895.5 | 92.26
19:30 | 0 | 88 | 8 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 17 | 17 | 0 | 115 | 48 | 0 | 0 | 0 | 54 | 25 | 0 | 380 | 267 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 17 | 19 | 20 | 0 | 0 | 35 | 0 | 0 | 0 | 12 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 575 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 26 | 183 | 39 | 50 | 50 | 0 | 9 | 17 | 0 | 58 | 0 | 0 | 0 | 285 | 320 | 347 | 43 | 42 | 0 | 2 | 163 | 16 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 0 | 0 | 24 | 6048 | 924 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 152 | 0 | 414 | 0 | 0 | 2.5 | 152 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 84 | 1244 | 54 | 4816.5 | 10864.5 | 92.26
20:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 17 | 17 | 0 | 115 | 16 | 0 | 0 | 0 | 54 | 25 | 0 | 380 | 252 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 17 | 18 | 19 | 0 | 0 | 35 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 29 | 576 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 26 | 182 | 36 | 50 | 50 | 0 | 9 | 17 | 0 | 64 | 0 | 0 | 0 | 285 | 320 | 347 | 39 | 42 | 0 | 2 | 163 | 16 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 0 | 0 | 24 | 5956 | 922 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 152 | 0 | 414 | 0 | 0 | 2.5 | 153 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 84 | 1244 | 54 | 4819.29 | 10775.29 | 92.25
21:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 17 | 0 | 115 | 16 | 0 | 0 | 0 | 17 | 25 | 0 | 300 | 273 | 0 | 0 | 0 | 24 | 300 | 0 | 0 | 0 | 0 | 18 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 576 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 26 | 183 | 33 | 27 | 50 | 0 | 0 | 17 | 0 | 60 | 0 | 0 | 0 | 300 | 320 | 347 | 43 | 42 | 0 | 2 | 163 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 24 | 5733 | 923 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 152 | 0 | 414 | 0 | 0 | 2.5 | 153 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 140 | 220 | 0 | 84 | 1244 | 54 | 4819.5 | 10552.5 | 92.25
22:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 17 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 282 | 0 | 0 | 0 | 24 | 260 | 0 | 0 | 0 | 0 | 18 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 35 | 578 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 1190 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 34 | 0 | 40 | 0 | 0 | 17 | 0 | 62 | 0 | 0 | 0 | 285 | 320 | 342 | 40 | 42 | 0 | 2 | 130 | 0 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 24 | 5516 | 924 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 153 | 0 | 380 | 0 | 0 | 2.5 | 153 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 8 | 100 | 180 | 0 | 84 | 1120 | 0 | 4477.5 | 9993.5 | 92.25
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 17 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 300 | 285 | 0 | 0 | 0 | 24 | 260 | 0 | 0 | 0 | 0 | 16 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 578 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 952 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 186 | 37 | 0 | 40 | 0 | 0 | 17 | 0 | 64 | 0 | 0 | 0 | 290 | 300 | 340 | 43 | 42 | 0 | 2 | 130 | 17 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 22 | 5256 | 923 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 153 | 0 | 380 | 0 | 0 | 2.5 | 160 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 100 | 180 | 0 | 74.98 | 1050 | 0 | 4269.48 | 9525.48 | 92.24
Total KWH | 0 | 1069440 | 340800 | 0 | 0 | 0 | 0 | 88863.64 | 8665200 | 0 | 0 | 155520 | 259560 | 0 | 1581984 | 322080 | 0 | 45306 | 31173 | 783360 | 525240 | 0 | 7587500 | 6605265 | 0 | 0 | 40798 | 553500 | 6830376 | 0 | 0 | 173431 | 34800 | 413400 | 448920 | 0 | 0 | 170618 | 25091 | 4800 | 0 | 559200 | 32279 | 33559 | 0 | 14400 | 14400 | 23520 | 961680 | 32618 | 523680 | 12574545.45 | 28436 | 0 | 187680 | 0 | 34291 | 3766185 | 0 | 0 | 0 | 24425452 | 127845 | 1080478 | 50181 | 4064727 | 0 | 0 | 0 | 565920 | 4543000 | 870120 | 403200 | 1092900 | 64800 | 191520 | 405790 | 0 | 1269120 | 0 | 435327 | 18672 | 7129500 | 6884300 | 8404000 | 958320 | 999000 | 0 | 58176 | 3503945 | 327744 | 0 | 1785600 | 717600 | 0 | 0 | 0 | 32760 | 230400 | 1252800 | 42240 | 10000 | 233910 | 535440 | 128258286.09 | 21361454 | 4127328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516240 | 0 | 0 | 14099019 | 0 | 0 | 15569 | 0 | 0 | 0 | 86768 | 0 | 0 | 9787 | 585581 | 19271 | 273000 | 3401909 | 0 | 1660382 | 0 | 3762645 | 0 | 8256581.8 | 0 | 22800 | 66942 | 3681000 | 1625890 | 60424 | 151020 | 30288 | 0 | 0 | 29463.6 | 902160 | 3508 | 0 | 5629000 | 134805 | 2808000 | 5109600 | 0 | 1236363.64 | 23879272.73 | 332400 | 103878471.77 | 232136757.86

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-01-2025 | during | 27-01-2025 | during | 27-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 3 | 3 | 97.3 | 97.3 | 5 | 5 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 352 | 401 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 380 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 241 | 259 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 19 | 18 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 20 | 0 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 15 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 26 | 8 | 52.19 | 52.19 | 26 | 26 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 79 | 115 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 72 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 28 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 17 | 17 | 36 | 36 | 36 | 36 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0.01 | 0.01 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0.01 | 0.01 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.27 | 1536 | 1855 | 4605.99 | 4585.99 | 2731.73 | 2711.73
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 161 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 64 | 64 | 64 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 17 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 21 | 4 | 14 | 4 | 14 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.75 | 0 | 3.75 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1194 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 19 | 14 | 6 | 6 | 6 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 576 | 575 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2018 | 2106 | 3398.47 | 3386.72 | 3398.47 | 3386.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | schedule outage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | schedule outage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 36 | 39 | 46.94 | 46.94 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 26 | 26 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 199 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 10 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 50 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 34 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 62 | 56 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | machine problem
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 50 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 54 | 0 | 54 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 704 | 720 | 1732.97 | 1678.97 | 1614.2 | 1560.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[8 empty] | during | 0 | during | 0 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 20 | 20 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 200 | 200 | 58 | 58 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 19 | 115 | 115 | 15 | 15 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 40.02 | 0 | 44 | 0 | 44 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 133.02 | 101 | 647.3 | 601.5 | 215.3 | 169.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 43 | 42 | 43 | 43 | 43 | 43 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 330 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 37 | 43 | 44 | 44 | 44 | 44 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 79 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 16 | 25 | 25 | 13 | 13 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 270 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 336 | 337 | 380 | 380 | 352 | 352 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1326 | 1302 | 1754.5 | 1754.5 | 1360.01 | 1360.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 920 | 923 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 173 | 128 | 410 | 410 | 192 | 192 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 81.26 | 0 | 76 | 0 | 76 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | S/D due to changing of ST Power Tx Radiators
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1174.26 | 1051 | 3465 | 3389 | 1353.02 | 1277.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 84.08 | 83 | 100 | 100 | 100 | 100 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 3 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 136 | 140 | 135 | 135 | 140 | 140 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1244 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 298 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.57 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 1741.65 | 2055 | 2277.12 | 2276.12 | 2239 | 2238
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Pond Cleaning.
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 144 | 162 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 157 | 152 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | -
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 3.46 | 0 | 4.25 | 0 | 4.25 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 648.6 | 753 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 47.87 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 87 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1504.43 | 1483.5 | 3139.03 | 2984.78 | 3068.03 | 2913.78
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 68 | 71 | 71 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 150 | 154 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0.01 | 0.01 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 0.01 | 0.01 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.9 | 0 | 2.8 | 0 | 1.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 16 | 0 | 16 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 153 | 0 | 145 | 0 | 145 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 402.9 | 222 | 626.8 | 483 | 610.42 | 448.02
System Total |  |  |  |  | 29204.66 | 28386.248 | 10540.26 | 10895.5 | 21647.18 | 21140.58 | 16590.18 | 16064.98
Forecast Scenario (27-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9060 |  | 0 |  | 9060
|  |  |  | 1:00 | 8560 |  | 0 |  | 8560
|  |  |  | 2:00 | 8060 |  | 0 |  | 8060
|  |  |  | 3:00 | 7750 |  | 0 |  | 7750
|  |  |  | 4:00 | 7600 |  | 0 |  | 7600
|  |  |  | 5:00 | 7520 |  | 0 |  | 7520
|  |  |  | 6:00 | 7920 |  | 0 |  | 7920
|  |  |  | 7:00 | 8700 |  | 0 |  | 8700
|  |  |  | 8:00 | 9600 |  | 0 |  | 9600
|  |  |  | 9:00 | 10050 |  | 0 |  | 10050
|  |  |  | 10:00 | 9850 |  | 0 |  | 9850
|  |  |  | 11:00 | 9900 |  | 0 |  | 9900
|  |  |  | 12:00 | 10450 |  | 0 |  | 10450
|  |  |  | 13:00 | 10700 |  | 0 |  | 10700
|  |  |  | 14:00 | 10340 |  | 0 |  | 10340
|  |  |  | 15:00 | 10000 |  | 0 |  | 10000
|  |  |  | 16:00 | 9600 |  | 0 |  | 9600
|  |  |  | 17:00 | 9740 |  | 0 |  | 9740
|  |  |  | 18:00 | 10790 |  | 0 |  | 10790
|  |  |  | 18:30 | 10850 |  | 0 |  | 10850
|  |  |  | 19:00 | 10940 |  | 0 |  | 10940
|  |  |  | 19:30 | 10880 |  | 0 |  | 10880
|  |  |  | 20:00 | 10820 |  | 0 |  | 10820
|  |  |  | 21:00 | 10510 |  | 0 |  | 10510
|  |  |  | 22:00 | 10130 |  | 0 |  | 10130
|  |  |  | 23:00 | 9480 |  | 0 |  | 9480
Probable Maximum Temperature: |  |  | 24.00°C
Probable Maximum Demand at Day Peak: |  |  | 10450.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10940.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10940.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 228.07 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:46 hrs on 27-01-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division
Formulas:
Effective Available Gen. on = [Forecasted Available Gen. on]

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-01-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10540.26 | MW | 12:00 Hr. | Energy Generated |  |  | 232.1368 |  | MKWHr.
| Day Peak Demand |  |  | 10592.26 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.703 |  | MKWHr.
| Evening Peak Generation |  |  | 10895.5 | MW | 19:00 Hr. | Energy Demand |  |  | 232.8398 |  | MKWHr.
| Evening Peak Demand |  |  | 10968.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 25 |  | °C
| Minimum Generation of the Day |  |  | 7448.22 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 812.72 |  | MMCFD
| Maximum Generation of the Day |  |  | 10895.5 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.5985 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.7183 | 0 | 4.6648 | 0 | 0 | 0.17343 | 0 | 0 | 36.5565 | Gas | 108.7697 | Gas | 388927155.494
| Chattogram Zone |  |  | 4.2899 | 37 | 0.57817 | 0 | 0.96168 | 0.15136 | 0 | 0.5592 | 43.5403 | Coal | 73.0515 | Coal | 505001705.8389
| Cumilla Zone |  |  | 12.6229 | 0 | 0.72837 | 0 | 0 | 0.43533 | 1.2691 | 0 | 15.0558 | HFO | 8.5773 | HFO | 160621211.39
| Mymensingh Zone |  |  | 0.04224 | 0 | 2.0514 | 0 | 0 | 0.24391 | 0 | 0 | 2.3375 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.7682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.7682 | Hydro | 0.96168 | Hydro | 96168
| Khulna Zone |  |  | 4.1273 | 0 | 0 | 0 | 0 | 0.51624 | 21.3615 | 0 | 26.005 | Solar | 3.4878 | Solar | 54260173.92
| Barishal Zone |  |  | 8.0524 | 30.7446 | 0.3324 | 0 | 0 | 0.003508 | 0 | 0 | 39.1329 | Import | 36.7296 | Import | 181991700.61
| Rajshahi Zone |  |  | 17.1485 | 0 | 0.1314 | 0 | 0 | 0.88138 | 14.099 | 0 | 32.2603 | Wind | 0.5592 | Wind | 8723520
| Rangpur Zone |  |  | 0 | 5.3069 | 0.090712 | 0 | 0 | 1.0826 | 0 | 0 | 6.4802
| Total |  |  | 108.7697 | 73.0515 | 8.5773 | 0 | 0.96168 | 3.4878 | 36.7296 | 0.5592 | 232.1368
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 388927155.494 |  | Hydro | 96168
|  |  |  | Coal | 505001705.8389 |  | Solar | 54260173.92
|  |  |  | HFO | 160621211.39 |  | Import | 181991700.61
|  |  |  | HSD | 0 |  | Wind | 8723520
[5 empty] | Total: | 129,96,21,635 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West |  |  |  | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.3615 | Peak Hr Flow | 923.00 MW at 19:00 hrs.
Energy Flow from West to East |  |  |  | 9675236.447 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.099 | Peak Hr Flow | 753.00 MW at 19:00 hrs.
Power Flow during Peak Demand |  |  |  | 454 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.2691 | Peak Hr Flow | 56.00 MW at 19:00 hrs.
Maximum Power Flow |  |  |  | 746 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 36.7296 | Peak Hr Flow | 1732.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3935
|  |  |  | Chattogram |  | 0 |  | 1034
|  |  |  | Cumilla |  | 0 |  | 854
|  |  |  | Mymensingh |  | 70 |  | 992
|  |  |  | Sylhet |  | 0 |  | 385
|  |  |  | Khulna |  | 0 |  | 1190
|  |  |  | Barishal |  | 0 |  | 280
|  |  |  | Rajshahi |  | 0 |  | 1062
|  |  |  | Rangpur |  | 0 |  | 752
|  |  |  | Total |  | 70 |  | 10484
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
|  | 8 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
|  | 9 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1404 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1839.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:08 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
| 08:08 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
| 08:28 | 16:50 | Ashuganj-Sreepur 230 kV Ckt-2 Scheduled S/D from Sirajgonj 230 end Due to Annual
Maintenance
| 08:32 | 16:22 | Khulshi-Madunaghat 132kV Ckt-1 Scheduled S/D from Madunaghat 132/33kV end Due to Annual
Maintenance
| 08:32 | 16:21 | Sholosohor 132/33kV S/S Sholoshahar-Madunaghat Ckt-1 Scheduled S/D Due to Annual
Maintenance
| 08:32 | 15:40 | Khulna (S)-Rampal Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to Annual
Maintenance Work. and from Rampal 400/230kV end Due to Khulna ALDC Required.
| 08:35 |  | Jamalpur 132/33kV S/S T-2 LT Project Work S/D Due to Bus DS replacement work
| 08:35 |  | Jamalpur 132/33kV S/S T-2 HT Project Work S/D Due to 132kv DS replacement work
| 08:38 | 16:00 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT Scheduled S/D
| 08:38 | 16:00 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT Scheduled S/D
|  | 08:40 | Jamalpur 132/33kV S/S Bus-B is restored.
| 08:45 |  | Jamalpur 132/33kV S/S Bus-A Project Work S/D Due to 132 kv bus A DS replacement work
| 08:52 | 16:25 | Aminbazar-Manikgonj PP 132kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual maintenance
| 08:58 | 17:17 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Scheduled S/D Due to Dead line Checking of
CKT - 2
| 09:06 | 15:27 | Chandraghona-Kaptai 132 kV Ckt-1 Scheduled S/D from Chandraghona 132/33kV end Due to
Annual maintenance
| 09:12 | 16:51 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-2 Scheduled S/D Due to Annual Maintenance
| 09:14 | 16:22 | Mogbazar 132/33kV S/S GT-1 LT Scheduled S/D Due to GT-01 Annual Maintenance
| 09:16 | 16:18 | Mogbazar 132/33kV S/S GT-1 HT Scheduled S/D Due to GT-01 Annual Maintenance
| 09:17 | 15:51 | Chuadanga-Jhenaidah 132 kV Ckt-1 Scheduled S/D from Jhenaidah 230/132kV end Due to Annual
maintenance at Chuadanga end and from Chuadanga 132/33kVend.
| 09:20 |  | Siddhirganj 132/33kV S/S 132kV MTR 1 Scheduled S/D Due to Annual maintenance
| 09:23 |  | Siddhirganj 230/132kV S/S MTR 1 HT Scheduled S/D Due to annual maintenance work
| 09:49 | 18:47 | Aminbazar-Meghnaghat 400kV Ckt-2 Forced S/D from Meghnaghat 400/230kV end Due to
requested by LDC
| 09:52 | 15:51 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end.
| 09:58 | 14:20 | Tongi 230/132/33kV S/S T-2 HT Scheduled S/D Due to Annual maintenance
| 09:58 | 14:20 | Tongi 230/132/33kV S/S T-2 LT Scheduled S/D Due to Annual maintenance
| 10:00 | 17:35 | Madunaghat 132/33kV S/S TR-2(517T) LT Scheduled S/D Due to Annual Maintenance
| 10:00 | 17:09 | Madunaghat 132/33kV S/S TR-2(517T) HT Scheduled S/D Due to Annual Maintenance.
| 10:05 | 17:29 | Rangpur 132/33kV S/S Rangpur-GTPS Scheduled S/D
| 10:12 | 16:05 | Hathazari 230/132/33kV S/S Raojan-02 Scheduled S/D Due to Annual maintenance (Dead end
line checking)
| 10:30 | 10:50 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to Tr-3 33 kV GCB gas refilling
work.
| 10:30 | 10:49 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to Tr-3 33 kV GCB gas refilling
work.
|  | 10:45 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
| 11:10 | 15:06 | Palashbari 132/33kV S/S TR1-414T LT Forced S/D Due to Oil leakage maintenance
| 11:11 | 15:05 | Palashbari 132/33kV S/S TR1-414T HT Forced S/D Due to Oil leakage maintenance
| 11:15 | 15:40 | Aminbazar 400/230/132kV S/S Bus-1 (400kV) Scheduled S/D Due to Annual maintenance
| 11:25 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
| 11:25 |  | Sirajgonj 225MW CCPP Unit-2 ST Shutdown with remarks:- None
| 11:32 | 18:34 | Ghatail 132/33kV S/S T-2 LT Forced S/D Due to To change 33 kV bus PT, work by Mpbs-1
| 11:33 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- GT
| 11:33 | 18:32 | Ghatail 132/33kV S/S T-2 HT Forced S/D Due to To change 33kV bus PT, work by Mpbs-1.
| 11:33 |  | Sirajgonj 225MW CCPP Unit-2 GT Shutdown with remarks:- None
| 12:00 |  | Day peak Generation is 10536 MW
| 14:42 | 15:39 | Rampur 230/132/33 S/S Agrabad-1 Scheduled S/D Due to Energy meter Change.
| 15:48 | 16:45 | Rampur 230/132/33 S/S Agrabad-2 Scheduled S/D Due to Energy meter Change.
|  | 16:39 | Chowmuhani-Ramganj 132 kV Ckt-2 is restored.
|  | 16:39 | Chowmuhani-Ramganj 132 kV Ckt-2 is restored.
| 19:00 |  | Evening Peak Generation: 10895 MW.
|  | 19:18 | Bhulta-Ghorasal 230 kV Ckt-1 is restored.
|  | 19:29 | Kabirpur -Kodda 132kV Ckt-1 is restored.
| 22:55 |  | Sirajgonj 225MW CCPP Unit-2 ST Ready with remarks:- None
| 22:55 |  | Sirajgonj 225MW CCPP Unit-2 GT Ready with remarks:- None
| 01:57 |  | Sirajgonj 225MW CCPP Unit-3 Shutdown with remarks:- ST
| 01:57 |  | Sirajgonj 225MW CCPP Unit-3 ST Shutdown with remarks:- As per instruction of NLDC
| 02:08 |  | Sirajgonj 225MW CCPP Unit-3 GT Shutdown with remarks:- As per instruction of NLDC
| 02:08 |  | Sirajgonj 225MW CCPP Unit-3 Shutdown with remarks:- GT
| 02:09 |  | Sirajgonj 225MW CCPP Unit-3 GT Ready with remarks:- None
| 02:09 |  | Sirajgonj 225MW CCPP Unit-3 ST Ready with remarks:- None
| 05:00 |  | Min. Gen. 7600 MW
| 07:09 |  | Bhulta-Ghorasal 230 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to Annual
Maintenance Work.
| 07:35 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
| 07:36 |  | Kallyanpur 132/33kV S/S GT-3 (132kV) LT Scheduled S/D Due to Annual Maintenance
| 07:36 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
| 07:37 |  | Kallyanpur 132/33kV S/S GT-3 (132kV) HT Scheduled S/D Due to Annual Maintenance
| 07:39 |  | Khulna (S)-Rampal Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end Due to Annual
maintenance work and from Rampal 400/230kV end Due to Khulna ALDC Required.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 3 | 88863.64 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 401 | 8665200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 7587500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 259 | 6605265 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 45306 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 6830376 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 155520 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 322080 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 31173 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 40798 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 413400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 448920 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 525240 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 15 | 553500 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 8 | 340800 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1581984 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1069440 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 783360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 173431 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 17 | 259560 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 17 | 34800 | -
Dhaka Area Total |  |  |  |  | 5841.27 | 1855 | 36556516.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 127845 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 187680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 961680 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3766185 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 34291 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 33559 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 17 | 32279 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 14400 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 21 | 523680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 4800 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 25091 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 32618 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 14400 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 170618 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 28436 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 24425452 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 14 | 559200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12574545.45 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2106 | 43540279.45
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4543000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 39 | 870120 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 26 | 565920 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4064727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1080478 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 10 | 50181 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 18672 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1092900 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 64800 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 56 | 1269120 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 405790 | machine problem
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 191520 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 50 | 403200 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 435327 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 720 | 15055755
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 42240 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1252800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 230400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 233910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 535440 | Unable to dispatch due to fuel shortages.
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 32760 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 101 | 2337550
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 42 | 999000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3503945 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 43 | 958320 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 58176 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 717600 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1785600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 327744 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7129500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 337 | 8404000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 6884300 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1302 | 30768185
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 923 | 21361454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 128 | 4127328 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 516240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to changing of ST Power Tx Radiators
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1051 | 26005022
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 83 | 1236363.64 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 134805 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2808000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 23879272.73 | -
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5109600 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 332400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5629000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3508 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2055 | 39132949.37
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 15569 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | Shutdown for Pond Cleaning.
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 162 | 3401909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 1660382 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 152 | 3762645 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8256581.8 | -
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 19271 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 66942 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 9787 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 86768 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 753 | 14099019 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 273000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 585581 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1483.5 | 32260254.8
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 68 | 1625890 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 154 | 3681000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 30288 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 29463.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 60424 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 151020 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 902160 | -
Rangpur Area Total |  |  |  |  | 950 | 222 | 6480245.6
Eastern Grid Total |  |  |  |  | 16771.748 | 6084 | 128258286.09
Western Grid Total |  |  |  |  | 11614.5 | 4811.5 | 103878471.77
National Grid Total |  |  |  |  | 28386.248 | 10895.5 | 232136757.86
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7130.53 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3284 | MW
i) Dhaka area |  |  | 3935.23 |  | MW | i) Khulna area |  |  |  | 1190.2 | MW
ii) Chattogram area |  |  | 1034.3 |  | MW | ii) Barishal area |  |  |  | 280 | MW
iii) Cumilla area |  |  | 854 |  | MW | iii) Rajshahi area |  |  |  | 1061.8 | MW
iv) Mymensingh area |  |  | 922 |  | MW | iv) Rangpur area |  |  |  | 752 | MW
v) Sylhet area |  |  | 385 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10414.53 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 61 | 18:30 | 133 | Purbachal | 14 | 13:00
2 | AKSML | 109 | 01:00 | 68 | Jamalpur | 98 | 18:30 | 134 | Purbasadipur | 99 | 18:30
3 | Aftabnagar | 24 | 12:00 | 69 | Jashore | 109 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 72 | 13:00 | 70 | Jhenaidah | 100 | 08:00 | 136 | Rahim | 46 | 16:00
5 | Agrabad | 62 | 18:00 | 71 | Joydebpur | 148 | 12:00 | 137 | Rajbari | 54 | 18:00
6 | Amnura | 45 | 18:30 | 72 | Joypurhat | 45 | 08:00 | 138 | Rajendrapur | 98 | 18:30
7 | Ashuganj | 69 | 14:00 | 73 | Juldah | 11 | 07:00 | 139 | Rajshahi | 74 | 21:00
8 | BSRM | 194 | 09:00 | 74 | KSRM | 28 | 07:00 | 140 | Rajshahi-230 | 64 | 13:00
9 | Bagerhat | 73 | 18:30 | 75 | Kabirpur | 200 | 20:00 | 141 | Ramganj | 82 | 19:30
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 52 | 18:00 | 142 | Rampur | 25 | 18:00
11 | Bakulia | 63 | 18:30 | 77 | Kallyanpur | 60 | 14:00 | 143 | Rangamati | 12 | 18:00
12 | Banani | 28.4 | 14:00 | 78 | Kalurghat | 30 | 14:00 | 144 | Rangpur | 93 | 14:00
13 | Bangabhaban | 7 | 10:00 | 79 | Kamrangirchar | 52 | 13:00 | 145 | Ruppur | 4.2 | 15:00
14 | Barapukuria | 57 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 16 | 03:00
15 | Barguna | 14 | 19:30 | 81 | Kazla | 59 | 00:00 | 147 | Saidpur | 104 | 18:30
16 | Barishal | 85 | 14:00 | 82 | Keranigonj | 60 | 13:00 | 148 | Satkhira | 94 | 18:30
17 | Barishal-230 | 56 | 08:00 | 83 | Khagrachori | 28 | 18:00 | 149 | Satmasjid | 83 | 13:00
18 | Baroaulia | 44 | 18:00 | 84 | Khulna | 80 | 13:00 | 150 | Savar | 174 | 12:00
19 | Baroirhat | 52 | 18:00 | 85 | Khulshi | 139 | 15:00 | 151 | SevenRings | 16.95 | 00:00
20 | Bashundhara | 127 | 13:00 | 86 | Kishoreganj | 126 | 20:00 | 152 | ShahCement | 32 | 23:00
21 | BashundharaCement | 11 | 01:00 | 87 | Kodda | 269 | 18:30 | 153 | Shahjadpur | 61 | 18:30
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 26 | 18:00 | 154 | Shahjibazar | 86 | 19:00
23 | Benapole | 48 | 08:00 | 89 | Kurigram | 58 | 08:00 | 155 | Shahmirpur | 48 | 17:00
24 | Bhaluka | 114 | 18:30 | 90 | Kushtia | 102 | 18:30 | 156 | Shariatpur | 52 | 20:00
25 | Bhandaria | 35 | 21:00 | 91 | Lalbag | 53 | 11:00 | 157 | Sherpur | 110 | 00:00
26 | Bhangura | 28 | 18:30 | 92 | Lalmonirhat | 54 | 18:30 | 158 | Shikalbaha | 16 | 18:00
27 | Bheramara(GK) | 40 | 18:30 | 93 | MI_Cement | 18.5 | 15:00 | 159 | Shitalakhya | 63.6 | 12:00
28 | Bhulta | 241 | 11:00 | 94 | Madanganj | 16 | 17:00 | 160 | Sholosohor | 34 | 12:00
29 | Bog-Sherpur | 64 | 09:00 | 95 | Madaripur | 67 | 20:00 | 161 | Shyampur | 160 | 10:00
30 | Bogura | 107 | 18:30 | 96 | Madartek | 57.57 | 13:00 | 162 | Siddhirganj | 110 | 12:00
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 38 | 18:00 | 163 | Sirajganj | 84 | 19:00
32 | Brahmanbaria | 101 | 19:30 | 98 | Magura | 46 | 18:30 | 164 | Sonargaon | 80 | 21:00
33 | Cantonment | 76 | 13:00 | 99 | Mahasthangarh | 50 | 18:30 | 165 | Sreemongol | 45 | 18:00
34 | Chandpur | 42 | 18:30 | 100 | Manikganj | 105 | 18:30 | 166 | Sreepur | 79 | 18:00
35 | Chandraghona | 24 | 18:30 | 101 | Maniknagar | 48 | 13:00 | 167 | Srinagar | 29.27 | 21:00
36 | Chapai | 60 | 11:00 | 102 | Matarbari | 36 | 18:00 | 168 | Sunamganj | 38 | 18:00
37 | Charsaidpur | 40 | 09:00 | 103 | Matuail | 58 | 12:00 | 169 | Sylhet | 28 | 18:00
38 | Chauddagram | 44 | 12:00 | 104 | Millgate | 67 | 12:00 | 170 | Sylhet-132 | 75 | 18:00
39 | Chhatak | 23 | 18:30 | 105 | Mirpur | 92 | 13:00 | 171 | TK | 21.5 | 18:30
40 | Chowmuhani | 141 | 20:00 | 106 | Mirsorai | 9 | 18:00 | 172 | Tangail | 152 | 08:00
41 | Chuadanga | 72 | 08:00 | 107 | Mirzapur | 44 | 13:00 | 173 | Thakurgaon | 75 | 18:30
42 | Coxsbazar | 107 | 18:00 | 108 | Mithapukur | 65 | 18:30 | 174 | Tongi | 104 | 11:00
43 | Cumilla(N) | 119 | 13:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 22 | 18:00
44 | Cumilla(S) | 129 | 14:00 | 110 | Mogbazar | 95.3 | 13:00 | 176 | Ullon | 35 | 14:00
45 | Daudkandi | 90 | 18:30 | 111 | Mongla | 25 | 12:00 | 177 | Uttara | 54 | 18:00
46 | Dhaka | 22 | 10:00 | 112 | Motijheel | 26 | 13:00 | 178 | UttaraNew | 33 | 13:00
47 | Dhamrai | 104 | 12:00 | 113 | Muktagacha | 28 | 09:00 | 179 | Zigatola | 56 | 13:00
48 | Dhanmondi | 95 | 13:00 | 114 | Munshiganj | 66 | 13:00
49 | Dohazari | 70 | 19:00 | 115 | Mymensingh | 176 | 09:00
50 | Faridpur | 107 | 18:30 | 116 | Naogaon | 107 | 09:00
51 | Fatullah | 69 | 12:00 | 117 | Narail | 41 | 20:00
52 | Fenchuganj | 25 | 18:00 | 118 | Narinda | 62 | 13:00
53 | Feni | 64 | 18:00 | 119 | Narshingdi | 147 | 18:30
54 | GPH | 99 | 02:00 | 120 | Natore | 100 | 20:00
55 | Ghatail | 30 | 09:00 | 121 | Nawabganj | 30.4 | 13:00
56 | Ghorashal | 8 | 07:00 | 122 | Netrakona | 141 | 18:00
57 | Ghorashal-230 | 58 | 17:00 | 123 | New | 59.5 | 16:00
58 | Goalpara | 22 | 08:00 | 124 | Niamatpur | 83 | 08:00
59 | Gollamari | 48 | 13:00 | 125 | Noapara | 35 | 18:30
60 | Gopalganj | 78.8 | 18:30 | 126 | PHP | 8 | 00:00
61 | Gulshan | 68 | 14:00 | 127 | Pabna | 63 | 18:30
62 | Halishahar | 40 | 17:00 | 128 | Palashbari | 84 | 18:30
63 | HaripurSBU | 175 | 16:00 | 129 | Panchagarh | 44 | 18:30
64 | Hasnabad | 69 | 11:00 | 130 | Patuakhali | 56 | 21:00
65 | Hathazari | 55 | 13:00 | 131 | Payra | 14 | 12:00
66 | Ishurdi | 61 | 18:30 | 132 | Postogola | 39 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9053.92 | 0 |  | 9053.92
1:00 | 8468.87 | 0 |  | 8468.87
2:00 | 8079.63 | 0 |  | 8079.63
3:00 | 7723.17 | 0 |  | 7723.17
4:00 | 7606.59 | 0 |  | 7606.59
5:00 | 7448.22 | 0 |  | 7448.22
6:00 | 7859.26 | 0 |  | 7859.26
7:00 | 8751.54 | 0 |  | 8751.54
8:00 | 9759.62 | 23 |  | 9783.62
9:00 | 10276.97 | 20 |  | 10297.97
10:00 | 10052.48 | 10 |  | 10062.48
11:00 | 10065.7 | 30 |  | 10096.7
12:00 | 10540.26 | 50 |  | 10592.26
13:00 | 10727.51 | 60 |  | 10790.51
14:00 | 10202.58 | 70 |  | 10275.58
15:00 | 9858.56 | 60 |  | 9921.56
16:00 | 9426.11 | 35 |  | 9463.11
17:00 | 9389.87 | 50 |  | 9441.87
18:00 | 10653.46 | 85 |  | 10742.46
19:00 | 10895.5 | 70 |  | 10968.5
19:30 | 10864.5 | 50 |  | 10916.5
20:00 | 10775.29 | 45 |  | 10822.29
21:00 | 10552.5 | 50 |  | 10604.5
22:00 | 9993.5 | 45 |  | 10040.5
23:00 | 9525.48 | 0 |  | 9525.48
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5074 | 3979.92 | 9053.92 | DAILY GENERATION CURVE
00:30 | 4870 | 3891.395 | 8761.395
01:00 | 4666 | 3802.87 | 8468.87 | 26-01-2025
01:30 | 4582.5 | 3691.75 | 8274.25
02:00 | 4499 | 3580.63 | 8079.63
02:30 | 4468 | 3433.4 | 7901.4
03:00 | 4437 | 3286.17 | 7723.17
03:30 | 4380 | 3284.88 | 7664.88
04:00 | 4323 | 3283.59 | 7606.59
04:30 | 4252 | 3275.405 | 7527.405
05:00 | 4181 | 3267.22 | 7448.22
05:30 | 4313.5 | 3340.24 | 7653.74
06:00 | 4446 | 3413.26 | 7859.26
06:30 | 4684.39 | 3621.01 | 8305.4
07:00 | 4922.78 | 3828.76 | 8751.54
07:30 | 5115.93 | 4139.65 | 9255.58
08:00 | 5309.08 | 4450.54 | 9759.62
08:30 | 5417.82 | 4600.475 | 10018.295
09:00 | 5526.56 | 4750.41 | 10276.97
09:30 | 5485.43 | 4679.295 | 10164.725
10:00 | 5444.3 | 4608.18 | 10052.48
10:30 | 5500.21 | 4558.88 | 10059.09
11:00 | 5556.12 | 4509.58 | 10065.7
11:30 | 5636.57 | 4666.41 | 10302.98
12:00 | 5717.02 | 4823.24 | 10540.26
12:30 | 5727.13 | 4906.755 | 10633.885
13:00 | 5737.24 | 4990.27 | 10727.51
13:30 | 5662.335 | 4802.71 | 10465.045
14:00 | 5587.43 | 4615.15 | 10202.58
14:30 | 5534.52 | 4496.05 | 10030.57
15:00 | 5481.61 | 4376.95 | 9858.56
15:30 | 5432.43 | 4209.905 | 9642.335
16:00 | 5383.25 | 4042.86 | 9426.11
16:30 | 5454.145 | 3953.845 | 9407.99
17:00 | 5525.04 | 3864.83 | 9389.87
17:30 | 5801.52 | 4220.145 | 10021.665
18:00 | 6078 | 4575.46 | 10653.46
18:30 | 6081 | 4693.48 | 10774.48
19:00 | 6084 | 4811.5 | 10895.5
19:30 | 6048 | 4816.5 | 10864.5
20:00 | 5956 | 4819.29 | 10775.29
20:30 | 5844.5 | 4819.395 | 10663.895 |  | Executive Engineer
21:00 | 5733 | 4819.5 | 10552.5 |  | Network Operation Division
21:30 | 5624.5 | 4648.5 | 10273
22:00 | 5516 | 4477.5 | 9993.5
22:30 | 5386 | 4373.49 | 9759.49
23:00 | 5256 | 4269.48 | 9525.48

## En-Curve
QF-LDC-12
Date | 26-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2748 | 1734.5 | 917 | 0 | 50 | 547.42 | 40 | 2815 | 0 | 25 | 164 | 0 | 0 | 13 | 0 | DAILY ENERGY CURVE
00:30 | 2728.5 | 1677.5 | 918.5 | 0 | 48 | 531.395 | 40 | 2625.5 | 0 | 27.5 | 145 | 0 | 0 | 19.5 | 0 | 26-01-2025
01:00 | 2709 | 1620.5 | 920 | 0 | 46 | 515.37 | 40 | 2436 | 0 | 30 | 126 | 0 | 0 | 26 | 0
01:30 | 2655.5 | 1636 | 864 | 0 | 45 | 500.75 | 40 | 2387 | 0 | 15 | 104 | 0 | 0 | 27 | 0 | Energy Generated | 232.1368 |  | MKWHr
02:00 | 2602 | 1651.5 | 808 | 0 | 44 | 486.13 | 40 | 2338 | 0 | 0 | 82 | 0 | 0 | 28 | 0 | Energy not Served | 0.703 |  | MKWHr
02:30 | 2592 | 1631 | 769 | 0 | 43 | 478.4 | 40 | 2239.5 | 0 | 0 | 82 | 0 | 0 | 26.5 | 0 | Total Energy Requirement | 232.8398 |  | MKWHr
03:00 | 2582 | 1610.5 | 730 | 0 | 42 | 470.67 | 40 | 2141 | 0 | 0 | 82 | 0 | 0 | 25 | 0
03:30 | 2566.5 | 1563 | 730 | 0 | 41 | 470.38 | 40 | 2139.5 | 0 | 0 | 79.5 | 0 | 0 | 35 | 0
04:00 | 2551 | 1515.5 | 730 | 0 | 40 | 470.09 | 40 | 2138 | 0 | 0 | 77 | 0 | 0 | 45 | 0
04:30 | 2555.5 | 1503.5 | 729.5 | 0 | 40 | 461.905 | 40 | 2111 | 0 | 0 | 50.5 | 0 | 0 | 35.5 | 0
05:00 | 2560 | 1491.5 | 729 | 0 | 40 | 453.72 | 40 | 2084 | 0 | 0 | 24 | 0 | 0 | 26 | 0
05:30 | 2644 | 1577 | 729.5 | 0 | 41 | 437.74 | 40 | 2120.5 | 0 | 0 | 32 | 0 | 0 | 32 | 0
06:00 | 2728 | 1662.5 | 730 | 0 | 42 | 421.76 | 40 | 2157 | 0 | 0 | 40 | 0 | 0 | 38 | 0
06:30 | 2742 | 1698 | 777 | 0 | 42 | 452.91 | 40 | 2418.5 | 4.49 | 24.5 | 63.5 | 0 | 0 | 42.5 | 0
07:00 | 2756 | 1733.5 | 824 | 0 | 42 | 484.06 | 40 | 2680 | 8.98 | 49 | 87 | 0 | 0 | 47 | 0
07:30 | 2737 | 1746.5 | 872 | 0 | 42 | 590.06 | 40 | 2925.76 | 56.26 | 70 | 132.5 | 0 | 0 | 43.5 | 11.5
08:00 | 2718 | 1759.5 | 920 | 0 | 42 | 696.06 | 40 | 3171.52 | 103.54 | 91 | 178 | 0 | 0 | 40 | 23
08:30 | 2743 | 1737.75 | 919.5 | 0 | 45 | 702.36 | 40 | 3317.825 | 181.86 | 92.5 | 204.5 | 0 | 0 | 34 | 21.5
09:00 | 2768 | 1716 | 919 | 0 | 48 | 708.66 | 40 | 3464.13 | 260.18 | 94 | 231 | 0 | 0 | 28 | 20
09:30 | 2791.5 | 1695.75 | 919 | 0 | 51 | 674.8 | 40 | 3292.65 | 344.025 | 94 | 236 | 0 | 0 | 26 | 15
10:00 | 2815 | 1675.5 | 919 | 0 | 54 | 640.94 | 40 | 3121.17 | 427.87 | 94 | 241 | 0 | 0 | 24 | 10
10:30 | 2856.5 | 1692 | 919.5 | 0 | 55 | 599.065 | 40 | 3045.595 | 480.93 | 94 | 249 | 0 | 0 | 27.5 | 20
11:00 | 2898 | 1708.5 | 920 | 0 | 56 | 557.19 | 40 | 2970.02 | 533.99 | 94 | 257 | 0 | 0 | 31 | 30
11:30 | 2854 | 1730.5 | 920 | 0 | 59 | 602.895 | 40 | 3171.05 | 549.535 | 94 | 257 | 0 | 0 | 25 | 40
12:00 | 2810 | 1752.5 | 920 | 0 | 62 | 648.6 | 40 | 3372.08 | 565.08 | 94 | 257 | 0 | 0 | 19 | 50
12:30 | 2818.5 | 1709.5 | 920 | 0 | 62 | 653.82 | 40 | 3486.86 | 548.705 | 94 | 281.5 | 0 | 0 | 19 | 55
13:00 | 2827 | 1666.5 | 920 | 0 | 62 | 659.04 | 40 | 3601.64 | 532.33 | 94 | 306 | 0 | 0 | 19 | 60
13:30 | 2788 | 1679 | 920 | 0 | 64 | 648.65 | 40 | 3420.965 | 499.93 | 94 | 292 | 0 | 0 | 18.5 | 65
14:00 | 2749 | 1691.5 | 920 | 0 | 66 | 638.26 | 40 | 3240.29 | 467.53 | 94 | 278 | 0 | 0 | 18 | 70
14:30 | 2740.5 | 1699 | 921.5 | 0 | 62 | 573.475 | 40 | 3207.145 | 401.95 | 94 | 271 | 0 | 0 | 20 | 65
15:00 | 2732 | 1706.5 | 923 | 0 | 58 | 508.69 | 40 | 3174 | 336.37 | 94 | 264 | 0 | 0 | 22 | 60
15:30 | 2726 | 1716.25 | 922.5 | 0 | 57 | 462.385 | 40 | 3077.5 | 258.2 | 94 | 264.5 | 0 | 0 | 24 | 47.5
16:00 | 2720 | 1726 | 922 | 0 | 56 | 416.08 | 40 | 2981 | 180.03 | 94 | 265 | 0 | 0 | 26 | 35
16:30 | 2652.5 | 1736 | 922.5 | 0 | 56 | 416.845 | 40 | 3039 | 111.645 | 98 | 316.5 | 0 | 0 | 19 | 42.5
17:00 | 2585 | 1746 | 923 | 0 | 56 | 417.61 | 40 | 3097 | 43.26 | 102 | 368 | 0 | 0 | 12 | 50
17:30 | 2635 | 1708.75 | 923 | 0 | 59.5 | 513.785 | 40 | 3261 | 21.63 | 213 | 634 | 0 | 0 | 12 | 67.5
18:00 | 2685 | 1671.5 | 923 | 0 | 63 | 609.96 | 40 | 3425 | 0 | 324 | 900 | 0 | 0 | 12 | 85
18:30 | 2789.5 | 1742 | 923 | 0 | 59.5 | 681.48 | 40 | 3540 | 0 | 251 | 735 | 0 | 0 | 13 | 77.5
19:00 | 2894 | 1812.5 | 923 | 0 | 56 | 753 | 40 | 3655 | 0 | 178 | 570 | 0 | 0 | 14 | 70
19:30 | 2909 | 1865.5 | 924 | 0 | 58 | 752 | 40 | 3655 | 0 | 178 | 471 | 0 | 0 | 12 | 50
20:00 | 2906 | 1847.5 | 922 | 0 | 64 | 753.79 | 40 | 3658 | 0 | 103 | 471 | 0 | 0 | 10 | 45
20:30 | 2885 | 1833 | 922.5 | 0 | 62 | 754.895 | 40 | 3658.5 | 0 | 94.5 | 405.5 | 0 | 0 | 8 | 47.5
21:00 | 2864 | 1818.5 | 923 | 0 | 60 | 756 | 40 | 3659 | 0 | 86 | 340 | 0 | 0 | 6 | 50
21:30 | 2793.5 | 1772.5 | 923.5 | 0 | 61 | 756 | 40 | 3562 | 0 | 78 | 281.5 | 0 | 0 | 5 | 47.5
22:00 | 2723 | 1726.5 | 924 | 0 | 62 | 756 | 40 | 3465 | 0 | 70 | 223 | 0 | 0 | 4 | 45
22:30 | 2707 | 1738 | 923.5 | 0 | 63 | 732 | 40 | 3274.49 | 0 | 52 | 223 | 0 | 0 | 6.5 | 22.5
23:00 | 2691 | 1749.5 | 923 | 0 | 64 | 708 | 40 | 3083.98 | 0 | 34 | 223 | 0 | 0 | 9 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 412 | 04:00 | 384 | 13:00 | Kaliakoir | 393 | 04:00 | 374 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 413 | 5:00 | 366 | 14:00 | Madunaghat | 408 | 05:00 | 394 | 13:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 411 | 04:00 | 385 | 12:00 | Meghnaghat | 410 | 05:00 | 383 | 13:00
| Bibiana | 400 | 06:00 | 392 | 11:00 | Payra | 416 | 04:00 | 404 | 12:00
| BIPTC | 408 | 03:00 | 393 | 09:00 | Rahanpur | 417 | 05:00 | 400 | 19:00
| Bogura | 415 | 04:00 | 394 | 19:00 | Rampal | 413 | 04:00 | 384 | 12:00
| Gopalganj | 415 | 05:00 | 389 | 13:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 238 | 05:00 | 221 | 13:00 | Haripur | 239 | 05:00 | 224 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 234 | 04:00 | 224 | 11:00 | Hasnabad | 237 | 05:00 | 225 | 11:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 236 | 04:00 | 223 | 12:00 | Hathazari | 233 | 04:00 | 225 | 11:00
| Ashuganj | 238 | 03:00 | 225 | 12:00 | Ishurdi | 244 | 04:00 | 228 | 19:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 03:00 | 225 | 12:00 | Jhenaidah | 241 | 04:00 | 222 | 13:00
| Baghabari | 243 | 03:00 | 229 | 18:30 | Kaliakoir | 234 | 03:00 | 218 | 12:00 | 230 kV MAX | 248 |  | 248 | 217
| Barapukuria | 227 | 02:00 | 217 | 08:00 | Keranigonj | 237 | 05:00 | 220 | 13:00 | 230 kV MIN | 217 |  | 244 | 218 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 227 | 02:00 | 217 | 08:00 | Khulna(S) | 242 | 05:00 | 221 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 246 | 04:00 | 234 | 12:00 | Madunaghat | 233 | 04:00 | 225 | 12:00 | 132 kV MAX | 142 |  | 142 | 114 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 242 | 04:00 | 226 | 13:00 | Madunaghat-400 | 234 | 05:00 | 225 | 13:00 | 132 kV MIN | 112 |  | 142 | 112 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 239 | 04:00 | 224 | 12:00 | Maniknagar | 239 | 05:00 | 224 | 12:00 | [35 empty] | 6:00
| Bibiana | 231 | 06:00 | 224 | 04:00 | Meghnaghat | 242 | 05:00 | 230 | 12:00 |  | 400 | [33 empty] | 392
| BIPTC | 243 | 04:00 | 226 | 13:00 | Meghnaghat-400 | 240 | 05:00 | 226 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 241 | 04:00 | 229 | 19:00 | Mirsorai | 233 | 05:00 | 221 | 12:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 240 | 04:00 | 227 | 19:00 | Rajshahi | 244 | 05:00 | 225 | 19:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 248 | 03:00 | 243 | 10:00 | Rampal | 239 | 03:00 | 220 | 12:00 |  | 132 |  |  | Ash 400-299274
| BSRM | 233 | 05:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 233 | 02:00 | 221 | 04:00 | Rampura | 239 | 05:00 | 224 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 246 | 05:00 | 230 | 12:00 | Shikalbaha | 232 | 02:00 | 221 | 12:00 |  | kaptai by call 399528
| Fenchuganj | 235 | 03:00 | 229 | 12:00 | Shyampur | 237 | 04:00 | 222 | 12:00
| Ghorashal | 240 | 01:00 | 230 | 12:00 | Siddhirganj | 238 | 01:00 | 229 | 15:00
| Ghorashal-230 | 236 | 04:00 | 221 | 12:00 | Sirajgonj | 247 | 04:00 | 237 | 12:00
| Gopalganj | 246 | 05:00 | 231 | 12:00 | Sreepur | 238 | 05:00 | 222 | 13:00
| GPH | 234 | 05:00 | 222 | 12:00 | Tongi | 234 | 04:00 | 220 | 11:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 138 | 04:00 | 128 | 13:00 | Kurigram | 133 | 01:00 | 115 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 138 | 02:00 | 127 | 13:00 | Kushtia | 141 | 03:00 | 131 | 19:00
| Agrabad | 134 | 04:00 | 127 | 12:00 | Lalbag | 139 | 04:00 | 129 | 12:00
| AKS | 130 | 00:00 | 127 | 09:00 | Lalmonirhat | 131 | 05:00 | 118 | 19:00
| Aminbazar | 137 | 04:00 | 126 | 12:00 | Madanganj | 136 | 01:00 | 128 | 16:00
| Amnura | 141 | 03:00 | 130 | 08:00 | Madaripur | 136 | 03:00 | 129 | 13:00
| Ashuganj | 140 | 00:00 | 135 | 12:00 | Madartek | 137 | 04:00 | 126 | 12:00
| Bagerhat | 140 | 03:00 | 124 | 18:30 | Madunaghat | 134 | 06:00 | 130 | 10:00
| Bajitpur | 136 | 02:00 | 130 | 08:00 | Magura | 142 | 04:00 | 128 | 13:00
| Bakulia | 133 | 03:00 | 128 | 12:00 | Mahasthangarh | 137 | 04:00 | 127 | 08:00
| Banani | 137 | 03:00 | 128 | 12:00 | Manikganj | 134 | 00:00 | 130 | 07:00
| Bangabhaban | 136 | 02:00 | 127 | 12:00 | Maniknagar | 135 | 01:00 | 127 | 12:00
| Barapukuria | 136 | 02:00 | 127 | 08:00 | Matarbari | 127 | 02:00 | 119 | 20:00
| Barguna | 138 | 18:00 | 132 | 13:00 | Matuail | 136.5 | 06:00 | 127 | 12:00
| Barishal | 137 | 04:00 | 128 | 12:00 | Millgate | 138 | 18:30 | 127 | 14:00
| Barishal-230 | 138 | 04:00 | 128 | 12:00 | Mirpur | 136 | 01:00 | 126 | 12:00
| Baroaulia | 133 | 01:00 | 129 | 09:00 | Mirzapur | 136 | 04:00 | 128 | 11:00
| Baroirhat | 131 | 00:00 | 125 | 11:00 | Mithapukur | 134 | 03:00 | 123 | 08:00
| Bashundhara | 138 | 03:00 | 127 | 11:00 | MI_Cement | 138 | 03:00 | 128 | 12:00
| BashundharaCement | 136 | 01:00 | 121 | 19:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 136 | 03:00 | 130 | 13:00 | Mogbazar | 140 | 05:00 | 129 | 12:00
| Benapole | 140 | 03:00 | 124 | 12:00 | Mongla | 138 | 03:00 | 125 | 13:00
| Bhaluka | 130 | 03:00 | 116 | 12:00 | Motijheel | 136 | 02:00 | 127 | 12:00
| Bhandaria | 134 | 03:00 | 126 | 13:00 | Muktagacha | 128 | 00:00 | 116 | 07:00
| Bhangura | 140 | 01:00 | 130 | 19:30 | Munshiganj | 137 | 03:00 | 128 | 12:00
| Bheramara | 140 | 03:00 | 131 | 19:00 | Mymensingh | 126 | 00:00 | 112 | 12:00
| Bheramara(GK) | 140 | 04:00 | 132 | 19:30 | Naogaon | 136 | 03:00 | 126 | 08:00
| Bhulta | 131 | 18:00 | 124 | 12:00 | Narail | 141 | 04:00 | 127 | 13:00
| Bog-Sherpur | 138 | 04:00 | 128 | 19:00 | Narinda | 135 | 01:00 | 127 | 12:00
| Bogura | 136 | 00:00 | 129 | 19:00 | Narshingdi | 132 | 00:00 | 118 | 12:00
| Bogura-230 | 139 | 05:00 | 130 | 09:00 | Natore | 139 | 04:00 | 130 | 19:00
| Brahmanbaria | 133 | 01:00 | 124 | 12:00 | Nawabganj | 138 | 03:00 | 129 | 12:00
| Cantonment | 138 | 04:00 | 128 | 13:00 | Netrakona | 125 | 01:00 | 112 | 11:00
| Chandpur | 130 | 01:00 | 124 | 12:00 | New | 137 | 04:00 | 126 | 12:00
| Chandraghona | 136 | 04:00 | 130 | 10:00 | Niamatpur | 140 | 00:00 | 133 | 08:00
| Chapai | 138 | 01:00 | 131 | 13:00 | Noapara | 140 | 03:00 | 126 | 13:00
| Charsaidpur | 137 | 01:00 | 127 | 13:00 | Pabna | 137 | 04:00 | 127 | 19:00
| Chauddagram | 133 | 03:00 | 124 | 12:00 | Palashbari | 132 | 03:00 | 120 | 08:00
| Chhatak | 137 | 02:00 | 129 | 13:00 | Panchagarh | 136 | 04:00 | 118 | 19:00
| Chowmuhani | 129 | 07:00 | 121 | 12:00 | Patuakhali | 138 | 18:00 | 131 | 13:00
| Chuadanga | 140 | 03:00 | 124 | 13:00 | Payra | 137 | 03:00 | 133 | 12:00
| Coxsbazar | 126 | 02:00 | 120 | 18:30 | PHP | 132 | 04:00 | 123 | 12:00
| Cumilla(N) | 137 | 02:00 | 129 | 12:00 | Postogola | 138 | 00:00 | 130 | 12:00
| Cumilla(S) | 137 | 05:00 | 128 | 12:00 | Purbachal | 138 | 02:00 | 127 | 12:00
| Daudkandi | 136 | 02:00 | 126 | 12:00 | Purbasadipur | 132 | 02:00 | 118 | 18:30
| Dhaka | 137 | 01:00 | 128 | 12:00 | Rahanpur | 140 | 00:00 | 135 | 08:00
| Dhamrai | 135 | 04:00 | 124 | 12:00 | Rahanpur-400 | 141 | 03:00 | 135 | 08:00
| Dhanmondi | 137 | 03:00 | 128 | 13:00 | Rahim | 136 | 04:00 | 126 | 12:00
| Dohazari | 131 | 06:00 | 126 | 12:00 | Rajbari | 136 | 04:00 | 127 | 12:00
| Faridpur | 135 | 01:00 | 129 | 12:00 | Rajendrapur | 133 | 01:00 | 124 | 13:00
| Fatullah | 139 | 04:00 | 128 | 13:00 | Rajshahi | 139 | 04:00 | 131 | 19:00
| Fenchuganj | 142 | 03:00 | 136 | 08:00 | Rajshahi-230 | 141 | 05:00 | 126 | 13:00
| Feni | 130 | 04:00 | 123 | 14:00 | Ramganj | 130 | 06:00 | 122 | 21:00
| Ghatail | 128 | 00:00 | 118 | 14:00 | Rampur | 135 | 05:00 | 127 | 12:00
| Ghorashal | 140 | 01:00 | 132 | 12:00 | Rampura | 137 | 04:00 | 128 | 12:00
| Goalpara | 139 | 04:00 | 126 | 13:00 | Rangamati | 135 | 03:00 | 128 | 12:00
| Gollamari | 140 | 04:00 | 128 | 13:00 | Rangpur | 130 | 03:00 | 120 | 08:00
| Gopalganj | 138 | 03:00 | 127 | 13:00 | Ruppur | 142 | 04:00 | 132 | 18:30
| Gopalganj-400 | 138 | 04:00 | 129 | 13:00 | Saidpur | 133 | 03:00 | 120 | 08:00
| Gulshan | 136 | 03:00 | 127 | 12:00 | Satkhira | 138 | 03:00 | 125 | 13:00
| Halishahar | 133 | 18:00 | 128 | 12:00 | Satmasjid | 138 | 04:00 | 127 | 13:00
| Haripur | 137 | 05:00 | 127 | 12:00 | Savar | 136 | 04:00 | 127 | 11:00
| HaripurSBU | 137 | 05:00 | 127 | 12:00 | SevenRings | 141 | 04:00 | 132 | 13:00
| Hasnabad | 139 | 01:00 | 130 | 11:00 | ShahCement | 137 | 01:00 | 127 | 13:00
| Hathazari | 136 | 04:00 | 131 | 12:00 | Shahjadpur | 140 | 00:00 | 134 | 19:00
| Ishurdi | 142 | 03:00 | 133 | 12:00 | Shahjibazar | 137 | 01:00 | 129 | 12:00
| Jaldhaka | 132 | 04:00 | 117 | 19:00 | Shahmirpur | 133 | 01:00 | 129 | 10:00
| Jamalpur | 127 | 00:00 | 114 | 07:00 | Shariatpur | 137 | 02:00 | 127 | 13:00
| Jashore | 138 | 02:00 | 124 | 13:00 | Sherpur | 125 | 00:00 | 112 | 11:00
| Jhenaidah | 141 | 03:00 | 128 | 13:00 | Shikalbaha | 123 | 01:00 | 117 | 12:00
| Jhenaidah-230 | 142 | 04:00 | 129 | 13:00 | Shikalbaha-230 | 134 | 02:00 | 129 | 12:00
| Joydebpur | 135 | 00:00 | 127 | 12:00 | Shitalakhya | 138 | 03:00 | 128 | 12:00
| Joypurhat | 136 | 01:00 | 126 | 08:00 | Sholosohor | 135 | 05:00 | 128 | 12:00
| Juldah | 131 | 00:00 | 128 | 09:00 | Shyampur | 136 | 00:00 | 130 | 12:00
| Kabirpur | 138 | 00:00 | 124 | 12:00 | Shyampur-230 | 139 | 05:00 | 128 | 12:00
| Kachua | 132 | 02:00 | 124 | 12:00 | Siddhirganj | 137 | 04:00 | 127 | 12:00
| Kaliakoir | 139 | 00:00 | 126 | 12:00 | Sirajganj | 138 | 02:00 | 130 | 18:30
| Kallyanpur | 135 | 03:00 | 126 | 11:00 | Sonargaon | 136 | 02:00 | 127 | 12:00
| Kalurghat | 135 | 04:00 | 129 | 12:00 | Sreemongol | 138 | 02:00 | 131 | 12:00
| Kamrangirchar | 138 | 03:00 | 125 | 12:00 | Sreepur | 130 | 05:00 | 119 | 12:00
| Kaptai | 136 | 2:00 | 125 | 12:00 | Srinagar | 139 | 03:00 | 128 | 13:00
| Kazla | 136 | 03:00 | 126 | 13:00 | SSM | 136 | 01:00 | 122 | 16:00
| Keranigonj | 138 | 05:00 | 128 | 12:00 | Sunamganj | 136 | 02:00 | 128 | 12:00
| Khagrachori | 135 | 05:00 | 128 | 12:00 | Sylhet | 138 | 03:00 | 130 | 13:00
| Khulna | 139 | 05:00 | 125 | 08:00 | Sylhet-132 | 137 | 00:00 | 131 | 13:00
| Khulna(S) | 141 | 05:00 | 127 | 13:00 | Tangail | 130 | 00:00 | 118 | 07:00
| Khulshi | 133 | 04:00 | 126 | 12:00 | Thakurgaon | 134 | 04:00 | 115 | 19:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 132 | 02:00 | 125 | 09:00 | TK | 134 | 07:00 | 129 | 12:00 |  |  | Nos | Nos | Nos
| Kodda | 136 | 01:00 | 128 | 12:00 | Tongi | 139 | 04:00 | 129 | 11:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 135 | 03:00 | 128 | 12:00 | Ullahpara | 140 | 02:00 | 130 | 19:00
| Kulaura | 139 | 00:00 | 135 | 12:00 | Ullon | 136 | 02:00 | 127 | 13:00
[6 empty] | Uttara | 137 | 03:00 | 126 | 12:00
[6 empty] | UttaraNew | 137 | 01:00 | 127 | 12:00
[6 empty] | Zigatola | 140 | 04:00 | 129 | 13:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.