## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-01-2025 | during | 28-01-2025 | during | 28-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 3 | 3 | 97.3 | 97.3 | 5 | 5 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 350 | 401 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 370 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 302 | 315 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 260 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 48 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 17.5 | 18 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 20 | 21 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 18 | 17 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 26 | 8 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 78 | 113 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 55 | 88 | 88 | 88 | 88 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 17 | 0 | 0 | 17 | 17 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.27 | 1564.5 | 1762 | 4550.99 | 4532.99 | 2789.91 | 2771.91
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 161 | 161 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 34 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 64 | 64 | 64 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 13 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.8 | 0 | 3.8 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1220 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 3 | 3 | 0 | 1 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 575 | 575 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 2045 | 2118 | 3391.52 | 3387.72 | 3391.52 | 3387.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 194 | 204 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 36 | 36 | 46.94 | 46.94 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 26 | 25 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 199 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 30 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 40 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 51 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 60 | 62 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | machine problem
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 63 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 50 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 50 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 681 | 826 | 1738.97 | 1678.97 | 1620.2 | 1560.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[8 empty] | during | 0 | during | 0 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 49 | 58 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.48 | 0 | 41 | 0 | 41 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 103.48 | 73 | 644.3 | 601.5 | 434.3 | 391.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 41 | 42 | 43 | 43 | 43 | 43 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 43 | 36 | 44 | 44 | 44 | 44 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 85 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 16 | 25 | 25 | 17 | 17 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 370 | 364 | 375 | 375 | 375 | 375 | FGMO Available, but GT Load set maximum 260MW
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1373 | 1378 | 1418.5 | 1418.5 | 1386.01 | 1386.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 923 | 924 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 185 | 177 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 79.66 | 0 | 74.5 | 0 | 74.5 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1187.66 | 1101 | 3579.5 | 3505 | 1925.5 | 1851
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 173 | 187 | 0 | 0 | 200 | 200 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 136 | 132 | 136 | 136 | 140 | 140 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1060 | 1192 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 265 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.54 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 1875.54 | 2062 | 2178.12 | 2177.12 | 2379 | 2378
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Pond Cleaning.
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 163 | 166 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | -
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 3.55 | 0 | 4.6 | 0 | 4.6 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 616 | 751.12 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 44.35 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 88 | 0 | 92 | 0 | 92 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1331.4 | 1384.62 | 3060.38 | 2913.78 | 3060.38 | 2913.78
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 67 | 69 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 167 | 157 | 150 | 150 | 150 | 150 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5 | 0 | 2.8 | 0 | 2.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 133 | 0 | 148 | 0 | 148 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 396 | 261 | 616.8 | 468 | 616.8 | 468
System Total |  |  |  |  | 29204.66 | 28386.248 | 10557.58 | 10965.62 | 21179.08 | 20683.58 | 17603.62 | 17108.12
Forecast Scenario (28-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9160 |  | 0 |  | 9160
|  |  |  | 1:00 | 8412 |  | 0 |  | 8412
|  |  |  | 2:00 | 8134 |  | 0 |  | 8134
|  |  |  | 3:00 | 7718 |  | 0 |  | 7718
|  |  |  | 4:00 | 7554 |  | 0 |  | 7554
|  |  |  | 5:00 | 7450 |  | 0 |  | 7450
|  |  |  | 6:00 | 7900 |  | 0 |  | 7900
|  |  |  | 7:00 | 8800 |  | 0 |  | 8800
|  |  |  | 8:00 | 9800 |  | 0 |  | 9800
|  |  |  | 9:00 | 10250 |  | 0 |  | 10250
|  |  |  | 10:00 | 9950 |  | 0 |  | 9950
|  |  |  | 11:00 | 10150 |  | 0 |  | 10150
|  |  |  | 12:00 | 10600 |  | 0 |  | 10600
|  |  |  | 13:00 | 10900 |  | 0 |  | 10900
|  |  |  | 14:00 | 10500 |  | 0 |  | 10500
|  |  |  | 15:00 | 9950 |  | 0 |  | 9950
|  |  |  | 16:00 | 9633 |  | 0 |  | 9633
|  |  |  | 17:00 | 9600 |  | 0 |  | 9600
|  |  |  | 18:00 | 10700 |  | 0 |  | 10700
|  |  |  | 18:30 | 10800 |  | 0 |  | 10800
|  |  |  | 19:00 | 11000 |  | 0 |  | 11000
|  |  |  | 19:30 | 11000 |  | 0 |  | 11000
|  |  |  | 20:00 | 10850 |  | 0 |  | 10850
|  |  |  | 21:00 | 10700 |  | 0 |  | 10700
|  |  |  | 22:00 | 10100 |  | 0 |  | 10100
|  |  |  | 23:00 | 9600 |  | 0 |  | 9600
Probable Maximum Temperature: |  |  | 24.60°C
Probable Maximum Demand at Day Peak: |  |  | 10600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 229.411 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:02 hrs on 28-01-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division
Formulas:
Effective Available Gen. on = [Forecasted Available Gen. on]

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-01-2025 | [28 empty] | Date: | 27-01-2025 | [28 empty] | Date: | 27-01-2025 | [28 empty] | Date: | 27-01-2025 | [28 empty] | Date: | 27-01-2025 | [19 empty] | Date: | 27-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [19 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 17 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 300 | 273 | 0 | 0 | 0 | 24 | 260 | 0 | 0 | 0 | 0 | 16 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 576 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 830 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 35 | 0 | 40 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 290 | 300 | 342 | 36 | 42 | 0 | 2 | 130 | 17 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 12 | 5074 | 925 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 153 | 0 | 320 | 0 | 0 | 2.5 | 156 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 75.75 | 940 | 0 | 3935.25 | 9009.25 | 92.24
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 272 | 0 | 0 | 0 | 24 | 260 | 0 | 0 | 0 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 576 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 616 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 25 | 183 | 38 | 0 | 40 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 295 | 280 | 347 | 43 | 42 | -1 | 2 | 130 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 48 | 0 | 0 | 0 | 12 | 4775 | 924 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 157 | 0 | 320 | 0 | 0 | 2.5 | 158 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 74.3 | 900 | 0 | 3705.8 | 8480.8 | 92.23
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 302 | 0 | 0 | 0 | 24 | 260 | 0 | 0 | 0 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 506 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 607 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 203 | 38 | 0 | 40 | 0 | 0 | 17 | 0 | 50 | 0 | 0 | 0 | 310 | 280 | 350 | 43 | 42 | 0 | 2 | 130 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 48 | 0 | 0 | 0 | 12 | 4742 | 782 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 60 | 0 | 414 | 0 | 0 | 0 | 160 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 76.67 | 750 | 0 | 3417.67 | 8159.67 | 92.23
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 264 | 0 | 0 | 0 | 25 | 260 | 0 | 0 | 0 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 504 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 608 | 0 | 43 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 38 | 0 | 45 | 0 | 0 | 15 | 0 | 52 | 0 | 0 | 0 | 310 | 250 | 340 | 43 | 42 | 0 | 2 | 130 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 0 | 0 | 0 | 12 | 4589 | 735 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 163 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 79 | 750 | 0 | 3328 | 7917 | 92.22
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 292 | 0 | 0 | 0 | 26 | 260 | 0 | 0 | 0 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 379 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 606 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 196 | 38 | 0 | 50 | 0 | 0 | 11 | 0 | 48 | 0 | 0 | 0 | 300 | 250 | 367 | 43 | 42 | 0 | 2 | 130 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 0 | 0 | 0 | 12 | 4504 | 735 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 161 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 76 | 550 | 0 | 3129 | 7633 | 92.22
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 286 | 0 | 0 | 0 | 26 | 260 | 0 | 0 | 0 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 375 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 609 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 191 | 38 | 0 | 50 | 0 | 0 | 11 | 0 | 40 | 0 | 0 | 0 | 305 | 240 | 367 | 43 | 42 | 0 | 2 | 130 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 18 | 0 | 0 | 0 | 12 | 4479 | 735 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 157 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 80 | 180 | 0 | 76 | 550 | 0 | 3121 | 7600 | 92.21
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 294 | 0 | 0 | 0 | 26 | 260 | 0 | 0 | 0 | 0 | 14 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 505 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 661 | 0 | 43 | 0 | 199 | 0 | 0 | 0 | 26 | 203 | 38 | 0 | 50 | 0 | 0 | 11 | 0 | 42 | 0 | 0 | 0 | 315 | 240 | 367 | 43 | 42 | 0 | 2 | 163 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 19 | 19 | 0 | 0 | 0 | 12 | 4721 | 735 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 155 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 140 | 220 | 0 | 74.46 | 580 | 0 | 3308.46 | 8029.46 | 92.21
07:00 | 0 | 14 | 6 | 0 | 0 | 0 | 0 | 3 | 359 | 0 | 0 | 0 | 0 | 0 | 30 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 301 | 0 | 0 | 0 | 26 | 260 | 0 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 576 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 780 | 1 | 43 | 0 | 199 | 0 | 0 | 0 | 26 | 193 | 38 | 0 | 50 | 0 | 0 | 11 | 0 | 54 | 0 | 2 | 0 | 305 | 270 | 367 | 43 | 42 | 0 | 2 | 163 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 19 | 46 | 0 | 0 | 0.65 | 20 | 5017.65 | 829 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.58 | 0 | 0 | 496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 123 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.05 | 0 | 157 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 275 | 6 | 140 | 220 | 0 | 75 | 840 | 0 | 3824.14 | 8841.79 | 92.2
08:00 | 0 | 48 | 18 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 68 | 48 | 0 | 0 | 0 | 25 | 17 | 0 | 300 | 261 | 0 | 0 | 0 | 26 | 260 | 0 | 0 | 5 | 0 | 19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 3 | 577 | 0 | 0 | 3 | 0 | 0 | 160 | 0 | 0 | 0 | 1001 | 5 | 43 | 0 | 199 | 0 | 0 | 0 | 26 | 182 | 39 | 9 | 50 | 0 | 0 | 15 | 0 | 52 | 0 | 14 | 0 | 300 | 300 | 367 | 43 | 42 | 0 | 2 | 163 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 19 | 46 | 0 | 0 | 6.94 | 24 | 5336.94 | 923 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5 | 0 | 0 | 716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 7.39 | 123 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.65 | 0 | 150 | 67 | 0 | 3 | 0 | 0 | 0 | 0.6 | 20 | 0.11 | 0 | 307 | 4 | 140 | 220 | 0 | 76 | 1080 | 18 | 4496.25 | 9833.19 | 92.2
09:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 78 | 48 | 0 | 0 | 0 | 35 | 17 | 0 | 300 | 281 | 0 | 0 | 0 | 22 | 260 | 0 | 0 | 12 | 0 | 17.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 3 | 575 | 0 | 0 | 18 | 0 | 0 | 160 | 0 | 0 | 0 | 1100 | 11 | 43 | 0 | 199 | 0 | 0 | 0 | 26 | 182 | 39 | 34 | 45 | 0 | 0 | 15 | 0 | 48 | 0 | 29 | 0 | 315 | 300 | 367 | 43 | 42 | 0 | 2 | 163 | 16 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 19 | 46 | 0 | 1 | 15.59 | 24 | 5558.09 | 923 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.58 | 0 | 0 | 713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 18.69 | 131 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.67 | 2.5 | 116 | 70 | 0 | 10 | 0 | 0 | 0 | 2.3 | 55 | 0.24 | 0 | 307 | 4 | 140 | 220 | 0 | 79 | 1150 | 35 | 4665.98 | 10224.07 | 92.19
10:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 78 | 48 | 0 | 0 | 0 | 35 | 25 | 0 | 320 | 300 | 0 | 0 | 0 | 22 | 260 | 0 | 0 | 18 | 0 | 17.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 3 | 504 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1102 | 15 | 43 | 0 | 199 | 0 | 0 | 0 | 26 | 202 | 39 | 16 | 40 | 0 | 0 | 15 | 0 | 50 | 0 | 42 | 0 | 290 | 320 | 367 | 43 | 42 | 0 | 2 | 120 | 8 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 19 | 49 | 0 | 1 | 28.21 | 24 | 5520.71 | 923 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.1 | 0 | 0 | 617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 31.18 | 134 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.73 | 2.5 | 110 | 66 | 0 | 17 | 0 | 0 | 0 | 3.6 | 94 | 0.39 | 0 | 200 | 4 | 140 | 180 | 0 | 113 | 1050 | 17 | 4438.5 | 9959.21 | 92.19
11:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 78 | 32 | 0 | 0 | 0 | 35 | 25 | 0 | 320 | 300 | 0 | 0 | 0 | 22 | 260 | 0 | 0 | 23 | 0 | 17.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 2 | 503 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1102 | 0 | 43 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 37 | 16 | 40 | 0 | 0 | 17 | 0 | 54 | 0 | 50 | 0 | 310 | 320 | 369 | 40 | 42 | 0 | 2 | 163 | 8 | 0 | 79 | 30 | 0 | 0 | 0 | 0 | 9 | 49 | 0 | 2 | 37.03 | 9 | 5534.53 | 924 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.89 | 0 | 0 | 615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 39.96 | 147 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.38 | 2.5 | 153 | 67 | 0 | 22 | 0 | 0 | 0 | 4.6 | 120 | 0.49 | 0 | 200 | 4 | 140 | 220 | 0 | 152 | 1050 | 17 | 4640.82 | 10175.35 | 92.19
12:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 78 | 32 | 0 | 0 | 0 | 35 | 25 | 0 | 320 | 302 | 0 | 0 | 0 | 18 | 260 | 0 | 0 | 26 | 0 | 17.5 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 4 | 575 | 0 | 0 | 19 | 0 | 0 | 161 | 0 | 0 | 0 | 1220 | 19 | 43 | 0 | 199 | 0 | 0 | 0 | 26 | 194 | 36 | 16 | 40 | 0 | 0 | 17 | 0 | 60 | 0 | 50 | 0 | 315 | 320 | 370 | 43 | 41 | 0 | 2 | 163 | 8 | 0 | 81 | 30 | 0 | 0 | 0 | 0 | 9 | 49 | 0 | 2 | 37.48 | 6 | 5766.98 | 923 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.66 | 0 | 0 | 616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 44.35 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.55 | 2.5 | 167 | 67 | 0 | 24 | 0 | 0 | 0 | 5 | 133 | 0.54 | 0 | 265 | 4 | 136 | 220 | 0 | 173 | 1060 | 17 | 4790.6 | 10557.58 | 92.18
13:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 7 | 0 | 0 | 78 | 32 | 0 | 0 | 0 | 72 | 25 | 0 | 320 | 270 | 0 | 0 | 0 | 13 | 260 | 0 | 0 | 26 | 0 | 15 | 20 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 11 | 575 | 0 | 0 | 21 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 18 | 43 | 0 | 199 | 0 | 0 | 0 | 26 | 182 | 34 | 44 | 40 | 0 | 19 | 17 | 0 | 66 | 0 | 48 | 0 | 310 | 320 | 370 | 43 | 41 | 0 | 2 | 163 | 8 | 0 | 84 | 30 | 0 | 0 | 0 | 0 | 9 | 49 | 0 | 2 | 41.52 | 6 | 5830.52 | 924 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.54 | 0 | 0 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 42.98 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.6 | 2.5 | 164 | 66 | 0 | 21 | 0 | 0 | 0 | 4.9 | 133 | 0.51 | 0 | 307 | 4 | 140 | 220 | 0 | 174 | 1190 | 17 | 5115.03 | 10945.55 | 92.18
14:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 17 | 0 | 0 | 78 | 32 | 0 | 0 | 0 | 72 | 25 | 0 | 320 | 296 | 0 | 0 | 0 | 13 | 260 | 0 | 0 | 22 | 0 | 19.2 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 7 | 503 | 0 | 0 | 32 | 0 | 0 | 161 | 0 | 0 | 0 | 1103 | 15 | 43 | 0 | 199 | 0 | 0 | 0 | 26 | 182 | 35 | 50 | 40 | 0 | 35 | 17 | 0 | 64 | 0 | 48 | 0 | 280 | 320 | 346 | 42 | 42 | 0 | 2 | 120 | 16 | 0 | 84 | 30 | 0 | 0 | 0 | 0 | 9 | 49 | 0 | 1 | 33.47 | 6 | 5631.67 | 924 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.52 | 0 | 0 | 758.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 35.41 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.93 | 2.5 | 160 | 66 | 0 | 20 | 0 | 0 | 0 | 3.9 | 117 | 0.46 | 0 | 251 | 4 | 140 | 180 | 0 | 172 | 1130 | 17 | 4878.09 | 10509.76 | 92.18
15:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 78 | 32 | 0 | 0 | 0 | 17 | 25 | 0 | 320 | 275 | 0 | 0 | 0 | 16 | 260 | 0 | 0 | 14 | 0 | 18.2 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 503 | 0 | 0 | 33 | 0 | 0 | 161 | 0 | 0 | 0 | 1103 | 12 | 43 | 0 | 197 | 0 | 0 | 0 | 26 | 182 | 36 | 16 | 40 | 0 | 35 | 17 | 0 | 62 | 0 | 30 | 0 | 300 | 320 | 335 | 42 | 41 | 0 | 2 | 120 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 49 | 0 | 1 | 19.69 | 6 | 5410.89 | 924 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.63 | 0 | 0 | 621.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 24.05 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.2 | 2.5 | 163 | 67 | 0 | 15 | 0 | 0 | 0 | 2.9 | 85 | 0.33 | 0 | 230 | 4 | 100 | 180 | 0 | 173 | 1080 | 17 | 4556.59 | 9967.48 | 92.17
16:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 0 | 1 | 0 | 56 | 16 | 0 | 0 | 0 | 17 | 25 | 0 | 320 | 316 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 7 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 4 | 503 | 0 | 0 | 33 | 0 | 0 | 161 | 0 | 0 | 0 | 1008 | 6 | 43 | 0 | 187 | 0 | 0 | 0 | 26 | 214 | 36 | 16 | 40 | 0 | 9 | 17 | 0 | 58 | 0 | 14 | 0 | 310 | 320 | 335 | 39 | 42 | 0 | 2 | 120 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 10.58 | 6 | 5283.58 | 924 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.77 | 0 | 0 | 621.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 12.4 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.12 | 2.5 | 160 | 68 | 0 | 7 | 0 | 0 | 0 | 1.6 | 39 | 0.18 | 0 | 230 | 3 | 100 | 180 | 0 | 173 | 1000 | 17 | 4354.65 | 9638.23 | 92.17
17:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 0 | 17 | 0 | 62 | 48 | 0 | 0 | 0 | 17 | 25 | 0 | 320 | 294 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 2 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 4 | 503 | 0 | 0 | 33 | 0 | 0 | 160 | 0 | 0 | 0 | 1180 | 1 | 51 | 0 | 197 | 0 | 0 | 0 | 25 | 195 | 35 | 16 | 40 | 0 | 9 | 17 | 0 | 58 | 0 | 4 | 0 | 320 | 320 | 356 | 33 | 41 | 0 | 2 | 163 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 2.46 | 6 | 5529.46 | 924 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.44 | 0 | 0 | 616.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 3.06 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.28 | 2.5 | 164 | 68 | 0 | 2 | 0 | 0 | 0 | 0.6 | 10 | 0.4 | 0 | 230 | 3 | 132 | 220 | 0 | 171 | 1000 | 17 | 4338.09 | 9867.55 | 92.17
18:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 35 | 17 | 0 | 101 | 48 | 0 | 0 | 0 | 90 | 25 | 0 | 320 | 306 | 0 | 0 | 17 | 17 | 260 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 15 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 11 | 576.7 | 0 | 0 | 33 | 0 | 15 | 160 | 0 | 0 | 0 | 1224 | 0 | 51 | 15 | 197 | 0 | 0 | 0 | 26 | 202 | 35 | 28 | 40 | 4 | 27 | 17 | 0 | 58 | 0 | 0 | 0 | 310 | 320 | 364 | 36 | 42 | 0 | 2 | 163 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 6 | 5958.7 | 924 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.68 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 2.5 | 162 | 69 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 178 | 1060 | 17 | 4632.18 | 10590.88 | 92.16
19:00 | 0 | 55 | 8 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 17 | 17 | 0 | 113 | 48 | 0 | 0 | 0 | 54 | 25 | 0 | 370 | 315 | 0 | 0 | 0 | 17 | 280 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 575 | 0 | 0 | 33 | 0 | 34 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 30 | 197 | 0 | 0 | 0 | 25 | 204 | 36 | 50 | 40 | 51 | 63 | 17 | 0 | 62 | 0 | 0 | 0 | 320 | 320 | 364 | 36 | 42 | 0 | 2 | 163 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 6 | 6157 | 924 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751.12 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 157 | 69 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 187 | 1192 | 17 | 4808.62 | 10965.62 | 92.16
19:30 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 3 | 402 | 0 | 0 | 17 | 17 | 0 | 130 | 48 | 0 | 0 | 0 | 35 | 25 | 0 | 370 | 285 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 575 | 0 | 0 | 33 | 0 | 34 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 60 | 197 | 0 | 0 | 0 | 25 | 182 | 36 | 50 | 40 | 17 | 64 | 17 | 0 | 56 | 0 | 0 | 0 | 295 | 320 | 336 | 36 | 42 | 0 | 2 | 163 | 21 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 6 | 6118 | 923 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751.12 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 160 | 69 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 188 | 1200 | 17 | 4820.62 | 10938.62
20:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 17 | 0 | 132 | 48 | 0 | 0 | 0 | 17 | 25 | 0 | 370 | 290 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 23 | 575 | 0 | 0 | 33 | 0 | 0 | 161 | 0 | 0 | 0 | 1224 | 0 | 51 | 60 | 197 | 0 | 0 | 0 | 26 | 182 | 37 | 50 | 40 | 17 | 26 | 17 | 0 | 56 | 0 | 0 | 0 | 300 | 320 | 336 | 36 | 42 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 6 | 5972 | 924 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752.76 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 160 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 188 | 1192 | 17 | 4781.26 | 10753.26 | 92.16
21:00 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 17 | 0 | 116 | 48 | 0 | 0 | 0 | 0 | 25 | 0 | 370 | 307 | 0 | 0 | 0 | 17 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 575 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 26 | 196 | 37 | 16 | 40 | 0 | 26 | 17 | 0 | 60 | 0 | 0 | 0 | 310 | 320 | 350 | 36 | 42 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 6 | 5861 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750.64 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 161 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 140 | 220 | 0 | 179 | 1192 | 0 | 4764.14 | 10625.14 | 92.15
22:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 17 | 0 | 114 | 32 | 0 | 0 | 0 | 0 | 25 | 0 | 370 | 302 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 575 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 1101 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 26 | 187 | 37 | 0 | 40 | 0 | 0 | 17 | 0 | 62 | 0 | 0 | 0 | 300 | 310 | 335 | 36 | 42 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 6 | 5617 | 923 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 656.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 165 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 140 | 220 | 0 | 179 | 1100 | 0 | 4469.85 | 10086.85 | 92.15
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 355 | 0 | 0 | 0 | 18 | 0 | 114 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 320 | 300 | 0 | 0 | 0 | 18 | 300 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 575 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 34 | 0 | 40 | 0 | 0 | 17 | 0 | 58 | 0 | 0 | 0 | 305 | 280 | 335 | 36 | 42 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 6 | 5427 | 923 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 162 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 179 | 1000 | 0 | 4230.52 | 9657.52 | 92.14
Total KWH | 0 | 890880 | 240480 | 0 | 0 | 0 | 0 | 90954.55 | 9050400 | 0 | 0 | 96120 | 160560 | 0 | 1801584 | 629280 | 0 | 0 | 0 | 558720 | 505800 | 0 | 7823000 | 7098385 | 0 | 0 | 45501 | 482100 | 6622121 | 0 | 0 | 150952 | 0 | 410400 | 473760 | 0 | 0 | 138000 | 0 | 0 | 0 | 169920 | 0 | 0 | 0 | 0 | 0 | 23039 | 971340 | 0 | 527040 | 12683636.36 | 0 | 0 | 351840 | 0 | 78618 | 3813610 | 0 | 0 | 0 | 23574543 | 98145 | 1115409 | 128799 | 4750545.45 | 0 | 0 | 0 | 623040 | 4707000 | 892008 | 502080 | 996040 | 94560 | 348600 | 382160 | 0 | 1302720 | 0 | 336845 | 0 | 7458000 | 7165800 | 8898000 | 953712 | 988000 | 0 | 58176 | 3705300 | 409416 | 0 | 1970880 | 717216 | 0 | 0 | 0 | 0 | 266400 | 1106400 | 0 | 9350 | 234090 | 260640 | 129941915.36 | 21017205 | 4182624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507600 | 0 | 0 | 14435583 | 0 | 0 | 0 | 0 | 0 | 0 | 191424 | 0 | 0 | 0 | 549710 | 0 | 258748 | 3590091 | 0 | 0 | 0 | 330945 | 0 | 10158473 | 0 | 21540 | 43308 | 3829000 | 1585745 | 70694 | 143662 | 0 | 0 | 0 | 30119.64 | 798480 | 3315 | 0 | 5651000 | 137015 | 2930000 | 5165080 | 0 | 3294545 | 24257454.55 | 265200 | 103448561.19 | 233390476.55

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-01-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10557.58 | MW | 12:00 Hr. | Energy Generated |  |  | 233.3905 |  | MKWHr.
| Day Peak Demand |  |  | 10599.58 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.67 |  | MKWHr.
| Evening Peak Generation |  |  | 10965.62 | MW | 19:00 Hr. | Energy Demand |  |  | 234.0605 |  | MKWHr.
| Evening Peak Demand |  |  | 11025.62 | MW | 19:00 Hr. | Maximum Temperature |  |  | 25 |  | °C
| Minimum Generation of the Day |  |  | 7600 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 796.62 |  | MMCFD
| Maximum Generation of the Day |  |  | 10965.62 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.5015 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.5569 | 0 | 4.4231 | 0 | 0 | 0.15095 | 0 | 0 | 37.131 | Gas | 109.2258 | Gas | 389699452.97
| Chattogram Zone |  |  | 4.3407 | 36.2582 | 0.56846 | 0 | 0.97134 | 0.12118 | 0 | 0.16992 | 42.4297 | Coal | 74.8759 | Coal | 503447199.3463
| Cumilla Zone |  |  | 13.4662 | 0 | 1.074 | 0 | 0 | 0.33685 | 1.3027 | 0 | 16.1798 | HFO | 8.2264 | HFO | 154458674.98
| Mymensingh Zone |  |  | 0 | 0 | 1.6334 | 0 | 0 | 0.24344 | 0 | 0 | 1.8769 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.3245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.3245 | Hydro | 0.97134 | Hydro | 97134
| Khulna Zone |  |  | 4.1826 | 0 | 0 | 0 | 0 | 0.5076 | 21.0172 | 0 | 25.7074 | Solar | 3.1656 | Solar | 49557081.384
| Barishal Zone |  |  | 8.2321 | 33.203 | 0.2652 | 0 | 0 | 0.003315 | 0 | 0 | 41.7036 | Import | 36.7555 | Import | 184095119.19
| Rajshahi Zone |  |  | 14.1228 | 0 | 0.19142 | 0 | 0 | 0.83 | 14.4356 | 0 | 29.5798 | Wind | 0.16992 | Wind | 2650752
| Rangpur Zone |  |  | 0 | 5.4147 | 0.070694 | 0 | 0 | 0.97226 | 0 | 0 | 6.4577
| Total |  |  | 109.2258 | 74.8759 | 8.2264 | 0 | 0.97134 | 3.1656 | 36.7555 | 0.16992 | 233.3905
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 389699452.97 |  | Hydro | 97134
|  |  |  | Coal | 503447199.3463 |  | Solar | 49557081.384
|  |  |  | HFO | 154458674.98 |  | Import | 184095119.19
|  |  |  | HSD | 0 |  | Wind | 2650752
[5 empty] | Total: | 128,40,05,413 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West |  |  |  | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.0172 | Peak Hr Flow | 924.00 MW at 19:00 hrs.
Energy Flow from West to East |  |  |  | 8390058 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.4356 | Peak Hr Flow | 751.12 MW at 19:00 hrs.
Power Flow during Peak Demand |  |  |  | 420 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3027 | Peak Hr Flow | 62.00 MW at 19:00 hrs.
Maximum Power Flow |  |  |  | 726 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 36.7555 | Peak Hr Flow | 1737.12 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3975
|  |  |  | Chattogram |  | 0 |  | 1134
|  |  |  | Cumilla |  | 0 |  | 885
|  |  |  | Mymensingh |  | 57 |  | 960
|  |  |  | Sylhet |  | 0 |  | 388
|  |  |  | Khulna |  | 0 |  | 1210
|  |  |  | Barishal |  | 0 |  | 286
|  |  |  | Rajshahi |  | 0 |  | 1072
|  |  |  | Rangpur |  | 0 |  | 749
|  |  |  | Total |  | 57 |  | 10659
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
|  | 7 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1074 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1740.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 15:55 | Candpur (Desh)- Chandpur 132kV Ckt-2 Scheduled S/D from Chandpur 132/33kV end Due to
Annual maintenance
| 08:30 | 03:45 | Kabirpur -Kodda 132kV Ckt-1 Project Work S/D from Kabirpur 132/33kV end Due to Piling
work will be done by G2G Project
| 08:30 | 18:22 | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Chauddagram 132/33kV end Due to Annual
Maintenance at Feni end. and from Feni 132/33kV end Due to For Line Side Isolator
Maintenance.
| 08:44 | 18:06 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to S/D
Instructed By NLDC
| 08:48 | 16:51 | Khulshi-Madunaghat 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to
Shutdown taken by Khulshi Grid substation
| 08:50 | 20:20 | Ishurdi 132/33kV S/S 132 kV Baghabari Line Scheduled S/D Due to annual maintenance in
baghabari side
| 08:53 | 15:01 | Chandraghona-Kaptai 132 kV Ckt-2 Scheduled S/D from Chandraghona 132/33kV end Due to
Annual maintenance Bay.
| 09:05 | 15:07 | Mogbazar 132/33kV S/S GT-2 LT Scheduled S/D Due to Annual Maintenance
| 09:07 | 15:05 | Mogbazar 132/33kV S/S GT-2 HT Scheduled S/D Due to Annual Maintenance
| 09:11 | 15:23 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Scheduled S/D Due to Deadline checking of
CKT-2
| 09:18 |  | Hathazari 230/132/33kV S/S Raojan-02 Scheduled S/D Due to dead line checking
| 09:18 | 14:27 | Chuadanga-Jhenaidah 132 kV Ckt-1 Scheduled S/D from Chuadanga 132/33kV end Due to
Maintenance work and from Jhenaidah 230/132kV end Due to Annual maintenance
| 09:21 | 16:33 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to IDRNPP Project.
| 09:30 | 14:12 | Sylhet (South) S/S Trafo-1 LT Scheduled S/D Due to Annual Maint...Work
| 09:31 | 14:10 | Sylhet (South) S/S Trafo-1 HT Scheduled S/D Due to Annual Maint...Work
| 09:32 | 15:43 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to
Annual Maintenance Work. and from Kishoreganj 132/33kV end Due to For Maintenance work
| 09:38 | 17:38 | Kabirpur -Tongi 132kV Ckt-1 Project Work S/D from Kabirpur 132/33kV end.
| 09:40 |  | Bhulta 400/230kV S/S 230kV Bus-02 Project Work S/D Due to For Project Work by EEGBPSP
Project.
| 09:48 | 18:03 | Ishurdi 230/132kV S/S 230/132 kV T-02 LT Scheduled S/D Due to annual maintenance
| 09:48 | 18:01 | Ishurdi 230/132kV S/S 230/132 kV T-02 HT Scheduled S/D Due to annual maintenance
| 10:02 | 19:15 | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D Due to G to G project work
| 10:07 |  | Rampur 230/132/33 S/S TR-1 LT Scheduled S/D Due to energy meter replacement
| 10:07 | 11:04 | Rampur 230/132/33 S/S TR-1 HT Scheduled S/D Due to energy meter replacement
| 10:10 | 14:22 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT Scheduled S/D Due to PI remove
| 10:11 | 14:22 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 HT Scheduled S/D Due to PI Removed
| 10:23 | 14:04 | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to annual maitenance work
| 10:23 | 14:03 | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to annual maintenance
| 10:24 |  | Bhulta-Haripur 230 kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Ordered by
NLDC. and from Bhulta 400/230kVend.
| 10:39 | 10:47 | Fatullah-Shyampur(New) 132 kV Ckt-2 Tripped from Fatullah 132/33kV end showing 1. 21
Trip 2. Zone-1 Trip relays.
| 10:45 |  | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-1 Scheduled S/D from Rangpur 132/33kV end
Due to Power Pant End maintenance work.
| 11:10 | 12:05 | Rampur 230/132/33 S/S Khulshi-1 Scheduled S/D Due to energy meter replacement
| 11:37 | 13:27 | Palashbari 132/33kV S/S TR2-404T HT Forced S/D Due to Oil leakage maintenance
| 11:37 | 13:28 | Palashbari 132/33kV S/S TR2-404T LT Forced S/D Due to Oil leakage maintenance
| 11:40 | 17:26 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Scheduled S/D Due to Annual maintenance
| 11:40 | 17:26 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Scheduled S/D Due to Annual maintenance
| 11:43 | 13:07 | Patuakhali 132/33kV S/S 405T (T-1) LT Forced S/D Due to জরুরি মেরামত কাজ
| 11:43 | 13:06 | Patuakhali 132/33kV S/S 405T (T-1) HT Forced S/D Due to জরুরি মেরামত কাজ
| 12:09 | 12:36 | Rampur 230/132/33 S/S Khulshi-2 Scheduled S/D Due to energy meter replacement
| 12:19 | 19:19 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Shutdown is taken from Baharampur end
| 14:17 | 16:21 | Sylhet (South) S/S Trafo-2 LT Scheduled S/D Due to Annual maintenance work
| 14:17 | 16:20 | Sylhet (South) S/S Trafo-2 HT Scheduled S/D Due to Annual maintenance work
| 14:26 | 16:25 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 LT Scheduled S/D Due to Annual maintenance
| 14:26 | 16:23 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 HT Scheduled S/D Due to Annual maintenance
| 14:35 | 16:46 | Bogura 132/33kV S/S Transformer-4 LT Scheduled S/D Due to Shut Down for Tan-Delta Test.
| 14:35 | 16:46 | Bogura 132/33kV S/S Transformer-4 HT Scheduled S/D Due to Shut Down for Tan-Delta Test.
|  | 16:29 | Khulna (S)-Rampal Ckt-2 is restored.
|  | 16:29 | Khulna (S)-Rampal Ckt-2 is restored.
|  | 16:53 | Kallyanpur 132/33kV S/S GT-3 (132kV) HT is restored.
|  | 16:54 | Kallyanpur 132/33kV S/S GT-3 (132kV) LT is restored.
|  | 17:20 | Jamalpur 132/33kV S/S Bus-A is restored.
| 17:28 | 20:36 | Jamalpur 132/33kV S/S Bus-B Project Work S/D Due to 132kv B-bus D.S loop connection of
T-2 transformer.
| 17:30 | 18:28 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-1 Project Work S/D from Jamalpur 132/33kV end
Due to 132kv B-bus D.S loop connection of T-2 transformer.
| 19:00 |  | Evening peak Generation is 10965 MW
|  | 20:31 | Jamalpur 132/33kV S/S T-2 HT is restored.
|  | 20:32 | Jamalpur 132/33kV S/S T-2 LT is restored.
| 05:00 |  | Minimum Generation: 7642 MW.
| 06:46 |  | Haripur-Sonargaon 132kV Ckt-1 Forced S/D from Sonargaon 132/33kV end Due to load
control purpose CB open at sonargaon end.
| 06:46 |  | Haripur-Sonargaon 132kV Ckt-2 Forced S/D from Sonargaon 132/33kV end Due to Load
control purpose CB open at Sonargaon end .
| 06:50 |  | Haripur-Madanganj 132kV Ckt-1 Forced S/D from Madanganj 132/33kV end Due to Order by
NLDC for load management purpose
| 06:51 |  | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Forced S/D Due to Order by NLDC
for load management purpose
| 06:53 |  | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to High
temperature junction point Maintenance.
| 07:23 |  | Rajbari 132/33kV S/S Transformer-1 LT Tripped showing 86.1, 86.2, over current, E/F. | [7 empty] | 35.0MW load
|  |  | relays Due to WZPDCL 33kv Sajjankanda feeder fault, R phase LA blast, Y phase DS burn and | [7 empty] | interrup.
disconnect.
| 07:23 | 07:58 | Rajbari 132/33kV S/S Transformer-2 LT Tripped showing 86.1, 86.2, over current, E/F. | [7 empty] | 35.0MW load
|  |  | relays Due to WZPDCL 33kv Sajjankanda feeder fault, R phase LA blast, Y phase DS burn and | [7 empty] | interrup.
disconnect.
| 07:23 | 07:56 | Rajbari 132/33kV S/S Transformer-2 HT Tripped showing 86.1, 86.2, over current, E/F. | [7 empty] | 35.0MW load
|  |  | relays Due to WZPDCL 33kv Sajjankanda feeder fault, R phase LA blast, Y phase DS burn and | [7 empty] | interrup.
disconnect.
| 07:46 |  | Jhenaidah-Khulna 230kV Ckt-1 Scheduled S/D from Jhenaidah 230/132kV end Due to Annual
maintenance and from Khulna(S) 230/132kV end Due to Annual maintenance work
| 07:59 |  | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) LT Scheduled S/D Due to Annual
Maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 3 | 90954.55 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 401 | 9050400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 7823000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 315 | 7098385 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6622121 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | -
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 96120 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 48 | 629280 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 45501 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 410400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 473760 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 505800 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 482100 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 8 | 240480 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 113 | 1801584 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 55 | 890880 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 558720 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 150952 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 17 | 160560 | Alternator-03 under maintenace
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5841.27 | 1762 | 37130997.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 98145 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 351840 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 971340 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 161 | 3813610 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 78618 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 527040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23039 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 138000 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 23574543 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 3 | 169920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12683636.36 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2118 | 42429731.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 204 | 4707000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | schedule outage
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | schedule outage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 36 | 892008 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 25 | 623040 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 4750545.45 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1115409 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 30 | 128799 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 996040 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 94560 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 62 | 1302720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 382160 | machine problem
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 63 | 348600 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 50 | 502080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 336845 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 826 | 16179806.45
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1106400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 266400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 234090 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 260640 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 73 | 1876880
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 42 | 988000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3705300 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 36 | 953712 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 58176 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 717216 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1970880 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 409416 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7458000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 364 | 8898000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7165800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1378 | 32324500
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 924 | 21017205 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 177 | 4182624 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 507600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | S/D due to changing of ST Power Tx Radiators
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1101 | 25707429
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 187 | 3294545 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 137015 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 132 | 2930000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1192 | 24257454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5165080 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 265200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5651000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3315 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2062 | 41703609.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | Shutdown for Pond Cleaning.
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 166 | 3590091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 330945 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 10158473 | -
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 43308 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 191424 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 21540 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 751.12 | 14435583 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 258748 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 549710 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1384.62 | 29579822
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 69 | 1585745 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3829000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30119.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 70694 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 143662 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 798480 | -
Rangpur Area Total |  |  |  |  | 950 | 261 | 6457700.64
Eastern Grid Total |  |  |  |  | 16771.748 | 6157 | 129941915.36
Western Grid Total |  |  |  |  | 11614.5 | 4808.62 | 103448561.19
National Grid Total |  |  |  |  | 28386.248 | 10965.62 | 233390476.55
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7285.2 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3316.3 | MW
i) Dhaka area |  |  | 3975 |  | MW | i) Khulna area |  |  |  | 1210 | MW
ii) Chattogram area |  |  | 1134.2 |  | MW | ii) Barishal area |  |  |  | 285.5 | MW
iii) Cumilla area |  |  | 885 |  | MW | iii) Rajshahi area |  |  |  | 1071.8 | MW
iv) Mymensingh area |  |  | 903 |  | MW | iv) Rangpur area |  |  |  | 749 | MW
v) Sylhet area |  |  | 388 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10601.5 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 59 | 18:30 | 133 | Purbachal | 14 | 13:00
2 | AKSML | 108 | 03:00 | 68 | Jamalpur | 100 | 22:00 | 134 | Purbasadipur | 103 | 18:30
3 | Aftabnagar | 25 | 13:00 | 69 | Jashore | 113 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 69 | 13:00 | 70 | Jhenaidah | 95 | 08:00 | 136 | Rahim | 43 | 13:00
5 | Agrabad | 78 | 13:00 | 71 | Joydebpur | 145 | 12:00 | 137 | Rajbari | 52 | 18:00
6 | Amnura | 46 | 18:30 | 72 | Joypurhat | 47 | 13:00 | 138 | Rajendrapur | 96 | 08:00
7 | Ashuganj | 71 | 13:00 | 73 | Juldah | 10 | 00:00 | 139 | Rajshahi | 74 | 21:00
8 | BSRM | 199 | 02:00 | 74 | KSRM | 31 | 15:00 | 140 | Rajshahi-230 | 66 | 13:00
9 | Bagerhat | 68 | 18:30 | 75 | Kabirpur | 227 | 18:30 | 141 | Ramganj | 84 | 20:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 51 | 19:30 | 142 | Rampur | 21 | 00:00
11 | Bakulia | 62 | 13:00 | 77 | Kallyanpur | 90 | 13:00 | 143 | Rangamati | 13 | 18:00
12 | Banani | 32 | 13:00 | 78 | Kalurghat | 32 | 15:00 | 144 | Rangpur | 95 | 18:30
13 | Bangabhaban | 8 | 11:00 | 79 | Kamrangirchar | 58 | 13:00 | 145 | Ruppur | 4 | 11:00
14 | Barapukuria | 61 | 18:30 | 80 | Kaptai | N/A | N/A | 146 | SSM | 15 | 00:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 91 | 13:00 | 147 | Saidpur | 102 | 12:00
16 | Barishal | 85 | 13:00 | 82 | Keranigonj | 60 | 13:00 | 148 | Satkhira | 96 | 08:00
17 | Barishal-230 | 54 | 18:00 | 83 | Khagrachori | 24 | 18:00 | 149 | Satmasjid | 82 | 14:00
18 | Baroaulia | 58 | 11:00 | 84 | Khulna | 70 | 13:00 | 150 | Savar | 170 | 12:00
19 | Baroirhat | 52 | 18:00 | 85 | Khulshi | 131 | 14:00 | 151 | SevenRings | 19.05 | 15:00
20 | Bashundhara | 136 | 13:00 | 86 | Kishoreganj | 120 | 18:30 | 152 | ShahCement | 32 | 00:00
21 | BashundharaCement | 7 | 12:00 | 87 | Kodda | 257 | 12:00 | 153 | Shahjadpur | 62 | 13:00
22 | Beanibazar | 44 | 19:00 | 88 | Kulaura | 27 | 18:00 | 154 | Shahjibazar | 88 | 19:00
23 | Benapole | 50 | 08:00 | 89 | Kurigram | 59 | 08:00 | 155 | Shahmirpur | 50 | 18:00
24 | Bhaluka | 108 | 09:00 | 90 | Kushtia | 106 | 18:30 | 156 | Shariatpur | 52 | 20:00
25 | Bhandaria | 34 | 21:00 | 91 | Lalbag | 53 | 13:00 | 157 | Sherpur | 110 | 00:00
26 | Bhangura | 26 | 20:00 | 92 | Lalmonirhat | 53 | 18:30 | 158 | Shikalbaha | 20 | 18:00
27 | Bheramara(GK) | 39 | 18:00 | 93 | MI_Cement | 17.5 | 01:00 | 159 | Shitalakhya | 62.8 | 12:00
28 | Bhulta | 234 | 10:00 | 94 | Madanganj | 20 | 13:00 | 160 | Sholosohor | 29 | 18:00
29 | Bog-Sherpur | 64 | 08:00 | 95 | Madaripur | 66 | 18:30 | 161 | Shyampur | 130 | 08:00
30 | Bogura | 112 | 19:00 | 96 | Madartek | 55.58 | 14:00 | 162 | Siddhirganj | 106 | 12:00
31 | Borhanuddin | 54 | 21:00 | 97 | Madunaghat | 37 | 13:00 | 163 | Sirajganj | 84 | 19:00
32 | Brahmanbaria | 102 | 18:30 | 98 | Magura | 46 | 18:30 | 164 | Sonargaon | 83 | 12:00
33 | Cantonment | 72 | 21:00 | 99 | Mahasthangarh | 50 | 08:00 | 165 | Sreemongol | 48 | 18:30
34 | Chandpur | 43 | 18:00 | 100 | Manikganj | 107 | 18:30 | 166 | Sreepur | 79 | 09:00
35 | Chandraghona | 26 | 18:00 | 101 | Maniknagar | 50 | 13:00 | 167 | Srinagar | 30.03 | 14:00
36 | Chapai | 58 | 09:00 | 102 | Matarbari | 36 | 18:30 | 168 | Sunamganj | 38 | 19:00
37 | Charsaidpur | 27 | 12:00 | 103 | Matuail | 58 | 10:00 | 169 | Sylhet | 28 | 13:00
38 | Chauddagram | 42 | 13:00 | 104 | Millgate | 69 | 12:00 | 170 | Sylhet-132 | 78 | 18:00
39 | Chhatak | 23 | 18:00 | 105 | Mirpur | 96 | 13:00 | 171 | TK | 21 | 18:30
40 | Chowmuhani | 143 | 18:30 | 106 | Mirsorai | 9 | 18:00 | 172 | Tangail | 150 | 07:00
41 | Chuadanga | 73 | 18:30 | 107 | Mirzapur | 50 | 14:00 | 173 | Thakurgaon | 73 | 18:30
42 | Coxsbazar | 101 | 18:00 | 108 | Mithapukur | 66 | 08:00 | 174 | Tongi | 107 | 11:00
43 | Cumilla(N) | 113 | 13:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 24 | 08:00
44 | Cumilla(S) | 129 | 14:00 | 110 | Mogbazar | 97.1 | 15:00 | 176 | Ullon | 35 | 13:00
45 | Daudkandi | 106 | 19:30 | 111 | Mongla | 32 | 05:00 | 177 | Uttara | 48 | 13:00
46 | Dhaka | 24 | 13:00 | 112 | Motijheel | 26 | 13:00 | 178 | UttaraNew | 35 | 13:00
47 | Dhamrai | 102 | 13:00 | 113 | Muktagacha | 27 | 07:00 | 179 | Zigatola | 52 | 13:00
48 | Dhanmondi | 92 | 13:00 | 114 | Munshiganj | 65 | 13:00
49 | Dohazari | 70 | 18:30 | 115 | Mymensingh | 169 | 13:00
50 | Faridpur | 106 | 18:30 | 116 | Naogaon | 106 | 09:00
51 | Fatullah | 71 | 12:00 | 117 | Narail | 39 | 18:30
52 | Fenchuganj | 24 | 19:00 | 118 | Narinda | 63.5 | 13:00
53 | Feni | 64 | 13:00 | 119 | Narshingdi | 148 | 19:30
54 | GPH | 98 | 09:00 | 120 | Natore | 103 | 18:30
55 | Ghatail | 33 | 08:00 | 121 | Nawabganj | 30.4 | 13:00
56 | Ghorashal | 8 | 00:00 | 122 | Netrakona | 131 | 07:00
57 | Ghorashal-230 | 66 | 18:00 | 123 | New | 65.2 | 12:00
58 | Goalpara | 26 | 13:00 | 124 | Niamatpur | 82 | 09:00
59 | Gollamari | 50 | 13:00 | 125 | Noapara | 35 | 18:30
60 | Gopalganj | 78.3 | 18:30 | 126 | PHP | 9 | 11:00
61 | Gulshan | 70 | 14:00 | 127 | Pabna | 64 | 18:30
62 | Halishahar | 45 | 11:00 | 128 | Palashbari | 86 | 18:30
63 | HaripurSBU | 186 | 11:00 | 129 | Panchagarh | 46 | 18:30
64 | Hasnabad | 70 | 12:00 | 130 | Patuakhali | 56 | 21:00
65 | Hathazari | 51 | 18:00 | 131 | Payra | 14 | 14:00
66 | Ishurdi | 61 | 18:30 | 132 | Postogola | 42 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9009.25 | 0 |  | 9009.25
1:00 | 8480.8 | 0 |  | 8480.8
2:00 | 8159.67 | 0 |  | 8159.67
3:00 | 7917 | 0 |  | 7917
4:00 | 7633 | 0 |  | 7633
5:00 | 7600 | 0 |  | 7600
6:00 | 8029.46 | 0 |  | 8029.46
7:00 | 8841.79 | 30 |  | 8872.79
8:00 | 9833.19 | 45 |  | 9880.19
9:00 | 10224.07 | 50 |  | 10276.07
10:00 | 9959.21 | 45 |  | 10006.21
11:00 | 10175.35 | 30 |  | 10206.35
12:00 | 10557.58 | 40 |  | 10599.58
13:00 | 10945.55 | 55 |  | 11002.55
14:00 | 10509.76 | 43 |  | 10554.76
15:00 | 9967.48 | 35 |  | 10004.48
16:00 | 9638.23 | 33 |  | 9672.23
17:00 | 9867.55 | 34 |  | 9903.55
18:00 | 10590.88 | 77 |  | 10670.88
19:00 | 10965.62 | 57 |  | 11025.62
19:30 | 10938.62 | 50 |  | 10990.62
20:00 | 10753.26 | 46 |  | 10801.26
21:00 | 10625.14 | 25 |  | 10651.14
22:00 | 10086.85 | 25 |  | 10112.85
23:00 | 9657.52 | 0 |  | 9657.52
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5074 | 3935.25 | 9009.25 | DAILY GENERATION CURVE
00:30 | 4924.5 | 3820.525 | 8745.025
01:00 | 4775 | 3705.8 | 8480.8 | 27-01-2025
01:30 | 4758.5 | 3561.735 | 8320.235
02:00 | 4742 | 3417.67 | 8159.67
02:30 | 4665.5 | 3372.835 | 8038.335
03:00 | 4589 | 3328 | 7917
03:30 | 4546.5 | 3228.5 | 7775
04:00 | 4504 | 3129 | 7633
04:30 | 4491.5 | 3125 | 7616.5
05:00 | 4479 | 3121 | 7600
05:30 | 4600 | 3214.73 | 7814.73
06:00 | 4721 | 3308.46 | 8029.46
06:30 | 4869.325 | 3566.3 | 8435.625
07:00 | 5017.65 | 3824.14 | 8841.79
07:30 | 5177.295 | 4160.195 | 9337.49
08:00 | 5336.94 | 4496.25 | 9833.19
08:30 | 5447.515 | 4581.115 | 10028.63
09:00 | 5558.09 | 4665.98 | 10224.07
09:30 | 5539.4 | 4552.24 | 10091.64
10:00 | 5520.71 | 4438.5 | 9959.21
10:30 | 5527.62 | 4539.66 | 10067.28
11:00 | 5534.53 | 4640.82 | 10175.35
11:30 | 5650.755 | 4715.71 | 10366.465
12:00 | 5766.98 | 4790.6 | 10557.58
12:30 | 5798.75 | 4952.815 | 10751.565
13:00 | 5830.52 | 5115.03 | 10945.55
13:30 | 5731.095 | 4996.56 | 10727.655
14:00 | 5631.67 | 4878.09 | 10509.76
14:30 | 5521.28 | 4717.34 | 10238.62
15:00 | 5410.89 | 4556.59 | 9967.48
15:30 | 5347.235 | 4455.62 | 9802.855
16:00 | 5283.58 | 4354.65 | 9638.23
16:30 | 5406.52 | 4346.37 | 9752.89
17:00 | 5529.46 | 4338.09 | 9867.55
17:30 | 5744.08 | 4485.135 | 10229.215
18:00 | 5958.7 | 4632.18 | 10590.88
18:30 | 6057.85 | 4720.4 | 10778.25
19:00 | 6157 | 4808.62 | 10965.62
19:30 | 6118 | 4820.62 | 10938.62
20:00 | 5972 | 4781.26 | 10753.26
20:30 | 5916.5 | 4772.7 | 10689.2 |  | Executive Engineer
21:00 | 5861 | 4764.14 | 10625.14 |  | Network Operation Division
21:30 | 5739 | 4616.995 | 10355.995
22:00 | 5617 | 4469.85 | 10086.85
22:30 | 5522 | 4350.185 | 9872.185
23:00 | 5427 | 4230.52 | 9657.52

## En-Curve
QF-LDC-12
Date | 27-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2620 | 1731.5 | 925 | 0 | 54 | 602 | 40 | 2797.75 | 0 | 17 | 206 | 0 | 0 | 16 | 0 | DAILY ENERGY CURVE
00:30 | 2614.5 | 1733.5 | 924.5 | 0 | 53 | 507 | 40 | 2670.525 | 0 | 8.5 | 175.5 | 0 | 0 | 18 | 0 | 27-01-2025
01:00 | 2609 | 1735.5 | 924 | 0 | 52 | 412 | 40 | 2543.3 | 0 | 0 | 145 | 0 | 0 | 20 | 0
01:30 | 2624.5 | 1757.25 | 853 | 0 | 51 | 410 | 40 | 2430.485 | 0 | 0 | 135 | 0 | 0 | 19 | 0 | Energy Generated | 233.3905 |  | MKWHr
02:00 | 2640 | 1779 | 782 | 0 | 50 | 408 | 40 | 2317.67 | 0 | 0 | 125 | 0 | 0 | 18 | 0 | Energy not Served | 0.67 |  | MKWHr
02:30 | 2585 | 1755 | 758.5 | 0 | 51 | 412.5 | 40 | 2319.335 | 0 | 0 | 99 | 0 | 0 | 18 | 0 | Total Energy Requirement | 234.0605 |  | MKWHr
03:00 | 2530 | 1731 | 735 | 0 | 52 | 417 | 40 | 2321 | 0 | 0 | 73 | 0 | 0 | 18 | 0
03:30 | 2555.5 | 1742.5 | 735 | 0 | 50 | 417 | 40 | 2155 | 0 | 0 | 63.5 | 0 | 0 | 16.5 | 0
04:00 | 2581 | 1754 | 735 | 0 | 48 | 417 | 40 | 1989 | 0 | 0 | 54 | 0 | 0 | 15 | 0
04:30 | 2572.5 | 1753.5 | 735 | 0 | 44 | 416.5 | 40 | 1986 | 0 | 0 | 54 | 0 | 0 | 15 | 0
05:00 | 2564 | 1753 | 735 | 0 | 40 | 416 | 40 | 1983 | 0 | 0 | 54 | 0 | 0 | 15 | 0
05:30 | 2605 | 1793.5 | 735 | 0 | 41 | 416.5 | 40 | 2112.23 | 0 | 0 | 59.5 | 0 | 0 | 12 | 0
06:00 | 2646 | 1834 | 735 | 0 | 42 | 417 | 40 | 2241.46 | 0 | 0 | 65 | 0 | 0 | 9 | 0
06:30 | 2635 | 1831.5 | 782 | 0 | 48 | 456.5 | 40 | 2505.73 | 3.895 | 34 | 90 | 0 | 0 | 9 | 15
07:00 | 2624 | 1829 | 829 | 0 | 54 | 496 | 40 | 2770 | 7.79 | 68 | 115 | 0 | 0 | 9 | 30
07:30 | 2637 | 1794 | 876 | 0 | 53 | 606 | 40 | 3014 | 52.49 | 91 | 163.5 | 0 | 0 | 10.5 | 37.5
08:00 | 2650 | 1759 | 923 | 0 | 52 | 716 | 40 | 3258 | 97.19 | 114 | 212 | 0 | 0 | 12 | 45
08:30 | 2651 | 1775 | 923 | 0 | 50 | 714.5 | 40 | 3327.5 | 168.63 | 120 | 250.5 | 0 | 0 | 8.5 | 47.5
09:00 | 2652 | 1791 | 923 | 0 | 48 | 713 | 40 | 3397 | 240.07 | 126 | 289 | 0 | 0 | 5 | 50
09:30 | 2671.5 | 1756.5 | 923 | 0 | 49 | 665 | 40 | 3271 | 311.64 | 126 | 273 | 0 | 0 | 5 | 47.5
10:00 | 2691 | 1722 | 923 | 0 | 50 | 617 | 40 | 3145 | 383.21 | 126 | 257 | 0 | 0 | 5 | 45
10:30 | 2688 | 1772.5 | 923.5 | 0 | 52 | 616 | 40 | 3186 | 421.28 | 118 | 244.5 | 0 | 0 | 5.5 | 37.5
11:00 | 2685 | 1823 | 924 | 0 | 54 | 615 | 40 | 3227 | 459.35 | 110 | 232 | 0 | 0 | 6 | 30
11:30 | 2692.5 | 1828 | 923.5 | 0 | 57 | 615.5 | 40 | 3377 | 487.965 | 110 | 230.5 | 0 | 0 | 4.5 | 35
12:00 | 2700 | 1833 | 923 | 0 | 60 | 616 | 40 | 3527 | 516.58 | 110 | 229 | 0 | 0 | 3 | 40
12:30 | 2695 | 1815.75 | 923.5 | 0 | 63 | 693 | 40 | 3613.5 | 515.315 | 110 | 281 | 0 | 0 | 1.5 | 47.5
13:00 | 2690 | 1798.5 | 924 | 0 | 66 | 770 | 40 | 3700 | 514.05 | 110 | 333 | 0 | 0 | 0 | 55
13:30 | 2676.5 | 1759.1 | 924 | 0 | 65 | 764.185 | 40 | 3542.5 | 476.87 | 110 | 366.5 | 0 | 0 | 3 | 49
14:00 | 2663 | 1719.7 | 924 | 0 | 64 | 758.37 | 40 | 3385 | 439.69 | 110 | 400 | 0 | 0 | 6 | 43
14:30 | 2638.5 | 1717.2 | 924 | 0 | 63 | 690.175 | 40 | 3352 | 376.745 | 101 | 330 | 0 | 0 | 6 | 39
15:00 | 2614 | 1714.7 | 924 | 0 | 62 | 621.98 | 40 | 3319 | 313.8 | 92 | 260 | 0 | 0 | 6 | 35
15:30 | 2631 | 1731.6 | 924 | 0 | 60 | 621.53 | 40 | 3230.5 | 234.725 | 84 | 241 | 0 | 0 | 4.5 | 34
16:00 | 2648 | 1748.5 | 924 | 0 | 58 | 621.08 | 40 | 3142 | 155.65 | 76 | 222 | 0 | 0 | 3 | 33
16:30 | 2663 | 1792.5 | 924 | 0 | 58 | 618.945 | 40 | 3229 | 98.445 | 92 | 233 | 0 | 0 | 4 | 33.5
17:00 | 2678 | 1836.5 | 924 | 0 | 58 | 616.81 | 40 | 3316 | 41.24 | 108 | 244 | 0 | 0 | 5 | 34
17:30 | 2689.5 | 1845 | 924 | 0 | 58 | 685.245 | 40 | 3446.35 | 20.62 | 133 | 383 | 0 | 0 | 4.5 | 55.5
18:00 | 2701 | 1853.5 | 924 | 0 | 58 | 753.68 | 40 | 3576.7 | 0 | 158 | 522 | 0 | 0 | 4 | 77
18:30 | 2734 | 1888.5 | 924 | 0 | 60 | 752.4 | 40 | 3643.85 | 0 | 160 | 572 | 0 | 0 | 3.5 | 67
19:00 | 2767 | 1923.5 | 924 | 0 | 62 | 751.12 | 40 | 3711 | 0 | 162 | 622 | 0 | 0 | 3 | 57
19:30 | 2774 | 1876.5 | 923 | 0 | 56 | 751.12 | 40 | 3723 | 0 | 177 | 617 | 0 | 0 | 1 | 50
20:00 | 2774 | 1897.5 | 924 | 0 | 56 | 752.76 | 40 | 3716 | 0 | 151 | 442 | 0 | 0 | 0 | 46
20:30 | 2792.5 | 1915.5 | 923.5 | 0 | 58 | 751.7 | 40 | 3712 | 0 | 151 | 345 | 0 | 0 | 0 | 35.5
21:00 | 2811 | 1933.5 | 923 | 0 | 60 | 750.64 | 40 | 3708 | 0 | 151 | 248 | 0 | 0 | 0 | 25
21:30 | 2792 | 1928 | 923 | 0 | 61 | 703.495 | 40 | 3574 | 0 | 108.5 | 226 | 0 | 0 | 0 | 25
22:00 | 2773 | 1922.5 | 923 | 0 | 62 | 656.35 | 40 | 3440 | 0 | 66 | 204 | 0 | 0 | 0 | 25
22:30 | 2706 | 1901.5 | 923 | 0 | 60 | 616.185 | 40 | 3363 | 0 | 58 | 204.5 | 0 | 0 | 0 | 12.5
23:00 | 2639 | 1880.5 | 923 | 0 | 58 | 576.02 | 40 | 3286 | 0 | 50 | 205 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-01-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 412 | 03:00 | 385 | 12:00 | Kaliakoir | 391 | 02:00 | 373 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 412 | 4:00 | 381 | 12:00 | Madunaghat | 410 | 04:00 | 392 | 13:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 410 | 03:00 | 383 | 12:00 | Meghnaghat | 408 | 03:00 | 381 | 12:00
| Bibiana | 399 | 06:00 | 390 | 12:00 | Payra | 417 | 05:00 | 405 | 12:00
| BIPTC | 408 | 02:00 | 387 | 13:00 | Rahanpur | 416 | 03:00 | 397 | 18:30
| Bogura | 415 | 03:00 | 391 | 18:30 | Rampal | 414 | 05:00 | 383 | 18:30
| Gopalganj | 415 | 05:00 | 388 | 13:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 237 | 03:00 | 220 | 12:00 | Haripur | 234 | 00:00 | 225 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 233 | 04:00 | 223 | 11:00 | Hasnabad | 238 | 09:00 | 223 | 13:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 235 | 02:00 | 220 | 12:00 | Hathazari | 234 | 04:00 | 225 | 16:00
| Ashuganj | 239 | 01:00 | 225 | 12:00 | Ishurdi | 244 | 03:00 | 227 | 18:30 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 239 | 01:00 | 225 | 12:00 | Jhenaidah | 242 | 03:00 | 220 | 13:00
| Baghabari | 243 | 02:00 | 227 | 12:00 | Kaliakoir | 235 | 03:00 | 218 | 12:00 | 230 kV MAX | 248 |  | 248 | 215
| Barapukuria | 227 | 02:00 | 215 | 08:00 | Keranigonj | 237 | 05:00 | 220 | 12:00 | 230 kV MIN | 215 |  | 244 | 218 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 227 | 02:00 | 215 | 08:00 | Khulna(S) | 242 | 05:00 | 220 | 13:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 245 | 03:00 | 234 | 18:30 | Madunaghat | 233 | 05:00 | 223 | 12:00 | 132 kV MAX | 143 |  | 143 | 114 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 242 | 03:00 | 224 | 18:30 | Madunaghat-400 | 234 | 03:00 | 224 | 13:00 | 132 kV MIN | 111 |  | 142 | 111 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 239 | 03:00 | 223 | 12:00 | Maniknagar | 238 | 04:00 | 223 | 12:00 | [35 empty] | 6:00
| Bibiana | 232 | 06:00 | 225 | 07:00 | Meghnaghat | 240 | 00:00 | 230 | 12:00 |  | 400 | [33 empty] | 392
| BIPTC | 243 | 03:00 | 224 | 18:30 | Meghnaghat-400 | 239 | 05:00 | 224 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 241 | 03:00 | 228 | 09:00 | Mirsorai | 234 | 03:00 | 221 | 12:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 240 | 03:00 | 225 | 18:30 | Rajshahi | 242 | 03:00 | 224 | 13:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 248 | 04:00 | 242 | 10:00 | Rampal | 239 | 03:00 | 219 | 12:00 |  | 132 |  |  | Ash 400-299274
| BSRM | 233 | 03:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 234 | 01:00 | 222 | 12:00 | Rampura | 239 | 03:00 | 223 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 246 | 03:00 | 229 | 12:00 | Shikalbaha | 232 | 03:00 | 223 | 13:00 |  | kaptai by call 399528
| Fenchuganj | 236 | 07:00 | 227 | 16:00 | Shyampur | 237 | 03:00 | 220 | 13:00
| Ghorashal | 235 | 08:00 | 230 | 00:00 | Siddhirganj | 236 | 00:00 | 225 | 12:00
| Ghorashal-230 | 236 | 03:00 | 221 | 12:00 | Sirajgonj | 247 | 03:00 | 235 | 18:30
| Gopalganj | 245 | 03:00 | 230 | 13:00 | Sreepur | 239 | 03:00 | 224 | 13:00
| GPH | 233 | 03:00 | 220 | 12:00 | Tongi | 234 | 04:00 | 218 | 11:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 137 | 02:00 | 127 | 12:00 | Kurigram | 131 | 00:00 | 115 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 138 | 02:00 | 128 | 12:00 | Kushtia | 141 | 03:00 | 130 | 18:00
| Agrabad | 134 | 02:00 | 126 | 12:00 | Lalbag | 139 | 03:00 | 129 | 12:00
| AKS | 130 | 00:00 | 125 | 12:00 | Lalmonirhat | 127 | 02:00 | 115 | 08:00
| Aminbazar | 135 | 01:00 | 124 | 12:00 | Madanganj | 136 | 03:00 | 127 | 12:00
| Amnura | 140 | 04:00 | 130 | 08:00 | Madaripur | 137 | 05:00 | 129 | 12:00
| Ashuganj | 140 | 01:00 | 135 | 12:00 | Madartek | 137 | 03:00 | 127 | 12:00
| Bagerhat | 137 | 02:00 | 123 | 18:30 | Madunaghat | 134 | 01:00 | 128 | 12:00
| Bajitpur | 136 | 02:00 | 128 | 18:30 | Magura | 141 | 02:00 | 127 | 13:00
| Bakulia | 133 | 02:00 | 127 | 12:00 | Mahasthangarh | 136 | 03:00 | 124 | 18:30
| Banani | 137 | 07:00 | 127 | 12:00 | Manikganj | 134 | 20:00 | 124 | 12:00
| Bangabhaban | 135 | 01:00 | 125 | 13:00 | Maniknagar | 136 | 05:00 | 125 | 13:00
| Barapukuria | 136 | 01:00 | 126 | 08:00 | Matarbari | 128 | 04:00 | 118 | 18:00
| Barguna | 137 | 04:00 | 133 | 12:00 | Matuail | 136 | 06:00 | 128 | 12:00
| Barishal | 136 | 02:00 | 128 | 11:00 | Millgate | 138 | 02:00 | 127 | 12:00
| Barishal-230 | 135 | 03:00 | 129 | 12:00 | Mirpur | 135 | 03:00 | 125 | 12:00
| Baroaulia | 133 | 00:00 | 128 | 12:00 | Mirzapur | 133 | 01:00 | 126 | 16:00
| Baroirhat | 130 | 19:30 | 122 | 12:00 | Mithapukur | 135 | 04:00 | 121 | 08:00
| Bashundhara | 138 | 03:00 | 127 | 12:00 | MI_Cement | 138 | 05:00 | 128 | 12:00
| BashundharaCement | 136 | 03:00 | 127 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 138 | 05:00 | 131 | 12:00 | Mogbazar | 139 | 05:00 | 126 | 13:00
| Benapole | 139 | 04:00 | 123 | 12:00 | Mongla | 137 | 04:00 | 121 | 18:30
| Bhaluka | 129 | 04:00 | 117 | 12:00 | Motijheel | 135 | 01:00 | 125 | 13:00
| Bhandaria | 133 | 04:00 | 126 | 12:00 | Muktagacha | 123 | 02:00 | 117 | 06:00
| Bhangura | 139 | 02:00 | 129 | 12:00 | Munshiganj | 136 | 03:00 | 128 | 12:00
| Bheramara | 141 | 03:00 | 131 | 18:00 | Mymensingh | 128 | 04:00 | 113 | 13:00
| Bheramara(GK) | 141 | 05:00 | 131 | 18:00 | Naogaon | 136 | 03:00 | 125 | 08:00
| Bhulta | 130 | 00:00 | 123 | 12:00 | Narail | 141 | 04:00 | 125 | 13:00
| Bog-Sherpur | 138 | 03:00 | 126 | 18:30 | Narinda | 136 | 05:00 | 125 | 13:00
| Bogura | 138 | 05:00 | 128 | 18:30 | Narshingdi | 134 | 03:00 | 118 | 18:30
| Bogura-230 | 138 | 03:00 | 129 | 09:00 | Natore | 139 | 06:00 | 129 | 18:00
| Brahmanbaria | 135 | 06:00 | 124 | 18:30 | Nawabganj | 139 | 04:00 | 129 | 12:00
| Cantonment | 139 | 05:00 | 128 | 12:00 | Netrakona | 125 | 03:00 | 111 | 13:00
| Chandpur | 134 | 18:30 | 123 | 17:00 | New | 139 | 02:00 | 127 | 12:00
| Chandraghona | 134 | 00:00 | 128 | 12:00 | Niamatpur | 140 | 03:00 | 132 | 08:00
| Chapai | 138 | 01:00 | 130 | 10:00 | Noapara | 140 | 03:00 | 125 | 13:00
| Charsaidpur | 137 | 03:00 | 128 | 12:00 | Pabna | 138 | 03:00 | 125 | 12:00
| Chauddagram | 133 | 03:00 | 124 | 12:00 | Palashbari | 134 | 05:00 | 120 | 08:00
| Chhatak | 136 | 04:00 | 128 | 18:00 | Panchagarh | 136 | 03:00 | 117 | 08:00
| Chowmuhani | 128 | 06:00 | 120 | 12:00 | Patuakhali | 136 | 08:00 | 132 | 10:00
| Chuadanga | 141 | 04:00 | 121 | 13:00 | Payra | 137 | 03:00 | 133 | 13:00
| Coxsbazar | 128 | 04:00 | 119 | 12:00 | PHP | 132 | 03:00 | 121 | 12:00
| Cumilla(N) | 136 | 01:00 | 128 | 12:00 | Postogola | 137 | 00:00 | 130 | 12:00
| Cumilla(S) | 134 | 04:00 | 127 | 12:00 | Purbachal | 138 | 02:00 | 127 | 12:00
| Daudkandi | 134 | 04:00 | 125 | 12:00 | Purbasadipur | 132 | 03:00 | 116 | 08:00
| Dhaka | 138 | 04:00 | 127 | 12:00 | Rahanpur | 141 | 01:00 | 134 | 14:00
| Dhamrai | 132 | 03:00 | 126 | 16:00 | Rahanpur-400 | 141 | 03:00 | 134 | 09:00
| Dhanmondi | 137 | 04:00 | 127.5 | 12:00 | Rahim | 135 | 04:00 | 127 | 12:00
| Dohazari | 132 | 04:00 | 125 | 12:00 | Rajbari | 136 | 03:00 | 127 | 13:00
| Faridpur | 136 | 03:00 | 128 | 18:30 | Rajendrapur | 134 | 03:00 | 126 | 17:00
| Fatullah | 139 | 04:00 | 129 | 12:00 | Rajshahi | 139 | 05:00 | 130 | 18:00
| Fenchuganj | 139 | 00:00 | 136 | 12:00 | Rajshahi-230 | 140 | 03:00 | 126 | 13:00
| Feni | 130 | 01:00 | 124 | 12:00 | Ramganj | 130 | 03:00 | 120 | 12:00
| Ghatail | 125 | 00:00 | 121 | 07:00 | Rampur | 134 | 04:00 | 127 | 12:00
| Ghorashal | 140 | 05:00 | 133 | 12:00 | Rampura | 137 | 03:00 | 127 | 12:00
| Goalpara | 141 | 03:00 | 127 | 12:00 | Rangamati | 135 | 04:00 | 127 | 12:00
| Gollamari | 140 | 04:00 | 127 | 13:00 | Rangpur | 132 | 03:00 | 120 | 18:30
| Gopalganj | 138 | 03:00 | 126 | 18:30 | Ruppur | 142 | 03:00 | 132 | 18:30
| Gopalganj-400 | 138 | 03:00 | 128 | 13:00 | Saidpur | 133 | 03:00 | 118 | 08:00
| Gulshan | 136 | 03:00 | 127 | 12:00 | Satkhira | 139 | 05:00 | 123 | 13:00
| Halishahar | 133 | 00:00 | 127 | 12:00 | Satmasjid | 138 | 03:00 | 127 | 13:00
| Haripur | 134 | 00:00 | 127 | 12:00 | Savar | 136 | 04:00 | 125 | 11:00
| HaripurSBU | 134 | 01:00 | 127 | 12:00 | SevenRings | 142 | 03:00 | 133 | 13:00
| Hasnabad | 138 | 00:00 | 132 | 12:00 | ShahCement | 137 | 03:00 | 128 | 12:00
| Hathazari | 136 | 04:00 | 130 | 12:00 | Shahjadpur | 140 | 00:00 | 132 | 12:00
| Ishurdi | 143 | 03:00 | 132 | 18:30 | Shahjibazar | 138 | 06:00 | 129 | 18:30
| Jaldhaka | 133 | 04:00 | 114 | 08:00 | Shahmirpur | 134 | 06:00 | 128 | 11:00
| Jamalpur | 122 | 11:00 | 115 | 17:00 | Shariatpur | 137 | 04:00 | 128 | 12:00
| Jashore | 138 | 02:00 | 123 | 13:00 | Sherpur | 121 | 09:00 | 113 | 07:00
| Jhenaidah | 141 | 02:00 | 128 | 13:00 | Shikalbaha | 123 | 03:00 | 116 | 12:00
| Jhenaidah-230 | 142 | 03:00 | 129 | 13:00 | Shikalbaha-230 | 135 | 03:00 | 127 | 12:00
| Joydebpur | 137 | 03:00 | 127 | 12:00 | Shitalakhya | 138 | 05:00 | 128 | 12:00
| Joypurhat | 137 | 03:00 | 124 | 13:00 | Sholosohor | 135 | 05:00 | 127 | 12:00
| Juldah | 132 | 06:00 | 127 | 12:00 | Shyampur | 135 | 00:00 | 129 | 12:00
| Kabirpur | 138 | 19:30 | 124 | 12:00 | Shyampur-230 | 139 | 03:00 | 129 | 12:00
| Kachua | 132 | 02:00 | 124 | 12:00 | Siddhirganj | 137 | 04:00 | 128 | 12:00
| Kaliakoir | 139 | 01:00 | 126 | 12:00 | Sirajganj | 139 | 04:00 | 126 | 18:00
| Kallyanpur | 137 | 3:00 | 125 | 12:00 | Sonargaon | 135 | 01:00 | 126 | 12:00
| Kalurghat | 134 | 02:00 | 128 | 12:00 | Sreemongol | 138 | 03:00 | 131 | 13:00
| Kamrangirchar | 138 | 01:00 | 123 | 12:00 | Sreepur | 130 | 03:00 | 120 | 13:00
| Kaptai | 137 | 3:00 | 132 | 11:00 | Srinagar | 139 | 03:00 | 128 | 12:00
| Kazla | 137 | 05:00 | 125 | 13:00 | SSM | 138 | 00:00 | 128 | 05:00
| Keranigonj | 138 | 03:00 | 128 | 12:00 | Sunamganj | 137 | 03:00 | 127 | 13:00
| Khagrachori | 135 | 03:00 | 127 | 12:00 | Sylhet | 138 | 03:00 | 131 | 13:00
| Khulna | 138 | 04:00 | 125 | 12:00 | Sylhet-132 | 137 | 01:00 | 131 | 12:00
| Khulna(S) | 140 | 03:00 | 127 | 13:00 | Tangail | 128 | 00:00 | 123 | 12:00
| Khulshi | 132 | 03:00 | 127 | 18:00 | Thakurgaon | 133 | 03:00 | 113 | 08:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 132 | 00:00 | 124 | 09:00 | TK | 134 | 04:00 | 128 | 12:00 |  |  | Nos | Nos | Nos
| Kodda | 137 | 14:00 | 125 | 11:00 | Tongi | 138 | 04:00 | 129 | 11:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 135 | 01:00 | 129 | 11:00 | Ullahpara | 139 | 02:00 | 129 | 11:00
| Kulaura | 139 | 00:00 | 135 | 12:00 | Ullon | 136 | 01:00 | 127 | 12:00
[6 empty] | Uttara | 137 | 04:00 | 125 | 12:00
[6 empty] | UttaraNew | 137 | 02:00 | 124 | 12:00
[6 empty] | Zigatola | 140 | 05:00 | 130 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.