## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-01-2025 | during | 29-01-2025 | during | 29-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 3 | 3 | 97.3 | 97.3 | 3 | 3 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 350 | 404 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 350 | 450 | 450 | 350 | 350 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 309 | 282 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 0 | 55 | 0 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 40 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 17.5 | 18 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 21 | 21 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 7.5 | 18 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 25 | 8 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 90 | 127 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 88 | 88 | 88 | 88 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 15 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 24 | 0 | 24 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 18 | 18 | 17 | 17 | 17 | 17 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.27 | 1709 | 1796 | 4510.99 | 4549.99 | 3897.9 | 3936.9
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 148 | 147 | 140 | 140 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 56 | 64 | 56 | 64 | temp problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 17 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 3.7 | 0 | 3.7 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 0 | 0 | 0 | 1 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 577 | 575 | 575 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1892 | 2070 | 3373.42 | 3377.72 | 3383.42 | 3387.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 218 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 37 | 30 | 46.94 | 46.94 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 26 | 25 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 187 | 197 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 30 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 35 | 45 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 62 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 119 | 9 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 16 | 34 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 50 | 0 | 56 | 0 | 56 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 844 | 753 | 1734.97 | 1678.97 | 1616.2 | 1560.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[8 empty] | during | 0 | during | 0 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.8 | 0 | 1.8 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 19 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 35.31 | 0 | 42 | 0 | 42 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 120.31 | 94 | 645.3 | 601.5 | 435.3 | 391.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 36 | 36 | 40 | 40 | 40 | 40 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2 | 2 | 2.5 | 2.5 | 2 | 2 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 15 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 377 | 370 | 385 | 385 | 385 | 385 | FGMO Available, but GT Load set maximum 260MW
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1382 | 1378 | 1424.5 | 1424.5 | 1400.01 | 1400.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 924 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 215 | 191 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 76.98 | 0 | 77 | 0 | 77 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1215.98 | 1115 | 3582 | 3505 | 1978 | 1901
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 186 | 188 | 270 | 330 | 270 | 330 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 0 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 140 | 140 | 136 | 136 | 140 | 140 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1180 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 260 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.54 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 1873.54 | 2059 | 2448.12 | 2507.12 | 2449 | 2508
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 40 | 40 | 40 | 40 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 0 | 0 | 0 | 0 | Shutdown for Pond Cleaning.
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 168 | 162 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | -
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 100 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.49 | 0 | 4.25 | 0 | 4.25 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 613.36 | 757 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 52.93 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 84 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1339.28 | 1460.5 | 3033.03 | 2883.78 | 3033.03 | 2883.78
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 69 | 70 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 153 | 170 | 150 | 150 | 150 | 150 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 36 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.7 | 0 | 2.8 | 0 | 2.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 90 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 130 | 0 | 138 | 0 | 138 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 379.7 | 366 | 622.8 | 482 | 622.8 | 482
System Total |  |  |  |  | 29204.66 | 28386.248 | 10755.81 | 11091.5 | 21375.13 | 21010.58 | 18815.66 | 18451.11
Forecast Scenario (29-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9200 |  | 0 |  | 9200
|  |  |  | 1:00 | 8500 |  | 0 |  | 8500
|  |  |  | 2:00 | 8200 |  | 0 |  | 8200
|  |  |  | 3:00 | 7850 |  | 0 |  | 7850
|  |  |  | 4:00 | 7650 |  | 0 |  | 7650
|  |  |  | 5:00 | 7650 |  | 0 |  | 7650
|  |  |  | 6:00 | 8050 |  | 0 |  | 8050
|  |  |  | 7:00 | 8850 |  | 0 |  | 8850
|  |  |  | 8:00 | 9750 |  | 0 |  | 9750
|  |  |  | 9:00 | 10250 |  | 0 |  | 10250
|  |  |  | 10:00 | 10200 |  | 0 |  | 10200
|  |  |  | 11:00 | 10300 |  | 0 |  | 10300
|  |  |  | 12:00 | 10700 |  | 0 |  | 10700
|  |  |  | 13:00 | 11100 |  | 0 |  | 11100
|  |  |  | 14:00 | 10700 |  | 0 |  | 10700
|  |  |  | 15:00 | 9850 |  | 0 |  | 9850
|  |  |  | 16:00 | 9550 |  | 0 |  | 9550
|  |  |  | 17:00 | 9850 |  | 0 |  | 9850
|  |  |  | 18:00 | 10650 |  | 0 |  | 10650
|  |  |  | 18:30 | 10850 |  | 0 |  | 10850
|  |  |  | 19:00 | 11050 |  | 0 |  | 11050
|  |  |  | 19:30 | 11000 |  | 0 |  | 11000
|  |  |  | 20:00 | 10800 |  | 0 |  | 10800
|  |  |  | 21:00 | 10650 |  | 0 |  | 10650
|  |  |  | 22:00 | 10150 |  | 0 |  | 10150
|  |  |  | 23:00 | 9650 |  | 0 |  | 9650
Probable Maximum Temperature: |  |  | 26.60°C
Probable Maximum Demand at Day Peak: |  |  | 10700.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 11050.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11050.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 231.15 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:02 hrs on 29-01-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division
Formulas:
Effective Available Gen. on = [Forecasted Available Gen. on]

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-01-2025 | [28 empty] | Date: | 28-01-2025 | [28 empty] | Date: | 28-01-2025 | [28 empty] | Date: | 28-01-2025 | [28 empty] | Date: | 28-01-2025 | [19 empty] | Date: | 28-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [19 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 18 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 320 | 260 | 0 | 0 | 0 | 18 | 300 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 575 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 918 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 35 | 0 | 40 | 0 | 0 | 17 | 0 | 54 | 0 | 0 | 0 | 300 | 280 | 336 | 33 | 42 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 6 | 5141 | 924 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 158 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 220 | 0 | 178 | 990 | 0 | 4157.49 | 9298.49 | 92.14
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 18 | 0 | 89 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 280 | 0 | 0 | 0 | 18 | 300 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 575 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 788 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 34 | 0 | 40 | 0 | 0 | 15 | 0 | 50 | 0 | 0 | 0 | 290 | 280 | 335 | 36 | 42 | 0 | 2 | 130 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 9 | 0 | 0 | 0 | 6 | 4895 | 925 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 2.5 | 158 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 184 | 800 | 0 | 3706.14 | 8601.14 | 92.13
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 18 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 300 | 0 | 0 | 0 | 18 | 300 | 0 | 0 | 0 | 0 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 575 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 604 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 192 | 34 | 0 | 40 | 0 | 0 | 15 | 0 | 50 | 0 | 0 | 0 | 285 | 250 | 335 | 36 | 42 | 0 | 2 | 130 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 2 | 4679 | 924 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 2.5 | 155 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 100 | 180 | 0 | 180 | 700 | 0 | 3609.75 | 8288.75 | 92.13
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 18 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 285 | 0 | 0 | 0 | 18 | 300 | 0 | 0 | 0 | 0 | 16 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 404 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 35 | 0 | 45 | 0 | 0 | 11 | 0 | 52 | 0 | 0 | 0 | 290 | 250 | 347 | 36 | 42 | 0 | 2 | 130 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4485 | 735 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 2.5 | 153 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 100 | 180 | 0 | 178.03 | 600 | 0 | 3318.3 | 7803.3 | 92.12
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 18 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 288 | 0 | 0 | 0 | 20 | 300 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 404 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 611 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 185 | 35 | 0 | 45 | 0 | 0 | 11 | 0 | 42 | 0 | 0 | 0 | 295 | 250 | 335 | 36 | 42 | 0 | 2 | 130 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4469 | 734 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 422.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 2.5 | 156 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 180 | 0 | 179 | 500 | 0 | 3203.49 | 7672.49 | 92.12
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 265 | 0 | 0 | 0 | 20 | 300 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 403 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 611 | 0 | 51 | 0 | 158 | 0 | 0 | 0 | 26 | 185 | 35 | 0 | 70 | 0 | 0 | 11 | 0 | 46 | 0 | 0 | 0 | 290 | 250 | 335 | 36 | 42 | 0 | 2 | 130 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4409 | 735 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 2.5 | 157 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 180 | 0 | 173 | 540 | 0 | 3234.29 | 7643.29 | 92.11
06:00 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 292 | 0 | 0 | 0 | 20 | 300 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 576 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 726 | 0 | 51 | 0 | 108 | 0 | 0 | 0 | 26 | 186 | 35 | 0 | 70 | 0 | 0 | 11 | 0 | 50 | 0 | 0 | 0 | 295 | 250 | 335 | 33 | 42 | 0 | 2 | 130 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 4694 | 735 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 2.5 | 157 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 100 | 180 | 0 | 175 | 620 | 0 | 3329.32 | 8023.32 | 92.11
07:00 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 63 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 320 | 275 | 0 | 0 | 0 | 20 | 300 | 0 | 0 | 0 | 0 | 18.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 577 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 873 | 1 | 51 | 0 | 195 | 0 | 0 | 0 | 26 | 183 | 36 | 0 | 50 | 0 | 0 | 5 | 0 | 42 | 0 | 2 | 0 | 295 | 250 | 338 | 33 | 42 | 0 | 2 | 130 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 46 | 0 | 0 | 0.43 | 0 | 4988.93 | 830 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.52 | 0 | 0 | 599.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63 | 122 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.04 | 2.5 | 151 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.01 | 0 | 250 | 0 | 100 | 180 | 0 | 178 | 730 | 0 | 3735.83 | 8724.76 | 92.1
08:00 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 6 | 11 | 0 | 85 | 32 | 0 | 0 | 0 | 35 | 17 | 8 | 320 | 292 | 0 | 0 | 0 | 20 | 300 | 0 | 0 | 6 | 0 | 18 | 22 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 12 | 576 | 0 | 0 | 2 | 0 | 0 | 147 | 0 | 0 | 0 | 1000 | 4 | 51 | 0 | 195 | 0 | 0 | 0 | 26 | 182 | 36 | 2 | 50 | 0 | 14 | 11 | 0 | 46 | 0 | 12 | 0 | 285 | 250 | 345 | 36 | 42 | 0 | 2 | 130 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 46 | 0 | 0 | 5.92 | 6 | 5253.92 | 924 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5 | 0 | 0 | 648.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 7.87 | 127 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.71 | 2.5 | 157 | 70 | 0 | 3 | 0 | 0 | 0 | 0.5 | 24 | 0.11 | 0 | 250 | 0 | 140 | 220 | 0 | 180 | 960 | 8 | 4331.5 | 9585.42 | 92.1
09:00 | 0 | 3 | 25 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 47 | 18 | 0 | 88 | 32 | 0 | 0 | 17 | 35 | 17 | 12 | 320 | 285 | 0 | 0 | 0 | 18.5 | 300 | 0 | 0 | 14 | 0 | 18 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 4 | 520 | 0 | 0 | 18 | 0 | 0 | 147 | 0 | 0 | 0 | 1000 | 10 | 51 | 2 | 195 | 0 | 0 | 0 | 26 | 183 | 33 | 16 | 40 | 0 | 46 | 13 | 0 | 44 | 0 | 25 | 0 | 305 | 305 | 372 | 37 | 42 | 0 | 2 | 163 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 46 | 0 | 1 | 13.96 | 6 | 5495.46 | 925 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.69 | 0 | 0 | 663.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 24.54 | 128 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.1 | 2.5 | 155 | 69 | 0 | 8 | 0 | 0 | 0 | 1.5 | 56 | 0.25 | 0 | 250 | 0 | 140 | 220 | 0 | 182 | 1020 | 17 | 4577.34 | 10072.8 | 92.09
10:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 54 | 18 | 0 | 88 | 32 | 0 | 0 | 54 | 35 | 23 | 12 | 300 | 305 | 0 | 0 | 0 | 18.5 | 300 | 0 | 0 | 21 | 0 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 3 | 505 | 0 | 0 | 19 | 0 | 0 | 147 | 0 | 0 | 0 | 960 | 15 | 51 | 28 | 200 | 0 | 0 | 0 | 26 | 183 | 33 | 16 | 40 | 0 | 109 | 17 | 0 | 58 | 0 | 40 | 0 | 290 | 310 | 372 | 37 | 42 | 0 | 2 | 163 | 15 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 55 | 0 | 1 | 23.1 | 6 | 5644.6 | 925 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.33 | 0 | 0 | 658.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 38.54 | 137 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 3.2 | 2.5 | 120 | 69 | 0 | 13 | 0 | 0 | 0 | 3.4 | 92 | 0.39 | 0 | 200 | 0 | 100 | 220 | 0 | 186 | 960 | 17 | 4501.81 | 10146.41 | 92.09
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 54 | 18 | 0 | 87 | 32 | 0 | 0 | 55 | 17 | 23 | 12 | 300 | 292 | 0 | 0 | 0 | 18.5 | 300 | 0 | 0 | 25 | 0 | 17.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 503 | 0 | 0 | 19 | 0 | 0 | 147 | 0 | 0 | 0 | 950 | 18 | 51 | 60 | 187 | 0 | 0 | 0 | 26 | 203 | 37 | 16 | 35 | 0 | 119 | 17 | 0 | 60 | 0 | 49 | 0 | 310 | 320 | 377 | 33 | 42 | 0 | 2 | 163 | 15 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 19 | 55 | 0 | 2 | 32.57 | 6 | 5735.57 | 925 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.88 | 0 | 0 | 612.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 47.66 | 159 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.07 | 2.5 | 150 | 71 | 0 | 19 | 0 | 0 | 0 | 4.3 | 115 | 0.49 | 0 | 200 | 0 | 100 | 220 | 0 | 187 | 950 | 17 | 4560.46 | 10296.03 | 92.09
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 35 | 18 | 0 | 90 | 40 | 0 | 0 | 55 | 17 | 25 | 15 | 300 | 309 | 0 | 0 | 0 | 7.5 | 300 | 0 | 0 | 29 | 0 | 17.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 5 | 577 | 0 | 0 | 19 | 0 | 0 | 148 | 0 | 0 | 0 | 1100 | 0 | 51 | 30 | 187 | 0 | 0 | 0 | 26 | 218 | 37 | 16 | 35 | 0 | 119 | 17 | 0 | 58 | 0 | 50 | 0 | 315 | 320 | 377 | 36 | 42 | 0 | 2 | 163 | 15 | 0 | 82 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 2 | 35.31 | 6 | 5947.31 | 924 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.98 | 0 | 0 | 613.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 52.93 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.49 | 2.5 | 153 | 69 | 0 | 23 | 0 | 0 | 0 | 4.7 | 130 | 0.54 | 0 | 260 | 0 | 140 | 220 | 0 | 186 | 1050 | 17 | 4808.5 | 10755.81 | 92.08
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 33 | 18 | 0 | 96 | 48 | 0 | 0 | 55 | 17 | 25 | 0 | 300 | 299 | 0 | 0 | 0 | 13.5 | 300 | 0 | 0 | 31 | 0 | 17.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 10 | 577 | 0 | 0 | 19 | 0 | 0 | 148 | 0 | 0 | 0 | 1214 | 17 | 51 | 25 | 195 | 0 | 0 | 0 | 26 | 189 | 37 | 16 | 35 | 0 | 117 | 17 | 0 | 68 | 0 | 51 | 0 | 320 | 320 | 377 | 33 | 41 | 0 | 2 | 120 | 8 | 0 | 85 | 28 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 2 | 32.62 | 6 | 6011.62 | 925 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.85 | 0 | 0 | 702.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 53.8 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.51 | 2.5 | 160 | 70 | 0 | 22 | 0 | 0 | 0 | 4.6 | 122 | 0.5 | 0 | 307 | 0 | 136 | 220 | 0 | 188 | 1180 | 9 | 5069.91 | 11081.53 | 92.08
14:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 17 | 18 | 0 | 96 | 48 | 0 | 0 | 55 | 17 | 25 | 0 | 300 | 277 | 0 | 0 | 0 | 13.5 | 300 | 0 | 0 | 24 | 0 | 17.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 7 | 575 | 0 | 0 | 19 | 0 | 0 | 147 | 0 | 0 | 0 | 1170 | 15 | 51 | 0 | 195 | 0 | 0 | 0 | 26 | 184 | 37 | 16 | 35 | 0 | 118 | 17 | 0 | 70 | 0 | 41 | 0 | 320 | 320 | 377 | 36 | 42 | 0 | 2 | 120 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 2 | 29.05 | 6 | 5894.05 | 925 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.71 | 0 | 0 | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 47.3 | 170 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 3.95 | 2.5 | 155 | 72 | 0 | 17 | 0 | 0 | 0 | 3.9 | 111 | 0.47 | 0 | 250 | 0 | 136 | 180 | 0 | 184 | 1192 | 0 | 4902.83 | 10796.88 | 92.08
15:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 345 | 0 | 0 | 0 | 18 | 0 | 96 | 48 | 0 | 0 | 55 | 0 | 25 | 0 | 300 | 293 | 0 | 0 | 0 | 13.5 | 300 | 0 | 0 | 17 | 0 | 17.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 504 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1025 | 11 | 51 | 0 | 195 | 0 | 0 | 0 | 25 | 183 | 34 | 0 | 40 | 0 | 117 | 17 | 0 | 64 | 0 | 31 | 0 | 285 | 320 | 376 | 36 | 42 | 0 | 2 | 120 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 1 | 21.1 | 6 | 5543.1 | 925 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.76 | 0 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 33.88 | 169 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 2.91 | 2.5 | 158 | 69 | 0 | 13 | 0 | 0 | 0 | 2.7 | 78 | 0 | 0 | 219 | 5 | 136 | 220 | 0 | 185 | 1000 | 0 | 4534.75 | 10077.85 | 92.07
16:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 18 | 0 | 96 | 48 | 0 | 0 | 55 | 0 | 25 | 0 | 300 | 307 | 0 | 0 | 0 | 13.5 | 300 | 0 | 0 | 9 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 454 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1005 | 6 | 51 | 0 | 197 | 0 | 0 | 0 | 25 | 192 | 35 | 0 | 40 | 0 | 116 | 17 | 0 | 50 | 0 | 19 | 0 | 290 | 320 | 322 | 36 | 42 | 0 | 2 | 120 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 19 | 68 | 0 | 1 | 9.87 | 6 | 5416.37 | 925 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.39 | 0 | 0 | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 19.39 | 169 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 1.69 | 2.5 | 159 | 69 | 0 | 8 | 0 | 0 | 0 | 1.5 | 41 | 0.19 | 0 | 200 | 5 | 100 | 180 | 0 | 188 | 900 | 0 | 4229.66 | 9646.03 | 92.07
17:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 334 | 0 | 0 | 0 | 18 | 0 | 96 | 48 | 0 | 0 | 55 | 0 | 25 | 0 | 300 | 277 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 2 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 7 | 505 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1210 | 1 | 51 | 0 | 197 | 0 | 0 | 0 | 25 | 183 | 20 | 0 | 40 | 0 | 55 | 17 | 0 | 56 | 0 | 4 | 0 | 300 | 320 | 370 | 36 | 42 | 0 | 2 | 163 | 23 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 0 | 0 | 2.44 | 6 | 5590.44 | 925 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.45 | 0 | 0 | 661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 3.13 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.28 | 2.5 | 161 | 69 | 0 | 2 | 0 | 0 | 0 | 0.4 | 11 | 0.51 | 0 | 250 | 5 | 136 | 220 | 0 | 186 | 940 | 0 | 4364.27 | 9954.71 | 92.07
18:00 | 0 | 52 | 26 | 0 | 0 | 0 | 0 | 3 | 317 | 0 | 0 | 17 | 18 | 0 | 120 | 82 | 0 | 0 | 55 | 35 | 25 | 0 | 300 | 308 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 575 | 0 | 0 | 19 | 0 | 0 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 64 | 197 | 0 | 0 | 0 | 26 | 202 | 30 | 12 | 45 | 0 | 55 | 17 | 0 | 60 | 0 | 0 | 0 | 295 | 320 | 370 | 36 | 42 | 0 | 2 | 163 | 24 | 0 | 85 | 30 | 0 | 0 | 0 | 1 | 19 | 58 | 0 | 0 | 0 | 6 | 5935 | 925 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 16 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 161 | 69 | 72 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 7 | 136 | 220 | 0 | 187 | 1020 | 10 | 4755.5 | 10690.5 | 92.06
19:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 3 | 404 | 0 | 0 | 17 | 18 | 0 | 127 | 64 | 0 | 0 | 0 | 54 | 25 | 0 | 350 | 282 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 575 | 0 | 0 | 32 | 0 | 0 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 100 | 197 | 0 | 0 | 0 | 25 | 183 | 30 | 34 | 45 | 0 | 9 | 17 | 0 | 62 | 0 | 0 | 0 | 305 | 320 | 370 | 36 | 42 | 0 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 17 | 19 | 58 | 0 | 0 | 0 | 0 | 6091 | 924 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 25 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 170 | 70 | 90 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 188 | 1180 | 17 | 5000.5 | 11091.5 | 92.06
19:30 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 3 | 404 | 0 | 0 | 17 | 18 | 0 | 117 | 64 | 0 | 0 | 0 | 17 | 25 | 0 | 350 | 275 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 575 | 0 | 0 | 33 | 0 | 0 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 100 | 197 | 0 | 0 | 0 | 25 | 183 | 32 | 34 | 45 | 0 | 9 | 17 | 0 | 64 | 0 | 0 | 0 | 295 | 320 | 370 | 36 | 42 | 0 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 17 | 19 | 58 | 0 | 0 | 0 | 0 | 6003 | 924 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 25 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 170 | 71 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 186 | 1200 | 17 | 4940.5 | 10943.5
20:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 3 | 404 | 0 | 0 | 0 | 18 | 0 | 117 | 64 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 297 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 575 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 90 | 197 | 0 | 0 | 0 | 25 | 199 | 32 | 34 | 45 | 0 | 9 | 17 | 0 | 58 | 0 | 0 | 0 | 300 | 320 | 370 | 36 | 42 | 0 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 17 | 19 | 58 | 0 | 0 | 0 | 0 | 5963 | 925 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 170 | 71 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 140 | 220 | 0 | 188 | 1192 | 0 | 4845.5 | 10808.5 | 92.06
21:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 404 | 0 | 0 | 0 | 18 | 0 | 115 | 64 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 297 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 575 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1224 | 0 | 43 | 50 | 197 | 0 | 0 | 0 | 25 | 183 | 32 | 34 | 45 | 0 | 9 | 17 | 0 | 58 | 0 | 0 | 0 | 310 | 300 | 370 | 36 | 42 | 0 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 17 | 19 | 58 | 0 | 0 | 0 | 0 | 5870 | 925 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.84 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 165 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 140 | 220 | 0 | 188 | 1182 | 0 | 4832.34 | 10702.34 | 92.05
22:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 402 | 0 | 0 | 0 | 18 | 0 | 115 | 48 | 0 | 0 | 0 | 0 | 25 | 0 | 350 | 275 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 0 | 17 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 575 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1110 | 0 | 43 | 0 | 197 | 0 | 0 | 0 | 26 | 183 | 29 | 0 | 45 | 0 | 0 | 17 | 0 | 56 | 0 | 0 | 0 | 290 | 300 | 370 | 36 | 42 | 0 | 2 | 163 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 17 | 19 | 58 | 0 | 0 | 0 | 0 | 5597 | 923 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 167 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 140 | 220 | 0 | 186 | 1100 | 0 | 4590.49 | 10187.49 | 92.05
23:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 17 | 0 | 114 | 30 | 0 | 0 | 0 | 0 | 25 | 0 | 300 | 293 | 0 | 0 | 0 | 18 | 335 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 575 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 186 | 32 | 0 | 40 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 290 | 235 | 370 | 36 | 42 | 0 | 2 | 120 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 17 | 19 | 58 | 0 | 0 | 0 | 0 | 5340 | 923 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 664.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 2.5 | 166 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 190 | 1000 | 0 | 4347.52 | 9687.52 | 92.05
Total KWH | 0 | 698880 | 332640 | 0 | 0 | 0 | 0 | 81545.45 | 8787600 | 0 | 0 | 324360 | 388080 | 0 | 2169216 | 827040 | 0 | 0 | 521332 | 264960 | 512280 | 63360 | 7785000 | 7020771 | 0 | 0 | 0 | 385300 | 7464340 | 0 | 0 | 176428 | 0 | 420000 | 506160 | 0 | 0 | 101618 | 0 | 0 | 0 | 5760 | 0 | 0 | 0 | 0 | 0 | 18359 | 958060 | 0 | 545760 | 12974545.46 | 0 | 0 | 205440 | 0 | 0 | 3466851 | 0 | 0 | 0 | 23438179 | 104760 | 1200136 | 528581 | 4533090.9 | 0 | 0 | 0 | 621120 | 4627000 | 807624 | 286080 | 1041000 | 0 | 1079400 | 369800 | 0 | 1309440 | 0 | 321164 | 0 | 7271000 | 6897600 | 8947000 | 855720 | 994000 | 0 | 58128 | 3614973 | 507792 | 0 | 2044800 | 716256 | 0 | 0 | 0 | 95760 | 315600 | 1065600 | 0 | 10200 | 206340 | 82560 | 130956389.81 | 21037818 | 4883616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470880 | 0 | 0 | 14606546 | 0 | 0 | 0 | 0 | 0 | 0 | 290320 | 0 | 0 | 42715 | 550810 | 0 | 325504 | 3707182 | 0 | 0 | 0 | 0 | 0 | 9534545 | 0 | 26880 | 66888 | 3807000 | 1615855 | 241333 | 128822 | 55344 | 0 | 0 | 27654.69 | 777600 | 3390 | 0 | 5477000 | 90383 | 2890000 | 5188450 | 0 | 4392727 | 23056000 | 138000 | 103433262.69 | 234389652.5

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-01-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10755.81 | MW | 12:00 Hr. | Energy Generated |  |  | 234.3897 |  | MKWHr.
| Day Peak Demand |  |  | 10834.81 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.302 |  | MKWHr.
| Evening Peak Generation |  |  | 11091.5 | MW | 19:00 Hr. | Energy Demand |  |  | 235.6917 |  | MKWHr.
| Evening Peak Demand |  |  | 11180.5 | MW | 19:00 Hr. | Maximum Temperature |  |  | 26 |  | °C
| Minimum Generation of the Day |  |  | 7643.29 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 801.75 |  | MMCFD
| Maximum Generation of the Day |  |  | 11091.5 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.5767 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.963 | 0 | 5.5899 | 0 | 0 | 0.17643 | 0 | 0 | 38.7293 | Gas | 108.4437 | Gas | 386501942.4125
| Chattogram Zone |  |  | 4.0126 | 36.4127 | 0.30706 | 0 | 0.95806 | 0.12312 | 0 | 0.00576 | 41.8193 | Coal | 74.7613 | Coal | 495353411.6928
| Cumilla Zone |  |  | 13.1998 | 0 | 1.8941 | 0 | 0 | 0.32116 | 1.3094 | 0 | 16.7244 | HFO | 10.1182 | HFO | 190585954.68
| Mymensingh Zone |  |  | 0 | 0 | 1.5595 | 0 | 0 | 0.21654 | 0 | 0 | 1.7761 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.9073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.9073 | Hydro | 0.95806 | Hydro | 95806
| Khulna Zone |  |  | 4.8836 | 0 | 0 | 0 | 0 | 0.47088 | 21.0378 | 0 | 26.3923 | Solar | 3.1488 | Solar | 48917164.274
| Barishal Zone |  |  | 8.1688 | 32.9257 | 0.138 | 0 | 0 | 0.00339 | 0 | 0 | 41.236 | Import | 36.9538 | Import | 185586085.06
| Rajshahi Zone |  |  | 13.3086 | 0 | 0.33304 | 0 | 0 | 0.90319 | 14.6065 | 0 | 29.1514 | Wind | 0.00576 | Wind | 89856
| Rangpur Zone |  |  | 0 | 5.4229 | 0.29668 | 0 | 0 | 0.93408 | 0 | 0 | 6.6536
| Total |  |  | 108.4437 | 74.7613 | 10.1182 | 0 | 0.95806 | 3.1488 | 36.9538 | 0.00576 | 234.3897
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 386501942.4125 |  | Hydro | 95806
|  |  |  | Coal | 495353411.6928 |  | Solar | 48917164.274
|  |  |  | HFO | 190585954.68 |  | Import | 185586085.06
|  |  |  | HSD | 0 |  | Wind | 89856
[5 empty] | Total: | 130,71,30,220 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West |  |  |  | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.0378 | Peak Hr Flow | 924.00 MW at 19:00 hrs.
Energy Flow from West to East |  |  |  | 7557686000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.6065 | Peak Hr Flow | 757.00 MW at 19:00 hrs.
Power Flow during Peak Demand |  |  |  | 542 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3094 | Peak Hr Flow | 62.00 MW at 19:00 hrs.
Maximum Power Flow |  |  |  | 726 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 36.9538 | Peak Hr Flow | 1743.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 20 |  | 4039
|  |  |  | Chattogram |  | 0 |  | 1186
|  |  |  | Cumilla |  | 0 |  | 878
|  |  |  | Mymensingh |  | 65 |  | 970
|  |  |  | Sylhet |  | 0 |  | 367
|  |  |  | Khulna |  | 0 |  | 1213
|  |  |  | Barishal |  | 0 |  | 290
|  |  |  | Rajshahi |  | 0 |  | 1085
|  |  |  | Rangpur |  | 0 |  | 768
|  |  |  | Total |  | 85 |  | 10796
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282
|  | 7 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1074 |  |  |  | Total | 666.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1740.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:05 | Rajbari 132/33kV S/S Transformer-1 LT is restored.
| 08:13 | 18:23 | Aminbazar-Kallyanpur 132kV Ckt-2 Scheduled S/D from Kallyanpur 132/33kV end Due to Annual
maintenance
| 08:13 | 13:02 | Bagerhat 132/33kV S/S Transformer-2 (413 T) LT Scheduled S/D Due to Install PT-2 on 33kv
bus section-2
| 08:14 | 13:02 | Bagerhat 132/33kV S/S Transformer-2 (413 T) HT Scheduled S/D Due to Install PT-2 on 33kv
bus section-2
| 08:20 | 16:05 | Magura 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to PBS Annual Maintenance of Bus | [7 empty] | 26.0MW load
|  |  | section 2&3 | [7 empty] | interrup.
| 08:20 | 16:02 | Magura 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to PBS Annual Maintenance of Bus | [7 empty] | 26.0MW load
|  |  | section 2&3 | [7 empty] | interrup.
| 08:24 |  | AKSML-Khulshi 132kV Ckt-1 Scheduled S/D from Khulshi 132/33kV end Due to Annual
Maintenance(Dead Line Checking)
| 08:31 | 16:42 | Gopalganj(N)-Madaripur 132kV Ckt-3 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance and from Gopalganj 400/132kVend.
| 08:31 | 16:42 | Madaripur 132/33kV S/S Gopaganj North CKT-04 Scheduled S/D Due to Annual Maintenance
| 08:35 | 17:38 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Hasnabad 230kV Grid SS taken S/D intructed by NLDC
| 08:37 | 14:19 | Sreepur 230/132/33kV S/S 230/132 kV T-2 LT Scheduled S/D Due to Annual Maintenance
| 08:39 | 15:45 | Sirajganj-Ullahpara 132KV Ckt-2 Scheduled S/D from Sirajganj 132/33kV end Due to Annual
maintenance
| 08:39 | 14:18 | Sreepur 230/132/33kV S/S 230/132 kV T-2 HT Scheduled S/D Due to Annual Maintenance
| 08:41 | 16:42 | Gopalganj 400/132kV S/S 132kV Madaripur Ckt-4 Scheduled S/D
| 08:54 | 16:58 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to IDRNPP Project work.
| 09:00 | 17:11 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) HT Scheduled S/D Due to Annual
Maintenance
| 09:12 | 17:34 | Bogura-Natore 132 kV Ckt-1 Scheduled S/D from Bogura 132/33kV end Due to OPGW Maintenance
work.
| 09:13 | 17:35 | Bogura-Natore 132 kV Ckt-2 Scheduled S/D from Bogura 132/33kV end Due to OPGW Maintenance
work.
| 09:19 | 16:08 | Magura 132/33kV S/S T-3 (425T) LT Scheduled S/D Due to PBS Annual Maintenance of Bus | [7 empty] | 26.0MW load
|  |  | section 2&3 | [7 empty] | interrup.
| 09:20 | 14:25 | Cumilla(N)-Cumilla(S) 132 kV Ckt-1 Scheduled S/D from Cumilla(S) 132/33kV end Due to
Annual maintenance
| 09:27 | 11:31 | Madanganj 132/33kV S/S Madanganj -DPDC Char sayedpur 132k Ckt-2 Forced S/D Due to Port
Head Blue Phase grounding emergency repair maintenance for red hot.
| 09:51 | 17:21 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to Dead line cheaking
of savar ss end
| 10:10 | 18:25 | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D
| 10:10 | 16:18 | Tongi 230/132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintenance work
| 10:10 | 16:17 | Tongi 230/132/33kV S/S T-3 HT Scheduled S/D Due to Annual maintenance work
| 10:16 | 19:59 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Shutdown is taken from Baharampur end
| 10:55 | 15:37 | Faridpur 132/33kV S/S Transformer-3 HT Tripped showing Micom relays Due to 33kv xlpe
cable blast
| 10:55 |  | Faridpur 132/33kV S/S Transformer-3 LT Tripped showing Micom relays Due to 33 kv xlpe
blast
| 11:10 | 13:29 | Lalmonirhat 132/33kV S/S Transformer T-2 415T LT Scheduled S/D Due to T2 Transformer s/d | [7 empty] | 14.0MW load
|  |  | for CT, PT Test. | [7 empty] | interrup.
| 11:10 | 13:29 | Lalmonirhat 132/33kV S/S Transformer T-2 415T HT Scheduled S/D Due to T2 Transformer s/d | [7 empty] | 14.0MW load
|  |  | for CT, PT Test. | [7 empty] | interrup.
| 11:17 | 16:52 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Scheduled S/D Due to Annual maintenance
|  | 11:25 | Haripur-Meghnaghat 230kV Ckt-2 is restored.
|  | 11:30 | Haripur-Madanganj 132kV Ckt-1 is restored.
|  | 11:30 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 is restored.
|  | 11:37 | Haripur-Sonargaon 132kV Ckt-1 is restored.
|  | 11:38 | Haripur-Sonargaon 132kV Ckt-2 is restored.
| 11:42 |  | Savar 132/33kV S/S Main Bus Scheduled S/D Due to Interlock implement work.
| 12:00 |  | Day Peak Generation = 10,755MW
| 12:42 | 00:43 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to Due to low Grid voltage . | [7 empty] | 1.0MW load
interrup.
| 12:42 |  | Rampal 400/230kV S/S Gopalganj Line-2 Reactor Forced S/D Due to Due to low Grid voltage . | [7 empty] | 1.0MW load
interrup.
| 12:42 | 00:26 | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due to low Grid voltage . | [7 empty] | 1.0MW load
interrup.
| 13:11 | 15:28 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Scheduled S/D Due to Energy Meter | [7 empty] | 1.0MW load
|  |  | Replacement (132KV Side) | [7 empty] | interrup.
| 13:11 | 15:31 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Scheduled S/D Due to Energy Meter | [7 empty] | 1.0MW load
|  |  | Replacement (132KV Side) | [7 empty] | interrup.
| 14:25 | 17:09 | Rampura 230/132kV S/S Auto Transformer - 02 LT Scheduled S/D Due to The project work to
remove the upper jack BUS of the Auto TX-02.
|  | 14:49 | Jhenaidah-Khulna 230kV Ckt-1 is restored.
| 15:06 | 16:13 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT Forced S/D Due to Red Hot Maintenance
| 15:08 | 16:11 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) HT Forced S/D Due to Red Hot Maintenance
|  | 15:18 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-1 is restored.
|  | 17:12 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) LT is restored.
| 19:30 |  | Bogura(west) to Ruppur Nuclear Power Plant Circuit (400 KV single ckt) First Time
synchronize at 19:30
| 20:02 | 20:08 | Bhulta-Haripur 230 kV Ckt-2 Tripped from Haripur 230/132kV end showing No Relay relays
Due to Unknown
| 00:00 |  | Ashuganj 420 MW CCPP(East) GT Forced Shutdown with remarks:- None
| 00:00 |  | Ashuganj 420 MW CCPP(East) ST Forced Shutdown with remarks:- None
|  | 00:24 | Bhulta-Haripur 230 kV Ckt-1 is restored.
| 05:00 |  | Minimum Generation is 7501 MW
| 07:52 |  | Jhenaidah-Khulna 230kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end Due to Annual
Maintenance Work. and from Jhenaidah 230/132kV end Due to As per ALDC order
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 3 | 81545.45 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 404 | 8787600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 7785000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 282 | 7020771 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7464340 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 324360 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 827040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 521332 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 420000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 506160 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 25 | 512280 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 18 | 385300 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 8 | 332640 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 127 | 2169216 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 698880 | Partial Shutdown due to maintenance
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 63360 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 264960 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 176428 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 18 | 388080 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 5841.27 | 1796 | 38729292.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 104760 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 205440 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 958060 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 147 | 3466851 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 17 | 545760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 18359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 101618 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 23438179 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 0 | 5760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12974545.46 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 2070 | 41819332.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4627000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 30 | 807624 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 25 | 621120 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 197 | 4533090.9 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1200136 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 528581 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 45 | 1041000 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 0 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 62 | 1309440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 369800 | machine problem
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 1079400 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 286080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 321164 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 753 | 16724435.9
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1065600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 19 | 315600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 206340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 82560 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 95760 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 94 | 1776060
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 42 | 994000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3614973 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 36 | 855720 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 2 | 58128 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 716256 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2044800 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 507792 | Gas shortage
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7271000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 370 | 8947000 | FGMO Available, but GT Load set maximum 260MW
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 6897600 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1378 | 31907269
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 924 | 21037818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 191 | 4883616 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 470880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1115 | 26392314
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 188 | 4392727 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 90383 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 140 | 2890000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1180 | 23056000 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5188450 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 138000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5477000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3390 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2059 | 41235950
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | Shutdown for Pond Cleaning.
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 162 | 3707182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9534545 | -
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 66888 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 42715 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 290320 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26880 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 757 | 14606546 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 325504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 550810 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1460.5 | 29151390
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 70 | 1615855 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 3807000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 36 | 55344 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 27654.69 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 241333 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 128822 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 777600 | -
Rangpur Area Total |  |  |  |  | 950 | 366 | 6653608.69
Eastern Grid Total |  |  |  |  | 16771.748 | 6091 | 130956389.81
Western Grid Total |  |  |  |  | 11614.5 | 5000.5 | 103433262.69
National Grid Total |  |  |  |  | 28386.248 | 11091.5 | 234389652.5
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7354.55 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3356 | MW
i) Dhaka area |  |  | 4018.55 |  | MW | i) Khulna area |  |  |  | 1213 | MW
ii) Chattogram area |  |  | 1186 |  | MW | ii) Barishal area |  |  |  | 290 | MW
iii) Cumilla area |  |  | 878 |  | MW | iii) Rajshahi area |  |  |  | 1085 | MW
iv) Mymensingh area |  |  | 905 |  | MW | iv) Rangpur area |  |  |  | 768 | MW
v) Sylhet area |  |  | 367 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10710.55 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 62 | 18:30 | 133 | Purbachal | 15 | 13:00
2 | AKSML | 106 | 08:00 | 68 | Jamalpur | 88 | 00:00 | 134 | Purbasadipur | 108 | 13:00
3 | Aftabnagar | 24 | 12:00 | 69 | Jashore | 111 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 76 | 13:00 | 70 | Jhenaidah | 96 | 08:00 | 136 | Rahim | 39 | 11:00
5 | Agrabad | 66 | 18:00 | 71 | Joydebpur | 137 | 12:00 | 137 | Rajbari | 54 | 18:30
6 | Amnura | 46 | 08:00 | 72 | Joypurhat | 46 | 09:00 | 138 | Rajendrapur | 100 | 13:00
7 | Ashuganj | 68 | 13:00 | 73 | Juldah | 11 | 10:00 | 139 | Rajshahi | 77 | 20:00
8 | BSRM | 196 | 22:00 | 74 | KSRM | 37 | 19:00 | 140 | Rajshahi-230 | 67 | 13:00
9 | Bagerhat | 68 | 18:30 | 75 | Kabirpur | 225 | 09:00 | 141 | Ramganj | 82 | 20:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 51 | 18:00 | 142 | Rampur | 23 | 23:00
11 | Bakulia | 63 | 18:00 | 77 | Kallyanpur | 63 | 13:00 | 143 | Rangamati | 13 | 18:00
12 | Banani | 30 | 13:00 | 78 | Kalurghat | 30 | 11:00 | 144 | Rangpur | 97 | 18:00
13 | Bangabhaban | 8 | 12:00 | 79 | Kamrangirchar | 52.4 | 19:00 | 145 | Ruppur | 4.2 | 11:00
14 | Barapukuria | 60 | 19:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 14 | 01:00
15 | Barguna | 14 | 18:30 | 81 | Kazla | 85 | 13:00 | 147 | Saidpur | 102 | 09:00
16 | Barishal | 95 | 13:00 | 82 | Keranigonj | 62 | 13:00 | 148 | Satkhira | 90 | 08:00
17 | Barishal-230 | 54 | 18:30 | 83 | Khagrachori | 33 | 18:00 | 149 | Satmasjid | 84 | 14:00
18 | Baroaulia | 54 | 08:00 | 84 | Khulna | 67 | 19:30 | 150 | Savar | 155 | 12:00
19 | Baroirhat | 54 | 13:00 | 85 | Khulshi | 146 | 20:00 | 151 | SevenRings | 6.75 | 13:00
20 | Bashundhara | 136 | 13:00 | 86 | Kishoreganj | 122 | 14:00 | 152 | ShahCement | 24 | 16:00
21 | BashundharaCement | 12 | 12:00 | 87 | Kodda | 260 | 11:00 | 153 | Shahjadpur | 58 | 18:30
22 | Beanibazar | 44 | 18:00 | 88 | Kulaura | 27 | 18:30 | 154 | Shahjibazar | 82 | 19:30
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 59 | 08:00 | 155 | Shahmirpur | 49 | 15:00
24 | Bhaluka | 116 | 08:00 | 90 | Kushtia | 110 | 13:00 | 156 | Shariatpur | 52 | 21:00
25 | Bhandaria | 34 | 20:00 | 91 | Lalbag | 51 | 13:00 | 157 | Sherpur | 118 | 22:00
26 | Bhangura | 28 | 18:30 | 92 | Lalmonirhat | 53 | 18:30 | 158 | Shikalbaha | 20 | 11:00
27 | Bheramara(GK) | 41 | 18:30 | 93 | MI_Cement | 17.6 | 13:00 | 159 | Shitalakhya | 62.8 | 12:00
28 | Bhulta | 240.5 | 14:00 | 94 | Madanganj | 20 | 12:00 | 160 | Sholosohor | 29 | 16:00
29 | Bog-Sherpur | 66 | 09:00 | 95 | Madaripur | 67 | 20:00 | 161 | Shyampur | 162 | 13:00
30 | Bogura | 113 | 19:00 | 96 | Madartek | 62.02 | 13:00 | 162 | Siddhirganj | 98 | 12:00
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 34 | 13:00 | 163 | Sirajganj | 84 | 19:00
32 | Brahmanbaria | 102 | 18:30 | 98 | Magura | 55 | 18:00 | 164 | Sonargaon | 88 | 09:00
33 | Cantonment | 81 | 13:00 | 99 | Mahasthangarh | 52 | 09:00 | 165 | Sreemongol | 47 | 18:30
34 | Chandpur | 43 | 13:00 | 100 | Manikganj | 110 | 21:00 | 166 | Sreepur | 84 | 15:00
35 | Chandraghona | 26 | 18:00 | 101 | Maniknagar | 50 | 13:00 | 167 | Srinagar | 29.4 | 21:00
36 | Chapai | 67 | 12:00 | 102 | Matarbari | 33 | 18:00 | 168 | Sunamganj | 40 | 18:00
37 | Charsaidpur | 73 | 11:00 | 103 | Matuail | 60 | 12:00 | 169 | Sylhet | 24 | 18:30
38 | Chauddagram | 42 | 13:00 | 104 | Millgate | 63 | 11:00 | 170 | Sylhet-132 | 80 | 18:00
39 | Chhatak | 23 | 18:00 | 105 | Mirpur | 96 | 13:00 | 171 | TK | 21 | 18:00
40 | Chowmuhani | 141 | 18:00 | 106 | Mirsorai | 8 | 11:00 | 172 | Tangail | 156 | 18:00
41 | Chuadanga | 75 | 13:00 | 107 | Mirzapur | 34 | 07:00 | 173 | Thakurgaon | 82 | 18:30
42 | Coxsbazar | 100 | 18:00 | 108 | Mithapukur | 68 | 18:00 | 174 | Tongi | 103 | 08:00
43 | Cumilla(N) | 110 | 13:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 23 | 08:00
44 | Cumilla(S) | 134 | 13:00 | 110 | Mogbazar | 88.3 | 14:00 | 176 | Ullon | 35 | 13:00
45 | Daudkandi | 102 | 18:00 | 111 | Mongla | 35 | 12:00 | 177 | Uttara | 52 | 13:00
46 | Dhaka | 26 | 13:00 | 112 | Motijheel | 27 | 13:00 | 178 | UttaraNew | 35 | 13:00
47 | Dhamrai | 110 | 09:00 | 113 | Muktagacha | 29 | 15:00 | 179 | Zigatola | 52 | 13:00
48 | Dhanmondi | 84.5 | 13:00 | 114 | Munshiganj | 79 | 12:00
49 | Dohazari | 68 | 19:30 | 115 | Mymensingh | 180 | 18:30
50 | Faridpur | 106 | 19:00 | 116 | Naogaon | 100 | 08:00
51 | Fatullah | 72 | 12:00 | 117 | Narail | 40 | 18:30
52 | Fenchuganj | 25 | 18:00 | 118 | Narinda | 60 | 13:00
53 | Feni | 64 | 14:00 | 119 | Narshingdi | 143 | 19:30
54 | GPH | 101 | 00:00 | 120 | Natore | 106 | 13:00
55 | Ghatail | 40 | 18:00 | 121 | Nawabganj | 32.4 | 13:00
56 | Ghorashal | 8 | 00:00 | 122 | Netrakona | 139 | 08:00
57 | Ghorashal-230 | 66 | 18:00 | 123 | New | 88.3 | 12:00
58 | Goalpara | 22 | 12:00 | 124 | Niamatpur | 83 | 13:00
59 | Gollamari | 58 | 13:00 | 125 | Noapara | 35 | 18:30
60 | Gopalganj | 79 | 18:30 | 126 | PHP | 8 | 04:00
61 | Gulshan | 72 | 13:00 | 127 | Pabna | 65 | 18:30
62 | Halishahar | 39 | 15:00 | 128 | Palashbari | 88 | 18:30
63 | HaripurSBU | 177 | 09:00 | 129 | Panchagarh | 44 | 18:30
64 | Hasnabad | 70 | 18:30 | 130 | Patuakhali | 55.5 | 21:00
65 | Hathazari | 52 | 13:00 | 131 | Payra | 14 | 13:00
66 | Ishurdi | 62 | 18:30 | 132 | Postogola | 43 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9298.49 | 0 |  | 9298.49
1:00 | 8601.14 | 49 |  | 8652.14
2:00 | 8288.75 | 26 |  | 8315.75
3:00 | 7803.3 | 25 |  | 7829.3
4:00 | 7672.49 | 25 |  | 7698.49
5:00 | 7643.29 | 25 |  | 7669.29
6:00 | 8023.32 | 45 |  | 8070.32
7:00 | 8724.76 | 70 |  | 8797.76
8:00 | 9585.42 | 85 |  | 9674.42
9:00 | 10072.8 | 193 |  | 10274.8
10:00 | 10146.41 | 102 |  | 10253.41
11:00 | 10296.03 | 75 |  | 10374.03
12:00 | 10755.81 | 76 |  | 10834.81
13:00 | 11081.53 | 80 |  | 11165.53
14:00 | 10796.88 | 74 |  | 10873.88
15:00 | 10077.85 | 16 |  | 10094.85
16:00 | 9646.03 | 17 |  | 9664.03
17:00 | 9954.71 | 17 |  | 9972.71
18:00 | 10690.5 | 48 |  | 10740.5
19:00 | 11091.5 | 85 |  | 11180.5
19:30 | 10943.5 | 74 |  | 11020.5
20:00 | 10808.5 | 69 |  | 10880.5
21:00 | 10702.34 | 60 |  | 10765.34
22:00 | 10187.49 | 40 |  | 10229.49
23:00 | 9687.52 | 0 |  | 9687.52
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 28-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2634 | 1830.5 | 924 | 0 | 54 | 568.99 | 40 | 3039 | 0 | 17 | 191 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2594 | 1795.5 | 924.5 | 0 | 52 | 492.315 | 40 | 2882 | 0 | 8.5 | 161 | 0 | 0 | 0 | 24.5 | 28-01-2025
01:00 | 2554 | 1760.5 | 925 | 0 | 50 | 415.64 | 40 | 2725 | 0 | 0 | 131 | 0 | 0 | 0 | 49
01:30 | 2547 | 1767 | 924.5 | 0 | 50 | 418.445 | 40 | 2579.5 | 0 | 0 | 118.5 | 0 | 0 | 0 | 37.5 | Energy Generated | 234.3897 |  | MKWHr
02:00 | 2540 | 1773.5 | 924 | 0 | 50 | 421.25 | 40 | 2434 | 0 | 0 | 106 | 0 | 0 | 0 | 26 | Energy not Served | 1.302 |  | MKWHr
02:30 | 2545 | 1767 | 829.5 | 0 | 51 | 422.01 | 40 | 2300.515 | 0 | 0 | 91 | 0 | 0 | 0 | 25.5 | Total Energy Requirement | 235.6917 |  | MKWHr
03:00 | 2550 | 1760.5 | 735 | 0 | 52 | 422.77 | 40 | 2167.03 | 0 | 0 | 76 | 0 | 0 | 0 | 25
03:30 | 2539 | 1763 | 734.5 | 0 | 47 | 422.88 | 40 | 2118.515 | 0 | 0 | 72 | 0 | 0 | 1 | 25
04:00 | 2528 | 1765.5 | 734 | 0 | 42 | 422.99 | 40 | 2070 | 0 | 0 | 68 | 0 | 0 | 2 | 25
04:30 | 2541 | 1731.5 | 734.5 | 0 | 44 | 419.89 | 40 | 2087 | 0 | 0 | 59 | 0 | 0 | 1 | 25
05:00 | 2554 | 1697.5 | 735 | 0 | 46 | 416.79 | 40 | 2104 | 0 | 0 | 50 | 0 | 0 | 0 | 25
05:30 | 2518 | 1687 | 735 | 0 | 48 | 434.805 | 40 | 2314 | 0 | 2 | 54.5 | 0 | 0 | 0 | 35
06:00 | 2482 | 1676.5 | 735 | 0 | 50 | 452.82 | 40 | 2524 | 0 | 4 | 59 | 0 | 0 | 0 | 45
06:30 | 2475 | 1708.25 | 782.5 | 0 | 46 | 525.975 | 40 | 2676.5 | 3.315 | 28 | 88.5 | 0 | 0 | 0 | 57.5
07:00 | 2468 | 1740 | 830 | 0 | 42 | 599.13 | 40 | 2829 | 6.63 | 52 | 118 | 0 | 0 | 0 | 70
07:30 | 2522 | 1754.75 | 877 | 0 | 44 | 623.72 | 40 | 3011 | 51.62 | 54.5 | 176.5 | 0 | 0 | 0 | 77.5
08:00 | 2576 | 1769.5 | 924 | 0 | 46 | 648.31 | 40 | 3193 | 96.61 | 57 | 235 | 0 | 0 | 0 | 85
08:30 | 2641 | 1789.25 | 924.5 | 0 | 45 | 656.035 | 40 | 3194.5 | 165.825 | 58.5 | 314.5 | 0 | 0 | 0 | 139
09:00 | 2706 | 1809 | 925 | 0 | 44 | 663.76 | 40 | 3196 | 235.04 | 60 | 394 | 0 | 0 | 0 | 193
09:30 | 2693.5 | 1805 | 925 | 0 | 51 | 661.105 | 40 | 3098 | 303.5 | 75.5 | 457 | 0 | 0 | 0 | 147.5
10:00 | 2681 | 1801 | 925 | 0 | 58 | 658.45 | 40 | 3000 | 371.96 | 91 | 520 | 0 | 0 | 0 | 102
10:30 | 2707.5 | 1794.75 | 925 | 0 | 59 | 635.505 | 40 | 3005.5 | 416.965 | 100 | 537 | 0 | 0 | 0 | 88.5
11:00 | 2734 | 1788.5 | 925 | 0 | 60 | 612.56 | 40 | 3011 | 461.97 | 109 | 554 | 0 | 0 | 0 | 75
11:30 | 2764 | 1796.5 | 924.5 | 0 | 59 | 612.96 | 40 | 3203 | 478.96 | 113 | 534 | 0 | 0 | 0 | 75.5
12:00 | 2794 | 1804.5 | 924 | 0 | 58 | 613.36 | 40 | 3395 | 495.95 | 117 | 514 | 0 | 0 | 0 | 76
12:30 | 2776 | 1786.5 | 924.5 | 0 | 63 | 657.755 | 40 | 3545.5 | 503.415 | 121 | 501 | 0 | 0 | 0 | 78
13:00 | 2758 | 1768.5 | 925 | 0 | 68 | 702.15 | 40 | 3696 | 510.88 | 125 | 488 | 0 | 0 | 0 | 80
13:30 | 2719.5 | 1745 | 925 | 0 | 69 | 730.075 | 40 | 3647 | 475.13 | 125 | 463.5 | 0 | 0 | 0 | 77
14:00 | 2681 | 1721.5 | 925 | 0 | 70 | 758 | 40 | 3598 | 439.38 | 125 | 439 | 0 | 0 | 0 | 74
14:30 | 2673.5 | 1731.5 | 925 | 0 | 67 | 713 | 40 | 3379 | 378.365 | 125.5 | 404 | 0 | 0 | 0.5 | 45
15:00 | 2666 | 1741.5 | 925 | 0 | 64 | 668 | 40 | 3160 | 317.35 | 126 | 369 | 0 | 0 | 1 | 16
15:30 | 2628 | 1732.25 | 925 | 0 | 57 | 666 | 40 | 3067.5 | 244.69 | 126 | 373.5 | 0 | 0 | 2 | 16.5
16:00 | 2590 | 1723 | 925 | 0 | 50 | 664 | 40 | 2975 | 172.03 | 126 | 378 | 0 | 0 | 3 | 17
16:30 | 2644.5 | 1750.25 | 925 | 0 | 53 | 662.5 | 40 | 3148 | 107.12 | 126 | 342.5 | 0 | 0 | 1.5 | 17
17:00 | 2699 | 1777.5 | 925 | 0 | 56 | 661 | 40 | 3321 | 42.21 | 126 | 307 | 0 | 0 | 0 | 17
17:30 | 2705.5 | 1794 | 925 | 0 | 58 | 708 | 40 | 3415.5 | 21.105 | 193 | 462.5 | 0 | 0 | 0 | 32.5
18:00 | 2712 | 1810.5 | 925 | 0 | 60 | 755 | 40 | 3510 | 0 | 260 | 618 | 0 | 0 | 0 | 48
18:30 | 2762.5 | 1840 | 924.5 | 0 | 61 | 756 | 40 | 3612 | 0 | 242 | 653 | 0 | 0 | 0 | 66.5
19:00 | 2813 | 1869.5 | 924 | 0 | 62 | 757 | 40 | 3714 | 0 | 224 | 688 | 0 | 0 | 0 | 85
19:30 | 2816 | 1857.5 | 924 | 0 | 64 | 754 | 40 | 3733 | 0 | 224 | 531 | 0 | 0 | 0 | 74
20:00 | 2832 | 1884.5 | 925 | 0 | 58 | 755 | 40 | 3727 | 0 | 175 | 412 | 0 | 0 | 0 | 69
20:30 | 2814.5 | 1890.5 | 925 | 0 | 58 | 755.42 | 40 | 3719 | 0 | 162 | 391 | 0 | 0 | 0 | 64.5
21:00 | 2797 | 1896.5 | 925 | 0 | 58 | 755.84 | 40 | 3711 | 0 | 149 | 370 | 0 | 0 | 0 | 60
21:30 | 2794.5 | 1875 | 924 | 0 | 57 | 755.915 | 40 | 3584.5 | 0 | 115.5 | 298.5 | 0 | 0 | 0 | 50
22:00 | 2792 | 1853.5 | 923 | 0 | 56 | 755.99 | 40 | 3458 | 0 | 82 | 227 | 0 | 0 | 0 | 40
22:30 | 2757 | 1825 | 923 | 0 | 54 | 710.005 | 40 | 3329.5 | 0 | 73 | 226 | 0 | 0 | 0 | 20
23:00 | 2722 | 1796.5 | 923 | 0 | 52 | 664.02 | 40 | 3201 | 0 | 64 | 225 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5141 | 4157.49 | 9298.49 | DAILY GENERATION CURVE
00:30 | 5018 | 3931.815 | 8949.815
01:00 | 4895 | 3706.14 | 8601.14 | 28-01-2025
01:30 | 4787 | 3657.945 | 8444.945
02:00 | 4679 | 3609.75 | 8288.75
02:30 | 4582 | 3464.025 | 8046.025
03:00 | 4485 | 3318.3 | 7803.3
03:30 | 4477 | 3260.895 | 7737.895
04:00 | 4469 | 3203.49 | 7672.49
04:30 | 4439 | 3218.89 | 7657.89
05:00 | 4409 | 3234.29 | 7643.29
05:30 | 4551.5 | 3281.805 | 7833.305
06:00 | 4694 | 3329.32 | 8023.32
06:30 | 4841.465 | 3532.575 | 8374.04
07:00 | 4988.93 | 3735.83 | 8724.76
07:30 | 5121.425 | 4033.665 | 9155.09
08:00 | 5253.92 | 4331.5 | 9585.42
08:30 | 5374.69 | 4454.42 | 9829.11
09:00 | 5495.46 | 4577.34 | 10072.8
09:30 | 5570.03 | 4539.575 | 10109.605
10:00 | 5644.6 | 4501.81 | 10146.41
10:30 | 5690.085 | 4531.135 | 10221.22
11:00 | 5735.57 | 4560.46 | 10296.03
11:30 | 5841.44 | 4684.48 | 10525.92
12:00 | 5947.31 | 4808.5 | 10755.81
12:30 | 5979.465 | 4939.205 | 10918.67
13:00 | 6011.62 | 5069.91 | 11081.53
13:30 | 5952.835 | 4986.37 | 10939.205
14:00 | 5894.05 | 4902.83 | 10796.88
14:30 | 5718.575 | 4718.79 | 10437.365
15:00 | 5543.1 | 4534.75 | 10077.85
15:30 | 5479.735 | 4382.205 | 9861.94
16:00 | 5416.37 | 4229.66 | 9646.03
16:30 | 5503.405 | 4296.965 | 9800.37
17:00 | 5590.44 | 4364.27 | 9954.71
17:30 | 5762.72 | 4559.885 | 10322.605
18:00 | 5935 | 4755.5 | 10690.5
18:30 | 6013 | 4878 | 10891
19:00 | 6091 | 5000.5 | 11091.5
19:30 | 6003 | 4940.5 | 10943.5
20:00 | 5963 | 4845.5 | 10808.5
20:30 | 5916.5 | 4838.92 | 10755.42 |  | Executive Engineer
21:00 | 5870 | 4832.34 | 10702.34 |  | Network Operation Division
21:30 | 5733.5 | 4711.415 | 10444.915
22:00 | 5597 | 4590.49 | 10187.49
22:30 | 5468.5 | 4469.005 | 9937.505
23:00 | 5340 | 4347.52 | 9687.52

## Volt
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2025-01-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour |  |  | `
| Aminbazar | 406 | 05:00 | 381 | 12:00 | Kaliakoir | 393 | 05:00 | 370 | 12:00 | [31 empty] | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra
| Ashuganj | 412 | 5:00 | 379 | 12:00 | Madunaghat | 410 | 05:00 | 393 | 13:00 |  | 200 kV Voltage | [31 empty] | 400 kV Voltage
| Bhulta | 412 | 05:00 | 381 | 12:00 | Meghnaghat | 410 | 05:00 | 384 | 12:00
| Bibiana | 401 | 06:00 | 390 | 12:00 | Payra | 418 | 05:00 | 405 | 12:00
| BIPTC | 407 | 02:00 | 369 | 21:00 | Rahanpur | 417 | 05:00 | 398 | 09:00
| Bogura | 415 | 05:00 | 392 | 12:00 | Rampal | 415 | 05:00 | 380 | 12:00
| Gopalganj | 415 | 05:00 | 386 | 12:00 | [5 empty] | Time/SS | Ghorasal | Ishurdi | Ashuganj | Serajganj | Baghabari | Barapukuria | Bogra | Rajshahi | Khulna(S) | Rampura | Haripur | Hasnabad | Aminbazar | Tongi | Comilla(N) | Hathazari | Meghnaghat | Fenchuganj | Siddhirganj | Maniknagar | Old Airport | Barisal | Bhola 225 MW | AKSML | BSRM | GPH | BIBIYANA | Bhulta | Ashuganj (S) | KALIAKOR | Bheramara | Bibiyana | Bhulta | Ashuganj(N) | Kaliakoir | Gopalganj | Payra | Shyampur | Jhenaidah
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV |  | Maximum | 235 | 237 | 240 | 235 | 233 | 230 | 233 | 236 | 237 | 227 | 222 | 225 | 227 | 230 | 229 | 240 | 228 | 245 | 229 | 227 | 226 | 241 | 244 | 233 | 234 | 238 | 240 | 228 | 242 | 229 | 399 | 410 | 392 | 398 | 397 | 421 | 423 | 225 | 234
| Agargaon | 238 | 04:00 | 220 | 12:00 | Haripur | 239 | 05:00 | 224 | 12:00 | Time | 1:00 | 8:00 | 5:00 | 5:00 | 5:00 | 10:00 | 9:00 | 18:00 | 9:00 | 5:00 | 6:00 | 22:00 | 7:00 | 7:00 | 5:00 | 18:30 | 8:00 | 8:00 | 6:00 | 5:00 | 5:00 | 7:00 | 9:00 | 15:00 | 18:30 | 18:30 | 5:00 | 4:00 | 6:00 | 5:00 | 22:00 | 8:00 | 5:00 | 6:00 | 5:00 | 9:00 | 9:00 | 5:00 | 9:00
| AKSML | 234 | 04:00 | 221 | 12:00 | Hasnabad | 235 | 06:00 | 221 | 12:00 | Minimum | 230 | 228 | 227 | 229 | 227 | 221 | 225 | 226 | 226 | 214 | 215 | 213 | 214 | 215 | 221 | 229 | 220 | 240 | 217 | 214 | 212 | 232 | 237 | 228 | 222 | 226 | 235 | 217 | 230 | 215 | 392 | 403 | 369 | 376 | 382 | 399 | 412 | 213 | 223
| Aminbazar | 236 | 05:00 | 220 | 12:00 | Hathazari | 233 | 01:00 | 225 | 12:00
| Ashuganj | 238 | 03:00 | 225 | 13:00 | Ishurdi | 243 | 04:00 | 225 | 12:00 | Time | 7:00 | 20:00 | 16:00 | 16:00 | 16:00 | 20:00 | 1:00 | 21:00 | 1:00 | 16:00 | 11:00 | 16:00 | 16:00 | 15:00 | 11:00 | 9:00 | 13:00 | 11:00 | 15:00 | 15:00 | 16:00 | 24:00 | 1:00 | 12:00 | 9:00 | 12:00 | 11:00 | 16:00 | 17:00 | 16:00 | 15:00 | 3:00 | 16:00 | 16:00 | 16:00 | 24:00 | 1:00 | 16:00 | 21:00
| Ashuganj-400 | 238 | 03:00 | 225 | 13:00 | Jhenaidah | 241 | 05:00 | 218 | 12:00
| Baghabari | 241 | 02:00 | 227 | 11:00 | Kaliakoir | 235 | 05:00 | 218 | 12:00 | 230 kV MAX | 249 |  | 249 | 216
| Barapukuria | 226 | 04:00 | 216 | 08:00 | Keranigonj | 237 | 04:00 | 219 | 12:00 | 230 kV MIN | 216 |  | 243 | 218 |  |  |  | Substation | Total | Updated
| Barapukuria-230 | 226 | 04:00 | 216 | 08:00 | Khulna(S) | 242 | 05:00 | 220 | 12:00 | [8 empty] | 132 kV | 147 | 23/5/21
| Barishal | 246 | 05:00 | 233 | 12:00 | Madunaghat | 234 | 05:00 | 225 | 12:00 | 132 kV MAX | 142 |  | 142 | 111 |  |  |  | 230 kV | 32 | [14 empty] | 18:30
| Bheramara | 242 | 05:00 | 224 | 12:00 | Madunaghat-400 | 235 | 05:00 | 225 | 13:00 | 132 kV MIN | 110 |  | 142 | 110 |  |  |  | 400 kV | 13 | [25 empty] | 403
| Bhulta | 241 | 05:00 | 222 | 12:00 | Maniknagar | 237 | 05:00 | 223 | 11:00 | [35 empty] | 6:00
| Bibiana | 232 | 00:00 | 224 | 04:00 | Meghnaghat | 243 | 04:00 | 228 | 12:00 |  | 400 | [33 empty] | 392
| BIPTC | 242 | 03:00 | 223 | 12:00 | Meghnaghat-400 | 240 | 05:00 | 225 | 12:00 |  | Ashuganj 400 kV = ash North-299667
| Bogura | 241 | 05:00 | 227 | 09:00 | Mirsorai | 234 | 03:00 | 222 | 12:00 | ` |  |  |  | 230 | [30 empty] | 21:00
| Bogura-400 | 240 | 05:00 | 226 | 12:00 | Rajshahi | 242 | 05:00 | 223 | 12:00 |  | rampur-charged |  |  | B.P-499228
| Borhanuddin | 249 | 05:00 | 240 | 12:00 | Rampal | 240 | 05:00 | 222 | 05:00 |  | 132 |  |  | Ash 400-299274
| BSRM | 234 | 05:00 | 222 | 13:00 | Rampur | N/A | N/A | N/A | N/A |  | Megna
| Cumilla(N) | 235 | 03:00 | 222 | 12:00 | Rampura | 240 | 05:00 | 221 | 12:00 |  | Maniknagar=narinda | 132 kv
| Faridpur | 246 | 04:00 | 229 | 12:00 | Shikalbaha | 233 | 05:00 | 223 | 12:00 |  | kaptai by call 399528
| Fenchuganj | 235 | 00:00 | 224 | 12:00 | Shyampur | 238 | 05:00 | 221 | 12:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Siddhirganj | 235 | 00:00 | 225 | 12:00
| Ghorashal-230 | 237 | 05:00 | 218 | 12:00 | Sirajgonj | 247 | 05:00 | 235 | 12:00
| Gopalganj | 246 | 05:00 | 229 | 12:00 | Sreepur | 239 | 05:00 | 224 | 12:00
| GPH | 234 | 05:00 | 222 | 13:00 | Tongi | 232 | 04:00 | 214 | 11:00 |  | Madu-399663
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV |  |  | Meg-299636
| Aftabnagar | 137 | 02:00 | 126 | 12:00 | Kurigram | 131 | 00:00 | 118 | 08:00 |  | Gopalganj-230 | 599470
| Agargaon | 139 | 05:00 | 127 | 12:00 | Kushtia | 140 | 01:00 | 130 | 12:00
| Agrabad | 133 | 04:00 | 128 | 12:00 | Lalbag | 140 | 05:00 | 128 | 12:00
| AKS | 132 | 03:00 | 126 | 21:00 | Lalmonirhat | 127 | 03:00 | 116 | 08:00
| Aminbazar | 136 | 05:00 | 126 | 12:00 | Madanganj | 136 | 07:00 | 127 | 12:00
| Amnura | 140 | 03:00 | 129 | 09:00 | Madaripur | 139 | 05:00 | 128 | 12:00
| Ashuganj | 140 | 01:00 | 135 | 12:00 | Madartek | 137 | 05:00 | 126 | 12:00
| Bagerhat | 136 | 01:00 | 122 | 12:00 | Madunaghat | 135 | 03:00 | 129 | 12:00
| Bajitpur | 136 | 03:00 | 126 | 12:00 | Magura | 141 | 03:00 | 127 | 12:00
| Bakulia | 133 | 01:00 | 123 | 05:00 | Mahasthangarh | 136 | 03:00 | 124 | 09:00
| Banani | 137 | 02:00 | 125 | 12:00 | Manikganj | 135 | 22:00 | 128 | 12:00
| Bangabhaban | 136 | 04:00 | 125 | 12:00 | Maniknagar | 136 | 04:00 | 126 | 12:00
| Barapukuria | 135 | 04:00 | 126 | 08:00 | Matarbari | 127 | 03:00 | 118 | 13:00
| Barguna | 137 | 05:00 | 132 | 13:00 | Matuail | 136 | 05:00 | 128 | 12:00
| Barishal | 136 | 05:00 | 127 | 12:00 | Millgate | 138 | 04:00 | 123 | 12:00
| Barishal-230 | 137 | 03:00 | 128 | 12:00 | Mirpur | 137 | 05:00 | 126 | 12:00
| Baroaulia | 132 | 00:00 | 128 | 20:00 | Mirzapur | 133 | 00:00 | 126 | 12:00
| Baroirhat | 130 | 00:00 | 125 | 13:00 | Mithapukur | 135 | 04:00 | 121 | 09:00
| Bashundhara | 138 | 03:00 | 124 | 12:00 | MI_Cement | 138 | 03:00 | 128 | 12:00
| BashundharaCement | 136 | 08:00 | 127 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
| Beanibazar | 137 | 00:00 | 130 | 13:00 | Mogbazar | 139 | 05:00 | 126 | 13:00
| Benapole | 138 | 02:00 | 121 | 12:00 | Mongla | 137 | 04:00 | 122 | 12:00
| Bhaluka | 128 | 05:00 | 116 | 02:00 | Motijheel | 136 | 04:00 | 125 | 12:00
| Bhandaria | 132 | 00:00 | 126 | 12:00 | Muktagacha | 123 | 04:00 | 113 | 12:00
| Bhangura | 139 | 02:00 | 129 | 12:00 | Munshiganj | 137 | 07:00 | 127 | 12:00
| Bheramara | 140 | 05:00 | 131 | 12:00 | Mymensingh | 128 | 04:00 | 111 | 12:00
| Bheramara(GK) | 139 | 02:00 | 130 | 12:00 | Naogaon | 137 | 05:00 | 125 | 08:00
| Bhulta | 130 | 00:00 | 124 | 14:00 | Narail | 139 | 03:00 | 126 | 12:00
| Bog-Sherpur | 138 | 05:00 | 126 | 12:00 | Narinda | 136 | 04:00 | 126 | 12:00
| Bogura | 137 | 04:00 | 128 | 09:00 | Narshingdi | 133 | 04:00 | 116 | 12:00
| Bogura-230 | 139 | 05:00 | 128 | 09:00 | Natore | 139 | 05:00 | 129 | 12:00
| Brahmanbaria | 134 | 05:00 | 124 | 12:00 | Nawabganj | 139 | 03:00 | 127 | 12:00
| Cantonment | 139 | 05:00 | 127 | 12:00 | Netrakona | 126 | 00:00 | 110 | 12:00
| Chandpur | 129 | 05:00 | 125 | 13:00 | New | 138 | 00:00 | 125 | 12:00
| Chandraghona | 136 | 05:00 | 130 | 12:00 | Niamatpur | 140 | 02:00 | 132 | 09:00
| Chapai | 138 | 03:00 | 130 | 12:00 | Noapara | 139 | 03:00 | 124 | 12:00
| Charsaidpur | 138 | 08:00 | 128 | 12:00 | Pabna | 138 | 03:00 | 125 | 12:00
| Chauddagram | 133 | 03:00 | 126 | 19:00 | Palashbari | 134 | 05:00 | 120 | 08:00
| Chhatak | 138 | 05:00 | 127 | 13:00 | Panchagarh | 135 | 05:00 | 118 | 09:00
| Chowmuhani | 130 | 03:00 | 123 | 20:00 | Patuakhali | 136 | 02:00 | 132 | 12:00
| Chuadanga | 141 | 03:00 | 124 | 12:00 | Payra | 138 | 03:00 | 133 | 14:00
| Coxsbazar | 127 | 03:00 | 118 | 12:00 | PHP | 131 | 03:00 | 124 | 22:00
| Cumilla(N) | 137 | 05:00 | 129 | 13:00 | Postogola | 140 | 04:00 | 131 | 13:00
| Cumilla(S) | 136 | 03:00 | 127 | 12:00 | Purbachal | 138 | 02:00 | 126 | 12:00
| Daudkandi | 132 | 03:00 | 123 | 09:00 | Purbasadipur | 131 | 03:00 | 116 | 08:00
| Dhaka | 137 | 01:00 | 126 | 12:00 | Rahanpur | 140 | 23:00 | 133 | 12:00
| Dhamrai | 133 | 00:00 | 122 | 10:00 | Rahanpur-400 | 141 | 03:00 | 134 | 09:00
| Dhanmondi | 138 | 04:00 | 127 | 12:00 | Rahim | 134 | 05:00 | 127 | 12:00
| Dohazari | 131 | 05:00 | 120 | 19:30 | Rajbari | 137 | 05:00 | 126 | 12:00
| Faridpur | 137 | 04:00 | 128 | 12:00 | Rajendrapur | 135 | 05:00 | 124 | 13:00
| Fatullah | 139 | 04:00 | 129 | 12:00 | Rajshahi | 139 | 05:00 | 130 | 12:00
| Fenchuganj | 140 | 02:00 | 134 | 13:00 | Rajshahi-230 | 140 | 03:00 | 125 | 13:00
| Feni | 133 | 05:00 | 125 | 19:30 | Ramganj | 129 | 03:00 | 120 | 20:00
| Ghatail | 126 | 09:00 | 118 | 12:00 | Rampur | 135 | 05:00 | 127 | 13:00
| Ghorashal | 139 | 04:00 | 131 | 12:00 | Rampura | 138 | 05:00 | 127 | 13:00
| Goalpara | 139 | 05:00 | 126 | 12:00 | Rangamati | 135 | 04:00 | 128 | 12:00
| Gollamari | 140 | 05:00 | 126 | 12:00 | Rangpur | 132 | 03:00 | 118 | 09:00
| Gopalganj | 138 | 04:00 | 127 | 12:00 | Ruppur | 141 | 05:00 | 132 | 12:00
| Gopalganj-400 | 138 | 03:00 | 128 | 12:00 | Saidpur | 132 | 04:00 | 119 | 09:00
| Gulshan | 136 | 05:00 | 126 | 12:00 | Satkhira | 139 | 04:00 | 123 | 12:00
| Halishahar | 134 | 04:00 | 128 | 13:00 | Satmasjid | 138 | 04:00 | 127 | 13:00
| Haripur | 136 | 05:00 | 128 | 12:00 | Savar | 138 | 04:00 | 125 | 11:00
| HaripurSBU | 136 | 05:00 | 128 | 13:00 | SevenRings | 142 | 05:00 | 133 | 12:00
| Hasnabad | 139 | 02:00 | 130 | 12:00 | ShahCement | 138 | 08:00 | 128 | 12:00
| Hathazari | 135 | 00:00 | 130 | 12:00 | Shahjadpur | 142 | 03:00 | 131 | 15:00
| Ishurdi | 142 | 03:00 | 132 | 12:00 | Shahjibazar | 137 | 04:00 | 129 | 12:00
| Jaldhaka | 129 | 00:00 | 116 | 08:00 | Shahmirpur | 133 | 04:00 | 128 | 11:00
| Jamalpur | 125 | 16:00 | 111 | 03:00 | Shariatpur | 137 | 01:00 | 126 | 12:00
| Jashore | 139 | 01:00 | 123 | 12:00 | Sherpur | 122 | 16:00 | 110 | 03:00
| Jhenaidah | 141 | 03:00 | 128 | 12:00 | Shikalbaha | 123 | 02:00 | 117 | 12:00
| Jhenaidah-230 | 142 | 05:00 | 128 | 12:00 | Shikalbaha-230 | 136 | 05:00 | 128 | 12:00
| Joydebpur | 137 | 05:00 | 127 | 12:00 | Shitalakhya | 138 | 03:00 | 128 | 12:00
| Joypurhat | 135 | 00:00 | 123 | 09:00 | Sholosohor | 134 | 04:00 | 128 | 13:00
| Juldah | 133 | 02:00 | 129 | 17:00 | Shyampur | 136 | 08:00 | 129 | 12:00
| Kabirpur | 138 | 00:00 | 122 | 12:00 | Shyampur-230 | 139 | 05:00 | 127 | 12:00
| Kachua | 133 | 05:00 | 126 | 13:00 | Siddhirganj | 136 | 02:00 | 128 | 12:00
| Kaliakoir | 140 | 05:00 | 125 | 12:00 | Sirajganj | 138 | 03:00 | 126 | 12:00
| Kallyanpur | 134 | 03:00 | 124 | 12:00 | Sonargaon | 134 | 02:00 | 117 | 09:00
| Kalurghat | 135 | 03:00 | 129 | 12:00 | Sreemongol | 139 | 04:00 | 130 | 12:00
| Kamrangirchar | 138 | 01:00 | 122 | 12:00 | Sreepur | 130 | 03:00 | 119 | 12:00
| Kaptai | 136 | 2:00 | 126 | 12:00 | Srinagar | 139 | 05:00 | 128 | 12:00
| Kazla | 136 | 05:00 | 125 | 13:00 | SSM | 135 | 10:00 | 130 | 20:00
| Keranigonj | 139 | 04:00 | 127 | 12:00 | Sunamganj | 135 | 01:00 | 126 | 13:00
| Khagrachori | 134 | 02:00 | 127 | 13:00 | Sylhet | 139 | 05:00 | 129 | 13:00
| Khulna | 139 | 05:00 | 124 | 12:00 | Sylhet-132 | 138 | 06:00 | 130 | 12:00
| Khulna(S) | 141 | 05:00 | 127 | 12:00 | Tangail | 129 | 02:00 | 121 | 12:00
| Khulshi | 134 | 04:00 | 126 | 12:00 | Thakurgaon | 132 | 05:00 | 115 | 09:00 |  |  | 132 kV S/S | 230 kV S/S | 400 kV S/S
| Kishoreganj | 131 | 00:00 | 121 | 12:00 | TK | 134 | 03:00 | 129 | 12:00 |  |  | Nos | Nos | Nos
| Kodda | 136 | 00:00 | 125 | 12:00 | Tongi | 138 | 04:00 | 127 | 11:00 |  |  | 173 | 39 | 9 | 221
| KSRM | 133 | 00:00 | 128 | 12:00 | Ullahpara | 139 | 03:00 | 129 | 12:00
| Kulaura | 139 | 01:00 | 133 | 13:00 | Ullon | 138 | 03:00 | 126 | 13:00
[6 empty] | Uttara | 137 | 03:00 | 126 | 12:00
[6 empty] | UttaraNew | 138 | 03:00 | 126 | 12:00
[6 empty] | Zigatola | 140 | 05:00 | 129 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7
360
.