## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 30-01-2025 | [28 empty] | Date: | 30-01-2025 | [28 empty] | Date: | 30-01-2025 | [28 empty] | Date: | 30-01-2025 | [28 empty] | Date: | 30-01-2025 | [19 empty] | Date: | 30-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [19 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 225 | 276 | 0 | 0 | 0 | 21 | 335 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 505 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 897 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 26 | 183 | 30 | 0 | 45 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 295 | 290 | 381 | 36 | 42 | 0 | 2 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 70 | 0 | 0 | 0 | 0 | 4971 | 925 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 103 | 0 | 414 | 0 | 0 | 2.5 | 164 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 140 | 220 | 0 | 294 | 850 | 0 | 4161.5 | 9132.5 | 91.96
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 225 | 275 | 0 | 0 | 0 | 21 | 335 | 0 | 0 | 0 | 0 | 16.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 183 | 27 | 0 | 45 | 0 | 0 | 17 | 0 | 56 | 0 | 0 | 0 | 305 | 290 | 381 | 33 | 42 | 0 | 2 | 113 | 22 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 4577.5 | 925 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 2.5 | 160 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 140 | 220 | 0 | 295 | 850 | 0 | 4051.5 | 8629 | 91.96
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 280 | 296 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 0 | 0 | 16.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 198 | 27 | 0 | 50 | 0 | 0 | 11 | 0 | 56 | 0 | 0 | 0 | 305 | 280 | 381 | 33 | 42 | 0 | 2 | 113 | 22 | 0 | 41 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4506.5 | 793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 2.5 | 160 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 294 | 700 | 0 | 3642.5 | 8149 | 91.96
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 360 | 292 | 0 | 0 | 0 | 22 | 335 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 199 | 0 | 0 | 0 | 26 | 182 | 27 | 0 | 70 | 0 | 0 | 11 | 0 | 44 | 0 | 0 | 0 | 310 | 280 | 381 | 33 | 42 | 0 | 2 | 113 | 22 | 0 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4448 | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 130 | 0 | 395 | 0 | 0 | 2.5 | 160 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 296 | 600 | 0 | 3453.5 | 7901.5 | 91.95
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 360 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 360 | 287 | 0 | 0 | 0 | 22 | 280 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 128 | 0 | 0 | 0 | 5 | 192 | 27 | 0 | 70 | 0 | 0 | 11 | 0 | 52 | 0 | 0 | 0 | 320 | 280 | 381 | 33 | 42 | 0 | 2 | 113 | 22 | 0 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4233 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 2.5 | 160 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 295 | 560 | 0 | 3435.5 | 7668.5 | 91.95
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 300 | 298 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 0 | 5 | 0 | 128 | 0 | 0 | 0 | 5 | 199 | 27 | 0 | 70 | 0 | 0 | 11 | 0 | 46 | 0 | 0 | 0 | 310 | 280 | 381 | 5 | 42 | 0 | 2 | 113 | 22 | 0 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4072 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 190 | 0 | 414 | 0 | 0 | 2.5 | 165 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 140 | 220 | 0 | 293 | 560 | 0 | 3497.5 | 7569.5 | 91.95
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 300 | 303 | 0 | 0 | 0 | 22 | 250 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 39 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 695 | 0 | 51 | 0 | 195 | 0 | 0 | 0 | 11 | 197 | 25 | 0 | 70 | 0 | 0 | 11 | 0 | 52 | 0 | 0 | 0 | 315 | 250 | 380 | 25 | 42 | 0 | 2 | 113 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 46 | 0 | 0 | 0 | 0 | 4483 | 782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 187 | 0 | 414 | 0 | 0 | 2.5 | 161 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 140 | 220 | 0 | 294 | 600 | 0 | 3631.5 | 8114.5 | 91.94
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 0 | 0 | 0 | 50 | 32 | 0 | 0 | 0 | 0 | 8.5 | 0 | 300 | 311 | 0 | 0 | 0 | 5 | 250 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 875 | 1 | 51 | 0 | 199 | 0 | 0 | 0 | 24 | 211 | 25 | 0 | 70 | 0 | 0 | 11 | 0 | 48 | 0 | 2 | 0 | 310 | 250 | 380 | 33 | 42 | 0 | 2 | 113 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 0 | 0 | 0.6 | 0 | 4829.1 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.43 | 0 | 0 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | 140 | 0 | 0 | 0 | 166 | 0 | 414 | 0 | 0.04 | 2.5 | 161 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.13 | 0 | 250 | 6 | 140 | 220 | 0 | 294 | 820 | 0 | 4086.71 | 8915.81 | 91.94
08:00 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 1 | 0 | 0 | 78 | 32 | 0 | 0 | 0 | 54 | 22 | 0 | 300 | 314 | 0 | 0 | 17 | 8 | 250 | 0 | 0 | 4 | 0 | 17 | 22 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 20 | 578 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1075 | 6 | 51 | 0 | 197 | 0 | 0 | 0 | 24 | 210 | 29 | 12 | 50 | 5 | 1 | 15 | 0 | 56 | 0 | 12 | 0 | 320 | 260 | 380 | 33 | 42 | 0 | 2 | 113 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 0 | 0 | 6.8 | 0 | 5268.8 | 642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.24 | 0 | 0 | 761.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 6.98 | 136 | 0 | 0 | 0 | 168 | 0 | 414 | 0 | 0.56 | 2.5 | 160 | 69 | 0 | 3 | 0 | 0 | 0 | 0.5 | 25 | 0.1 | 0 | 307 | 5 | 140 | 220 | 0 | 290 | 1090 | 24 | 4487.1 | 9755.9 | 91.94
09:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 381 | 0 | 0 | 30 | 0 | 0 | 95 | 16 | 0 | 0 | 0 | 108 | 0 | 0 | 300 | 284 | 0 | 0 | 35 | 18 | 250 | 0 | 0 | 10 | 0 | 19 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 40 | 0 | 8 | 577 | 0 | 0 | 13 | 0 | 10 | 0 | 0 | 0 | 0 | 1227 | 11 | 51 | 0 | 197 | 0 | 0 | 0 | 25 | 183 | 24 | 54 | 50 | 39 | 32 | 15 | 0 | 58 | 0 | 28 | 0 | 315 | 320 | 380 | 33 | 42 | 0 | 2 | 113 | 22 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 1 | 15.79 | 0 | 5752.04 | 641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.79 | 0 | 0 | 756.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 17.62 | 136 | 0 | 0 | 0 | 171 | 0 | 393 | 0 | 1.69 | 2.5 | 169 | 69 | 0 | 5 | 0 | 0 | 0 | 1.6 | 55 | 0.24 | 0 | 307 | 4 | 100 | 220 | 0 | 292 | 1140 | 54 | 4592.33 | 10344.37 | 91.93
10:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 17 | 0 | 0 | 128 | 16 | 0 | 0 | 0 | 72 | 0 | 0 | 300 | 265 | 0 | 0 | 17 | 19.5 | 250 | 0 | 0 | 15 | 0 | 15 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 9 | 576 | 0 | 0 | 20 | 0 | 17 | 0 | 0 | 0 | 0 | 1135 | 15 | 51 | 0 | 197 | 0 | 0 | 0 | 26 | 183 | 24 | 50 | 50 | 17 | 26 | 5 | 0 | 56 | 0 | 41 | 0 | 285 | 320 | 324 | 31 | 42 | 0 | 2 | 113 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 1 | 24.49 | 2 | 5540.99 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.29 | 0 | 0 | 657.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 25.65 | 137 | 0 | 0 | 0 | 174 | 0 | 393 | 0 | 2.29 | 2.5 | 167 | 69 | 0 | 14 | 0 | 0 | 0 | 3 | 78 | 0.36 | 0 | 250 | 4 | 100 | 180 | 0 | 290 | 1050 | 35 | 4613.2 | 10154.19 | 91.93
11:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 353 | 0 | 0 | 17 | 0 | 0 | 131 | 16 | 0 | 0 | 0 | 72 | 0 | 0 | 300 | 297 | 0 | 0 | 17 | 19.5 | 300 | 0 | 0 | 9 | 0 | 19 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 9 | 578 | 0 | 0 | 19 | 0 | 17 | 0 | 0 | 0 | 0 | 1110 | 17 | 51 | 4 | 197 | 0 | 0 | 0 | 26 | 202 | 24 | 50 | 50 | 17 | 26 | 17 | 0 | 56 | 0 | 52 | 0 | 300 | 320 | 367 | 36 | 42 | 0 | 2 | 113 | 22 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 1 | 21.7 | 6 | 5664.2 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.16 | 0 | 0 | 613.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 36.1 | 149 | 0 | 0 | 0 | 180 | 0 | 414 | 0 | 3.2 | 2.5 | 168 | 69 | 0 | 18 | 0 | 0 | 0 | 3.7 | 104 | 0.36 | 0 | 250 | 3 | 132 | 180 | 0 | 207 | 1030 | 35 | 4586.41 | 10250.61 | 91.93
12:00 | 0 | 58 | 26 | 0 | 0 | 0 | 0 | 3 | 335 | 0 | 0 | 17 | 0 | 0 | 122 | 32 | 0 | 0 | 0 | 72 | 0 | 0 | 300 | 254 | 0 | 0 | 17 | 19.5 | 275 | 0 | 0 | 13 | 0 | 20 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 9 | 578 | 0 | 0 | 22 | 0 | 17 | 0 | 0 | 0 | 0 | 1224 | 18 | 51 | 12 | 197 | 0 | 0 | 0 | 27 | 183 | 24 | 54 | 50 | 17 | 26 | 17 | 0 | 58 | 0 | 56 | 0 | 300 | 320 | 375 | 36 | 42 | 0 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 1 | 31.66 | 6 | 5738.16 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.78 | 0 | 0 | 750.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 40.95 | 152 | 0 | 0 | 0 | 183 | 0 | 393 | 0 | 2.5 | 2.5 | 166 | 70 | 0 | 15 | 0 | 0 | 0 | 4 | 131 | 0.39 | 0 | 250 | 4 | 132 | 220 | 0 | 302 | 1130 | 72 | 5004.51 | 10742.67 | 91.92
13:00 | 0 | 70 | 26 | 0 | 0 | 0 | 0 | 3 | 405 | 0 | 0 | 25 | 0 | 0 | 117 | 32 | 0 | 0 | 0 | 108 | 0 | 0 | 300 | 288 | 0 | 0 | 35 | 19.5 | 250 | 0 | 0 | 17 | 0 | 20 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 9 | 577 | 0 | 0 | 32 | 0 | 17 | 0 | 0 | 0 | 0 | 1212 | 15 | 51 | 10 | 197 | 0 | 0 | 0 | 29 | 190 | 29 | 74 | 50 | 27 | 36 | 17 | 0 | 72 | 0 | 51 | 0 | 305 | 320 | 360 | 33 | 41 | 0 | 5 | 80 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 1 | 28.72 | 6 | 5879.22 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.57 | 0 | 0 | 758.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 26.05 | 152 | 0 | 0 | 0 | 160 | 0 | 395 | 0 | 2.13 | 2.5 | 167 | 68 | 0 | 20 | 0 | 0 | 0 | 4.1 | 128 | 0.33 | 0 | 280 | 4 | 120 | 180 | 0 | 297 | 1182 | 90 | 5042.27 | 10921.49 | 91.92
14:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 359 | 0 | 0 | 35 | 0 | 0 | 115 | 16 | 0 | 0 | 0 | 108 | 0 | 0 | 300 | 289 | 0 | 0 | 35 | 19.5 | 300 | 0 | 0 | 9 | 0 | 20 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 7 | 503 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 14 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 190 | 30 | 92 | 50 | 17 | 53 | 17 | 0 | 64 | 0 | 41 | 0 | 310 | 320 | 322 | 33 | 41 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 1 | 14.2 | 6 | 5653.7 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.51 | 0 | 0 | 661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 30.84 | 152 | 0 | 0 | 0 | 140 | 0 | 397 | 0 | 2.22 | 2.5 | 173 | 68 | 0 | 10 | 0 | 0 | 0 | 3.4 | 100 | 0.33 | 0 | 250 | 4 | 100 | 180 | 0 | 252 | 1182 | 54 | 4777.8 | 10431.5 | 91.92
15:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 352 | 0 | 0 | 35 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 72 | 0 | 0 | 300 | 285 | 0 | 0 | 17 | 19.5 | 300 | 0 | 0 | 11 | 0 | 20 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 8 | 503 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 10 | 51 | 0 | 195 | 0 | 0 | 0 | 29 | 184 | 30 | 70 | 50 | 17 | 34 | 17 | 0 | 58 | 0 | 34 | 0 | 310 | 320 | 323 | 36 | 41 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 16.61 | 6 | 5475.11 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.14 | 0 | 0 | 661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 22.61 | 152 | 0 | 0 | 0 | 140 | 0 | 393 | 0 | 1.89 | 2.5 | 177 | 65 | 0 | 10 | 0 | 0 | 0 | 2 | 66 | 0.3 | 0 | 250 | 4 | 100 | 180 | 0 | 251 | 1182 | 17 | 4689.44 | 10164.55 | 91.91
16:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 377 | 0 | 0 | 17 | 0 | 0 | 60 | 16 | 0 | 0 | 0 | 35 | 0 | 0 | 300 | 271 | 0 | 0 | 0 | 19.5 | 280 | 0 | 0 | 6 | 0 | 20 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 4 | 576 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 5 | 43 | 0 | 195 | 0 | 0 | 0 | 29 | 182 | 26 | 34 | 50 | 0 | 17 | 17 | 0 | 56 | 0 | 13 | 0 | 305 | 320 | 323 | 36 | 41 | 0 | 5 | 113 | 8 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 6.72 | 6 | 5270.22 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.43 | 0 | 0 | 634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11.38 | 153 | 0 | 0 | 0 | 140 | 0 | 395 | 0 | 1.05 | 2.5 | 177 | 65 | 0 | 6 | 0 | 0 | 0 | 1.3 | 29 | 0.13 | 0 | 200 | 4 | 134 | 220 | 0 | 250 | 1150 | 17 | 4552.79 | 9823.01 | 91.91
17:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 406 | 0 | 0 | 17 | 0 | 0 | 70 | 82 | 0 | 0 | 0 | 35 | 0 | 0 | 300 | 286 | 0 | 0 | 5 | 19.5 | 250 | 0 | 0 | 2 | 0 | 20 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 576 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 1 | 51 | 3 | 195 | 0 | 0 | 0 | 29 | 189 | 26 | 34 | 50 | 1 | 17 | 17 | 0 | 64 | 0 | 3 | 0 | 320 | 320 | 336 | 33 | 41 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 1.88 | 6 | 5418.38 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.02 | 0 | 0 | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 7 | 16 | 2.96 | 153 | 0 | 0 | 0 | 140 | 0 | 401 | 0 | 0.28 | 2.5 | 181 | 66 | 13 | 1 | 0 | 0 | 0 | 0.3 | 6 | 0.03 | 0 | 200 | 4 | 134 | 220 | 0 | 252 | 1140 | 17 | 4544.09 | 9962.47 | 91.91
18:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 405 | 0 | 0 | 22 | 0 | 0 | 112 | 82 | 0 | 3 | 17 | 72 | 0 | 7 | 300 | 290 | 0 | 0 | 35 | 19.5 | 250 | 0 | 0 | 0 | 0 | 19 | 22 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 30 | 24 | 0 | 4 | 3 | 0 | 40 | 2 | 18 | 576 | 10 | 0 | 9 | 0 | 18 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 33 | 195 | 0 | 0 | 0 | 29 | 192 | 26 | 45 | 70 | 17 | 34 | 17 | 0 | 38 | 0 | 0 | 7 | 305 | 320 | 333 | 36 | 41 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 1 | 9 | 59 | 0 | 0 | 0 | 6 | 5756.5 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 658 | 0 | 0 | 14 | 0 | 0 | 0 | 99 | 0 | 15 | 16 | 0 | 30 | 0 | 153 | 0 | 0 | 0 | 202 | 0 | 406 | 0 | 0 | 2.5 | 182 | 65 | 68 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 134 | 220 | 0 | 253 | 1130 | 100 | 4960.5 | 10717 | 91.9
19:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 347 | 0 | 0 | 54 | 0 | 0 | 131 | 64 | 0 | 55 | 54 | 72 | 0 | 12 | 420 | 294 | 0 | 0 | 35 | 19.5 | 300 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 23 | 503 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 78 | 195 | 0 | 0 | 0 | 29 | 182 | 26 | 114 | 50 | 77 | 103 | 17 | 0 | 36 | 0 | 0 | 24 | 280 | 320 | 323 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 40 | 9 | 58 | 0 | 0 | 0 | 1 | 6190.5 | 641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 745 | 0 | 0 | 22 | 0 | 0 | 0 | 99 | 0 | 11 | 25 | 0 | 24 | 0 | 153 | 0 | 0 | 0 | 202 | 0 | 394 | 0 | 0 | 5.5 | 183 | 65 | 90 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 136 | 220 | 0 | 301 | 1130 | 150 | 4948.5 | 11139 | 91.9
19:30 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 346 | 0 | 0 | 35 | 0 | 0 | 131 | 64 | 0 | 0 | 0 | 35 | 0 | 12 | 420 | 320 | 0 | 0 | 17 | 19.5 | 300 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 100 | 195 | 0 | 0 | 0 | 29 | 194 | 26 | 115 | 50 | 51 | 73 | 17 | 0 | 34 | 0 | 0 | 0 | 310 | 320 | 335 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 35 | 9 | 67 | 0 | 0 | 0 | 0 | 5979.5 | 641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 0 | 29 | 0 | 0 | 0 | 99 | 0 | 13 | 16 | 0 | 24 | 0 | 152 | 0 | 0 | 0 | 202 | 0 | 409 | 0 | 0 | 5.5 | 180 | 65 | 90 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 136 | 220 | 0 | 311 | 1130 | 150 | 4979.5 | 10959
20:00 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 3 | 361 | 0 | 0 | 35 | 0 | 0 | 131 | 48 | 0 | 0 | 0 | 35 | 20 | 12 | 420 | 278 | 0 | 0 | 0 | 19.5 | 335 | 0 | 0 | 0 | 7 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 100 | 197 | 0 | 0 | 0 | 29 | 182 | 26 | 68 | 50 | 51 | 55 | 17 | 0 | 30 | 0 | 0 | 0 | 295 | 320 | 316 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 36 | 9 | 58 | 0 | 0 | 0 | 0 | 5853.5 | 640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 38 | 16 | 0 | 24 | 0 | 144 | 0 | 0 | 0 | 201 | 0 | 395 | 0 | 0 | 5.5 | 182 | 65 | 90 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 136 | 220 | 0 | 310 | 1130 | 150 | 4953.5 | 10807 | 91.9
21:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 3 | 406 | 0 | 0 | 35 | 0 | 0 | 131 | 32 | 0 | 0 | 0 | 35 | 22 | 0 | 420 | 298 | 0 | 0 | 0 | 21 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 26 | 577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 182 | 27 | 68 | 50 | 17 | 55 | 17 | 0 | 40 | 0 | 0 | 0 | 310 | 320 | 324 | 36 | 42 | 0 | 5 | 113 | 8 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 0 | 5781 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758.17 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 200 | 0 | 394 | 0 | 0 | 5.5 | 181 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 136 | 220 | 0 | 308 | 1130 | 72 | 4884.67 | 10665.67 | 91.89
22:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 132 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 420 | 287 | 0 | 0 | 0 | 21 | 335 | 0 | 0 | 0 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 28 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 182 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 42 | 0 | 0 | 0 | 305 | 290 | 322 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 0 | 5506 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 754.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 181 | 0 | 393 | 0 | 0 | 5.5 | 180 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 138 | 220 | 0 | 309 | 1130 | 0 | 4740.62 | 10246.62 | 91.89
23:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 132 | 16 | 0 | 0 | 0 | 0 | 22 | 0 | 340 | 293 | 0 | 0 | 0 | 21 | 300 | 0 | 0 | 0 | 0 | 20.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31 | 577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 182 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 275 | 148 | 347 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 0 | 0 | 0 | 0 | 5237.5 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 659.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0 | 0 | 141 | 0 | 314 | 0 | 0 | 5.5 | 180 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 8 | 100 | 220 | 0 | 311 | 1130 | 0 | 4466.35 | 9703.85 | 91.89
Total KWH | 0 | 842880 | 373440 | 0 | 0 | 0 | 0 | 80500 | 9194400 | 0 | 0 | 412920 | 0 | 0 | 2294064 | 546720 | 0 | 73756 | 62578 | 977760 | 237240 | 30720 | 7823000 | 7074298 | 0 | 0 | 311320 | 463800 | 6962730 | 0 | 0 | 106062 | 26400 | 448800 | 501480 | 0 | 0 | 317400 | 12545 | 0 | 0 | 73440 | 46580 | 27672 | 0 | 3840 | 8640 | 20859 | 972000 | 18340 | 586080 | 12560000 | 10036 | 0 | 236160 | 0 | 149709 | 0 | 0 | 0 | 0 | 24649088 | 114210 | 1155686 | 309454 | 4583273 | 0 | 0 | 0 | 598560 | 4695000 | 649440 | 949440 | 1299500 | 448320 | 635040 | 359770 | 0 | 1237440 | 0 | 327855 | 21696 | 7451000 | 6861400 | 8889000 | 748512 | 990000 | 0 | 89520 | 2700409 | 513432 | 0 | 1713600 | 712608 | 0 | 0 | 0 | 84600 | 181200 | 1096800 | 0 | 6200 | 171060 | 52080 | 128183362 | 19898909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306000 | 0 | 0 | 14765455 | 0 | 0 | 41541 | 0 | 0 | 0 | 349728 | 0 | 18878 | 52502 | 294440 | 66741 | 216000 | 3619118 | 0 | 0 | 0 | 4149309 | 0 | 9733600 | 0 | 18660 | 64620 | 4146000 | 1585745 | 263795 | 107247 | 86880 | 0 | 0 | 23798.16 | 699840 | 2577 | 0 | 5760000 | 138554 | 3111000 | 5281220 | 0 | 7025454 | 24453818.18 | 939600 | 107221029.34 | 235404391.34

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 31-01-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-01-2025 | during | 31-01-2025 | during | 31-01-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 3 | 3 | 97.3 | 97.3 | 3 | 3 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 335 | 347 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 420 | 450 | 450 | 360 | 360 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 254 | 294 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 275 | 300 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 8 | 0 | 8 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 54 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 20 | 19 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 22 | 22 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 19.5 | 19.5 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 26 | 26 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 122 | 131 | 134 | 134 | 134 | 134 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 58 | 50 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 12 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 72 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 26 | 0 | 26 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 0 | 17 | 17 | 17 | 17 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0.01 | 0.01 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0.01 | 0.01 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.27 | 1585.5 | 1994.5 | 4569.99 | 4551.99 | 2833.92 | 2815.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 22 | 21 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 56 | 56 | 56 | 56 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 21 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 9 | 23 | 2 | 20 | 2 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 3.37 | 0 | 3.37 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 0 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 578 | 503 | 210 | 575 | 575 | 575 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1946 | 1847 | 2868.09 | 3228.72 | 3233.09 | 3228.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 182 | 221 | 221 | 221 | 221 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 24 | 26 | 46.94 | 46.94 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 27 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 197 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 12 | 78 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 24 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 77 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 58 | 36 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 26 | 103 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 54 | 114 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 56 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 772 | 982 | 1728.97 | 1678.97 | 1626.2 | 1576.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[8 empty] | during | 0 | during | 0 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 31.66 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 1 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 0 | 40 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 105.66 | 108 | 649.2 | 601.5 | 439.2 | 391.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 42 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 113 | 113 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 36 | 36 | 40 | 40 | 40 | 40 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 2.5 | 2.5 | 2.5 | 2.5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 24 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 375 | 323 | 380 | 380 | 380 | 380 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1329 | 1259 | 1099.5 | 1099.5 | 1109.51 | 1109.51
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 641 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 45 | 45 | 45 | 45 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 40.78 | 0 | 73 | 0 | 73 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 964.78 | 641 | 3168 | 3095 | 1724 | 1651
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 302 | 301 | 450 | 450 | 270 | 330 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 132 | 136 | 136 | 136 | 140 | 140 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1130 | 1130 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 72 | 150 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.39 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 2110.39 | 2251 | 2628.12 | 2627.12 | 2449 | 2508
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 22 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 11 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 152 | 153 | 0 | 0 | 0 | 0 | GT air intake filter DP high.
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 183 | 202 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 393 | 394 | 413.79 | 413.79 | 413 | 413 | -
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 24 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 5.5 | 8.25 | 8.25 | 8.25 | 8.25 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 99 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 2.5 | 0 | 4.3 | 0 | 4.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 750.39 | 745 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 40.95 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 19 | 0 | 90 | 0 | 90 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1543.34 | 1680.5 | 2891.08 | 2746.78 | 2890.29 | 2745.99
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 70 | 65 | 70 | 70 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 166 | 183 | 160 | 160 | 150 | 150 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 38 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 90 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 131 | 0 | 135 | 0 | 135 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 386 | 376 | 639.8 | 492 | 629.8 | 482
System Total |  |  |  |  | 29204.66 | 28386.248 | 10742.67 | 11139 | 20242.75 | 20121.58 | 16935.01 | 16508.84
Forecast Scenario (31-01-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9150 |  | 0 |  | 9150
|  |  |  | 1:00 | 8450 |  | 0 |  | 8450
|  |  |  | 2:00 | 8050 |  | 0 |  | 8050
|  |  |  | 3:00 | 7700 |  | 0 |  | 7700
|  |  |  | 4:00 | 7500 |  | 0 |  | 7500
|  |  |  | 5:00 | 7300 |  | 0 |  | 7300
|  |  |  | 6:00 | 7300 |  | 0 |  | 7300
|  |  |  | 7:00 | 7450 |  | 0 |  | 7450
|  |  |  | 8:00 | 8700 |  | 0 |  | 8700
|  |  |  | 9:00 | 9200 |  | 0 |  | 9200
|  |  |  | 10:00 | 9000 |  | 0 |  | 9000
|  |  |  | 11:00 | 9250 |  | 0 |  | 9250
|  |  |  | 12:00 | 9750 |  | 0 |  | 9750
|  |  |  | 13:00 | 10500 |  | 0 |  | 10500
|  |  |  | 14:00 | 8950 |  | 0 |  | 8950
|  |  |  | 15:00 | 8400 |  | 0 |  | 8400
|  |  |  | 16:00 | 8000 |  | 0 |  | 8000
|  |  |  | 17:00 | 8500 |  | 0 |  | 8500
|  |  |  | 18:00 | 9250 |  | 0 |  | 9250
|  |  |  | 18:30 | 9650 |  | 0 |  | 9650
|  |  |  | 19:00 | 10300 |  | 0 |  | 10300
|  |  |  | 19:30 | 9800 |  | 0 |  | 9800
|  |  |  | 20:00 | 9750 |  | 0 |  | 9750
|  |  |  | 21:00 | 9600 |  | 0 |  | 9600
|  |  |  | 22:00 | 9500 |  | 0 |  | 9500
|  |  |  | 23:00 | 9200 |  | 0 |  | 9200
Probable Maximum Temperature: |  |  | 27.00°C
Probable Maximum Demand at Day Peak: |  |  | 9750.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 10300.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 10300.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 210.75 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:20 hrs on 31-01-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division
Formulas:
Effective Available Gen. on = [Forecasted Available Gen. on]

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 30-01-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10742.67 | MW | 12:00 Hr. | Energy Generated |  |  | 235.4044 |  | MKWHr.
| Day Peak Demand |  |  | 10815.67 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.184 |  | MKWHr.
| Evening Peak Generation |  |  | 11139 | MW | 19:00 Hr. | Energy Demand |  |  | 236.5884 |  | MKWHr.
| Evening Peak Demand |  |  | 11226 | MW | 19:00 Hr. | Maximum Temperature |  |  | 27 |  | °C
| Minimum Generation of the Day |  |  | 7569.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 740.63 |  | MMCFD
| Maximum Generation of the Day |  |  | 11139 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 5.671 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.7862 | 0 | 5.9526 | 0 | 0 | 0.10606 | 0 | 0 | 38.8449 | Gas | 103.4805 | Gas | 370268297.35
| Chattogram Zone |  |  | 0.58608 | 37.2091 | 0.83092 | 0 | 0.972 | 0.13507 | 0 | 0.07344 | 39.8066 | Coal | 80.1801 | Coal | 515010145.2914
| Cumilla Zone |  |  | 13.3412 | 0 | 2.3639 | 0 | 0 | 0.32786 | 1.2374 | 0 | 17.2705 | HFO | 12.3818 | HFO | 227446923.83
| Mymensingh Zone |  |  | 0 | 0 | 1.4147 | 0 | 0 | 0.17726 | 0 | 0 | 1.5919 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.6695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6695 | Hydro | 0.972 | Hydro | 97200
| Khulna Zone |  |  | 0 | 0 | 0 | 0 | 0 | 0.306 | 19.8989 | 0 | 20.2049 | Solar | 2.4148 | Solar | 37853242.036
| Barishal Zone |  |  | 8.5308 | 37.2393 | 0.9396 | 0 | 0 | 0.002577 | 0 | 0 | 46.7122 | Import | 35.9018 | Import | 183154386.39
| Rajshahi Zone |  |  | 17.5666 | 0 | 0.52939 | 0 | 0 | 0.5291 | 14.7655 | 0 | 33.3906 | Wind | 0.07344 | Wind | 1145664
| Rangpur Zone |  |  | 0 | 5.7317 | 0.35068 | 0 | 0 | 0.83089 | 0 | 0 | 6.9133
| Total |  |  | 103.4805 | 80.1801 | 12.3818 | 0 | 0.972 | 2.4148 | 35.9018 | 0.07344 | 235.4044
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 370268297.35 |  | Hydro | 97200
|  |  |  | Coal | 515010145.2914 |  | Solar | 37853242.036
|  |  |  | HFO | 227446923.83 |  | Import | 183154386.39
|  |  |  | HSD | 0 |  | Wind | 1145664
[5 empty] | Total: | 133,49,75,858 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 19.8989 | Peak Hr Flow | 641.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 7790400 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.7655 | Peak Hr Flow | 745.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 400 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.2374 | Peak Hr Flow | 36.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 682 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 35.9018 | Peak Hr Flow | 1422.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3987
|  |  |  | Chattogram |  | 0 |  | 1152
|  |  |  | Cumilla |  | 0 |  | 877
|  |  |  | Mymensingh |  | 83 |  | 988
|  |  |  | Sylhet |  | 0 |  | 374
|  |  |  | Khulna |  | 0 |  | 1220
|  |  |  | Barishal |  | 0 |  | 298
|  |  |  | Rajshahi |  | 0 |  | 1078
|  |  |  | Rangpur |  | 0 |  | 780
|  |  |  | Total |  | 83 |  | 10754
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 GT |  |  | 282 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
|  | 7 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132
[5 empty] | Total | 1074 |  |  |  | Total | 720.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1794.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 | 14:25 | Kachua 132/33kV S/S Main Bus-1 Project Work S/D Due to Busbar Extention/Jumpering works
at existing Kachua 132/33kV Grid substation by ESPNER Project.
| 08:30 | 14:58 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintenance work done by Hasanabad & Munshiganj SS.
| 08:33 | 14:43 | Rajbari 132/33kV S/S Faridpur - 2 Scheduled S/D
| 08:49 | 17:22 | Gopalganj(N)-Madaripur 132kV Ckt-3 Scheduled S/D from Madaripur 132/33kV end Due to
Annual Maintenance and from Gopalganj 400/132kVend.
| 08:49 | 17:26 | Madaripur 132/33kV S/S Gopaganj North CKT-04 Scheduled S/D Due to Annual Maintenance
| 08:53 | 17:25 | Gopalganj 400/132kV S/S 132kV Madaripur Ckt-4 Scheduled S/D
| 08:56 | 16:33 | Cumilla(N)-Cumilla(S) 132 kV Ckt-3 Scheduled S/D from Cumilla(S) 132/33kV end Due to
Annual Maintenance
| 09:12 | 15:54 | Moghbazar-Rampura 132kV Ckt-1 Scheduled S/D from Mogbazar 132/33kV end Due to Annual
Maintenance and from Rampura 230/132kV end Due to Mogbajar & NLDC
| 09:18 | 14:19 | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Scheduled S/D Due to Annual Maintenance | [7 empty] | 30.0MW load
interrup.
| 09:18 | 14:19 | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT Scheduled S/D Due to Annual maintenance | [7 empty] | 30.0MW load
interrup.
| 09:19 |  | Jashore 132/33kV S/S 132 kV Bus-A Project Work S/D
| 09:26 | 15:08 | Ghorashal 230kV S/S TARFO-2 LT Tripped showing SIEMENS 33KV O/C & E/F RELAY relays Due to | [7 empty] | 65.0MW load
|  |  | Trip for PBS 33KV Y phase loop connection burn | [7 empty] | interrup.
| 09:28 | 11:27 | BIPTC S/S 10CF22 Forced S/D Due to Tripped by impedance 21R
| 09:58 | 18:14 | Aminbazar 400/230/132kV S/S 400/132kV Interim Transformer LT Scheduled S/D Due to Annual
maintenance
| 10:03 | 17:49 | Aminbazar 400/230/132kV S/S 400/132kV Interim Transformer HT Scheduled S/D Due to Annual
maintenance
| 10:08 | 19:53 | Bhulta-Haripur 230 kV Ckt-2 Project Work S/D from Bhulta 400/230kV end Due to 230kV
Haripur Ckt-02 Shutdown taken by EEGBPSP for Project Work. and from Haripur 230/132kV end
Due to Work on other end.
| 11:05 | 11:18 | Natore 132/33kV S/S TR-4 (435 T) HT Tripped showing No. relays Due to TRTUD manpower | [7 empty] | 18.0MW load
|  |  | working into T-4 HT panel. | [7 empty] | interrup.
| 11:06 | 11:19 | Natore 132/33kV S/S TR-4 (435 T) LT Tripped showing No relays Due to Not tripped, | [7 empty] | 18.0MW load
|  |  | manually open. | [7 empty] | interrup.
| 11:15 | 19:46 | BIPTC S/S Baharampur-4 Scheduled S/D Due to taken from india
| 12:00 |  | Day Peak Generation: 10738 MW.
|  | 14:42 | Faridpur 132/33kV S/S 132 KV Rajbari ckt-2 is restored.
| 15:08 |  | 230/33kV, 120/140 MVA Transformer was switched on at Ghorashal GIS grid Substation.
|  | 16:09 | BSRM-Cumilla(N) 230 kV Ckt-2 is restored.
| 16:10 | 16:51 | Ghatail 132/33kV S/S T-1 LT Forced S/D Due to Security Light Fitting. | [7 empty] | 30.0MW load
interrup.
| 16:12 | 16:52 | Ghatail 132/33kV S/S T-2 LT Forced S/D Due to Security Light Fitting. | [7 empty] | 30.0MW load
interrup.
| 17:57 | 20:27 | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) Forced S/D Due to Red Hot
Maintenance at other end.
| 19:00 |  | Evening Peak Gen. 11139 MW
| 21:06 |  | The 20/230 kV, 440 MVA unit transformer was switched on for the first time at Rupsha 800
Megawatt Combined Cycle Power Plant, Unit-1.
|  | 22:24 | Bhulta-Ghorasal 230 kV Ckt-2 is restored.
| 23:08 |  | Bibiyana South 400 MW Tripped with remarks:- st
| 23:08 |  | Bibiyana South 400 MW Synchronized with remarks:- st tripped-2308
|  | 23:18 | Bhulta 400/230kV S/S 230kV Bus-02 is restored.
| 23:18 |  | Bibiyana South 400 MW Tripped with remarks:- gt
| 00:00 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
| 00:00 |  | Sirajgonj 225MW CCPP Unit-1 ST Shutdown with remarks:- Due to GT air intake filter DP
high.
| 00:14 |  | Sirajgonj 225MW CCPP Unit-1 GT Shutdown with remarks:- Due to GT air intake filter DP
high.
| 00:14 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- GT
| 01:38 |  | MI_Cement 132/33kV S/S MI Cement HT Tripped showing over current relay relays. | [7 empty] | 16.0MW load
interrup.
|  | 03:41 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor is restored.
|  | 03:42 | Rampal 400/230kV S/S Gopalganj Line-2 Reactor is restored.
| 05:00 |  | Minimum Generation = 7,656MW
| 05:57 | 06:20 | Cumilla(S) 132/33kV S/S TR-2 LT Tripped showing RET650 ,REF 615 relays Due to 33KV Feeder | [7 empty] | 8.0MW load
|  |  | Fault | [7 empty] | interrup.
| 05:57 | 06:20 | Cumilla(S) 132/33kV S/S TR-1 LT Tripped showing RET-650,REF-615 relays Due to 33KV Kasba | [7 empty] | 8.0MW load
|  |  | feeder fault. | [7 empty] | interrup.
| 06:50 |  | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end Due to Conductor
stringing for relocated route. Tower no 4,5.
| 07:20 |  | Rangpur 132/33kV S/S T-1(414T) LT Scheduled S/D | [7 empty] | 65.0MW load
interrup.
| 07:21 |  | Rangpur 132/33kV S/S T-1(414T) HT Scheduled S/D Due to None
| 07:22 |  | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D
| 07:23 |  | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D
| 07:26 |  | BSRM-Cumilla(N) 230 kV Ckt-1 Project Work S/D from BSRM 230/33kV end. and from Cumilla(N)
230/132/33kVend.
| 07:28 |  | Halishahar 132/33kV S/S 403T(TR-1) HT Project Work S/D Due to Gis project work.
| 07:33 |  | Keranigonj 230/132/33kV S/S 132 kV Lalbagh Ckt. 3 Scheduled S/D Due to Dead line
checking.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 30-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 3 | 80500 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 347 | 9194400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 7823000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 294 | 7074298 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 73756 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6962730 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 412920 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 546720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 54 | 62578 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 311320 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19 | 448800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 501480 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 237240 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 19.5 | 463800 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 26 | 373440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 2294064 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 50 | 842880 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 12 | 30720 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 977760 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 106062 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 0 | 0 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 17 | 26400 | -
Dhaka Area Total |  |  |  |  | 5841.27 | 1994.5 | 38844868
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | U#1 Gas Shortage, U#2 Turbine Blade Damage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 114210 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 21 | 236160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 972000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 149709 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 27672 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 21 | 46580 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 3840 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 23 | 586080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20859 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 12545 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 18340 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 8640 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 317400 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 10036 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 24649088 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 0 | 73440 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 503 | 12560000 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 1847 | 39806599
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4695000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 26 | 649440 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 598560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4583273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1155686 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 78 | 309454 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 24 | 21696 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1299500 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 77 | 448320 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 36 | 1237440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 359770 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 103 | 635040 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 114 | 949440 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 327855 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 982 | 17270474
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1096800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 181200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 171060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 1 | 52080 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 40 | 84600 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 108 | 1591940
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 42 | 990000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 113 | 2700409 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 36 | 748512 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 89520 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 712608 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1713600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 24 | 513432 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7451000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 323 | 8889000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 6861400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1259 | 30669481
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 641 | 19898909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 306000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 641 | 20204909
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 301 | 7025454 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 138554 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 136 | 3111000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1130 | 24453818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5281220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 939600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5760000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2577 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2251 | 46712223.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 22 | 41541 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 11 | 18878 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 153 | 3619118 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 202 | 4149309 | Plant is in Standby as per NLDC request.
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 394 | 9733600 | -
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 24 | 66741 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 5.5 | 64620 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 52502 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 99 | 349728 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 18660 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 745 | 14765455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 216000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 294440 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1680.5 | 33390592
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 65 | 1585745 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 183 | 4146000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 38 | 86880 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 23798.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 263795 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 107247 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 699840 | -
Rangpur Area Total |  |  |  |  | 950 | 376 | 6913305.16
Eastern Grid Total |  |  |  |  | 16771.748 | 6190.5 | 128183362
Western Grid Total |  |  |  |  | 11614.5 | 4948.5 | 107221029.34
National Grid Total |  |  |  |  | 28386.248 | 11139 | 235404391.34
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 30-01-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7294.41 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3375.9 | MW
i) Dhaka area |  |  | 3986.61 |  | MW | i) Khulna area |  |  |  | 1220.2 | MW
ii) Chattogram area |  |  | 1151.8 |  | MW | ii) Barishal area |  |  |  | 297.5 | MW
iii) Cumilla area |  |  | 877 |  | MW | iii) Rajshahi area |  |  |  | 1078.2 | MW
iv) Mymensingh area |  |  | 905 |  | MW | iv) Rangpur area |  |  |  | 780 | MW
v) Sylhet area |  |  | 374 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10670.31 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 64 | 18:30 | 133 | Purbachal | 14 | 13:00
2 | AKSML | 102 | 04:00 | 68 | Jamalpur | 86 | 00:00 | 134 | Purbasadipur | 111 | 18:30
3 | Aftabnagar | 26 | 13:00 | 69 | Jashore | 111 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 76 | 13:00 | 70 | Jhenaidah | 96 | 08:00 | 136 | Rahim | 39 | 10:00
5 | Agrabad | 60 | 18:00 | 71 | Joydebpur | 126 | 20:00 | 137 | Rajbari | 56 | 18:30
6 | Amnura | 48 | 09:00 | 72 | Joypurhat | 52 | 09:00 | 138 | Rajendrapur | 94 | 19:00
7 | Ashuganj | 68 | 13:00 | 73 | Juldah | 11 | 12:00 | 139 | Rajshahi | 76 | 19:00
8 | BSRM | 193 | 21:00 | 74 | KSRM | 32 | 08:00 | 140 | Rajshahi-230 | 59 | 13:00
9 | Bagerhat | 68 | 18:30 | 75 | Kabirpur | 233 | 18:00 | 141 | Ramganj | 86 | 18:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 53 | 20:00 | 142 | Rampur | 25 | 18:00
11 | Bakulia | 64 | 13:00 | 77 | Kallyanpur | 57 | 13:00 | 143 | Rangamati | 13 | 18:00
12 | Banani | 35.6 | 13:00 | 78 | Kalurghat | 30 | 10:00 | 144 | Rangpur | 96 | 14:00
13 | Bangabhaban | 8 | 10:00 | 79 | Kamrangirchar | 59 | 13:00 | 145 | Ruppur | 4.4 | 11:00
14 | Barapukuria | 61 | 10:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 14 | 02:00
15 | Barguna | 14 | 19:00 | 81 | Kazla | 87 | 13:00 | 147 | Saidpur | 105 | 09:00
16 | Barishal | 93 | 12:00 | 82 | Keranigonj | 59 | 13:00 | 148 | Satkhira | 90 | 19:00
17 | Barishal-230 | 54 | 20:00 | 83 | Khagrachori | 22 | 18:00 | 149 | Satmasjid | 86 | 13:00
18 | Baroaulia | 64.2 | 10:00 | 84 | Khulna | 81 | 13:00 | 150 | Savar | 176 | 12:00
19 | Baroirhat | 53 | 18:00 | 85 | Khulshi | 143 | 18:00 | 151 | SevenRings | 17.85 | 19:30
20 | Bashundhara | 133 | 13:00 | 86 | Kishoreganj | 124 | 19:00 | 152 | ShahCement | 27 | 12:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kodda | 262 | 12:00 | 153 | Shahjadpur | 58 | 18:30
22 | Beanibazar | 48 | 18:00 | 88 | Kulaura | 28 | 18:00 | 154 | Shahjibazar | 82 | 18:30
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 60 | 18:00 | 155 | Shahmirpur | 41.5 | 23:00
24 | Bhaluka | 122 | 15:00 | 90 | Kushtia | 112 | 18:30 | 156 | Shariatpur | 53 | 20:00
25 | Bhandaria | 32 | 19:30 | 91 | Lalbag | 51 | 19:00 | 157 | Sherpur | 104 | 00:00
26 | Bhangura | 27 | 18:30 | 92 | Lalmonirhat | 48 | 18:30 | 158 | Shikalbaha | 18 | 00:00
27 | Bheramara(GK) | 41 | 18:30 | 93 | MI_Cement | 17.2 | 03:00 | 159 | Shitalakhya | 64.3 | 13:00
28 | Bhulta | 237.5 | 10:00 | 94 | Madanganj | 17 | 11:00 | 160 | Sholosohor | 30 | 12:00
29 | Bog-Sherpur | 66 | 09:00 | 95 | Madaripur | 66 | 13:00 | 161 | Shyampur | 170 | 11:00
30 | Bogura | 117 | 18:30 | 96 | Madartek | 61.28 | 13:00 | 162 | Siddhirganj | 97 | 12:00
31 | Borhanuddin | 54 | 21:00 | 97 | Madunaghat | 34 | 13:00 | 163 | Sirajganj | 80 | 08:00
32 | Brahmanbaria | 104 | 14:00 | 98 | Magura | 46 | 18:30 | 164 | Sonargaon | 83 | 12:00
33 | Cantonment | 80 | 13:00 | 99 | Mahasthangarh | 56 | 18:30 | 165 | Sreemongol | 53 | 21:00
34 | Chandpur | 42 | 19:00 | 100 | Manikganj | 108 | 18:30 | 166 | Sreepur | 84 | 18:30
35 | Chandraghona | 26 | 18:00 | 101 | Maniknagar | 52 | 13:00 | 167 | Srinagar | 30 | 14:00
36 | Chapai | 65 | 08:00 | 102 | Matarbari | 39 | 18:30 | 168 | Sunamganj | 36 | 18:00
37 | Charsaidpur | 40 | 00:00 | 103 | Matuail | 60 | 16:00 | 169 | Sylhet | 24 | 18:00
38 | Chauddagram | 45 | 13:00 | 104 | Millgate | 74 | 12:00 | 170 | Sylhet-132 | 76 | 16:00
39 | Chhatak | 22 | 18:30 | 105 | Mirpur | 97 | 18:00 | 171 | TK | 21 | 19:00
40 | Chowmuhani | 143 | 18:30 | 106 | Mirsorai | 8 | 16:00 | 172 | Tangail | 144 | 07:00
41 | Chuadanga | 71 | 18:30 | 107 | Mirzapur | 36 | 18:00 | 173 | Thakurgaon | 79 | 18:30
42 | Coxsbazar | 102 | 18:00 | 108 | Mithapukur | 70 | 08:00 | 174 | Tongi | 111 | 12:00
43 | Cumilla(N) | 134 | 20:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 23 | 08:00
44 | Cumilla(S) | 131 | 13:00 | 110 | Mogbazar | 98.1 | 13:00 | 176 | Ullon | 35 | 13:00
45 | Daudkandi | 110 | 20:00 | 111 | Mongla | 32 | 10:00 | 177 | Uttara | 60 | 13:00
46 | Dhaka | 28 | 12:00 | 112 | Motijheel | 26 | 13:00 | 178 | UttaraNew | 35 | 13:00
47 | Dhamrai | 96 | 08:00 | 113 | Muktagacha | 27 | 10:00 | 179 | Zigatola | 57 | 18:30
48 | Dhanmondi | 97 | 13:00 | 114 | Munshiganj | 71 | 13:00
49 | Dohazari | 74 | 18:00 | 115 | Mymensingh | 158 | 18:00
50 | Faridpur | 108 | 18:30 | 116 | Naogaon | 101 | 08:00
51 | Fatullah | 70 | 12:00 | 117 | Narail | 41 | 18:30
52 | Fenchuganj | 25 | 13:00 | 118 | Narinda | 63 | 13:00
53 | Feni | 67 | 18:00 | 119 | Narshingdi | 150 | 20:00
54 | GPH | 102 | 01:00 | 120 | Natore | 105 | 18:30
55 | Ghatail | 40 | 17:00 | 121 | Nawabganj | 29.6 | 14:00
56 | Ghorashal | 14 | 22:00 | 122 | Netrakona | 140 | 07:00
57 | Ghorashal-230 | 66 | 07:00 | 123 | New | 72.7 | 12:00
58 | Goalpara | 24 | 18:30 | 124 | Niamatpur | 84 | 09:00
59 | Gollamari | 50 | 13:00 | 125 | Noapara | 36 | 18:30
60 | Gopalganj | 76.6 | 18:30 | 126 | PHP | 9 | 19:30
61 | Gulshan | 74 | 13:00 | 127 | Pabna | 66 | 18:30
62 | Halishahar | 47 | 18:30 | 128 | Palashbari | 92 | 18:30
63 | HaripurSBU | 165 | 11:00 | 129 | Panchagarh | 44 | 18:30
64 | Hasnabad | 71 | 12:00 | 130 | Patuakhali | 57.1 | 21:00
65 | Hathazari | 54 | 18:00 | 131 | Payra | 14 | 13:00
66 | Ishurdi | 63 | 18:30 | 132 | Postogola | 43 | 13:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 30-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9132.5 | 0 |  | 9132.5
1:00 | 8629 | 29 |  | 8659
2:00 | 8149 | 26 |  | 8176
3:00 | 7901.5 | 28 |  | 7930.5
4:00 | 7668.5 | 26 |  | 7695.5
5:00 | 7569.5 | 25 |  | 7595.5
6:00 | 8114.5 | 25 |  | 8140.5
7:00 | 8915.81 | 45 |  | 8962.84
8:00 | 9755.9 | 60 |  | 9818.9
9:00 | 10344.37 | 90 |  | 10438.37
10:00 | 10154.19 | 47 |  | 10203.19
11:00 | 10250.61 | 65 |  | 10318.61
12:00 | 10742.67 | 70 |  | 10815.67
13:00 | 10921.49 | 65 |  | 10989.49
14:00 | 10431.5 | 60 |  | 10494.5
15:00 | 10164.55 | 30 |  | 10195.9
16:00 | 9823.01 | 35 |  | 9859.59
17:00 | 9962.47 | 45 |  | 10009.47
18:00 | 10717 | 80 |  | 10801
19:00 | 11139 | 83 |  | 11226
19:30 | 10959 | 88 |  | 11051
20:00 | 10807 | 85 |  | 10896
21:00 | 10665.67 | 73 |  | 10741.96
22:00 | 10246.62 | 47 |  | 10295.62
23:00 | 9703.85 | 45 |  | 9750.85
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 30-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4971 | 4161.5 | 9132.5 | DAILY GENERATION CURVE
00:30 | 4774.25 | 4106.5 | 8880.75
01:00 | 4577.5 | 4051.5 | 8629 | 30-01-2025
01:30 | 4542 | 3847 | 8389
02:00 | 4506.5 | 3642.5 | 8149
02:30 | 4477.25 | 3548 | 8025.25
03:00 | 4448 | 3453.5 | 7901.5
03:30 | 4340.5 | 3444.5 | 7785
04:00 | 4233 | 3435.5 | 7668.5
04:30 | 4152.5 | 3466.5 | 7619
05:00 | 4072 | 3497.5 | 7569.5
05:30 | 4277.5 | 3564.5 | 7842
06:00 | 4483 | 3631.5 | 8114.5
06:30 | 4656.05 | 3859.105 | 8515.155
07:00 | 4829.1 | 4086.71 | 8915.81
07:30 | 5048.95 | 4286.905 | 9335.855
08:00 | 5268.8 | 4487.1 | 9755.9
08:30 | 5510.42 | 4539.715 | 10050.135
09:00 | 5752.04 | 4592.33 | 10344.37
09:30 | 5646.515 | 4602.765 | 10249.28
10:00 | 5540.99 | 4613.2 | 10154.19
10:30 | 5602.595 | 4599.805 | 10202.4
11:00 | 5664.2 | 4586.41 | 10250.61
11:30 | 5701.18 | 4795.46 | 10496.64
12:00 | 5738.16 | 5004.51 | 10742.67
12:30 | 5808.69 | 5023.39 | 10832.08
13:00 | 5879.22 | 5042.27 | 10921.49
13:30 | 5766.46 | 4910.035 | 10676.495
14:00 | 5653.7 | 4777.8 | 10431.5
14:30 | 5564.405 | 4733.62 | 10298.025
15:00 | 5475.11 | 4689.44 | 10164.55
15:30 | 5372.665 | 4621.115 | 9993.78
16:00 | 5270.22 | 4552.79 | 9823.01
16:30 | 5344.3 | 4548.44 | 9892.74
17:00 | 5418.38 | 4544.09 | 9962.47
17:30 | 5587.44 | 4752.295 | 10339.735
18:00 | 5756.5 | 4960.5 | 10717
18:30 | 5973.5 | 4954.5 | 10928
19:00 | 6190.5 | 4948.5 | 11139
19:30 | 5979.5 | 4979.5 | 10959
20:00 | 5853.5 | 4953.5 | 10807
20:30 | 5817.25 | 4919.085 | 10736.335 |  | Executive Engineer
21:00 | 5781 | 4884.67 | 10665.67 |  | Network Operation Division
21:30 | 5643.5 | 4812.645 | 10456.145
22:00 | 5506 | 4740.62 | 10246.62
22:30 | 5371.75 | 4603.485 | 9975.235
23:00 | 5237.5 | 4466.35 | 9703.85

## En-Curve
QF-LDC-12
Date | 30-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2821 | 1694.5 | 925 | 0 | 52 | 426 | 40 | 2980 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 2752 | 1675.25 | 925 | 0 | 54 | 424.5 | 40 | 2856.5 | 0 | 0 | 149.5 | 0 | 0 | 4 | 14.5 | 30-01-2025
01:00 | 2683 | 1656 | 925 | 0 | 56 | 423 | 40 | 2733 | 0 | 0 | 105 | 0 | 0 | 8 | 29
01:30 | 2625.5 | 1691 | 859 | 0 | 56 | 423 | 40 | 2607.5 | 0 | 0 | 77.5 | 0 | 0 | 9.5 | 27.5 | Energy Generated | 235.4044 |  | MKWHr
02:00 | 2568 | 1726 | 793 | 0 | 56 | 423 | 40 | 2482 | 0 | 0 | 50 | 0 | 0 | 11 | 26 | Energy not Served | 1.184 |  | MKWHr
02:30 | 2560.5 | 1748.75 | 763.5 | 0 | 50 | 416.5 | 40 | 2383 | 0 | 0 | 50 | 0 | 0 | 13 | 27 | Total Energy Requirement | 236.5884 |  | MKWHr
03:00 | 2553 | 1771.5 | 734 | 0 | 44 | 410 | 40 | 2284 | 0 | 0 | 50 | 0 | 0 | 15 | 28
03:30 | 2521 | 1728 | 734.5 | 0 | 48 | 410 | 40 | 2247 | 0 | 0 | 42 | 0 | 0 | 14.5 | 27
04:00 | 2489 | 1684.5 | 735 | 0 | 52 | 410 | 40 | 2210 | 0 | 0 | 34 | 0 | 0 | 14 | 26
04:30 | 2502.5 | 1618 | 735 | 0 | 49 | 410 | 40 | 2215.5 | 0 | 0 | 34 | 0 | 0 | 15 | 25.5
05:00 | 2516 | 1551.5 | 735 | 0 | 46 | 410 | 40 | 2221 | 0 | 0 | 34 | 0 | 0 | 16 | 25
05:30 | 2497 | 1666 | 758.5 | 0 | 49 | 411.5 | 40 | 2347.5 | 0 | 0 | 61.5 | 0 | 0 | 11 | 25
06:00 | 2478 | 1780.5 | 782 | 0 | 52 | 413 | 40 | 2474 | 0 | 0 | 89 | 0 | 0 | 6 | 25
06:30 | 2473 | 1768.25 | 805.5 | 0 | 50 | 492 | 40 | 2761 | 3.905 | 16 | 102 | 0 | 0 | 3.5 | 35
07:00 | 2468 | 1756 | 829 | 0 | 48 | 571 | 40 | 3048 | 7.81 | 32 | 115 | 0 | 0 | 1 | 45
07:30 | 2463.5 | 1775.75 | 735.5 | 0 | 52 | 666.11 | 40 | 3308.5 | 47.995 | 50 | 196 | 0 | 0 | 0.5 | 52.5
08:00 | 2459 | 1795.5 | 642 | 0 | 56 | 761.22 | 40 | 3569 | 88.18 | 68 | 277 | 0 | 0 | 0 | 60
08:30 | 2459.5 | 1767.5 | 641.5 | 0 | 57 | 759.055 | 40 | 3675 | 146.08 | 80 | 424.5 | 0 | 0 | 0 | 75
09:00 | 2460 | 1739.5 | 641 | 0 | 58 | 756.89 | 40 | 3781 | 203.98 | 92 | 572 | 0 | 0 | 0 | 90
09:30 | 2444 | 1688.25 | 782.5 | 0 | 57 | 707 | 40 | 3659 | 242.03 | 92 | 537.5 | 0 | 0 | 0 | 68.5
10:00 | 2428 | 1637 | 924 | 0 | 56 | 657.11 | 40 | 3537 | 280.08 | 92 | 503 | 0 | 0 | 0 | 47
10:30 | 2495.5 | 1670.5 | 924.5 | 0 | 56 | 635.25 | 40 | 3474.5 | 306.15 | 92 | 508 | 0 | 0 | 0 | 56
11:00 | 2563 | 1704 | 925 | 0 | 56 | 613.39 | 40 | 3412 | 332.22 | 92 | 513 | 0 | 0 | 0 | 65
11:30 | 2528.5 | 1706 | 924.5 | 0 | 57 | 681.89 | 40 | 3566 | 354.25 | 104 | 534.5 | 0 | 0 | 0 | 67.5
12:00 | 2494 | 1708 | 924 | 0 | 58 | 750.39 | 40 | 3720 | 376.28 | 116 | 556 | 0 | 0 | 0 | 70
12:30 | 2498 | 1691 | 924.5 | 0 | 65 | 754.49 | 40 | 3751.5 | 376.59 | 122 | 608.5 | 0 | 0 | 0.5 | 67.5
13:00 | 2502 | 1674 | 925 | 0 | 72 | 758.59 | 40 | 3783 | 376.9 | 128 | 661 | 0 | 0 | 1 | 65
13:30 | 2466.5 | 1691.5 | 925 | 0 | 68 | 709.795 | 40 | 3670.5 | 347.7 | 110 | 646.5 | 0 | 0 | 1 | 62.5
14:00 | 2431 | 1709 | 925 | 0 | 64 | 661 | 40 | 3558 | 318.5 | 92 | 632 | 0 | 0 | 1 | 60
14:30 | 2423 | 1709 | 925 | 0 | 61 | 661 | 40 | 3543 | 291.025 | 92 | 551.5 | 0 | 0 | 1.5 | 45
15:00 | 2415 | 1709 | 925 | 0 | 58 | 661 | 40 | 3528 | 263.55 | 92 | 471 | 0 | 0 | 2 | 30
15:30 | 2433 | 1706 | 925 | 0 | 57 | 647.5 | 40 | 3523 | 190.78 | 97 | 373.5 | 0 | 0 | 1 | 32.5
16:00 | 2451 | 1703 | 925 | 0 | 56 | 634 | 40 | 3518 | 118.01 | 102 | 276 | 0 | 0 | 0 | 35
16:30 | 2463.5 | 1733 | 924.5 | 0 | 60 | 626 | 40 | 3521.5 | 75.24 | 157 | 292 | 0 | 0 | 0 | 40
17:00 | 2476 | 1763 | 924 | 0 | 64 | 618 | 40 | 3525 | 32.47 | 212 | 308 | 0 | 0 | 0 | 45
17:30 | 2519 | 1762 | 924 | 0 | 51 | 638 | 40 | 3565.5 | 16.235 | 294.5 | 529.5 | 0 | 0 | 0 | 62.5
18:00 | 2562 | 1761 | 924 | 0 | 38 | 658 | 40 | 3606 | 0 | 377 | 751 | 0 | 0 | 0 | 80
18:30 | 2533.5 | 1815 | 782.5 | 0 | 37 | 701.5 | 40 | 3659.5 | 0 | 367.5 | 991.5 | 0 | 0 | 0 | 81.5
19:00 | 2505 | 1869 | 641 | 0 | 36 | 745 | 40 | 3713 | 0 | 358 | 1232 | 0 | 0 | 0 | 83
19:30 | 2542 | 1927 | 641 | 0 | 34 | 755 | 40 | 3724 | 0 | 322 | 974 | 0 | 0 | 0 | 88
20:00 | 2538 | 1905 | 640 | 0 | 30 | 759 | 40 | 3722 | 0 | 292 | 881 | 0 | 0 | 0 | 85
20:30 | 2555 | 1911.25 | 781.5 | 0 | 35 | 758.585 | 40 | 3757 | 0 | 217.5 | 680.5 | 0 | 0 | 0 | 79
21:00 | 2572 | 1917.5 | 923 | 0 | 40 | 758.17 | 40 | 3792 | 0 | 143 | 480 | 0 | 0 | 0 | 73
21:30 | 2545 | 1918.5 | 924 | 0 | 41 | 756.145 | 40 | 3791.5 | 0 | 100.5 | 339.5 | 0 | 0 | 0 | 60
22:00 | 2518 | 1919.5 | 925 | 0 | 42 | 754.12 | 40 | 3791 | 0 | 58 | 199 | 0 | 0 | 0 | 47
22:30 | 2363.5 | 1869.25 | 925 | 0 | 45 | 706.985 | 40 | 3768.5 | 0 | 58 | 199 | 0 | 0 | 0 | 46
23:00 | 2209 | 1819 | 925 | 0 | 48 | 659.85 | 40 | 3746 | 0 | 58 | 199 | 0 | 0 | 0 | 45
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 30-01-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 410 | 04:00 | 384 | 12:00 | Payra | 416 | 03:00 | 406 | 11:00
Ashuganj | 406 | 2:00 | 379 | 12:00 | Rahanpur | 417 | 04:00 | 401 | 08:00
Bhulta | 406 | 04:00 | 380 | 12:00 | Rampal | 417 | 02:00 | 385 | 12:00
Bibiana | 398 | 01:00 | 391 | 11:00
BIPTC | 409 | 04:00 | 386 | 11:00
Bogura | 416 | 04:00 | 395 | 08:00
Gopalganj | 413 | 02:00 | 389 | 12:00
Kaliakoir | 388 | 04:00 | 372 | 12:00
Madunaghat | 410 | 05:00 | 392 | 12:00
Meghnaghat | 408 | 04:00 | 383 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 03:00 | 221 | 12:00 | Keranigonj | 236 | 07:00 | 219 | 12:00
AKSML | 233 | 05:00 | 220 | 12:00 | Khulna(S) | 241 | 03:00 | 222 | 12:00
Aminbazar | 236 | 03:00 | 220 | 12:00 | Madunaghat | 233 | 05:00 | 28 | 19:00
Ashuganj | 238 | 05:00 | 226 | 12:00 | Madunaghat-400 | 235 | 04:00 | 223 | 13:00
Ashuganj-400 | 238 | 05:00 | 226 | 12:00 | Maniknagar | 235 | 04:00 | 220 | 12:00
Baghabari | 240 | 01:00 | 227 | 12:00 | Meghnaghat | 240 | 02:00 | 227 | 12:00
Barapukuria | 226 | 03:00 | 215 | 08:00 | Meghnaghat-400 | 238 | 04:00 | 225 | 12:00
Barapukuria-230 | 226 | 03:00 | 215 | 08:00 | Mirsorai | 233 | 05:00 | 221 | 16:00
Barishal | 245 | 03:00 | 233 | 12:00 | Rajshahi | 239 | 04:00 | 224 | 10:00
Bheramara | 239 | 06:00 | 222 | 12:00 | Rampal | 239 | 02:00 | 220 | 12:00
Bhulta | 236 | 03:00 | 221 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 03:00 | 223 | 12:00 | Rampura | 235 | 01:00 | 222 | 12:00
BIPTC | 241 | 06:00 | 223 | 12:00 | Shikalbaha | 234 | 05:00 | 221 | 12:00
Bogura | 241 | 03:00 | 228 | 08:00 | Shyampur | 235 | 03:00 | 220 | 12:00
Bogura-400 | 239 | 02:00 | 227 | 08:00 | Siddhirganj | 232 | 00:00 | 224 | 14:00
Borhanuddin | 248 | 02:00 | 238 | 14:00 | Sirajgonj | 245 | 02:00 | 237 | 12:00
BSRM | 233 | 04:00 | 219 | 12:00 | Sreepur | 238 | 01:00 | 227 | 12:00
Cumilla(N) | 232 | 04:00 | 222 | 12:00 | Tongi | 231 | 04:00 | 216 | 12:00
Faridpur | 243 | 06:00 | 230 | 12:00
Fenchuganj | 234 | 01:00 | 226 | 11:00
Ghorashal | 240 | 01:00 | 230 | 07:00
Ghorashal-230 | 234 | 02:00 | 220 | 12:00
Gopalganj | 244 | 02:00 | 231 | 12:00
GPH | 233 | 04:00 | 221 | 13:00
Haripur | 237 | 05:00 | 221 | 12:00
Hasnabad | 236 | 06:00 | 223 | 11:00
Hathazari | 230 | 00:00 | 224 | 15:00
Ishurdi | 241 | 06:00 | 226 | 10:00
Jhenaidah | 239 | 03:00 | 223 | 13:00
Kaliakoir | 232 | 02:00 | 217 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 124 | 12:00 | Magura | 138 | 00:00 | 126 | 12:00
Agargaon | 137 | 02:00 | 127 | 12:00 | Mahasthangarh | 136 | 03:00 | 125 | 08:00
Agrabad | 135 | 04:00 | 127 | 15:00 | Manikganj | 134 | 13:00 | 130 | 12:00
AKS | 132 | 05:00 | 127 | 10:00 | Maniknagar | 135 | 04:00 | 125 | 12:00
Aminbazar | 136 | 05:00 | 125 | 12:00 | Matarbari | 131 | 05:00 | 118 | 19:30
Amnura | 141 | 18:30 | 130 | 08:00 | Matuail | 134 | 03:00 | 127 | 12:00
Ashuganj | 140 | 02:00 | 135 | 12:00 | Millgate | 137 | 01:00 | 123 | 12:00
Bagerhat | 137 | 02:00 | 124 | 12:00 | Mirpur | 135 | 03:00 | 125 | 12:00
Bajitpur | 133 | 19:00 | 30 | 08:00 | Mirzapur | 132 | 00:00 | 126 | 12:00
Bakulia | 134 | 04:00 | 127 | 12:00 | Mithapukur | 134 | 04:00 | 120 | 08:00
Banani | 135 | 01:00 | 126 | 12:00 | MI_Cement | 136 | 04:00 | 127 | 13:00
Bangabhaban | 135 | 05:00 | 125 | 13:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 136 | 03:00 | 125 | 08:00 | Mogbazar | 138 | 03:00 | 123 | 13:00
Barguna | 139 | 18:30 | 133 | 22:00 | Mongla | 135 | 00:00 | 123 | 12:00
Barishal | 135 | 04:00 | 127 | 12:00 | Motijheel | 135 | 04:00 | 125 | 13:00
Barishal-230 | 137 | 03:00 | 128 | 12:00 | Muktagacha | 124 | 09:00 | 114 | 06:00
Baroaulia | 133 | 03:00 | 127 | 12:00 | Munshiganj | 135 | 05:00 | 127 | 12:00
Baroirhat | 132 | 19:00 | 125 | 12:00 | Mymensingh | 125 | 01:00 | 110 | 01:00
Bashundhara | 137 | 02:00 | 124 | 12:00 | Naogaon | 136 | 04:00 | 124 | 12:00
BashundharaCement | 134 | 04:00 | 127 | 17:00 | Narail | 140 | 03:00 | 125 | 12:00
Beanibazar | 136 | 02:00 | 130 | 12:00 | Narinda | 135 | 4:00 | 124 | 12:00
Benapole | 139 | 04:00 | 121 | 12:00 | Narshingdi | 130 | 01:00 | 116 | 13:00
Bhaluka | 127 | 00:00 | 118 | 12:00 | Natore | 137 | 00:00 | 128 | 13:00
Bhandaria | 135 | 04:00 | 125 | 12:00 | Nawabganj | 138 | 03:00 | 127 | 12:00
Bhangura | 140 | 04:00 | 129 | 12:00 | Netrakona | 125 | 03:00 | 115 | 12:00
Bheramara | 138 | 00:00 | 127 | 12:00 | New | 138 | 02:00 | 125 | 12:00
Bheramara(GK) | 140 | 03:00 | 128 | 12:00 | Niamatpur | 139 | 00:00 | 133 | 08:00
Bhulta | 128 | 03:00 | 122 | 12:00 | Noapara | 139 | 03:00 | 124 | 12:00
Bog-Sherpur | 137 | 04:00 | 127 | 08:00 | Pabna | 137 | 03:00 | 125 | 13:00
Bogura | 138 | 03:00 | 129 | 09:00 | Palashbari | 133 | 04:00 | 120 | 08:00
Bogura-230 | 139 | 08:00 | 129 | 09:00 | Panchagarh | 138 | 19:30 | 118 | 08:00
Brahmanbaria | 130 | 00:00 | 124 | 13:00 | Patuakhali | 137 | 20:00 | 132 | 14:00
Cantonment | 137 | 02:00 | 127 | 12:00 | Payra | 139 | 18:00 | 134 | 09:00
Chandpur | 138 | 19:00 | 123 | 22:00 | PHP | 132 | 19:00 | 124 | 12:00
Chandraghona | 136 | 04:00 | 129 | 12:00 | Postogola | 139 | 05:00 | 129 | 12:00
Chapai | 139 | 02:00 | 131 | 08:00 | Purbachal | 136 | 05:00 | 125 | 13:00
Charsaidpur | 135 | 02:00 | 126 | 12:00 | Purbasadipur | 133 | 19:30 | 117 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 132 | 05:00 | 126 | 12:00 | Rahanpur | 141 | 01:00 | 136 | 07:00
Chhatak | 135 | 01:00 | 128 | 13:00 | Rahanpur-400 | 142 | 04:00 | 135 | 08:00
Chowmuhani | 134 | 19:00 | 122 | 22:00 | Rahim | 134 | 05:00 | 126 | 13:00
Chuadanga | 139 | 02:00 | 123 | 12:00 | Rajbari | 135 | 01:00 | 127 | 12:00
Coxsbazar | 125 | 00:00 | 119 | 22:00 | Rajendrapur | 135 | 03:00 | 128 | 12:00
Cumilla(N) | 135 | 04:00 | 129 | 12:00 | Rajshahi | 139 | 02:00 | 129 | 12:00
Cumilla(S) | 135 | 05:00 | 127 | 09:00 | Rajshahi-230 | 138 | 02:00 | 127 | 13:00
Daudkandi | 132 | 05:00 | 125 | 12:00 | Ramganj | 134 | 19:00 | 121 | 22:00
Dhaka | 136 | 05:00 | 126 | 12:00 | Rampur | 134 | 04:00 | 128 | 11:00
Dhamrai | 130 | 03:00 | 126 | 10:00 | Rampura | 135 | 01:00 | 126 | 12:00
Dhanmondi | 136 | 03:00 | 127.5 | 12:00 | Rangamati | 135 | 05:00 | 128 | 13:00
Dohazari | 132 | 04:00 | 125 | 12:00 | Rangpur | 132 | 05:00 | 118 | 09:00
Faridpur | 135 | 01:00 | 128 | 12:00 | Ruppur | 140 | 00:00 | 131 | 12:00
Fatullah | 137 | 03:00 | 128 | 12:00 | Saidpur | 135 | 05:00 | 120 | 08:00
Fenchuganj | 139 | 00:00 | 134 | 12:00 | Satkhira | 138 | 03:00 | 124 | 12:00
Feni | 131 | 19:00 | 123 | 22:00 | Satmasjid | 137 | 03:00 | 126 | 13:00
Ghatail | 126 | 00:00 | 117 | 07:00 | Savar | 134 | 18:30 | 34 | 19:00
Ghorashal | 139 | 01:00 | 133 | 12:00 | SevenRings | 140 | 02:00 | 134 | 11:00
Goalpara | 139 | 09:00 | 127 | 11:00 | ShahCement | 135 | 02:00 | 126 | 12:00
Gollamari | 139 | 02:00 | 127 | 12:00 | Shahjadpur | 140 | 00:00 | 133 | 08:00
Gopalganj | 137 | 02:00 | 126 | 12:00 | Shahjibazar | 136 | 05:00 | 129 | 13:00
Gopalganj-400 | 138 | 02:00 | 129 | 12:00 | Shahmirpur | 135 | 03:00 | 128 | 12:00
Gulshan | 134 | 01:00 | 125 | 12:00 | Shariatpur | 137 | 04:00 | 127 | 12:00
Halishahar | 134 | 06:00 | 128 | 12:00 | Sherpur | 119 | 00:00 | 105 | 01:00
Haripur | 134 | 03:00 | 126 | 12:00 | Shikalbaha | 123 | 01:00 | 117 | 13:00
HaripurSBU | 134 | 03:00 | 126 | 12:00 | Shikalbaha-230 | 136 | 05:00 | 127 | 12:00
Hasnabad | 137 | 01:00 | 130 | 12:00 | Shitalakhya | 136 | 04:00 | 127 | 13:00
Hathazari | 135 | 00:00 | 130 | 12:00 | Sholosohor | 135 | 01:00 | 128 | 12:00
Ishurdi | 140 | 00:00 | 131 | 10:00 | Shyampur | 136 | 03:00 | 127 | 12:00
Jaldhaka | 130 | 20:00 | 114 | 08:00 | Shyampur-230 | 137 | 03:00 | 127 | 12:00
Jamalpur | 123 | 09:00 | 108 | 01:00 | Siddhirganj | 135 | 05:00 | 127 | 12:00
Jashore | 139 | 02:00 | 123 | 12:00 | Sirajganj | 139 | 04:00 | 127 | 10:00
Jhenaidah | 140 | 02:00 | 127 | 12:00 | Sonargaon | 133 | 00:00 | 125 | 12:00
Jhenaidah-230 | 140 | 01:00 | 127 | 12:00 | Sreemongol | 136 | 06:00 | 129 | 12:00
Joydebpur | 136 | 03:00 | 130 | 07:00 | Sreepur | 129 | 01:00 | 121 | 12:00
Joypurhat | 136 | 03:00 | 122 | 12:00 | Srinagar | 137 | 02:00 | 128 | 12:00
Juldah | 133 | 02:00 | 128 | 11:00 | SSM | 138 | 07:00 | 130 | 12:00
Kabirpur | 138 | 20:00 | 122 | 12:00 | Sunamganj | 134 | 03:00 | 127 | 13:00
Kachua | 136 | 19:00 | 124 | 23:00 | Sylhet | 137 | 06:00 | 130 | 13:00
Kaliakoir | 139 | 23:00 | 128 | 11:00 | Sylhet-132 | 136 | 01:00 | 131 | 12:00
Kallyanpur | 134 | 04:00 | 126 | 11:00 | Tangail | 129 | 13:00 | 122 | 06:00
Kalurghat | 135 | 03:00 | 129 | 11:00 | Thakurgaon | 137 | 20:00 | 114 | 08:00
Kamrangirchar | 138 | 01:00 | 124 | 12:00 | TK | 133 | 07:00 | 129 | 12:00
Kaptai | 136 | 1:00 | 132 | 13:00 | Tongi | 138 | 04:00 | 129 | 12:00
Kazla | 135 | 05:00 | 124 | 13:00 | Ullahpara | 139 | 02:00 | 130 | 08:00
Keranigonj | 138 | 07:00 | 127 | 12:00 | Ullon | 135 | 02:00 | 126 | 12:00
Khagrachori | 135 | 05:00 | 127 | 13:00 | Uttara | 136 | 03:00 | 125 | 12:00
Khulna | 138 | 01:00 | 125 | 12:00 | UttaraNew | 135 | 02:00 | 124 | 12:00
Khulna(S) | 140 | 03:00 | 128 | 12:00 | Zigatola | 138 | 03:00 | 129 | 12:00
Khulshi | 132 | 01:00 | 127 | 12:00
Kishoreganj | 131 | 02:00 | 123 | 07:00
Kodda | 138 | 23:00 | 128 | 12:00
KSRM | 135 | 04:00 | 127 | 12:00
Kulaura | 139 | 05:00 | 133 | 12:00
Kurigram | 131 | 03:00 | 120 | 07:00
Kushtia | 139 | 02:00 | 127 | 12:00
Lalbag | 138 | 03:00 | 128 | 12:00
Lalmonirhat | 131 | 04:00 | 119 | 08:00
Madanganj | 134 | 04:00 | 127 | 17:00
Madaripur | 138 | 04:00 | 128 | 12:00
Madartek | 135 | 03:00 | 125 | 12:00
Madunaghat | 135 | 05:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division