## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [10 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [10 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 31-01-2025 | [28 empty] | Date: | 31-01-2025 | [28 empty] | Date: | 31-01-2025 | [28 empty] | Date: | 31-01-2025 | [28 empty] | Date: | 31-01-2025 | [19 empty] | Date: | 31-01-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [19 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchuganj 44MW (Energyprima) | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Amnura 50 MW PP(Sinha) | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.190 MW | 365.000 MW | 260.000 MW | 174.800 MW | 174.800 MW | 97.700 MW | 400.370 MW | 40.000 MW | 0.000 MW | 53.970 MW | 36.090 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 0.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 47.998 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 35.090 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 132 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 340 | 267 | 0 | 0 | 0 | 21 | 300 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 182 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 46 | 0 | 0 | 0 | 300 | 0 | 346 | 36 | 42 | 0 | 5 | 113 | 24 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 59 | 0 | 0 | 0 | 0 | 4983 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 663.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 119 | 0 | 314 | 0 | 0 | 2.5 | 174 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 130 | 220 | 0 | 310 | 1130 | 0 | 4358.89 | 9341.89 | 91.88
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 265 | 0 | 0 | 0 | 22 | 300 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37 | 577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 941 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 52 | 0 | 0 | 0 | 280 | 0 | 348 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 19 | 18 | 0 | 0 | 0 | 4674 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 515.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 314 | 0 | 0 | 2.5 | 172 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 7 | 130 | 220 | 0 | 311 | 1120 | 0 | 4121.1 | 8795.1 | 91.88
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 344 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 282 | 0 | 0 | 0 | 22 | 300 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 38 | 577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 911 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 40 | 0 | 0 | 0 | 280 | 0 | 348 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 19 | 17 | 0 | 0 | 0 | 4572 | 746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 310 | 0 | 0 | 2.5 | 172 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 130 | 220 | 0 | 311 | 1100 | 0 | 3794.65 | 8366.65 | 91.88
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 341 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 289 | 0 | 0 | 0 | 24 | 260 | 0 | 0 | 0 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 40 | 579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 30 | 0 | 70 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 300 | 0 | 348 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 4424 | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 309 | 0 | 0 | 2.5 | 164 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 130 | 220 | 0 | 312 | 1000 | 0 | 3619.65 | 8043.65 | 91.87
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 341 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 258 | 0 | 0 | 0 | 24 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 197 | 0 | 0 | 0 | 29 | 183 | 30 | 0 | 70 | 0 | 0 | 17 | 0 | 34 | 0 | 0 | 0 | 300 | 0 | 348 | 33 | 42 | 0 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 4240.5 | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 309 | 0 | 0 | 2.5 | 163 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 136 | 220 | 0 | 306 | 900 | 0 | 3519.11 | 7759.61 | 91.87
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 341 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 300 | 0 | 0 | 0 | 24 | 260 | 0 | 0 | 0 | 0 | 14.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 703 | 0 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 186 | 30 | 0 | 70 | 0 | 0 | 17 | 0 | 32 | 0 | 0 | 0 | 295 | 0 | 335 | 33 | 42 | 0 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 4170.5 | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 310 | 0 | 0 | 2.5 | 165 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 136 | 220 | 0 | 318 | 850 | 0 | 3485.42 | 7655.92 | 91.87
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 341 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 271 | 0 | 0 | 0 | 24 | 260 | 0 | 0 | 0 | 0 | 14.7 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 789 | 0 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 194 | 30 | 0 | 70 | 0 | 0 | 15 | 0 | 18 | 0 | 0 | 0 | 300 | 0 | 335 | 36 | 42 | 0 | 5 | 113 | 16 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 3 | 15 | 18 | 0 | 0 | 0 | 4239.7 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 416.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 339 | 0 | 0 | 2.5 | 164 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 136 | 220 | 0 | 313 | 890 | 0 | 3551.12 | 7790.82 | 91.86
07:00 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 3 | 341 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 320 | 0 | 0 | 0 | 17 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 904 | 1 | 51 | 0 | 148 | 0 | 0 | 0 | 29 | 208 | 30 | 0 | 70 | 0 | 0 | 11 | 0 | 40 | 0 | 0 | 0 | 290 | 0 | 335 | 36 | 42 | 0 | 5 | 113 | 16 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 56 | 19 | 0 | 0.03 | 0 | 4403.03 | 734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 564.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 111 | 0 | 355 | 0 | 0.01 | 2.5 | 162 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.01 | 0 | 150 | 6 | 100 | 180 | 0 | 315 | 950 | 0 | 3701.2 | 8104.23 | 91.86
08:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 3 | 354 | 0 | 0 | 0 | 0 | 0 | 68 | 4 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 302 | 0 | 0 | 0 | 17 | 300 | 0 | 0 | 2 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 12 | 578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 4 | 51 | 0 | 185 | 0 | 0 | 0 | 29 | 193 | 30 | 0 | 50 | 0 | 0 | 15 | 0 | 48 | 0 | 7 | 0 | 320 | 0 | 335 | 36 | 42 | 0 | 5 | 113 | 16 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 9 | 55 | 22 | 0 | 2.58 | 0 | 4879.58 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.87 | 0 | 0 | 597.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 2.86 | 0 | 0 | 0 | 0 | 110 | 0 | 414 | 0 | 0.22 | 2.5 | 165 | 69 | 0 | 1 | 0 | 0 | 0 | 0.6 | 15 | 0.08 | 0 | 280 | 5 | 136 | 220 | 0 | 313 | 990 | 0 | 3841.2 | 8720.78 | 91.86
09:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 3 | 380 | 0 | 0 | 0 | 0 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 281 | 0 | 0 | 0 | 25 | 300 | 0 | 0 | 4 | 0 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 15 | 577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1195 | 10 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 182 | 30 | 0 | 50 | 0 | 0 | 15 | 0 | 48 | 0 | 7 | 0 | 310 | 0 | 335 | 36 | 42 | 0 | 5 | 113 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 21 | 0 | 16.13 | 0 | 5033.13 | 546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.13 | 0 | 0 | 696.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 9.39 | 0 | 0 | 0 | 0 | 119 | 0 | 394 | 0 | 0.22 | 2.5 | 167 | 69 | 0 | 3 | 0 | 0 | 0 | 1.8 | 49 | 0.11 | 0 | 290 | 5 | 136 | 220 | 0 | 273 | 1100 | 0 | 4111.91 | 9145.04 | 91.85
10:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 3 | 372 | 0 | 0 | 0 | 0 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 262 | 0 | 0 | 0 | 7.5 | 290 | 0 | 0 | 7 | 0 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 9 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 13 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 183 | 30 | 0 | 50 | 0 | 0 | 17 | 0 | 44 | 0 | 7 | 0 | 295 | 0 | 335 | 33 | 42 | 0 | 5 | 113 | 16 | 0 | 85 | 30 | 0 | 0 | 0 | 0 | 9 | 58 | 21 | 0 | 19.87 | 1 | 4739.37 | 849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.71 | 0 | 0 | 708.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 8.58 | 0 | 0 | 0 | 0 | 134 | 0 | 394 | 0 | 0.95 | 2.5 | 166 | 69 | 0 | 7 | 0 | 0 | 0 | 3 | 108 | 0.13 | 0 | 250 | 5 | 100 | 220 | 0 | 263 | 1100 | 0 | 4441.3 | 9180.67 | 91.85
11:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 3 | 380 | 0 | 0 | 0 | 0 | 0 | 69 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 0 | 0 | 0 | 24 | 290 | 0 | 0 | 11 | 0 | 16 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 14 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 16 | 51 | 0 | 187 | 0 | 0 | 0 | 29 | 201 | 30 | 0 | 70 | 0 | 0 | 17 | 0 | 60 | 0 | 19 | 0 | 295 | 0 | 335 | 27 | 41 | 0 | 5 | 113 | 0 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 19 | 1 | 36.16 | 6 | 4756.16 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 675.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 30.32 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 0 | 1.44 | 2.5 | 164 | 69 | 0 | 17 | 0 | 0 | 0 | 3.5 | 137 | 0.1 | 0 | 292 | 5 | 100 | 220 | 0 | 240 | 1050 | 0 | 4618.18 | 9374.34 | 91.85
12:00 | 0 | 34 | 26 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 11 | 0 | 0 | 70 | 16 | 0 | 1 | 2 | 48 | 0 | 0 | 400 | 265 | 0 | 0 | 25 | 24 | 310 | 0 | 0 | 22 | 0 | 20 | 14 | 0 | 0 | 8 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 2 | 2 | 40 | 2 | 6 | 220 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 1197 | 16 | 51 | 7 | 187 | 0 | 0 | 0 | 29 | 189 | 26 | 15 | 50 | 9 | 8 | 17 | 0 | 66 | 0 | 21 | 0 | 325 | 0 | 335 | 28 | 41 | 0 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 0 | 0 | 5 | 19 | 58 | 19 | 1 | 33.62 | 6 | 4998.62 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.87 | 0 | 0 | 692.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 38.87 | 0 | 0 | 0 | 0 | 213 | 0 | 403 | 0 | 4.11 | 2.5 | 163 | 69 | 35 | 26 | 0 | 0 | 0 | 4.1 | 118 | 0.07 | 0 | 307 | 5 | 132 | 220 | 0 | 191 | 1090 | 150 | 4894.57 | 9893.19 | 91.84
13:00 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 51 | 0 | 0 | 92 | 0 | 0 | 45 | 35 | 162 | 17 | 0 | 400 | 281 | 0 | 0 | 35 | 24 | 330 | 0 | 0 | 21 | 0 | 17 | 14 | 0 | 0 | 35 | 16 | 0 | 0 | 3 | 0 | 0 | 0 | 60 | 22 | 3 | 40 | 32 | 15 | 213 | 17 | 0 | 0 | 1 | 54 | 0 | 0 | 0 | 0 | 1080 | 16 | 51 | 52 | 187 | 0 | 0 | 0 | 29 | 183 | 30 | 70 | 50 | 112 | 40 | 17 | 0 | 76 | 3 | 11 | 0 | 295 | 0 | 335 | 33 | 42 | 0 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 0 | 0 | 17 | 19 | 58 | 18 | 2 | 32.4 | 6 | 5604.4 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.24 | 0 | 0 | 755.78 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 48.28 | 2 | 0 | 0 | 0 | 220 | 0 | 394 | 0 | 3.76 | 2.5 | 162 | 69 | 95 | 26 | 17 | 0 | 0 | 4.1 | 132 | 0.04 | 0 | 280 | 5 | 132 | 220 | 0 | 195 | 1000 | 150 | 4959.7 | 10564.1 | 91.84
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 357 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 17 | 54 | 17 | 9 | 300 | 299 | 0 | 0 | 0 | 24 | 300 | 0 | 0 | 12 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 25 | 216 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 1005 | 14 | 10 | 50 | 107 | 0 | 0 | 0 | 29 | 204 | 30 | 115 | 50 | 51 | 70 | 17 | 0 | 68 | 0 | 21 | 0 | 300 | 0 | 303 | 36 | 41 | 0 | 0 | 113 | 22 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 19 | 58 | 20 | 2 | 36.78 | 6 | 4800.78 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7 | 0 | 0 | 693.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 45.58 | 15 | 0 | 0 | 0 | 150 | 0 | 366 | 0 | 3.88 | 2.5 | 162 | 69 | 34 | 22 | 0 | 0 | 0 | 3.8 | 126 | 0.18 | 0 | 200 | 5 | 80 | 180 | 0 | 0 | 1000 | 54 | 4209.69 | 9010.47 | 91.83
15:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 352 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 300 | 270 | 0 | 0 | 0 | 24 | 300 | 0 | 0 | 9 | 0 | 18.7 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 22 | 218 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1005 | 11 | 20 | 0 | 190 | 0 | 0 | 0 | 29 | 184 | 30 | 50 | 50 | 0 | 27 | 16 | 0 | 56 | 0 | 10 | 0 | 295 | 0 | 288 | 33 | 41 | 0 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 48 | 22 | 1 | 22.44 | 6 | 4443.14 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.25 | 0 | 0 | 662.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 31.54 | 50 | 0 | 0 | 0 | 150 | 0 | 320 | 0 | 2.78 | 2.5 | 166 | 67 | 0 | 12 | 0 | 0 | 0 | 2.4 | 107 | 0.1 | 0 | 200 | 4 | 132 | 220 | 0 | 0 | 1000 | 0 | 4103.22 | 8546.36 | 91.82
16:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 351 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 300 | 267 | 0 | 0 | 0 | 24 | 300 | 0 | 0 | 6 | 0 | 18.7 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 14 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 945 | 5 | 51 | 0 | 192 | 0 | 0 | 0 | 29 | 184 | 29 | 16 | 50 | 0 | 9 | 15 | 0 | 56 | 0 | 2 | 0 | 285 | 0 | 288 | 36 | 41 | 0 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 48 | 22 | 1 | 10.62 | 6 | 4323.32 | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.09 | 0 | 0 | 655.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 17.44 | 49 | 0 | 0 | 0 | 213 | 0 | 314 | 0 | 1.45 | 2.5 | 169 | 66 | 0 | 6 | 0 | 0 | 0 | 1.3 | 52 | 0.07 | 0 | 200 | 4 | 132 | 220 | 0 | 0 | 1000 | 0 | 3864.52 | 8187.84 | 91.82
17:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 3 | 352 | 0 | 0 | 5 | 0 | 0 | 70 | 16 | 0 | 1 | 7 | 54 | 17 | 0 | 300 | 293 | 0 | 0 | 17 | 24 | 300 | 0 | 0 | 2 | 0 | 15 | 14 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 32 | 0 | 0 | 12 | 2 | 0 | 40 | 0 | 35 | 217 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 903 | 1 | 51 | 3 | 195 | 0 | 0 | 60 | 28 | 191 | 29 | 16 | 50 | 1 | 9 | 15 | 0 | 58 | 0 | 3 | 0 | 320 | 0 | 288 | 36 | 41 | 0 | 5 | 113 | 22 | 0 | 86 | 30 | 0 | 0 | 0 | 8 | 18 | 58 | 22 | 0 | 3.64 | 6 | 4563.64 | 719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.51 | 0 | 0 | 569.49 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 3.82 | 50 | 0 | 0 | 0 | 220 | 0 | 328 | 0 | 0.35 | 2.5 | 166 | 66 | 0 | 2 | 0 | 0 | 0 | 0.3 | 11 | 0.01 | 0 | 200 | 5 | 132 | 220 | 0 | 0 | 1000 | 2 | 3749.98 | 8313.62 | 91.81
18:00 | 0 | 51 | 15 | 0 | 0 | 0 | 0 | 3 | 301 | 0 | 0 | 29 | 0 | 0 | 70 | 16 | 0 | 15 | 29 | 108 | 17 | 0 | 300 | 271 | 0 | 0 | 30 | 24 | 300 | 0 | 0 | 0 | 17 | 15 | 14 | 0 | 0 | 26 | 10 | 1 | 0 | 1 | 51 | 24 | 0 | 12 | 12 | 0 | 40 | 15 | 37 | 363 | 17 | 0 | 18 | 0 | 24 | 0 | 0 | 0 | 0 | 1052 | 0 | 51 | 30 | 195 | 0 | 0 | 50 | 29 | 183 | 29 | 42 | 50 | 23 | 30 | 16 | 0 | 66 | 0 | 0 | 40 | 295 | 0 | 288 | 36 | 40 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 22 | 18 | 58 | 22 | 0 | 0 | 6 | 5204 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556.98 | 0 | 0 | 42 | 0 | 0 | 0 | 100 | 0 | 7 | 0 | 0 | 24 | 0 | 63 | 0 | 0 | 0 | 189 | 0 | 314 | 0 | 0 | 2.5 | 168 | 66 | 34 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 6 | 100 | 180 | 0 | 0 | 930 | 82 | 4099.48 | 9303.48 | 91.81
19:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 350 | 0 | 0 | 54 | 0 | 0 | 78 | 16 | 0 | 0 | 0 | 108 | 17 | 0 | 350 | 265 | 0 | 0 | 35 | 32 | 335 | 0 | 0 | 0 | 8 | 11 | 14 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 362 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 0 | 51 | 50 | 195 | 0 | 0 | 115 | 29 | 182 | 29 | 113 | 70 | 51 | 54 | 16 | 0 | 60 | 0 | 0 | 0 | 280 | 0 | 288 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 58 | 30 | 0 | 0 | 7 | 5500 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 679.25 | 0 | 0 | 26 | 0 | 0 | 0 | 99 | 0 | 19 | 0 | 0 | 30 | 0 | 118 | 0 | 0 | 0 | 167 | 0 | 377 | 0 | 0 | 2.5 | 168 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 130 | 220 | 0 | 0 | 1060 | 82 | 4182.75 | 9682.75 | 91.8
19:30 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 54 | 0 | 0 | 78 | 16 | 0 | 0 | 0 | 108 | 17 | 0 | 350 | 277 | 0 | 0 | 35 | 32 | 335 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 41 | 407 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 195 | 0 | 0 | 170 | 29 | 182 | 29 | 115 | 75 | 51 | 54 | 16 | 0 | 64 | 0 | 0 | 0 | 290 | 0 | 288 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 58 | 30 | 0 | 0 | 12 | 5611 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756.1 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 167 | 0 | 381 | 0 | 0 | 2.5 | 170 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1120 | 82 | 4194.6 | 9805.6
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 406 | 0 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 108 | 17 | 0 | 350 | 275 | 0 | 0 | 17 | 32 | 335 | 0 | 0 | 0 | 0 | 11 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 406 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 195 | 0 | 0 | 230 | 29 | 183 | 29 | 115 | 80 | 51 | 54 | 17 | 0 | 66 | 0 | 0 | 0 | 280 | 0 | 288 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 58 | 30 | 0 | 0 | 12 | 5567 | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753.61 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 0 | 0 | 0 | 167 | 0 | 380 | 0 | 0 | 2.5 | 172 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1130 | 82 | 4203.11 | 9770.11 | 91.8
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 377 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 300 | 306 | 0 | 0 | 0 | 32 | 300 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 405 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 265 | 29 | 202 | 29 | 34 | 80 | 0 | 0 | 17 | 0 | 66 | 0 | 0 | 0 | 295 | 0 | 288 | 36 | 41 | 0 | 2 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 58 | 32 | 0 | 0 | 12 | 5224.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 173 | 0 | 414 | 0 | 0 | 2.5 | 168 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1130 | 35 | 4441.5 | 9666 | 91.79
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 350 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 300 | 275 | 0 | 0 | 0 | 32 | 270 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 405 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 197 | 0 | 0 | 270 | 29 | 182 | 29 | 7 | 80 | 0 | 0 | 17 | 0 | 62 | 0 | 0 | 0 | 300 | 0 | 288 | 36 | 41 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 58 | 10 | 0 | 0 | 12 | 5021.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 174 | 0 | 384 | 0 | 0 | 2.5 | 166 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 132 | 220 | 0 | 0 | 1132 | 35 | 4414.48 | 9435.98 | 91.79
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 350 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 293 | 0 | 0 | 0 | 33 | 270 | 0 | 0 | 0 | 0 | 11.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 197 | 0 | 0 | 200 | 29 | 186 | 29 | 0 | 70 | 0 | 0 | 17 | 0 | 62 | 0 | 0 | 0 | 295 | 0 | 298 | 36 | 42 | 0 | 5 | 113 | 23 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 18 | 58 | 20 | 0 | 0 | 12 | 4810.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 169 | 0 | 395 | 0 | 0 | 2.5 | 166 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 132 | 220 | 0 | 0 | 1132 | 0 | 4228.5 | 9039 | 91.78
Total KWH | 0 | 478080 | 203112 | 0 | 0 | 0 | 0 | 138000 | 8809200 | 0 | 0 | 240660 | 0 | 0 | 1580688 | 127680 | 0 | 91991 | 149520 | 876960 | 371520 | 21120 | 7751000 | 6852829 | 0 | 0 | 187449 | 603700 | 7014794 | 0 | 0 | 98736 | 19200 | 343800 | 445680 | 0 | 0 | 225818 | 45164 | 7680 | 0 | 8640 | 164444 | 38976 | 0 | 120000 | 49920 | 14398 | 980000 | 90330 | 779520 | 9956363.64 | 53527 | 0 | 74880 | 4876.2 | 260945 | 0 | 0 | 0 | 0 | 24425452 | 107325 | 1123782 | 225818 | 4449455 | 0 | 0 | 1254000 | 695040 | 4628000 | 710928 | 781440 | 1466390 | 472800 | 418320 | 387070 | 0 | 1248000 | 9130 | 99318 | 35712 | 7271000 | 0 | 7980000 | 821160 | 987000 | 0 | 108288 | 2713582 | 490128 | 0 | 2060160 | 718752 | 0 | 0 | 0 | 86400 | 314400 | 1087200 | 462720 | 8150 | 204940 | 120240 | 117253300.84 | 18419636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170640 | 0 | 0 | 15005455 | 0 | 0 | 80321 | 0 | 36960 | 0 | 203586 | 0 | 11846 | 13291 | 470440 | 41438 | 241500 | 940909 | 0 | 0 | 0 | 3896036 | 0 | 8607854 | 0 | 20760 | 66582 | 4085000 | 1625890 | 261254 | 121771 | 78672 | 0 | 0 | 24893.16 | 872052 | 1030.5 | 0 | 5673000 | 146352 | 2994000 | 5274740 | 0 | 3876363 | 25261090.91 | 649200 | 99172562.57 | 216425863.41

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-02-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-01-2025 | during | 01-02-2025 | during | 01-02-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 3 | 3 | 97.3 | 97.3 | 21 | 21 | Gas shortage
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.37 | 401 | 401 | 400.37 | 400.37 | 400.37 | 400.37 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 350 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 265 | 277 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 1 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 13 | 13 | 13 | 13 | -
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 210 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 310 | 335 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 11 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 2 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 25 | 35 | 55 | 55 | 55 | 55 | -
21 | Bosila 108MW PP(CLC) | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
22 | Summit Power Ashulia | Gas | IPP |  | 44.75 | 33.75 | 20 | 10 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 24.3 | 23 | 14 | 14 | 23 | 23 | 23 | 23 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 17 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 24 | 32 | 33 | 33 | 33 | 33 | Low gas pressure
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.19 | 26 | 0 | 52.19 | 52.19 | 25 | 25 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 70 | 78 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 17 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 48 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 22 | 0 | 13 | 0 | 13 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 36.09 | 0 | 0 | 17 | 17 | 17 | 17 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0.01 | 0.01 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 0.01 | 0.01 | Gas shortage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Dhaka Area Total |  |  |  |  | 6407.05 | 5841.27 | 1692 | 1747 | 4571.99 | 4558.99 | 2882.73 | 2869.73
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 9 | 0 | 105 | 105 | 105 | 105 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 72 | 72 | 72 | 72 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 36 | 85 | 85 | 85 | 85 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 2 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 6 | 41 | 4 | 20 | 4 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 2 | 0 | 3.45 | 0 | 3.45 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54.36 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 2 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 2 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 8 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1197 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB |  | 60 | 60 | 1 | 0 | 1 | 1 | 1 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 220 | 407 | 575 | 575 | 400 | 400 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4917.36 | 4915.22 | 1505 | 1802 | 3251.17 | 3245.72 | 3076.17 | 3070.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 189 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 0 | 0 | 0 | 0 | schedule outage
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 170 | 0 | 0 | 0 | 0 | schedule outage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 26 | 29 | 46.94 | 46.94 | 41 | 41 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 29 | 29 | 30 | 30 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 187 | 195 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 7 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 75 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 9 | 51 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Import (Tripura) | Import | Import |  | 160 | 160 | 66 | 64 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 16 | 20.83 | 20.83 | 17 | 17 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 54 | 113 | 113 | 113 | 113 | -
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 15 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 21 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 675 | 1031 | 1728.97 | 1678.97 | 1610.2 | 1560.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[8 empty] | during | 0 | during | 0 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 19 | 30 | 210 | 210 | 25 | 25 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) | HFO | IPP |  | 95 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.7 | 0 | 1.7 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 58 | 200 | 200 | 55 | 55 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 19 | 18 | 115 | 115 | 8 | 8 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 33.62 | 0 | 39.7 | 0 | 39.7 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 22 | 22 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54.5 | 54.5 | 5 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 749.5 | 749.21 | 141.62 | 118 | 642.9 | 601.5 | 205.9 | 164.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 41 | 42 | 42 | 42 | 42 | 42 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 113 | 113 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 28 | 36 | 40 | 40 | 40 | 40 | -
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0.01 | 0.01 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 335 | 288 | 380 | 380 | 352 | 352 | FGMO Available
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 985 | 913 | 1102 | 1102 | 1050.01 | 1050.01
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | -
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 623 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 40 | 40 | 40 | 40 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 28.87 | 0 | 73 | 0 | 73 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 0 | 1234 | 1234 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 952.87 | 623 | 3173 | 3100 | 1729 | 1656
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 1320 | 1320 | 191 | 0 | 0 | 0 | 270 | 330 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 7 | 10.12 | 10.12 | 7 | 7 | Dead bus operation
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 132 | 132 | 136 | 136 | 140 | 140 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1090 | 1120 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 150 | 82 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.07 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 3585.1 | 2095.07 | 1868 | 2177.12 | 2177.12 | 2408 | 2468
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Coal shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 42 | 42 | 42 | 42 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 42 | 42 | 42 | 42 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 45 | 45 | 45 | 45 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 214 | 214 | 0 | 119 | 214 | 214 | 0 | 0 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 213 | 167 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 403 | 381 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 2.5 | 2.5 | 8.25 | 8.25 | 8.25 | 8.25 | Partial Shutdown due to maintenance
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 40 | 100 | 100 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6.55 | 6.09 | 4.11 | 0 | 4.35 | 0 | 4.35 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 692.05 | 756.1 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 38.87 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 78 | 0 | 52 | 0 | 52 | 0 | -
Rajshahi Area Total |  |  |  |  | 3475.55 | 3393.2 | 1431.53 | 1465.6 | 3067.13 | 2960.78 | 2811.34 | 2704.99
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 69 | 68 | 69 | 69 | 70 | 70 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 163 | 170 | 160 | 160 | 150 | 150 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20 | 0 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.1 | 0 | 4.8 | 0 | 4.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 26 | 0 | 24 | 0 | 24 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 118 | 0 | 91 | 0 | 137.01 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 415.1 | 238 | 590.8 | 491 | 627.81 | 482
System Total |  |  |  |  | 29204.66 | 28386.248 | 9893.19 | 9805.6 | 20305.08 | 19916.08 | 16401.16 | 16026.15
Forecast Scenario (01-02-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 9050 |  | 0 |  | 9050
|  |  |  | 1:00 | 8700 |  | 0 |  | 8700
|  |  |  | 2:00 | 8200 |  | 0 |  | 8200
|  |  |  | 3:00 | 7850 |  | 0 |  | 7850
|  |  |  | 4:00 | 7700 |  | 0 |  | 7700
|  |  |  | 5:00 | 7450 |  | 0 |  | 7450
|  |  |  | 6:00 | 7750 |  | 0 |  | 7750
|  |  |  | 7:00 | 8200 |  | 0 |  | 8200
|  |  |  | 8:00 | 9000 |  | 0 |  | 9000
|  |  |  | 9:00 | 9500 |  | 0 |  | 9500
|  |  |  | 10:00 | 9550 |  | 0 |  | 9550
|  |  |  | 11:00 | 9650 |  | 0 |  | 9650
|  |  |  | 12:00 | 10000 |  | 0 |  | 10000
|  |  |  | 13:00 | 10700 |  | 0 |  | 10700
|  |  |  | 14:00 | 10100 |  | 0 |  | 10100
|  |  |  | 15:00 | 9500 |  | 0 |  | 9500
|  |  |  | 16:00 | 9350 |  | 0 |  | 9350
|  |  |  | 17:00 | 9650 |  | 0 |  | 9650
|  |  |  | 18:00 | 10650 |  | 0 |  | 10650
|  |  |  | 18:30 | 10850 |  | 0 |  | 10850
|  |  |  | 19:00 | 11100 |  | 0 |  | 11100
|  |  |  | 19:30 | 11000 |  | 0 |  | 11000
|  |  |  | 20:00 | 10800 |  | 0 |  | 10800
|  |  |  | 21:00 | 10600 |  | 0 |  | 10600
|  |  |  | 22:00 | 10100 |  | 0 |  | 10100
|  |  |  | 23:00 | 9650 |  | 0 |  | 9650
Probable Maximum Temperature: |  |  | 28.40°C
Probable Maximum Demand at Day Peak: |  |  | 10000.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 224.80 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:37 hrs on 01-02-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division
Formulas:
Effective Available Gen. on = [Forecasted Available Gen. on]

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 31-01-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9893.19 | MW | 12:00 Hr. | Energy Generated |  |  | 216.4259 |  | MKWHr.
| Day Peak Demand |  |  | 9893.19 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.098 |  | MKWHr.
| Evening Peak Generation |  |  | 9805.6 | MW | 19:30 Hr. | Energy Demand |  |  | 216.5239 |  | MKWHr.
| Evening Peak Demand |  |  | 9805.6 | MW | 19:30 Hr. | Maximum Temperature |  |  | 27.6 |  | °C
| Minimum Generation of the Day |  |  | 7655.92 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 724.83 |  | MMCFD
| Maximum Generation of the Day |  |  | 10564.1 | MW | 13:00 Hr. | Production Cost per KWHr |  |  | 5.7512 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 32.3305 | 0 | 3.9765 | 0 | 0 | 0.098736 | 0 | 0 | 36.4057 | Gas | 93.364 | Gas | 337890131.99
| Chattogram Zone |  |  | 0.77952 | 34.3818 | 1.1366 | 0 | 0.98 | 0.12172 | 0 | 0.00864 | 37.4083 | Coal | 74.9032 | Coal | 500851247.6995
| Cumilla Zone |  |  | 14.7147 | 0 | 1.9432 | 0 | 0 | 0.099318 | 1.248 | 0 | 18.0052 | HFO | 10.041 | HFO | 184897486.44
| Mymensingh Zone |  |  | 0.46272 | 0 | 1.6082 | 0 | 0 | 0.21309 | 0 | 0 | 2.2841 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 23.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1501 | Hydro | 0.98 | Hydro | 98000
| Khulna Zone |  |  | 0 | 0 | 0 | 0 | 0 | 0.17064 | 18.4196 | 0 | 18.5903 | Solar | 2.456 | Solar | 39599046.361
| Barishal Zone |  |  | 8.4151 | 34.8105 | 0.6492 | 0 | 0 | 0.0010305 | 0 | 0 | 43.8758 | Import | 34.6731 | Import | 181246195.41
| Rajshahi Zone |  |  | 13.5114 | 0 | 0.38744 | 0 | 0 | 0.7327 | 15.0055 | 0 | 29.637 | Wind | 0.00864 | Wind | 134784
| Rangpur Zone |  |  | 0 | 5.7109 | 0.33993 | 0 | 0 | 1.0187 | 0 | 0 | 7.0695
| Total |  |  | 93.364 | 74.9032 | 10.041 | 0 | 0.98 | 2.456 | 34.6731 | 0.00864 | 216.4259
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 337890131.99 |  | Hydro | 98000
|  |  |  | Coal | 500851247.6995 |  | Solar | 39599046.361
|  |  |  | HFO | 184897486.44 |  | Import | 181246195.41
|  |  |  | HSD | 0 |  | Wind | 134784
[5 empty] | Total: | 124,47,16,891 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 18.4196 | Peak Hr Flow | 623.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 7026981 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 15.0055 | Peak Hr Flow | 756.10 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 296 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.248 | Peak Hr Flow | 64.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 708 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 34.6731 | Peak Hr Flow | 1443.10 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3268
|  |  |  | Chattogram |  | 0 |  | 1017
|  |  |  | Cumilla |  | 0 |  | 854
|  |  |  | Mymensingh |  | 0 |  | 892
|  |  |  | Sylhet |  | 0 |  | 343
|  |  |  | Khulna |  | 0 |  | 1067
|  |  |  | Barishal |  | 0 |  | 272
|  |  |  | Rajshahi |  | 0 |  | 992
|  |  |  | Rangpur |  | 0 |  | 691
|  |  |  | Total |  | 0 |  | 9396
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Sylhet 225 MW CCPP GT |  |  | 142
|  | 6 | Sirajgonj 400 MW CCPP Unit-4 ST |  |  | 132 | 6 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 792 |  |  |  | Total | 720.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1512.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 15:39 | Kachua 132/33kV S/S Main Bus-1 Project Work S/D Due to project Work
| 08:25 | 12:20 | Rampura 230/132kV S/S 230kV Busbar-2 Project Work S/D Due to G2G project work Shutdown
| 08:36 | 16:24 | Faridpur 132/33kV S/S 132 KV Rajbari ckt-2 Scheduled S/D Due to Annual Maintenance.
| 08:37 | 16:24 | Rajbari 132/33kV S/S Faridpur - 2 Scheduled S/D Due to annual maintenance
| 08:40 | 11:22 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Project Work S/D
| 08:40 | 11:23 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Project Work S/D
| 08:42 | 11:25 | Benapole-Jashore 132 kV Ckt-1 Forced S/D from Benapole 132/33kV end Due to Jessore 132kv | [7 empty] | 50.0MW load
|  |  | s/s maintenance | [7 empty] | interrup. Benapole
132/33kV end
| 08:42 | 11:25 | Benapole-Jashore 132 kV Ckt-2 Forced S/D from Benapole 132/33kV end Due to Jessore 132kv | [7 empty] | 50.0MW load
|  |  | s/s maintenance | [7 empty] | interrup. Benapole
132/33kV end
| 08:44 | 11:37 | Jashore-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end.
| 08:57 | 11:30 | Jashore-Noapara 132kV Ckt-2 Scheduled S/D from Noapara 132/33kV end.
| 08:59 | 11:23 | Jashore 132/33kV S/S 132 kV Bus-B Project Work S/D | [7 empty] | 100.0MW load
interrup.
| 09:05 |  | Kamrangirchar 132/33kV S/S GT-1 HT Scheduled S/D Due to Maintaince work
| 09:20 | 12:18 | Rajbari 132/33kV S/S Transformer-1 LT Project Work S/D Due to Punch point solve purpose.
| 09:21 | 12:16 | Rajbari 132/33kV S/S Transformer-1 HT Project Work S/D Due to Punch point solve purpose.
| 09:50 | 12:46 | Faridpur 132/33kV S/S Transformer-3 HT Forced S/D Due to 33 cable insulation failure
| 09:50 | 12:50 | Faridpur 132/33kV S/S Transformer-3 LT Forced S/D Due to Cable maintenance
|  | 10:31 | MI_Cement 132/33kV S/S MI Cement HT is restored.
|  | 11:20 | Rangpur 132/33kV S/S T-1(414T) HT is restored.
|  | 11:21 | Rangpur 132/33kV S/S T-1(414T) LT is restored.
|  | 11:23 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 is restored.
| 11:34 | 19:57 | BIPTC S/S Baharampur-4 Scheduled S/D Due to Taken from India
| 11:38 | 13:18 | Haripur 230/132kV S/S 132KV Bhulta-2 Scheduled S/D Due to ordered by NLDC
|  | 11:40 | Jashore 132/33kV S/S 132 kV Bus-A is restored.
|  | 11:56 | Halishahar 132/33kV S/S 403T(TR-1) HT is restored.
| 12:00 |  | Day peak Generation is 9888 MW
| 12:12 | 18:57 | Rangpur 132/33kV S/S Rangpur-GTPS Project Work S/D Due to G to G project
| 12:47 |  | Sirajgonj 225MW CCPP Unit-1 GT Synchronized with remarks:- ST startup process is going
on.
| 12:47 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 13:21 | 15:00 | Halishahar-Julda 132kV Ckt-1 Tripped from Halishahar 132/33kV end showing False signal
in Distance Relay. relays Due to False signal in Distance Relay.
|  | 15:00 | Halishahar 132/33kV S/S 423T(TR-3) HT is restored.
| 15:05 | 17:22 | Rajbari 132/33kV S/S Transformer-2 LT Project Work S/D Due to Project work SD.
| 15:06 | 17:11 | Rajbari 132/33kV S/S Transformer-2 HT Project Work S/D Due to Project work SD.
| 15:28 |  | Sirajgonj 400 MW CCPP Unit-4 GT Synchronized with remarks:- None
| 15:57 | 16:53 | Jamalpur 132/33kV S/S T-2 HT Project Work S/D Due to UMPL ckt-1 D.S. (Bus-B) replacement
work purpose.
| 15:57 | 16:53 | Jamalpur 132/33kV S/S T-2 LT Project Work S/D Due to UMPL ckt-1 D.S. (Bus-B) replacement
work purpose.
| 16:21 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 16:21 |  | Ashuganj South 360 MW GT was sync.
|  | 16:31 | BSRM-Cumilla(N) 230 kV Ckt-1 is restored.
|  | 16:31 | BSRM-Cumilla(N) 230 kV Ckt-1 is restored.
|  | 16:47 | Keranigonj 230/132/33kV S/S 132 kV Lalbagh Ckt. 3 is restored.
|  | 16:58 | Jamalpur 132/33kV S/S Bus-B is restored.
| 17:20 |  | Jamalpur 132/33kV S/S Bus-A Project Work S/D Due to UMPL ckt-1 D.S. (Bus-B) replacement
work purpose.
| 17:22 |  | Sirajgonj Gas 225MW Unit-1 ST was sync.
| 17:22 |  | Sirajgonj 225MW CCPP Unit-1 ST Synchronized with remarks:- None
| 17:40 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is ON with remarks:- As per instruction of NLDC
| 18:28 | 21:28 | Bheramara(GK) 132/33kV S/S TR-2 LT Tripped showing o/c relays Due to WZPDCL Aux Tr | [7 empty] | 13.0MW load
|  |  | 33/.4kV & PT Blast | [7 empty] | interrup.
| 18:28 | 19:46 | Bheramara(GK) 132/33kV S/S TR-1 LT Tripped showing o/c relays Due to WZPDCL Aux Tr | [7 empty] | 13.0MW load
|  |  | 33/.4kV & PT Blast | [7 empty] | interrup.
| 18:28 | 21:27 | Bheramara(GK) 132/33kV S/S TR-2 HT Tripped showing O/C relays Due to WZPDCL Aux Tr | [7 empty] | 13.0MW load
|  |  | 33/0.4kv & PT Blust | [7 empty] | interrup.
| 18:28 | 19:44 | Bheramara(GK) 132/33kV S/S TR-1 HT Tripped showing O/C relays Due to WZPDCL Aux | [7 empty] | 13.0MW load
|  |  | Transformer 33/0.4 kv & PT Blust | [7 empty] | interrup.
|  | 19:18 | Jamalpur United (20MW)-Jamalpur 132kV Ckt-1 is restored.
| 19:30 |  | Evening Peak Generation: 9805 MW.
| 21:10 | 22:25 | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to Pbs feeder fault and station aux-1
jumper wire maintenance.
| 21:37 | 22:06 | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to Pbs feeder fault and station aux-1
jumper wire maintenance
| 05:00 |  | Min. Gen. 7077 MW
| 05:14 |  | Aminbazar-Meghnaghat 400kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing
Differential relay relays Due to Line tripped
| 05:14 | 05:23 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing BCPU relays Due to Under | [7 empty] | 8.0MW load
|  |  | Frequency | [7 empty] | interrup.
| 05:45 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
| 05:47 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- GT
| 07:10 | 07:28 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Tripped from Ashuganj 230/132/33kV end showing
1.Distance A and B phase 2.Zone-2 relays.
| 07:40 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is OFF with remarks:- Due to foggy weather
| 07:42 |  | Naogaon 132/33kV S/S T-3 LT Scheduled S/D Due to Annual maintenance by NESCO Naogaon | [7 empty] | 36.0MW load
interrup.
| 07:42 |  | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Scheduled S/D from Barguna
132/33kV end Due to Barishal - Patuakhali line Annual Maintenance and from Barishal
132/33kV end Due to Annual maintenance work. and from Patuakhali 132/33kV end Due to
Annual Maintenance
| 07:43 |  | Naogaon 132/33kV S/S T-3 HT Scheduled S/D Due to Annual Maintenance by NESCO Naogaon | [7 empty] | 36.0MW load
interrup.
| 07:45 |  | Naogaon 132/33kV S/S T-1 LT Scheduled S/D Due to Annual Maintenance by NESCO Naogaon | [7 empty] | 20.0MW load
interrup.
| 07:45 |  | Naogaon 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance by NESCO Naogaon | [7 empty] | 20.0MW load
interrup.
| 07:46 |  | Naogaon 132/33kV S/S T-2 HT Scheduled S/D Due to Annual Maintenance by NESCO Naogaon | [7 empty] | 20.0MW load
interrup.
| 07:46 |  | Naogaon 132/33kV S/S T-1 HT Scheduled S/D Due to Annual Maintenance by NESCO Naogaon | [7 empty] | 20.0MW load
interrup.
| 07:57 |  | Naogaon 33 kv bus S/D. | [7 empty] | 70MW load interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 31-01-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 174.8 | 0 | 0 | Post HGPI under maintance due to Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | HGPI Maintenance Work is going on.
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 3 | 138000 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.37 | 401 | 8809200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | -
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 7751000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 277 | 6852829 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 91991 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | -
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | -
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7014794 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | -
16 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 240660 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 127680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 149520 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 187449 | -
21 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 10 | 343800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 445680 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 17 | 371520 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 32 | 603700 | Low gas pressure
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.19 | 0 | 203112 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 78 | 1580688 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 478080 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 21120 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 876960 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 98736 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 36.09 | 0 | 0 | Due to Alternator-03 shifting purpose
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Gas shortage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 0 | 0 | 19200 | -
Dhaka Area Total |  |  |  |  | 5841.27 | 1747 | 36405719
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 4876.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 107325 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 74880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 980000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 260945 | Bill delay and high diff. of USD exchange rate
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 38976 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 36 | 164444 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 120000 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 41 | 779520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 7680 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 14398 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 45164 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 90330 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 49920 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 225818 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 53527 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 24425452 | -
56 | Cox's Bazar Wind |  | PDB | 0 | 60 | 0 | 8640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 407 | 9956363.64 | U2 S/D 24/Jan/25 (Maintenance Work)
Chattogram Area Total |  |  |  |  | 4915.22 | 1802 | 37408258.84
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4628000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | To Facilitate Major Inspection
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 170 | 1254000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 29 | 710928 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 29 | 695040 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 195 | 4449455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1123782 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 225818 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 35712 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 75 | 1466390 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 472800 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
| Import (Tripura) |  | Import | 0 | 160 | 64 | 1248000 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 9130 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 387070 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 54 | 418320 | -
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 781440 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 99318 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1031 | 18005203
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 30 | 462720 | Low gas pressure
78 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 95 | 0 | 0 | -
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 58 | 1087200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 18 | 314400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 204940 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 120240 | Will be dispatch 6 Mw due to liquid fuel shortages
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 86400 | -
Mymensingh Area Total |  |  |  |  | 749.21 | 118 | 2284050
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 42 | 987000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 113 | 2713582 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 36 | 821160 | -
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 5 | 108288 | machine problem
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718752 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2060160 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 490128 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7271000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 288 | 7980000 | FGMO Available
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2368.568 | 913 | 23150070
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | -
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 623 | 18419636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Schedule Combustor Inspection
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 170640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 0 | Force Majeure: Refer GM(Commercial/BIFPCL) Letter
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 623 | 18590276
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 3876363 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 146352 | Dead bus operation
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 132 | 2994000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 25261090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5274740 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 82 | 649200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5673000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1030.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1868 | 43875776.41
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 80321 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | -
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 11846 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 119 | 940909 | GT air intake filter DP high.
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Plant is on standby as per NLDC requirement.
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 167 | 3896036 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 381 | 8607854 | -
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 41438 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 2.5 | 66582 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 13291 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 40 | 203586 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 36960 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20760 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 756.1 | 15005455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 241500 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 470440 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1465.6 | 29636978
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 68 | 1625890 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4085000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 78672 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 24893.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 261254 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 121771 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 872052 | -
Rangpur Area Total |  |  |  |  | 950 | 238 | 7069532.16
Eastern Grid Total |  |  |  |  | 16771.748 | 5611 | 117253300.84
Western Grid Total |  |  |  |  | 11614.5 | 4194.6 | 99172562.57
National Grid Total |  |  |  |  | 28386.248 | 9805.6 | 216425863.41
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 31-01-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6374.48 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3022.06 | MW
i) Dhaka area |  |  | 3268.28 |  | MW | i) Khulna area |  |  |  | 1067.06 | MW
ii) Chattogram area |  |  | 1017.2 |  | MW | ii) Barishal area |  |  |  | 272 | MW
iii) Cumilla area |  |  | 854 |  | MW | iii) Rajshahi area |  |  |  | 992 | MW
iv) Mymensingh area |  |  | 892 |  | MW | iv) Rangpur area |  |  |  | 691 | MW
v) Sylhet area |  |  | 343 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9396.54 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jaldhaka | 60 | 09:00 | 133 | Purbachal | 15 | 12:00
2 | AKSML | 108.3 | 07:00 | 68 | Jamalpur | 100 | 12:00 | 134 | Purbasadipur | 120 | 13:00
3 | Aftabnagar | 26 | 12:00 | 69 | Jashore | 106 | 13:00 | 135 | Rahanpur | 0 | 00:00
4 | Agargaon | 77 | 13:00 | 70 | Jhenaidah | 92 | 08:00 | 136 | Rahim | 25 | 01:00
5 | Agrabad | 52 | 12:00 | 71 | Joydebpur | 115 | 13:00 | 137 | Rajbari | 50 | 18:30
6 | Amnura | 45 | 08:00 | 72 | Joypurhat | 53 | 18:30 | 138 | Rajendrapur | 90 | 13:00
7 | Ashuganj | 63 | 13:00 | 73 | Juldah | 10 | 00:00 | 139 | Rajshahi | 76 | 13:00
8 | BSRM | 196 | 19:00 | 74 | KSRM | 26 | 11:00 | 140 | Rajshahi-230 | 62 | 13:00
9 | Bagerhat | 62 | 18:30 | 75 | Kabirpur | 163 | 12:00 | 141 | Ramganj | 90 | 13:00
10 | Bajitpur | 0 | 00:00 | 76 | Kachua | 55 | 13:00 | 142 | Rampur | 25 | 13:00
11 | Bakulia | 60 | 13:00 | 77 | Kallyanpur | 57 | 18:30 | 143 | Rangamati | 12 | 18:00
12 | Banani | 28.4 | 13:00 | 78 | Kalurghat | 19 | 00:00 | 144 | Rangpur | 106 | 13:00
13 | Bangabhaban | 2 | 00:00 | 79 | Kamrangirchar | 44 | 00:00 | 145 | Ruppur | 4.2 | 11:00
14 | Barapukuria | 60 | 13:00 | 80 | Kaptai | N/A | N/A | 146 | SSM | 16 | 01:00
15 | Barguna | 14 | 13:00 | 81 | Kazla | 81 | 12:00 | 147 | Saidpur | 94 | 13:00
16 | Barishal | 92 | 13:00 | 82 | Keranigonj | 53 | 13:00 | 148 | Satkhira | 85 | 18:30
17 | Barishal-230 | 52 | 13:00 | 83 | Khagrachori | 24 | 13:00 | 149 | Satmasjid | 90 | 13:00
18 | Baroaulia | 51 | 09:00 | 84 | Khulna | 75 | 13:00 | 150 | Savar | 146 | 12:00
19 | Baroirhat | 53 | 13:00 | 85 | Khulshi | 134 | 11:00 | 151 | SevenRings | 21.43 | 12:00
20 | Bashundhara | 133 | 13:00 | 86 | Kishoreganj | 134 | 13:00 | 152 | ShahCement | 23 | 12:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kodda | 176 | 00:00 | 153 | Shahjadpur | 49 | 18:00
22 | Beanibazar | 44 | 20:00 | 88 | Kulaura | 25 | 20:00 | 154 | Shahjibazar | 76 | 13:00
23 | Benapole | 52 | 08:00 | 89 | Kurigram | 64 | 08:00 | 155 | Shahmirpur | 41 | 01:00
24 | Bhaluka | 118 | 08:00 | 90 | Kushtia | 101 | 12:00 | 156 | Shariatpur | 56 | 13:00
25 | Bhandaria | 33 | 21:00 | 91 | Lalbag | 43 | 00:00 | 157 | Sherpur | 128 | 19:00
26 | Bhangura | 27 | 18:30 | 92 | Lalmonirhat | 52 | 08:00 | 158 | Shikalbaha | 14 | 21:00
27 | Bheramara(GK) | 37 | 18:30 | 93 | MI_Cement | 16.6 | 00:00 | 159 | Shitalakhya | 45.5 | 13:00
28 | Bhulta | 215 | 00:00 | 94 | Madanganj | 19 | 12:00 | 160 | Sholosohor | 24 | 12:00
29 | Bog-Sherpur | 60 | 09:00 | 95 | Madaripur | 71 | 13:00 | 161 | Shyampur | 140 | 01:00
30 | Bogura | 102 | 19:00 | 96 | Madartek | 59.77 | 13:00 | 162 | Siddhirganj | 76 | 12:00
31 | Borhanuddin | 53 | 21:00 | 97 | Madunaghat | 33 | 12:00 | 163 | Sirajganj | 70 | 18:30
32 | Brahmanbaria | 106 | 13:00 | 98 | Magura | 43 | 13:00 | 164 | Sonargaon | 77 | 00:00
33 | Cantonment | 80 | 13:00 | 99 | Mahasthangarh | 54 | 10:00 | 165 | Sreemongol | 48 | 18:00
34 | Chandpur | 48 | 13:00 | 100 | Manikganj | 95 | 00:00 | 166 | Sreepur | 69 | 09:00
35 | Chandraghona | 25 | 18:00 | 101 | Maniknagar | 44 | 13:00 | 167 | Srinagar | 34.6 | 13:00
36 | Chapai | 67 | 12:00 | 102 | Matarbari | 35 | 18:00 | 168 | Sunamganj | 38 | 20:00
37 | Charsaidpur | 41 | 12:00 | 103 | Matuail | 44 | 00:00 | 169 | Sylhet | 28 | 13:00
38 | Chauddagram | 49 | 13:00 | 104 | Millgate | 63 | 12:00 | 170 | Sylhet-132 | 80 | 13:00
39 | Chhatak | 21 | 19:30 | 105 | Mirpur | 97 | 12:00 | 171 | TK | 20 | 18:00
40 | Chowmuhani | 160 | 13:00 | 106 | Mirsorai | 8 | 18:00 | 172 | Tangail | 160 | 08:00
41 | Chuadanga | 69 | 13:00 | 107 | Mirzapur | 34 | 09:00 | 173 | Thakurgaon | 77 | 13:00
42 | Coxsbazar | 95 | 19:30 | 108 | Mithapukur | 68 | 18:00 | 174 | Tongi | 96 | 12:00
43 | Cumilla(N) | 114 | 20:00 | 109 | Modern | 0 | 00:00 | 175 | Ullahpara | 22 | 18:00
44 | Cumilla(S) | 113 | 13:00 | 110 | Mogbazar | 85.8 | 13:00 | 176 | Ullon | 42 | 13:00
45 | Daudkandi | 96 | 00:00 | 111 | Mongla | 30 | 00:00 | 177 | Uttara | 55 | 14:00
46 | Dhaka | 20 | 19:30 | 112 | Motijheel | 24 | 13:00 | 178 | UttaraNew | 38 | 13:00
47 | Dhamrai | 76 | 09:00 | 113 | Muktagacha | 31 | 08:00 | 179 | Zigatola | 56 | 13:00
48 | Dhanmondi | 85 | 13:00 | 114 | Munshiganj | 79 | 14:00
49 | Dohazari | 71 | 13:00 | 115 | Mymensingh | 194 | 13:00
50 | Faridpur | 96 | 18:30 | 116 | Naogaon | 94 | 13:00
51 | Fatullah | 56 | 00:00 | 117 | Narail | 39 | 18:30
52 | Fenchuganj | 27 | 13:00 | 118 | Narinda | 42 | 13:00
53 | Feni | 70 | 13:00 | 119 | Narshingdi | 139 | 00:00
54 | GPH | 82 | 07:00 | 120 | Natore | 100 | 13:00
55 | Ghatail | 42 | 08:00 | 121 | Nawabganj | 36 | 13:00
56 | Ghorashal | 13 | 00:00 | 122 | Netrakona | 134 | 09:00
57 | Ghorashal-230 | 58 | 00:00 | 123 | New | 56.2 | 12:00
58 | Goalpara | 28 | 13:00 | 124 | Niamatpur | 85 | 09:00
59 | Gollamari | 52 | 13:00 | 125 | Noapara | 45 | 13:00
60 | Gopalganj | 76.4 | 18:30 | 126 | PHP | 8 | 06:00
61 | Gulshan | 60 | 13:00 | 127 | Pabna | 56 | 18:30
62 | Halishahar | 27 | 18:00 | 128 | Palashbari | 90 | 08:00
63 | HaripurSBU | 147 | 06:00 | 129 | Panchagarh | 42 | 18:00
64 | Hasnabad | 66 | 14:00 | 130 | Patuakhali | 53 | 20:00
65 | Hathazari | 56 | 13:00 | 131 | Payra | 14 | 01:00
66 | Ishurdi | 54 | 18:30 | 132 | Postogola | 34 | 12:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 31-01-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9341.89 | 0 |  | 9341.89
1:00 | 8795.1 | 0 |  | 8795.1
2:00 | 8366.65 | 0 |  | 8366.65
3:00 | 8043.65 | 0 |  | 8043.65
4:00 | 7759.61 | 0 |  | 7759.61
5:00 | 7655.92 | 0 |  | 7655.92
6:00 | 7790.82 | 0 |  | 7790.82
7:00 | 8104.23 | 0 |  | 8104.23
8:00 | 8720.78 | 0 |  | 8720.78
9:00 | 9145.04 | 0 |  | 9145.04
10:00 | 9180.67 | 23 |  | 9204.67
11:00 | 9374.34 | 46 |  | 9422.34
12:00 | 9893.19 | 0 |  | 9893.19
13:00 | 10564.1 | 0 |  | 10564.1
14:00 | 9010.47 | 0 |  | 9010.47
15:00 | 8546.36 | 0 |  | 8546.36
16:00 | 8187.84 | 0 |  | 8187.84
17:00 | 8313.62 | 0 |  | 8313.62
18:00 | 9303.48 | 29 |  | 9333.48
19:00 | 9682.75 | 0 |  | 9682.75
19:30 | 9805.6 | 0 |  | 9805.6
20:00 | 9770.11 | 0 |  | 9770.11
21:00 | 9666 | 0 |  | 9666
22:00 | 9435.98 | 0 |  | 9435.98
23:00 | 9039 | 0 |  | 9039
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 31-01-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4983 | 4358.89 | 9341.89 | DAILY GENERATION CURVE
00:30 | 4828.5 | 4239.995 | 9068.495
01:00 | 4674 | 4121.1 | 8795.1 | 31-01-2025
01:30 | 4623 | 3957.875 | 8580.875
02:00 | 4572 | 3794.65 | 8366.65
02:30 | 4498 | 3707.15 | 8205.15
03:00 | 4424 | 3619.65 | 8043.65
03:30 | 4332.25 | 3569.38 | 7901.63
04:00 | 4240.5 | 3519.11 | 7759.61
04:30 | 4205.5 | 3502.265 | 7707.765
05:00 | 4170.5 | 3485.42 | 7655.92
05:30 | 4205.1 | 3518.27 | 7723.37
06:00 | 4239.7 | 3551.12 | 7790.82
06:30 | 4321.365 | 3626.16 | 7947.525
07:00 | 4403.03 | 3701.2 | 8104.23
07:30 | 4641.305 | 3771.2 | 8412.505
08:00 | 4879.58 | 3841.2 | 8720.78
08:30 | 4956.355 | 3976.555 | 8932.91
09:00 | 5033.13 | 4111.91 | 9145.04
09:30 | 4886.25 | 4276.605 | 9162.855
10:00 | 4739.37 | 4441.3 | 9180.67
10:30 | 4747.765 | 4529.74 | 9277.505
11:00 | 4756.16 | 4618.18 | 9374.34
11:30 | 4877.39 | 4756.375 | 9633.765
12:00 | 4998.62 | 4894.57 | 9893.19
12:30 | 5301.51 | 4927.135 | 10228.645
13:00 | 5604.4 | 4959.7 | 10564.1
13:30 | 5202.59 | 4584.695 | 9787.285
14:00 | 4800.78 | 4209.69 | 9010.47
14:30 | 4621.96 | 4156.455 | 8778.415
15:00 | 4443.14 | 4103.22 | 8546.36
15:30 | 4383.23 | 3983.87 | 8367.1
16:00 | 4323.32 | 3864.52 | 8187.84
16:30 | 4443.48 | 3807.25 | 8250.73
17:00 | 4563.64 | 3749.98 | 8313.62
17:30 | 4883.82 | 3924.73 | 8808.55
18:00 | 5204 | 4099.48 | 9303.48
18:30 | 5352 | 4141.115 | 9493.115
19:00 | 5500 | 4182.75 | 9682.75
19:30 | 5611 | 4194.6 | 9805.6
20:00 | 5567 | 4203.11 | 9770.11
20:30 | 5395.75 | 4322.305 | 9718.055 |  | Executive Engineer
21:00 | 5224.5 | 4441.5 | 9666 |  | Network Operation Division
21:30 | 5123 | 4427.99 | 9550.99
22:00 | 5021.5 | 4414.48 | 9435.98
22:30 | 4916 | 4321.49 | 9237.49
23:00 | 4810.5 | 4228.5 | 9039

## En-Curve
QF-LDC-12
Date | 31-01-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 1988 | 1810.5 | 926 | 0 | 46 | 663.39 | 40 | 3610 | 0 | 58 | 200 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 1972.5 | 1779.5 | 925.5 | 0 | 49 | 589.495 | 40 | 3512 | 0 | 29 | 171.5 | 0 | 0 | 0 | 0 | 31-01-2025
01:00 | 1957 | 1748.5 | 925 | 0 | 52 | 515.6 | 40 | 3414 | 0 | 0 | 143 | 0 | 0 | 0 | 0
01:30 | 1925 | 1757.5 | 835.5 | 0 | 46 | 465.875 | 40 | 3378 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | Energy Generated | 216.4259 |  | MKWHr
02:00 | 1893 | 1766.5 | 746 | 0 | 40 | 416.15 | 40 | 3342 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | Energy not Served | 0.098 |  | MKWHr
02:30 | 1881 | 1781.5 | 740 | 0 | 38 | 414.65 | 40 | 3211 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | Total Energy Requirement | 216.5239 |  | MKWHr
03:00 | 1869 | 1796.5 | 734 | 0 | 36 | 413.15 | 40 | 3080 | 0 | 0 | 75 | 0 | 0 | 0 | 0
03:30 | 1872.5 | 1778.75 | 734 | 0 | 35 | 413.38 | 40 | 2973.5 | 0 | 0 | 54.5 | 0 | 0 | 0 | 0
04:00 | 1876 | 1761 | 734 | 0 | 34 | 413.61 | 40 | 2867 | 0 | 0 | 34 | 0 | 0 | 0 | 0
04:30 | 1871.5 | 1774.5 | 734 | 0 | 33 | 414.265 | 40 | 2813.5 | 0 | 0 | 27 | 0 | 0 | 0 | 0
05:00 | 1867 | 1788 | 734 | 0 | 32 | 414.92 | 40 | 2760 | 0 | 0 | 20 | 0 | 0 | 0 | 0
05:30 | 1886 | 1773.6 | 734.5 | 0 | 25 | 415.77 | 40 | 2820 | 0 | 0 | 28.5 | 0 | 0 | 0 | 0
06:00 | 1905 | 1759.2 | 735 | 0 | 18 | 416.62 | 40 | 2880 | 0 | 0 | 37 | 0 | 0 | 0 | 0
06:30 | 1903 | 1695.85 | 734.5 | 0 | 29 | 490.475 | 40 | 2967.5 | 1.7 | 17 | 68.5 | 0 | 0 | 0 | 0
07:00 | 1901 | 1632.5 | 734 | 0 | 40 | 564.33 | 40 | 3055 | 3.4 | 34 | 100 | 0 | 0 | 0 | 0
07:30 | 1958.5 | 1702.5 | 619 | 0 | 44 | 580.7 | 40 | 3275 | 27.805 | 49 | 116 | 0 | 0 | 0 | 0
08:00 | 2016 | 1772.5 | 504 | 0 | 48 | 597.07 | 40 | 3495 | 52.21 | 64 | 132 | 0 | 0 | 0 | 0
08:30 | 2017.5 | 1765 | 525 | 0 | 48 | 646.915 | 40 | 3583 | 92.495 | 70 | 145 | 0 | 0 | 0 | 0
09:00 | 2019 | 1757.5 | 546 | 0 | 48 | 696.76 | 40 | 3671 | 132.78 | 76 | 158 | 0 | 0 | 0 | 0
09:30 | 2000 | 1726.25 | 697.5 | 0 | 46 | 702.595 | 40 | 3537 | 180.51 | 76 | 157 | 0 | 0 | 0 | 11.5
10:00 | 1981 | 1695 | 849 | 0 | 44 | 708.43 | 40 | 3403 | 228.24 | 76 | 156 | 0 | 0 | 0 | 23
10:30 | 2035.5 | 1700.75 | 886.5 | 0 | 52 | 691.875 | 40 | 3343.5 | 297.38 | 76 | 154 | 0 | 0 | 0 | 34.5
11:00 | 2090 | 1706.5 | 924 | 0 | 60 | 675.32 | 40 | 3284 | 366.52 | 76 | 152 | 0 | 0 | 0 | 46
11:30 | 2119.5 | 1764.5 | 924 | 0 | 63 | 683.685 | 40 | 3260.5 | 380.08 | 76 | 322 | 0 | 0 | 0.5 | 23
12:00 | 2149 | 1822.5 | 924 | 0 | 66 | 692.05 | 40 | 3237 | 393.64 | 76 | 492 | 0 | 0 | 1 | 0
12:30 | 2158 | 1829.5 | 915 | 0 | 71 | 723.915 | 40 | 3118 | 403.73 | 60.5 | 907 | 0 | 0 | 2 | 0
13:00 | 2167 | 1836.5 | 906 | 0 | 76 | 755.78 | 40 | 2999 | 413.82 | 45 | 1322 | 0 | 0 | 3 | 0
13:30 | 2056.5 | 1720.5 | 906.5 | 0 | 72 | 724.415 | 40 | 2825.5 | 396.87 | 31 | 1011.5 | 0 | 0 | 2.5 | 0
14:00 | 1946 | 1604.5 | 907 | 0 | 68 | 693.05 | 40 | 2652 | 379.92 | 17 | 701 | 0 | 0 | 2 | 0
14:30 | 1947.5 | 1654.35 | 907 | 0 | 62 | 677.85 | 40 | 2654 | 328.215 | 17 | 489 | 0 | 0 | 1.5 | 0
15:00 | 1949 | 1704.2 | 907 | 0 | 56 | 662.65 | 40 | 2656 | 276.51 | 17 | 277 | 0 | 0 | 1 | 0
15:30 | 1976 | 1711.2 | 812 | 0 | 56 | 659.16 | 40 | 2626.5 | 211.74 | 17 | 256.5 | 0 | 0 | 1 | 0
16:00 | 2003 | 1718.2 | 717 | 0 | 56 | 655.67 | 40 | 2597 | 146.97 | 17 | 236 | 0 | 0 | 1 | 0
16:30 | 2048 | 1758.85 | 718 | 0 | 57 | 612.58 | 40 | 2574.5 | 92.3 | 75 | 272.5 | 0 | 0 | 2 | 0
17:00 | 2093 | 1799.5 | 719 | 0 | 58 | 569.49 | 40 | 2552 | 37.63 | 133 | 309 | 0 | 0 | 3 | 0
17:30 | 2026 | 1759 | 812 | 0 | 62 | 563.235 | 40 | 2713 | 18.815 | 260 | 552.5 | 0 | 0 | 2 | 14.5
18:00 | 1959 | 1718.5 | 905 | 0 | 66 | 556.98 | 40 | 2874 | 0 | 387 | 796 | 0 | 0 | 1 | 29
18:30 | 2111 | 1757.5 | 764 | 0 | 63 | 618.115 | 40 | 3025.5 | 0 | 335 | 778.5 | 0 | 0 | 0.5 | 14.5
19:00 | 2263 | 1796.5 | 623 | 0 | 60 | 679.25 | 40 | 3177 | 0 | 283 | 761 | 0 | 0 | 0 | 0
19:30 | 2381 | 1817.5 | 623 | 0 | 64 | 756.1 | 40 | 3296 | 0 | 109 | 719 | 0 | 0 | 0 | 0
20:00 | 2451 | 1816.5 | 623 | 0 | 66 | 753.61 | 40 | 3307 | 0 | 57 | 656 | 0 | 0 | 0 | 0
20:30 | 2467.5 | 1820.75 | 764.5 | 0 | 66 | 752.305 | 40 | 3304 | 0 | 28.5 | 474.5 | 0 | 0 | 0 | 0
21:00 | 2484 | 1825 | 906 | 0 | 66 | 751 | 40 | 3301 | 0 | 0 | 293 | 0 | 0 | 0 | 0
21:30 | 2422.5 | 1813.5 | 906 | 0 | 64 | 755.99 | 40 | 3301 | 0 | 0 | 248 | 0 | 0 | 0 | 0
22:00 | 2361 | 1802 | 906 | 0 | 62 | 760.98 | 40 | 3301 | 0 | 0 | 203 | 0 | 0 | 0 | 0
22:30 | 2336.5 | 1809 | 906 | 0 | 62 | 710.49 | 40 | 3212 | 0 | 0 | 161.5 | 0 | 0 | 0 | 0
23:00 | 2312 | 1816 | 906 | 0 | 62 | 660 | 40 | 3123 | 0 | 0 | 120 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 31-01-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 407 | 17:00 | 392 | 11:00 | Payra | 415 | 04:00 | 408 | 09:00
Ashuganj | 414 | 4:00 | 388 | 7:00 | Rahanpur | 418 | 04:00 | 404 | 12:00
Bhulta | 408 | 17:00 | 392 | 12:00 | Rampal | 413 | 03:00 | 388 | 12:00
Bibiana | 407 | 17:00 | 395 | 10:00
BIPTC | 408 | 03:00 | 387 | 10:00
Bogura | 421 | 04:00 | 399 | 12:00
Gopalganj | 411 | 18:00 | 395 | 12:00
Kaliakoir | 395 | 17:00 | 383 | 12:00
Madunaghat | 410 | 18:00 | 398 | 09:00
Meghnaghat | 408 | 18:00 | 393 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 236 | 04:00 | 227 | 11:00 | Keranigonj | 235 | 04:00 | 225 | 12:00
AKSML | 238 | 18:00 | 225 | 11:00 | Khulna(S) | 241 | 03:00 | 225 | 12:00
Aminbazar | 237 | 18:00 | 225 | 04:00 | Madunaghat | 236 | 18:00 | 227 | 10:00
Ashuganj | 241 | 18:00 | 230 | 11:00 | Madunaghat-400 | 237 | 18:00 | 227 | 09:00
Ashuganj-400 | 241 | 18:00 | 230 | 11:00 | Maniknagar | 237 | 18:00 | 228 | 11:00
Baghabari | 238 | 01:00 | 228 | 12:00 | Meghnaghat | 240 | 05:00 | 235 | 00:00
Barapukuria | 226 | 02:00 | 219 | 08:00 | Meghnaghat-400 | 239 | 18:00 | 230 | 12:00
Barapukuria-230 | 226 | 02:00 | 219 | 08:00 | Mirsorai | 238 | 18:00 | 223 | 11:00
Barishal | 245 | 03:00 | 237 | 11:00 | Rajshahi | 238 | 03:00 | 223 | 12:00
Bheramara | 238 | 02:00 | 223 | 12:00 | Rampal | 238 | 03:00 | 222 | 12:00
Bhulta | 238 | 18:00 | 228 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 236 | 04:00 | 225 | 11:00 | Rampura | 238 | 18:00 | 228 | 11:00
BIPTC | 240 | 03:00 | 224 | 12:00 | Shikalbaha | 235 | 17:00 | 225 | 11:00
Bogura | 241 | 04:00 | 230 | 12:00 | Shyampur | 237 | 18:00 | 227 | 11:00
Bogura-400 | 240 | 04:00 | 230 | 12:00 | Siddhirganj | 239 | 16:00 | 230 | 11:00
Borhanuddin | 247 | 04:00 | 242 | 11:00 | Sirajgonj | 245 | 04:00 | 237 | 12:00
BSRM | 236 | 18:00 | 223 | 10:00 | Sreepur | 239 | 18:00 | 229 | 09:00
Cumilla(N) | 238 | 18:00 | 226 | 11:00 | Tongi | 235 | 17:00 | 224 | 11:00
Faridpur | 243 | 03:00 | 234 | 12:00
Fenchuganj | 237 | 15:00 | 227 | 09:00
Ghorashal | 240 | 18:00 | 230 | 00:00
Ghorashal-230 | 235 | 04:00 | 226 | 11:00
Gopalganj | 244 | 04:00 | 234 | 12:00
GPH | 236 | 18:00 | 225 | 10:00
Haripur | 239 | 18:00 | 229 | 12:00
Hasnabad | 238 | 01:00 | 229 | 10:00
Hathazari | 238 | 17:00 | 226 | 11:00
Ishurdi | 241 | 04:00 | 226 | 12:00
Jhenaidah | 240 | 04:00 | 222 | 12:00
Kaliakoir | 234 | 17:00 | 225 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 130 | 11:00 | Magura | 140 | 03:00 | 127 | 12:00
Agargaon | 137 | 04:00 | 131 | 12:00 | Mahasthangarh | 136 | 04:00 | 128 | 12:00
Agrabad | 135 | 17:00 | 128 | 11:00 | Manikganj | 137 | 17:00 | 125 | 04:00
AKS | 133 | 18:00 | 127 | 00:00 | Maniknagar | 136 | 18:30 | 129 | 12:00
Aminbazar | 137 | 18:00 | 130 | 11:00 | Matarbari | 131 | 10:00 | 119 | 08:00
Amnura | 141 | 18:00 | 128 | 12:00 | Matuail | 137 | 18:30 | 131.5 | 11:00
Ashuganj | 141 | 03:00 | 137 | 12:00 | Millgate | 138 | 18:00 | 130 | 12:00
Bagerhat | 138 | 02:00 | 123 | 14:00 | Mirpur | 136 | 18:00 | 128 | 11:00
Bajitpur | 135 | 16:00 | 130 | 08:00 | Mirzapur | 136 | 16:00 | 130 | 05:00
Bakulia | 135 | 18:00 | 128 | 11:00 | Mithapukur | 133 | 05:00 | 18 | 21:00
Banani | 136 | 04:00 | 130 | 11:00 | MI_Cement | 139 | 18:00 | 132.3 | 11:00
Bangabhaban | 136 | 18:00 | 128 | 12:00 | Modern | 0 | 00:00 | N/A | N/A
Barapukuria | 135 | 02:00 | 129 | 08:00 | Mogbazar | 137 | 06:00 | 130 | 12:00
Barguna | 140 | 13:00 | 133 | 09:00 | Mongla | 137 | 03:00 | 127 | 12:00
Barishal | 136 | 04:00 | 129 | 12:00 | Motijheel | 136 | 18:00 | 128 | 12:00
Barishal-230 | 136 | 03:00 | 131 | 08:00 | Muktagacha | 127 | 19:30 | 117 | 05:00
Baroaulia | 135 | 17:00 | 131 | 12:00 | Munshiganj | 138 | 18:00 | 131 | 11:00
Baroirhat | 136 | 18:00 | 127 | 00:00 | Mymensingh | 127 | 23:00 | 115 | 09:00
Bashundhara | 138 | 18:00 | 130 | 11:00 | Naogaon | 134 | 04:00 | 126 | 09:00
BashundharaCement | 138 | 18:00 | 131 | 11:00 | Narail | 141 | 04:00 | 127 | 12:00
Beanibazar | 137 | 16:00 | 132 | 11:00 | Narinda | 136 | 18:00 | 129 | 12:00
Benapole | 138 | 03:00 | 122 | 12:00 | Narshingdi | 136 | 18:00 | 124 | 00:00
Bhaluka | 128 | 05:00 | 118 | 09:00 | Natore | 137 | 02:00 | 129 | 12:00
Bhandaria | 135 | 04:00 | 127 | 12:00 | Nawabganj | 139 | 18:00 | 132 | 12:00
Bhangura | 138 | 02:00 | 131 | 12:00 | Netrakona | 125 | 22:00 | 112 | 08:00
Bheramara | 138 | 02:00 | 129 | 12:00 | New | 138 | 18:30 | 131 | 12:00
Bheramara(GK) | 138 | 03:00 | 129 | 12:00 | Niamatpur | 141 | 06:00 | 135 | 09:00
Bhulta | 133 | 17:00 | 127 | 00:00 | Noapara | 137 | 01:00 | 126 | 12:00
Bog-Sherpur | 137 | 04:00 | 129 | 12:00 | Pabna | 137 | 04:00 | 128 | 12:00
Bogura | 137 | 05:00 | 130 | 12:00 | Palashbari | 131 | 02:00 | 123 | 12:00
Bogura-230 | 138 | 04:00 | 130 | 12:00 | Panchagarh | 138 | 13:00 | 121 | 09:00
Brahmanbaria | 135 | 15:00 | 130 | 09:00 | Patuakhali | 139 | 13:00 | 133 | 08:00
Cantonment | 138 | 04:00 | 130 | 17:00 | Payra | 137 | 03:00 | 133 | 10:00
Chandpur | 138 | 13:00 | 124 | 11:00 | PHP | 134 | 14:00 | 125 | 11:00
Chandraghona | 136 | 17:00 | 131 | 09:00 | Postogola | 140 | 17:00 | 134 | 11:00
Chapai | 139 | 02:00 | 132 | 12:00 | Purbachal | 136 | 02:00 | 130 | 11:00
Charsaidpur | 139 | 18:00 | 132 | 10:00 | Purbasadipur | 130 | 03:00 | 121 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 136 | 18:30 | 127 | 11:00 | Rahanpur | 141 | 01:00 | 137 | 10:00
Chhatak | 137 | 02:00 | 130 | 11:00 | Rahanpur-400 | 142 | 04:00 | 136 | 12:00
Chowmuhani | 133 | 18:00 | 123 | 11:00 | Rahim | 134 | 03:00 | 131 | 10:00
Chuadanga | 138 | 04:00 | 127 | 12:00 | Rajbari | 134 | 02:00 | 128 | 12:00
Coxsbazar | 125 | 03:00 | 119 | 08:00 | Rajendrapur | 138 | 18:00 | 131 | 12:00
Cumilla(N) | 139 | 18:00 | 131 | 11:00 | Rajshahi | 139 | 03:00 | 130 | 12:00
Cumilla(S) | 136 | 15:00 | 127 | 12:00 | Rajshahi-230 | 138 | 03:00 | 128 | 12:00
Daudkandi | 137 | 18:00 | 129 | 11:00 | Ramganj | 135 | 20:00 | 122 | 10:00
Dhaka | 136 | 04:00 | 130 | 12:00 | Rampur | 136 | 18:00 | 130 | 00:00
Dhamrai | 135 | 03:00 | 130 | 11:00 | Rampura | 136 | 04:00 | 130 | 11:00
Dhanmondi | 137 | 02:00 | 130.5 | 12:00 | Rangamati | 136 | 18:30 | 130 | 10:00
Dohazari | 133 | 18:30 | 126 | 11:00 | Rangpur | 131 | 04:00 | 124 | 09:00
Faridpur | 135 | 03:00 | 130 | 12:00 | Ruppur | 140 | 05:00 | 131 | 12:00
Fatullah | 139 | 18:00 | 133 | 11:00 | Saidpur | 132 | 02:00 | 122 | 09:00
Fenchuganj | 142 | 17:00 | 137 | 10:00 | Satkhira | 139 | 03:00 | 127 | 08:00
Feni | 135 | 18:30 | 125 | 11:00 | Satmasjid | 137 | 18:00 | 130 | 12:00
Ghatail | 128 | 16:00 | 120 | 06:00 | Savar | 137 | 18:30 | 128 | 11:00
Ghorashal | 141 | 18:00 | 136 | 11:00 | SevenRings | 143 | 18:00 | 135 | 12:00
Goalpara | 141 | 03:00 | 130 | 12:00 | ShahCement | 139 | 18:00 | 132 | 10:00
Gollamari | 139 | 03:00 | 130 | 12:00 | Shahjadpur | 140 | 17:00 | 134 | 07:00
Gopalganj | 137 | 03:00 | 129 | 12:00 | Shahjibazar | 138 | 05:00 | 134 | 09:00
Gopalganj-400 | 137 | 03:00 | 131 | 12:00 | Shahmirpur | 136 | 18:00 | 130 | 00:00
Gulshan | 135 | 06:00 | 129 | 12:00 | Shariatpur | 136 | 02:00 | 129 | 12:00
Halishahar | 137 | 18:00 | 130 | 07:00 | Sherpur | 122 | 16:00 | 11 | 10:00
Haripur | 137 | 18:00 | 131 | 11:00 | Shikalbaha | 125 | 18:00 | 118 | 00:00
HaripurSBU | 137 | 18:00 | 131 | 11:00 | Shikalbaha-230 | 136 | 18:00 | 130 | 10:00
Hasnabad | 140 | 17:00 | 134 | 10:00 | Shitalakhya | 139 | 18:00 | 132 | 11:00
Hathazari | 139 | 17:00 | 132 | 01:00 | Sholosohor | 136 | 18:00 | 130 | 11:00
Ishurdi | 141 | 04:00 | 132 | 12:00 | Shyampur | 137 | 05:00 | 132 | 12:00
Jaldhaka | 129 | 13:00 | 122 | 08:00 | Shyampur-230 | 139 | 18:30 | 132 | 11:00
Jamalpur | 125 | 16:00 | 112 | 03:00 | Siddhirganj | 138 | 18:00 | 132 | 11:00
Jashore | 137 | 06:00 | 123 | 13:00 | Sirajganj | 138 | 03:00 | 130 | 08:00
Jhenaidah | 139 | 04:00 | 129 | 12:00 | Sonargaon | 137 | 18:00 | 130 | 11:00
Jhenaidah-230 | 141 | 04:00 | 129 | 12:00 | Sreemongol | 138 | 04:00 | 135 | 09:00
Joydebpur | 140 | 18:00 | 132 | 12:00 | Sreepur | 130 | 18:00 | 122 | 09:00
Joypurhat | 135 | 04:00 | 124 | 12:00 | Srinagar | 138 | 03:00 | 132 | 12:00
Juldah | 135 | 18:00 | 129 | 00:00 | SSM | 139 | 17:00 | 134 | 00:00
Kabirpur | 141 | 13:00 | 130 | 10:00 | Sunamganj | 137 | 04:00 | 129 | 11:00
Kachua | 138 | 08:00 | 126 | 09:00 | Sylhet | 138 | 03:00 | 132 | 12:00
Kaliakoir | 141 | 17:00 | 134 | 13:00 | Sylhet-132 | 139 | 05:00 | 132 | 11:00
Kallyanpur | 134 | 04:00 | 129 | 12:00 | Tangail | 131 | 16:00 | 123 | 12:00
Kalurghat | 135 | 04:00 | 131 | 09:00 | Thakurgaon | 134 | 13:00 | 119 | 09:00
Kamrangirchar | 139 | 16:00 | 130 | 09:00 | TK | 136 | 18:00 | 130 | 00:00
Kaptai | 137 | 18:00 | 133 | 11:00 | Tongi | 140 | 17:00 | 133 | 11:00
Kazla | 136 | 18:30 | 129 | 12:00 | Ullahpara | 138 | 01:00 | 132 | 12:00
Keranigonj | 138 | 18:00 | 131 | 11:00 | Ullon | 137 | 03:00 | 129 | 12:00
Khagrachori | 135 | 18:00 | 129 | 11:00 | Uttara | 136 | 18:00 | 128 | 12:00
Khulna | 137 | 01:00 | 128 | 12:00 | UttaraNew | 138 | 18:00 | 130 | 12:00
Khulna(S) | 140 | 03:00 | 130 | 12:00 | Zigatola | 139 | 18:00 | 132 | 12:00
Khulshi | 135 | 18:30 | 128 | 10:00
Kishoreganj | 132 | 16:00 | 124 | 09:00
Kodda | 140 | 13:00 | 131 | 21:00
KSRM | 137 | 18:00 | 131 | 04:00
Kulaura | 140 | 04:00 | 136 | 11:00
Kurigram | 130 | 04:00 | 122 | 07:00
Kushtia | 138 | 04:00 | 129 | 12:00
Lalbag | 139 | 18:00 | 129 | 12:00
Lalmonirhat | 130 | 03:00 | 121 | 19:30
Madanganj | 138 | 18:00 | 131 | 11:00
Madaripur | 136 | 04:00 | 130 | 12:00
Madartek | 136 | 04:00 | 130 | 11:00
Madunaghat | 136 | 18:00 | 130 | 10:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division